## 1-Available
Available SO2 Emission Control Technologies
Wet Flue Gas Desulfurization (WFGD)
Circulating Dry Scrubber (CDS)
Spray Dry Absorber (SDA)
Dry Sorbent Injection (DSI)
Base Case: SO2 Emission Limit, Low Sulfur Coal, and Good Combustion Practices

## 2-Feasible
Technically Feasible SO2 Emission Control Technologies
Wet Flue Gas Desulfurization (WFGD)
Circulating Dry Scrubber (CDS)
Spray Dry Absorber (SDA)
Dry Sorbent Injection (DSI)
Base Case: SO2 Emission Limit, Low Sulfur Coal, and Good Combustion Practices

## 3-Ranking
Ranking of Technically Feasible SO2 Emission Control Technologies
Control Technology | Control Efficiency Compared to Base Case (pct.) | SO2 Emission Rate (lb/MMBtu) | SO2 Emission Rate (lb/hr) | Potential SO2 Emissions (tpy) | Potential SO2 Emissions Reduction (tpy)
Dry Sorbent Injection (DSI) 1 | 95 | 0.01505 | 7.3008 | 31.9773 | 607.5688
Wet Flue Gas Desulfurization (WFGD) 2 | 93.3555 | 0.02 | 9.702 | 42.4948 | 597.0514
Circulating Dry Scrubber (CDS) | 86.711 | 0.04 | 19.404 | 84.9895 | 554.5566
Spray Dry Absorber (SDA) | 76.7442 | 0.07 | 33.957 | 148.7317 | 490.8145
Base Case: SO2 Emission Limit, Low Sulfur Coal, and Good Combustion Practices | 0 | 0.301 | 146.0151 | 639.5461 | 0
Note:
1 The SO2 control efficiency, in terms of percentage, for DSI is the vendor-provided emission reduction capability.
2 The SO2 emission rates, in terms of lb/MMBtu, for WFGD, CDS, and SDA are the average values for the top 20 percent performing coal-fired power plants per Table 1.3 of Section 5, Chapter 1 of the EPA Air Pollution Control Cost Manual (2021).

## 4-CostEffective
SO2 Cost-Effectiveness Summary
Control Technology | Total Capital Investment ($)1 | Total Annual Cost ($/year)2 | Emissions Reduction (tpy)3 | Cost-Effectiveness ($/ton SO2 Emissions Avoided)
Dry Sorbent Injection (DSI) | 43809890.7119 | 8122262.4607 | 607.5688 | 13368.4647
Base Case: SO2 Emission Limit, Low Sulfur Coal, and Good Combustion Practices | ~ | ~ | 0 | ~
Notes:
1Total Capital Investment is calculated in Table B of Appendix B.
2Total Annual Cost is calculated in Table B of Appendix B.
3Emissions reductions are calculated in Table 3 of this report.

## TableA-SO2_PTE
Table A. Potential to Emit Calculations for EUs 4 through 7 Supplemental BACT Analysis - SO2 Emissions
Aurora Energy, LLC - Chena Power Plant
Emissions Unit |  | Fuel Type | SO2 Emission Factor |  |  | Maximum Rating/Capacity |  | Allowable Annual Operation |  | Short Term SO2 Emissions |  | Potential SO2 Emissions
ID | Description |  | Reference | Factor
4 | Chena 1 Coal-Fired Boiler | Coal | Condition 15, Permit No. AQ0315TVP04, Revision 2 | 0.301 | lb/MMBtu | 76.8 | MMBtu/hr | 8760 | hr/yr | 23.1168 | lb/hr | 101.2516 | tpy
5 | Chena 2 Coal-Fired Boiler |  |  |  |  | 76.8 | MMBtu/hr | 8760 | hr/yr | 23.1168 | lb/hr | 101.2516 | tpy
6 | Chena 3 Coal-Fired Boiler |  |  |  |  | 76.8 | MMBtu/hr | 8760 | hr/yr | 23.1168 | lb/hr | 101.2516 | tpy
7 | Chena 5 Coal-Fired Boiler |  |  |  |  | 254.7 | MMBtu/hr | 8760 | hr/yr | 76.6647 | lb/hr | 335.7914 | tpy
Total SO2 Potential Emissions | [11 empty] | 639.5461 | tpy
Notes:
1 Conversion factors:
| Mass Conversion | 2000 | lb/ton
2 The combined SO2 emissions from the common stack for EU IDs 4 through 7 are limited to 0.301 lb/MMBtu per Condition 15 of Permit No. AQ0315TVP04, Revision 2.

## TableB-BACT_Cost
Table B. Dry Sorbent Injection (DSI) - Economic Analysis
Aurora Energy Chena Power Plant SO2 BACT Analysis
CAPITAL COSTS
DIRECT COSTS |  |  | Quantity | Unit | Unit Cost | Total | Notes
1. Purchased Equipment and Material Costs (PEMC)
|  | a. Basic equipment - DSI System | 1 | ea | 5990000 | 5990000 | BACT Process Systems, Inc. 7/28/2023 proposal
|  | b. Freight - DSI System | 1 | ea | 250000 | 250000 | BACT Process Systems, Inc. 7/28/2023 proposal
|  | c. Equipment - Baghouse system | 1 | ea | 2900000 | 2900000 | Stanley Consultants Jan 2024 cost estimate
|  | d. Freight - Baghouse system | 1 | ea | 348000 | 348000 | Stanley Consultants Jan 2024 cost estimate
|  | e. Continuous Emission Monitoring System | 1 | ea | 125257 | 125257 | Emerson 10/22/2019 cost estimate (equipment and shipping)
| Purchased Equipment and Material Cost (PEMC) |  |  |  | PEMC= | 9613257
2. Direct Installation Costs (DIC)
|  | a. Field installation - DSI | 1 | ea | 488847.07 | N/A
|  | b. Field installation - Baghouse | 1 | LOT | 322667.41 | N/A
|  | c. Structural | 1 | LOT | 31601762.7 | N/A
|  | d. Mechanical | 1 | LOT | 610883.77 | N/A
|  | e. Electrical | 1 | LOT | 1355710 | N/A
|  | f. Instrumentation and Controls | 1 | ea | 103407.81 | N/A
|  | g. Heavy Equipment | 1 | LOT | 834300 | N/A
|  | h. Demolition | 1 | LOT | 1000000 | N/A
| Direct Installation Costs (DIC) |  |  |  | DIC = | 14419885.5 | Conservatively estimated at 150% of PEMC
| Total Direct Costs (TDC) |  |  |  | TDC=PEMC+DIC= | 24033142.5
INDIRECT COSTS
3. Engineering, Construction Support
|  | a. Engineering Services | 1 | ea | 7483700 | 1922651.4 | Conservatively estimated at 20% of PEMC
|  | b. Mobilization/Demobilization | 5 | pct. TDC |  | 1201657.125 | Value changed as it is based on a percentage of the DIC, which has been lowered.
|  | c. Prime Contractor Indirect Labor | 10 | pct. |  | 4544213.7 | Stanley Consultants Jan 2024 cost estimate plus 10 pct. of CEMS PEMC.
|  | d. Contractor Overhead and Labor Burdens | 15 | pct. TDC |  | 3604971.375 | Value changed as it is based on a percentage of the DIC, which has been lowered.
|  | e. Equipment and Small Tools | 5 | pct. |  | 1159942.125 | Value changed as it is based on a percentage of the DIC, which has been lowered.
| 4. Contingency |  | 10 | pct. |  | 3454392.6825 | Default value of 10 percent of direct and indirect costs [CCM Section 5, Chapter 1, page 1-79]
| 5. Profit |  | 10 | pct. |  | 3454392.6825 | Value changed as it is based on a percentage of the DIC, which has been lowered.
| 6. Bond |  | 1 | pct. |  | 414527.1219 | Value changed as it is based on a percentage of the DIC, which has been lowered.
| 7. Performance testing |  | 1 | ea | 20000 | 20000 | Initial emissions performance test and CEMS RATA. Estimate based on recent source test costs at Aurora Energy.
| Total Indirect Costs (TIC) |  |  |  | TIC= | 19776748.2119
TOTAL CAPITAL INVESTMENT (TCI) |  |  |  |  | TCI = TDC+TIC= | 43809890.7119
ANNUAL COSTS
DIRECT COSTS |  |  | Quantity | Unit | Unit Cost | Total | Notes
| 1. Operating Labor |  | 365 | hours | 66.4 | 24236 | Assumes 0.5 hours per shift, 12 hour shifts [CCM Section 5, Chapter 1]. Burdened operator labor rate is $66.40/hr per Table C, Aurora Energy, 2023.
| 2. Supervisory Labor |  | 15 | pct. |  | 3635.4 | Assumes 15% of operator labor [CCM Section 5, Chapter 1]
| 3. Maintenance Labor |  | 365 | hours | 66.4 | 24236 | Assumes 0.5 hours per shift, 12 hour shifts [CCM Section 5, Chapter 1]. Burdened operator labor rate is $66.40/hr per Table C, Aurora Energy, 2023.
| 4. Maintenance Materials |  | 100 | pct. |  | 24236 | Assumes 100% of maintenance labor [CCM Section 5, Chapter 1]
| 5. Reagent |  | 3175.5 | ton | 563 | 1787806.5 | Sodium bicarbonate. Feed rate of 0.3625 tons per hour; unit cost includes rail delivery per BACT Process Systems, Inc. 7/28/2023 proposal.
| 6. Utilities | a. Electricity | 2735959.656 | kWh | 0.093 | 254444.248 | Steady state operating station service requirement for DSI equipment per demand in Table F at 8,760 hr/yr. Aurora Energy calculation of station service cost at $0.093/kWh for 2023.
|  | b. Waste Disposal (ash) | 2930.2525 | ton | 44 | 128931.1091 | Incremental increase in ash disposal cost due to DSI. Ash tonnage calculated in Table D. Unit cost is market rate in ash hauling contract.
| Total Direct Annual Costs (TDAC) |  |  |  | TDAC= | 2247525.2571
INDIRECT COSTS
| 7. Overhead |  | 60 | pct. |  | 45806.04 | 60 percent of total labor and material costs [CCM Section 1, Chapter 2, page 35]
| 8 Administrative Charges |  | 2 | pct. TCI |  | 876197.8142 | 2 percent of TCI [CCM Section 1, Chapter 2, page 35]
| 9. Property Tax |  | 1 | pct. TCI |  | 438098.9071 | 1 percent of TCI [CCM Section 1, Chapter 2, page 35]
| 10. Insurance |  | 1 | pct. TCI |  | 438098.9071 | 1 percent of TCI [CCM Section 1, Chapter 2, page 35]
| 11. Capital Recovery |  |  |  |  | 4076535.5351 | CRF x TCI
|  | Capital Recovery Factor (CRF) | 0.093051 |  |  |  | CRF = i(1+i)n / ((1+i)n-1) [CCM Section 1, Chapter 2, page 22]
|  | i = interest rate | 8.5 | pct. |  |  | Bank prime interest rate 7/27/2023 through 1/22/2024, https://www.federalreserve.gov/releases/h15/
|  | n = life of control equipment | 30 | years
| Total Indirect Annual Costs (TIAC) |  |  |  | TIAC= | 5874737.2035
TOTAL ANNUALIZED COST (TAC) |  |  |  |  | TAC = TDAC+TIAC= | 8122262.4607

## TableC-Labor_Rate
Table C. Full-time Burden Operator Labor Rate
Aurora Energy, LLC
|  |  | Per Hour* | CBA Section*
|  | Operator Wage Rate Y1 | 43.07 | 17.1
|  | Shift Diff. | 1.2921 | 17.2
|  | 401K (0.50/hr) | 0.5 | 15.3
|  | H&W (Annual cost/hrs) | 9.8242 | 15.1
|  | Pension | 10 | 15.2
|  | Reg Rate | 63.3942
|  | OT Rate | 84.9292
|  | Grave Rate | 64.6863
|  | Grave OT Rate | 86.8673
|  | Reg Hours | 838.5 | 5.2
|  | OT Hours | 113.75 | 5.2
|  | Grave Reg Hours | 1118 | 5.2
|  | Grave OT Hours | 113.75 | 5.2
|  | Reg Rate x Reg Hours | 53156.0164
|  | OT Rate x OT Hours | 9660.6938
|  | Grave Rate x Grave Reg Hours | 72319.2564
|  | Grave OT Rate x Grave OT Hours | 9881.1583
|  | Total Labor Cost for FT Burden Operator working day/graves | 145017.1249
|  | x 2 for Adding two Operators | 2
|  | Total Labor Cost for two FT Burden Operators | 290034.2497
|  | Annual Working Hours | 2184
|  | Average Hourly Rate | 66.3998
*Aurora Energy, LLC CBA 2023 - 2025

## TableD-Ash_Disposal
Table D. Projected Annual Ash Disposal Requirement for DSI
Aurora Energy Chena Power Plant SO2 BACT Analysis
| Value | Unit
Ash Generation Based on Potential to Emit, No SO2 Control
Max Annual Heat Input | 4222320000000 | Btu/lb
Coal Heat Content | 7536.4688 | Btu/lb1
Coal Use per Year | 560251775.7405 | lb/yr
Coal Use per Year | 280125.8879 | tpy
Coal Ash Content | 0.065332 | Fraction2
Total | 18301.2662 | tpy
| Value | Unit
Ash Generation due to Dry Sorbent Injection
Maximum SO2 Emission Rate | 0.301 | lb/MMBtu
SO2 Potential Emissions | 1270918.32 | lb/yr
SO2 Potential Emissions | 635.4592 | tpy
SO2 Emission Reduction | 603.6862 | tpy
NaHCO3 Use | 3175.5 | tpy
2(NaHCO3)/NaSO4 | 1.1831 | wt. ratio
Na2SO4/SO2 | 2.2188 | wt. ratio
Na2SO4 | 1339.4288 | tpy (in ash)
NaHCO3 | 1590.8237 | tpy (unreacted)
Total | 2930.2525 | tpy
Total Ash Disposal Requirement | 21231.5187 | tpy
Notes:
1 Coal heat content based on 2022 deliveries, shown in Table E.
2 Coal ash content based on 2022 deliveries, shown in Table E.

## TableE-2022_Coal_Samples
Table E. 2022 Rail Sample Analyses of Delivered Coal
Aurora Energy Chena Power Plant SO2 BACT Analysis
| Sample Date | Cars | AR BTU | AR Moisture | AR Ash | AR Volatiles | AR Carbon | AR Sulfur | Location | Bench | Seam | Tons
AURORA ENERGY LLC | 2022-01-01 | 13 | 7628 | 32.82 | 4.76 | 35.3 | 27.12 | 0.12 | JD |  | 4 | 1132.1
AURORA ENERGY LLC | 2022-01-03 | 10 | 7598 | 32.33 | 5.6 | 34.64 | 27.43 | 0.13 | JD |  | 4 | 903.3
AURORA ENERGY LLC | 2022-01-04 | 9 | 7545 | 32.52 | 5.62 | 34.79 | 27.08 | 0.14 | JD |  | 4 | 777.1
AURORA ENERGY LLC | 2022-01-05 | 6 | 7814 | 30.17 | 5.42 | 35.48 | 28.93 | 0.12 | JD |  | 4 | 497.7
AURORA ENERGY LLC | 2022-01-06 | 10 | 7542 | 32.71 | 5.29 | 34.59 | 27.41 | 0.13 | JD |  | 4 | 842.6
AURORA ENERGY LLC | 2022-01-07 | 7 | 7672 | 31.53 | 5.43 | 35.6 | 27.44 | 0.15 | JD |  | 4 | 604.35
AURORA ENERGY LLC | 2022-01-10 | 3 | 7590 | 32.3 | 5.34 | 34.74 | 27.63 | 0.13 | JD |  | 4 | 253.7
AURORA ENERGY LLC | 2022-01-11 | 6 | 7590 | 32.18 | 5.37 | 34.72 | 27.73 | 0.14 | JD |  | 4 | 560.2
AURORA ENERGY LLC | 2022-01-13 | 3 | 7611 | 32.06 | 5.36 | 35.02 | 27.57 | 0.12 | JD |  | 4 | 270.05
AURORA ENERGY LLC | 2022-01-14 | 4 | 7612 | 32.59 | 4.66 | 34.5 | 28.26 | 0.1 | JD |  | 4 | 346.1
AURORA ENERGY LLC | 2022-01-17 | 11 | 7610 | 32.86 | 4.47 | 34.51 | 28.16 | 0.09 | JD |  | 4 | 966.05
AURORA ENERGY LLC | 2022-01-18 | 8 | 7617 | 32.96 | 4.14 | 34.85 | 28.06 | 0.08 | JD |  | 4 | 710.45
AURORA ENERGY LLC | 2022-01-19 | 8 | 7817 | 31.76 | 3.63 | 35.63 | 28.99 | 0.08 | JD |  | 4 | 670.4
AURORA ENERGY LLC | 2022-01-20 | 9 | 7815 | 31.82 | 4.1 | 35.91 | 28.18 | 0.09 | JD |  | 4 | 788.45
AURORA ENERGY LLC | 2022-01-21 | 5 | 7617 | 32.73 | 4.43 | 34.54 | 28.31 | 0.09 | JD |  | 4 | 455.4
AURORA ENERGY LLC | 2022-01-24 | 9 | 7697 | 31.34 | 5.51 | 35.23 | 27.93 | 0.13 | JD |  | 4 | 776.8
AURORA ENERGY LLC | 2022-01-25 | 10 | 7749 | 31.18 | 5.08 | 35.54 | 28.21 | 0.12 | JD |  | 4 | 879.75
AURORA ENERGY LLC | 2022-01-26 | 10 | 7693 | 31.76 | 5.02 | 34.62 | 28.61 | 0.13 | JD |  | 4 | 882.65
AURORA ENERGY LLC | 2022-01-27 | 9 | 7594 | 32.1 | 5.77 | 34.69 | 27.45 | 0.14 | JD |  | 4 | 812.25
AURORA ENERGY LLC | 2022-01-28 | 5 | 7555 | 32.33 | 5.95 | 34.64 | 27.09 | 0.14 | JD |  | 4 | 464.15
AURORA ENERGY LLC | 2022-01-31 | 12 | 7641 | 32.68 | 4.46 | 35.13 | 27.73 | 0.11 | JD |  | 4 | 1047
AURORA ENERGY LLC | 2022-02-01 | 8 | 7648 | 32.99 | 4.07 | 34.58 | 28.36 | 0.09 | JD |  | 4 | 674.7
AURORA ENERGY LLC | 2022-02-02 | 7 | 7694 | 33.31 | 3.41 | 35.01 | 28.28 | 0.08 | JD |  | 4 | 605.35
AURORA ENERGY LLC | 2022-02-03 | 10 | 7644 | 32.59 | 4.14 | 35.35 | 27.92 | 0.09 | JD |  | 4 | 882.15
AURORA ENERGY LLC | 2022-02-07 | 12 | 7764 | 31.38 | 4.37 | 34.92 | 29.33 | 0.1 | BDL/JD | Q3 | 3/4 | 1040.5
AURORA ENERGY LLC | 2022-02-08 | 9 | 7785 | 30.61 | 4.82 | 35.49 | 29.09 | 0.09 | BDL/JD | Q3 | 3/4 | 783.6
AURORA ENERGY LLC | 2022-02-09 | 9 | 7647 | 32.23 | 4.4 | 34.64 | 28.73 | 0.09 | BDL/JD | Q3 | 3/4 | 776.5
AURORA ENERGY LLC | 2022-02-10 | 8 | 7645 | 31.13 | 5.42 | 34.39 | 29.06 | 0.11 | BDL/JD | Q3 | 3/4 | 740.6
AURORA ENERGY LLC | 2022-02-11 | 9 | 7624 | 31.36 | 5.56 | 34.73 | 28.36 | 0.1 | JD/BDL | Q3 | 3/4 | 837.55
AURORA ENERGY LLC | 2022-02-14 | 8 | 7671 | 30.99 | 5.47 | 34.91 | 28.64 | 0.09 | BDL/JD | Q3 | 3/4 | 709.1
AURORA ENERGY LLC | 2022-02-15 | 9 | 7723 | 30.12 | 5.93 | 34.93 | 29.02 | 0.09 | BDL/JD | Q3 | 3/4 | 824.6
AURORA ENERGY LLC | 2022-02-16 | 8 | 7702 | 30.64 | 5.53 | 34.59 | 29.24 | 0.1 | BDL/JD | Q3 | 3/4 | 699.25
AURORA ENERGY LLC | 2022-02-17 | 8 | 7751 | 30.73 | 5.22 | 35.39 | 28.66 | 0.1 | BDL/JD | Q3 | 3/4 | 707.6
AURORA ENERGY LLC | 2022-02-18 | 6 | 7588 | 33.19 | 4.14 | 34.74 | 27.94 | 0.09 | JD |  | 4 | 517.75
AURORA ENERGY LLC | 2022-02-22 | 10 | 7613 | 31.52 | 5.42 | 34.58 | 28.48 | 0.11 | JD |  | 4 | 882.3
AURORA ENERGY LLC | 2022-02-23 | 10 | 7519 | 33.57 | 4.3 | 34.33 | 27.8 | 0.09 | JD |  | 4 | 851.3
AURORA ENERGY LLC | 2022-02-24 | 9 | 7559 | 31.66 | 5.84 | 34.1 | 28.4 | 0.11 | BDL/JD | Q3 | 3/4 | 798.65
AURORA ENERGY LLC | 2022-02-25 | 9 | 7551 | 32.32 | 5.12 | 34.25 | 28.32 | 0.1 | BDL/JD | Q3 | 3/4 | 787.1
AURORA ENERGY LLC | 2022-02-28 | 9 | 7697 | 31.27 | 5.38 | 34.68 | 28.67 | 0.09 | BDL/JD | Q3 | 3/4 | 769.55
AURORA ENERGY LLC | 2022-03-01 | 12 | 7472 | 31.97 | 6.54 | 33.63 | 27.87 | 0.1 | BDL/JD | Q3 | 3/4 | 1065.2
AURORA ENERGY LLC | 2022-03-02 | 7 | 7505 | 31.68 | 6.95 | 33.68 | 27.7 | 0.11 | BDL/JD | Q3 | 3/4 | 649.25
AURORA ENERGY LLC | 2022-03-03 | 7 | 7479 | 31.34 | 7.31 | 33.64 | 27.72 | 0.12 | BDL/JD | Q3 | 3/4 | 653.3
AURORA ENERGY LLC | 2022-03-04 | 7 | 7525 | 31.1 | 6.7 | 34.24 | 27.97 | 0.12 | BDL/JD | Q3 | 3/4 | 625.6
AURORA ENERGY LLC | 2022-03-07 | 11 | 7569 | 31.12 | 6.77 | 34.07 | 28.03 | 0.12 | BDL/JD | Q3 | 3/4 | 993.2
AURORA ENERGY LLC | 2022-03-08 | 10 | 7586 | 30.46 | 6.88 | 34.67 | 28 | 0.11 | BDL/JD | Q3 | 3/4 | 920.1
AURORA ENERGY LLC | 2022-03-09 | 16 | 7406 | 31.55 | 7.47 | 33.68 | 27.3 | 0.11 | JD/BDL | Q3 | 3/3 | 1493.55
AURORA ENERGY LLC | 2022-03-11 | 8 | 7505 | 31.68 | 6.59 | 33.87 | 27.87 | 0.1 | JD/BDL | Q3 | 3/3 | 748.8
AURORA ENERGY LLC | 2022-03-21 | 8 | 7446 | 32.11 | 6.73 | 34.05 | 27.11 | 0.11 | JD/BDL | Q3 | 3/3 | 689.6
AURORA ENERGY LLC | 2022-03-22 | 9 | 7397 | 31.72 | 7.8 | 33.59 | 26.9 | 0.12 | JD/BDL | Q3 | 3/3 | 774.75
AURORA ENERGY LLC | 2022-03-23 | 20 | 7196 | 32.16 | 8.54 | 32.64 | 26.67 | 0.12 | JD/BDL | Q3 | 3/3 | 1794.5
AURORA ENERGY LLC | 2022-03-28 | 6 | 7411 | 31.13 | 7.96 | 33.84 | 27.08 | 0.13 | JD/BDL | Q3 | 3/3 | 565
AURORA ENERGY LLC | 2022-03-29 | 6 | 7551 | 30.51 | 7.23 | 34.42 | 27.84 | 0.12 | JD/BDL | Q3 | 3/3 | 547.95
AURORA ENERGY LLC | 2022-03-30 | 7 | 7403 | 31.59 | 7.36 | 34.02 | 27.04 | 0.12 | JD/BDL | Q3 | 3/3 | 644.4
AURORA ENERGY LLC | 2022-03-31 | 6 | 7525 | 31.4 | 6.66 | 34.44 | 27.49 | 0.1 | JD/BDL | Q3 | 3/3 | 561.65
AURORA ENERGY LLC | 2022-04-05 | 7 | 7558 | 30.5 | 7.1 | 34.51 | 27.89 | 0.1 | JD/BDL | Q3 | 3/3 | 654.65
AURORA ENERGY LLC | 2022-04-06 | 4 | 7566 | 30.39 | 6.83 | 34.79 | 27.99 | 0.09 | JD/BDL | Q3 | 3/3 | 331.2
AURORA ENERGY LLC | 2022-04-07 | 5 | 7583 | 31 | 6.41 | 35.26 | 27.34 | 0.09 | JD/BDL | Q3 | 3/3 | 390.6
AURORA ENERGY LLC | 2022-04-08 | 5 | 7635 | 30.87 | 6.09 | 35.04 | 28.01 | 0.09 | JD/BDL | Q3 | 3/3 | 446.25
AURORA ENERGY LLC | 2022-04-12 | 15 | 7647 | 31 | 5.98 | 34.68 | 28.35 | 0.1 | JD/BDL | Q3 | 3/3 | 1371.05
AURORA ENERGY LLC | 2022-04-13 | 15 | 7621 | 30.15 | 7.2 | 34.57 | 28.09 | 0.11 | JD/BDL | Q3 | 3/3 | 1402.05
AURORA ENERGY LLC | 2022-04-14 | 15 | 7657 | 30.54 | 6.68 | 34.63 | 28.16 | 0.11 | JD/BDL | Q3 | 3/3 | 1410.35
AURORA ENERGY LLC | 2022-04-15 | 15 | 7548 | 30.56 | 7.12 | 34.73 | 27.6 | 0.13 | JD/BDL | Q3 | 3/3 | 1435.95
AURORA ENERGY LLC | 2022-04-19 | 13 | 7572 | 30.38 | 7.2 | 34.52 | 27.9 | 0.1 | JD/BDL | Q3 | 3/3 | 1208.8
AURORA ENERGY LLC | 2022-04-20 | 12 | 7713 | 30.15 | 6.06 | 35.39 | 28.4 | 0.09 | JD/BDL | Q3 | 3/3 | 1092.9
AURORA ENERGY LLC | 2022-04-21 | 13 | 7656 | 31.04 | 6.01 | 34.87 | 28.09 | 0.09 | JD/BDL | Q3 | 3/3 | 1228.6
AURORA ENERGY LLC | 2022-04-22 | 12 | 7605 | 31.45 | 5.77 | 35.18 | 27.61 | 0.09 | JD/BDL | Q3 | 3/3 | 1131.95
AURORA ENERGY LLC | 2022-04-26 | 12 | 7541 | 30.86 | 7.35 | 34.13 | 27.67 | 0.1 | JD/BDL | Q3 | 3/3 | 1140.5
AURORA ENERGY LLC | 2022-04-27 | 12 | 7493 | 30.66 | 7.77 | 33.93 | 27.65 | 0.12 | JD/BDL | Q3 | 3/3 | 1132.4
AURORA ENERGY LLC | 2022-04-28 | 10 | 7468 | 31.44 | 7.12 | 33.96 | 27.49 | 0.1 | JD/BDL | Q3 | 3/3 | 943.8
AURORA ENERGY LLC | 2022-04-29 | 4 | 7495 | 32.17 | 6.17 | 33.95 | 27.72 | 0.11 | BDL/JD | Q3 | 3/4 | 357.5
AURORA ENERGY LLC | 2022-04-29 | 5 | 7233 | 33.64 | 6.33 | 33.33 | 26.7 | 0.1 | BDL/JD | Q3 | 3/4 | 454.7
AURORA ENERGY LLC | 2022-04-29 | 4 | 7439 | 31.92 | 6.54 | 33.94 | 27.6 | 0.12 | BDL/JD | Q3 | 3/4 | 364.55
AURORA ENERGY LLC | 2022-04-29 | 6 | 7636 | 30.24 | 6.94 | 34.64 | 28.19 | 0.1 | JD/BDL | Q3 | 3/3 | 562.95
AURORA ENERGY LLC | 2022-05-03 | 9 | 7627 | 29.95 | 6.9 | 34.99 | 28.16 | 0.1 | JD/BDL | Q3 | 3/3 | 846.05
AURORA ENERGY LLC | 2022-05-04 | 9 | 7592 | 30.48 | 6.82 | 34.43 | 28.27 | 0.1 | JD/BDL | Q3 | 3/3 | 860.15
AURORA ENERGY LLC | 2022-05-05 | 9 | 7486 | 31.83 | 6.54 | 34.19 | 27.44 | 0.1 | JD/BDL | Q3 | 3/3 | 858.9
AURORA ENERGY LLC | 2022-05-06 | 9 | 7548 | 30.79 | 7.12 | 34.64 | 27.45 | 0.1 | JD/BDL | Q3 | 3/3 | 878.4
AURORA ENERGY LLC | 2022-05-10 | 25 | 7211 | 31.34 | 9.59 | 32.92 | 26.16 | 0.13 | JD/BDL | Q3 | 3/3 | 2321.85
AURORA ENERGY LLC | 2022-05-12 | 8 | 7146 | 31.33 | 9.61 | 33.12 | 25.94 | 0.11 | JD/BDL | Q3 | 3/3 | 740.4
AURORA ENERGY LLC | 2022-05-16 | 4 | 6819 | 33.93 | 9.51 | 31.36 | 25.21 | 0.13 | JD/BDL | Q3 | 3/3 | 401.75
AURORA ENERGY LLC | 2022-05-19 | 6 | 7324 | 32.12 | 7.41 | 33.55 | 26.93 | 0.09 | JD/JD |  | 3/4 | 550.9
AURORA ENERGY LLC | 2022-05-23 | 18 | 7537 | 31.3 | 6.16 | 34.85 | 27.69 | 0.09 | JD/JD |  | 3/4 | 1607
AURORA ENERGY LLC | 2022-05-25 | 17 | 7543 | 31.08 | 6.69 | 34.54 | 27.7 | 0.08 | JD/JD |  | 3/4 | 1537.05
AURORA ENERGY LLC | 2022-05-26 | 13 | 7483 | 31.17 | 7.05 | 35.04 | 26.75 | 0.09 | JD/JD |  | 3/4 | 1208.8
AURORA ENERGY LLC | 2022-05-31 | 17 | 7454 | 31.52 | 6.66 | 34.73 | 27.09 | 0.09 | JD/JD |  | 4/3 | 1602.4
AURORA ENERGY LLC | 2022-06-01 | 17 | 7594 | 32.01 | 5.24 | 34.99 | 27.75 | 0.08 | JD/JD |  | 3/4 | 1579.7
AURORA ENERGY LLC | 2022-06-02 | 14 | 7613 | 31.51 | 5.43 | 35.22 | 27.85 | 0.07 | JD/JD |  | 3/4 | 1245.35
AURORA ENERGY LLC | 2022-06-03 | 9 | 7695 | 31.14 | 5.25 | 35.57 | 28.05 | 0.07 | JD/JD |  | 3/4 | 821.8
AURORA ENERGY LLC | 2022-06-06 | 11 | 7652 | 31.47 | 5.45 | 35.24 | 27.84 | 0.08 | JD/JD |  | 3/4 | 1019.8
AURORA ENERGY LLC | 2022-06-07 | 12 | 7552 | 31.34 | 6.18 | 34.88 | 27.61 | 0.08 | JD/JD |  | 3/4 | 1129.25
AURORA ENERGY LLC | 2022-06-09 | 11 | 7000 | 32.01 | 10.81 | 32.42 | 24.76 | 0.13 | JD/JD |  | 3/4 | 1045.6
AURORA ENERGY LLC | 2022-06-10 | 12 | 7416 | 31.67 | 6.93 | 34.36 | 27.05 | 0.1 | JD/JD |  | 3/4 | 1120.9
AURORA ENERGY LLC | 2022-06-20 | 4 | 7628 | 31.21 | 6.07 | 35.68 | 27.03 | 0.1 | JD/JD |  | 3/4 | 374.6
AURORA ENERGY LLC | 2022-06-21 | 5 | 7488 | 31.72 | 6.23 | 34.64 | 27.41 | 0.12 | JD/JD |  | 3/4 | 444.7
AURORA ENERGY LLC | 2022-06-23 | 4 | 7652 | 31.98 | 5.15 | 35.25 | 27.63 | 0.09 | JD/JD |  | 3/4 | 377.85
AURORA ENERGY LLC | 2022-06-24 | 7 | 7623 | 30.92 | 5.86 | 35.29 | 27.92 | 0.1 | JD/JD |  | 3/4 | 659.15
AURORA ENERGY LLC | 2022-06-27 | 14 | 7680 | 30.93 | 5.6 | 35.63 | 27.84 | 0.1 | JD/JD |  | 3/4 | 1327
AURORA ENERGY LLC | 2022-06-28 | 14 | 7584 | 30.87 | 6.3 | 34.88 | 27.96 | 0.11 | JD/JD |  | 3/4 | 1333.5
AURORA ENERGY LLC | 2022-06-30 | 14 | 7480 | 32.09 | 6.34 | 34.45 | 27.13 | 0.1 | JD/JD |  | 3/4 | 1316
AURORA ENERGY LLC | 2022-07-01 | 13 | 7199 | 32.37 | 8.34 | 33.5 | 25.79 | 0.14 | JD/JD |  | 3/4 | 1260
AURORA ENERGY LLC | 2022-07-05 | 11 | 7518 | 31.44 | 6.77 | 35.06 | 26.73 | 0.13 | JD/JD |  | 3/4 | 1023.35
AURORA ENERGY LLC | 2022-07-06 | 8 | 7581 | 31.46 | 6.08 | 35 | 27.46 | 0.12 | JD/JD |  | 3/4 | 711.65
AURORA ENERGY LLC | 2022-07-07 | 14 | 7581 | 31.51 | 6.05 | 35.03 | 27.41 | 0.12 | JD/JD |  | 3/4 | 1281.7
AURORA ENERGY LLC | 2022-07-08 | 11 | 7727 | 30.79 | 5.65 | 35.98 | 27.59 | 0.12 | JD/JD |  | 3/4 | 1006.05
AURORA ENERGY LLC | 2022-07-11 | 12 | 7644 | 30.96 | 6.17 | 35.43 | 27.46 | 0.12 | JD/JD |  | 3/4 | 1097.95
AURORA ENERGY LLC | 2022-07-12 | 11 | 7449 | 31.29 | 7.26 | 34.22 | 27.24 | 0.14 | JD/JD |  | 3/4 | 1027.95
AURORA ENERGY LLC | 2022-07-14 | 12 | 7658 | 29.29 | 6.75 | 35.89 | 28.07 | 0.13 | JD/BDL | Q3 | 3/3 | 1096.2
AURORA ENERGY LLC | 2022-07-15 | 11 | 7213 | 33.05 | 7.32 | 33.43 | 26.2 | 0.11 | JD/JD |  | 3/4 | 1032.2
AURORA ENERGY LLC | 2022-07-18 | 10 | 7568 | 31.61 | 5.58 | 34.99 | 27.82 | 0.12 | JD/JD |  | 3/4 | 927
AURORA ENERGY LLC | 2022-07-19 | 10 | 7534 | 31.67 | 6.17 | 34.72 | 27.45 | 0.12 | JD/JD |  | 3/4 | 935.75
AURORA ENERGY LLC | 2022-07-21 | 10 | 7534 | 31.54 | 6.21 | 35.13 | 27.12 | 0.12 | JD/JD |  | 3/4 | 976.5
AURORA ENERGY LLC | 2022-07-22 | 10 | 7498 | 32.28 | 6.2 | 34.37 | 27.16 | 0.12 | JD/JD |  | 3/4 | 928.1
AURORA ENERGY LLC | 2022-07-25 | 14 | 7507 | 31.16 | 6.93 | 34.7 | 27.22 | 0.13 | JD/JD |  | 3/4 | 1324.5
AURORA ENERGY LLC | 2022-07-26 | 12 | 7138 | 32.23 | 9.28 | 33.02 | 25.47 | 0.15 | JD/JD |  | 4/3 | 1096.35
AURORA ENERGY LLC | 2022-07-28 | 13 | 7588 | 31.86 | 5.76 | 34.68 | 27.71 | 0.13 | JD/JD |  | 3/4 | 1215.85
AURORA ENERGY LLC | 2022-07-29 | 11 | 7569 | 31.81 | 5.8 | 34.89 | 27.49 | 0.12 | JD/JD |  | 3/4 | 1045.65
AURORA ENERGY LLC | 2022-08-01 | 12 | 7499 | 31.77 | 6.28 | 34.96 | 26.99 | 0.12 | JD/JD |  | 3/4 | 1149.8
AURORA ENERGY LLC | 2022-08-02 | 11 | 7470 | 31.82 | 6.63 | 34.23 | 27.33 | 0.13 | JD/JD |  | 3/4 | 1037
AURORA ENERGY LLC | 2022-08-04 | 12 | 7517 | 31.82 | 6.5 | 35.04 | 26.65 | 0.14 | JD/JD |  | 3/4 | 1188.55
AURORA ENERGY LLC | 2022-08-05 | 11 | 7428 | 31.96 | 6.83 | 33.92 | 27.3 | 0.13 | JD/JD |  | 3/4 | 1022.65
AURORA ENERGY LLC | 2022-08-08 | 8 | 7353 | 31.99 | 7.32 | 34.07 | 26.63 | 0.13 | JD/JD |  | 3/4 | 734.35
AURORA ENERGY LLC | 2022-08-09 | 8 | 7487 | 32.62 | 6.16 | 34.63 | 26.59 | 0.13 | JD/JD |  | 3/4 | 766.8
AURORA ENERGY LLC | 2022-08-11 | 8 | 7173 | 32.48 | 8.3 | 33.53 | 25.68 | 0.15 | JD/JD |  | 3/4 | 755.35
AURORA ENERGY LLC | 2022-08-12 | 7 | 7169 | 31.93 | 8.81 | 33.61 | 25.66 | 0.18 | JD/JD |  | 3/4 | 651.75
AURORA ENERGY LLC | 2022-08-15 | 9 | 7194 | 31.92 | 8.75 | 33.55 | 25.79 | 0.14 | JD/JD |  | 3/4 | 842.55
AURORA ENERGY LLC | 2022-08-16 | 10 | 6944 | 32.83 | 9.54 | 32.64 | 24.99 | 0.15 | JD/JD |  | 3/4 | 924.1
AURORA ENERGY LLC | 2022-08-18 | 9 | 7416 | 30.21 | 8.27 | 34.46 | 27.06 | 0.18 | BDL/JD | R4 | 4/4 | 838.5
AURORA ENERGY LLC | 2022-08-19 | 10 | 7603 | 28.64 | 8.2 | 35.29 | 27.87 | 0.19 | BDL/JD | R4 | 4/3 | 895.05
AURORA ENERGY LLC | 2022-08-22 | 9 | 7472 | 30.68 | 7.71 | 34.11 | 27.51 | 0.18 | BDL/JD | R4 | 4/3 | 857.05
AURORA ENERGY LLC | 2022-08-23 | 10 | 7499 | 30.12 | 7.98 | 34.39 | 27.52 | 0.16 | BDL/JD | R4 | 4/3 | 966
AURORA ENERGY LLC | 2022-08-25 | 9 | 7539 | 30.6 | 7.3 | 34.6 | 27.51 | 0.15 | JD/BDL | R4 | 3/4 | 870.1
AURORA ENERGY LLC | 2022-08-26 | 10 | 7477 | 30.96 | 7.31 | 34.35 | 27.38 | 0.14 | BDL/JD | R4 | 4/3 | 943
AURORA ENERGY LLC | 2022-08-29 | 21 | 7171 | 31.58 | 9.25 | 33.22 | 25.94 | 0.17 | BDL/JD | R4 | 4/3 | 1979.6
AURORA ENERGY LLC | 2022-08-30 | 4 | 7235 | 32.28 | 8.14 | 33.51 | 26.07 | 0.17 | BDL/JD | R4 | 4/3 | 375.4
AURORA ENERGY LLC | 2022-09-01 | 14 | 7267 | 30.75 | 9 | 34.33 | 25.92 | 0.18 | BDL/JD | R4 | 4/3 | 1329.3
AURORA ENERGY LLC | 2022-09-02 | 10 | 7374 | 30.66 | 8.03 | 34.31 | 27.01 | 0.19 | JD/STK |  | 3 | 931.75
AURORA ENERGY LLC | 2022-09-06 | 33 | 7120 | 30.19 | 10.12 | 33.45 | 26.25 | 0.19 | JD/STK |  | 3 | 3088.6
AURORA ENERGY LLC | 2022-09-09 | 8 | 7671 | 30.24 | 6.82 | 34.89 | 28.05 | 0.14 | JD/BDL | R4 | 3/4 | 775.55
AURORA ENERGY LLC | 2022-09-13 | 17 | 7167 | 30.01 | 10.56 | 33.43 | 26.01 | 0.18 | JD/BDL | R4 | 3/4 | 1640.35
AURORA ENERGY LLC | 2022-09-14 | 11 | 7154 | 30.47 | 10.29 | 33.68 | 25.56 | 0.19 | JD/BDL | R4 | 3/4 | 1035.55
AURORA ENERGY LLC | 2022-09-14 | 13 | 7184 | 30.9 | 9.67 | 33.87 | 25.57 | 0.2 | JD/BDL | R4 | 3/4 | 1281.7
AURORA ENERGY LLC | 2022-09-16 | 6 | 7429 | 28.55 | 8.66 | 34.96 | 27.84 | 0.21 | BDL/STK | R4 | 4 | 566.25
AURORA ENERGY LLC | 2022-09-19 | 13 | 7405 | 30.2 | 8.38 | 34.35 | 27.08 | 0.22 | BDL/STK | R4 | 4 | 1276.65
AURORA ENERGY LLC | 2022-09-20 | 12 | 7486 | 29.78 | 8.59 | 34.41 | 27.21 | 0.21 | JD/BDL | R4 | 3/4 | 1112.05
AURORA ENERGY LLC | 2022-09-21 | 10 | 7704 | 29.41 | 7.12 | 35.43 | 28.04 | 0.2 | JD/BDL | R4 | 3/4 | 954.5
AURORA ENERGY LLC | 2022-09-24 | 14 | 7225 | 30.97 | 9.23 | 33.64 | 26.16 | 0.21 | JD/BDL | R4 | 3/4 | 1290.25
AURORA ENERGY LLC | 2022-09-26 | 14 | 7551 | 30.63 | 7.36 | 34.64 | 27.37 | 0.17 | JD/BDL | R4 | 3/4 | 1306.3
AURORA ENERGY LLC | 2022-09-27 | 8 | 7537 | 30.77 | 7.34 | 34.4 | 27.51 | 0.16 | JD/BDL | R4 | 3/4 | 752.5
AURORA ENERGY LLC | 2022-09-28 | 8 | 7572 | 31.28 | 6.45 | 34.78 | 27.49 | 0.14 | JD/BDL | R4 | 3/4 | 770.75
AURORA ENERGY LLC | 2022-09-30 | 14 | 7582 | 30.91 | 6.47 | 34.86 | 27.76 | 0.14 | JD/BDL | R4 | 3/4 | 1312.9
AURORA ENERGY LLC | 2022-10-04 | 16 | 7589 | 30.72 | 6.73 | 35.14 | 27.41 | 0.13 | JD/BDL | R4 | 3/4 | 1467.9
AURORA ENERGY LLC | 2022-10-05 | 15 | 7599 | 30.54 | 6.81 | 34.83 | 27.82 | 0.13 | JD/BDL | R4 | 3/4 | 1468.8
AURORA ENERGY LLC | 2022-10-06 | 6 | 7448 | 31.04 | 7.5 | 34.34 | 27.14 | 0.14 | JD/BDL | R4 | 3/4 | 557.25
AURORA ENERGY LLC | 2022-10-07 | 19 | 7610 | 29.93 | 7.11 | 35.08 | 27.88 | 0.14 | JD/BDL | R4 | 3/4 | 1837.1
AURORA ENERGY LLC | 2022-10-11 | 17 | 7586 | 30.46 | 7.13 | 35.37 | 27.05 | 0.13 | JD/BDL | R4 | 3/4 | 1552.7
AURORA ENERGY LLC | 2022-10-12 | 12 | 7451 | 30.71 | 7.88 | 35.16 | 26.26 | 0.16 | JD/BDL | R4 | 3/4 | 1153.45
AURORA ENERGY LLC | 2022-10-13 | 12 | 7531 | 31.3 | 6.81 | 34.42 | 27.47 | 0.15 | JD/BDL | R4 | 3/4 | 1137.95
AURORA ENERGY LLC | 2022-10-14 | 13 | 7584 | 30.06 | 7.44 | 34.66 | 27.85 | 0.16 | JD/BDL | R4 | 3/4 | 1251.4
AURORA ENERGY LLC | 2022-10-18 | 11 | 7636 | 29.78 | 7.41 | 34.86 | 27.95 | 0.19 | JD/BDL | R4 | 3/4 | 1066.5
AURORA ENERGY LLC | 2022-10-19 | 11 | 7629 | 29.91 | 7.34 | 34.84 | 27.92 | 0.19 | JD/BDL | R4 | 3/4 | 1064.9
AURORA ENERGY LLC | 2022-10-20 | 11 | 7606 | 30.47 | 7.02 | 34.78 | 27.74 | 0.16 | JD/BDL | R4 | 3/4 | 1059.2
AURORA ENERGY LLC | 2022-10-21 | 11 | 7503 | 31.61 | 6.74 | 34.41 | 27.25 | 0.16 | JD/BDL | R4 | 3/4 | 1041.9
AURORA ENERGY LLC | 2022-10-25 | 14 | 7586 | 30.33 | 7.64 | 34.71 | 27.32 | 0.16 | JD/BDL | R4 | 3/4 | 1353.65
AURORA ENERGY LLC | 2022-10-26 | 15 | 7600 | 30.2 | 7.66 | 34.77 | 27.38 | 0.16 | JD/BDL | R4 | 3/4 | 1447.15
AURORA ENERGY LLC | 2022-10-28 | 15 | 7627 | 29.42 | 7.92 | 35.27 | 27.39 | 0.17 | JD/BDL | R4 | 3/4 | 1462.15
AURORA ENERGY LLC | 2022-11-02 | 15 | 7651 | 30.26 | 6.93 | 35.71 | 27.11 | 0.13 | JD/BDL | R4 | 3/4 | 1439.85
AURORA ENERGY LLC | 2022-11-03 | 11 | 7630 | 30.15 | 7.03 | 34.94 | 27.88 | 0.14 | JD/BDL | R4 | 3/4 | 1035.1
AURORA ENERGY LLC | 2022-11-04 | 16 | 7593 | 29.85 | 7.23 | 34.98 | 27.95 | 0.13 | JD/BDL | R4 | 3/4 | 1404.15
AURORA ENERGY LLC | 2022-11-08 | 9 | 7516 | 31.1 | 7.07 | 34.48 | 27.35 | 0.13 | JD/BDL | R4 | 3/4 | 840.55
AURORA ENERGY LLC | 2022-11-09 | 10 | 7660 | 30.5 | 6.21 | 35.17 | 28.13 | 0.11 | JD/BDL | R4 | 3/4 | 945.5
AURORA ENERGY LLC | 2022-11-10 | 9 | 7696 | 29.9 | 6.48 | 35.18 | 28.45 | 0.13 | JD/BDL | R4 | 3/4 | 858.65
AURORA ENERGY LLC | 2022-11-11 | 10 | 7629 | 30.16 | 6.29 | 34.91 | 28.66 | 0.13 | JD/BDL | R4 | 3/4 | 942.5
AURORA ENERGY LLC | 2022-11-15 | 12 | 7487 | 31.02 | 6.87 | 34.24 | 27.87 | 0.13 | JD/BDL | R4 | 3/4 | 1149.05
AURORA ENERGY LLC | 2022-11-16 | 11 | 7600 | 31.54 | 5.68 | 34.78 | 28 | 0.11 | JD/JD |  | 4/3 | 993.7
AURORA ENERGY LLC | 2022-11-17 | 11 | 7740 | 31.6 | 4.77 | 35.8 | 27.84 | 0.1 | JD/JD |  | 3/4 | 1007.85
AURORA ENERGY LLC | 2022-11-18 | 11 | 7736 | 31.95 | 4.42 | 35.63 | 28 | 0.09 | JD/JD |  | 3/4 | 1030.85
AURORA ENERGY LLC | 2022-11-21 | 13 | 7741 | 31.55 | 4.58 | 35.71 | 28.17 | 0.09 | JD/JD |  | 4/3 | 1172.2
AURORA ENERGY LLC | 2022-11-22 | 12 | 7717 | 31.45 | 4.78 | 35.19 | 28.58 | 0.1 | JD/JD |  | 3/4 | 1095.6
AURORA ENERGY LLC | 2022-11-23 | 5 | 7675 | 31.74 | 5.06 | 35.2 | 28 | 0.13 | JD/JD |  | 4/3 | 461
AURORA ENERGY LLC | 2022-11-25 | 14 | 7698 | 31.36 | 5.1 | 35.32 | 28.23 | 0.12 | JD/JD |  | 4/3 | 1299.6
AURORA ENERGY LLC | 2022-11-29 | 11 | 7314 | 31.86 | 7.79 | 33.41 | 26.95 | 0.14 | JD/BDL | R4 | 4/4 | 893.5
AURORA ENERGY LLC | 2022-11-30 | 8 | 7463 | 32.33 | 6.21 | 34.02 | 27.45 | 0.13 | JD/BDL | R4 | 4/4 | 645.8
AURORA ENERGY LLC | 2022-12-01 | 11 | 7697 | 31.08 | 5.6 | 35.41 | 27.92 | 0.14 | JD/BDL | R4 | 4/4 | 920.5
AURORA ENERGY LLC | 2022-12-02 | 8 | 7745 | 30.45 | 5.72 | 35.6 | 28.24 | 0.13 | JD/BDL | R4 | 4/4 | 667.3
AURORA ENERGY LLC | 2022-12-06 | 12 | 7714 | 31.23 | 4.92 | 36 | 27.86 | 0.13 | JD/BDL | R4 | 4/4 | 1097.55
AURORA ENERGY LLC | 2022-12-07 | 14 | 7680 | 31.32 | 5.33 | 35.78 | 27.57 | 0.14 | JD/BDL | R4 | 4/4 | 1262.6
AURORA ENERGY LLC | 2022-12-08 | 15 | 7737 | 31.7 | 4.44 | 35.66 | 28.21 | 0.1 | JD/BDL | R4 | 4/4 | 1353.6
AURORA ENERGY LLC | 2022-12-09 | 13 | 7703 | 31.17 | 5 | 36.02 | 27.82 | 0.12 | JD/BDL | R4 | 4/4 | 1125.15
AURORA ENERGY LLC | 2022-12-13 | 12 | 7731 | 31.32 | 5.01 | 35.74 | 27.93 | 0.13 | JD/BDL | R4 | 4/4 | 1061.9
AURORA ENERGY LLC | 2022-12-14 | 14 | 7701 | 31.62 | 4.79 | 36.02 | 27.58 | 0.11 | JD/BDL | R4 | 4/4 | 1190.25
AURORA ENERGY LLC | 2022-12-15 | 6 | 7589 | 32.69 | 4.73 | 34.93 | 27.66 | 0.14 | JD/BDL | R4 | 4/4 | 520.55
AURORA ENERGY LLC | 2022-12-20 | 4 | 7493 | 31.56 | 6.5 | 34.51 | 27.43 | 0.1 | JD/STK |  | 4 | 362
Annual Average |  |  | 7536.4688 | 31.311 | 6.5332 | 34.6262 | 27.5346 | 0.12401
AR = as received

## TableF-DSI_Electrical_Equip
Table F. Estimated Station Service Electrical Load for DSI Equipment
Aurora Energy Chena Power Plant SO2 BACT Analysis
Do not use for electrical equipment sizing. Use only for approximating actual kW consumption under normal operating conditions.
SOURCE Equip Tag | EQUIPMENT Equip Tag | Load Name | MCC Starter Size | MCC Starter Type | Voltage [V] | Load [VA] | Load [HP] | Load [KW] | FLA | Load Factor | Adjusted Load (kVA) | PF | Adjusted Load (kW) | Notes
| 05B3A | Unloading Blower | 5 | FVNR | 480 |  | 125 |  | 150.356 | 0.1 | 12.5004 | 0.85 | 10.6253 | Only used for unloading
| 05B3B | Air Cooler for Unloading Blower | 1 | FVNR | 480 |  | 1 |  | 1.2028 | 0.1 | 0.1 | 0.8 | 0.080002 | Only used for unloading
| 06B3A | Bin Vent Exhaust Fan | 1 | FVNR | 480 |  | 7.5 |  | 9.0214 | 0.87 | 6.5252 | 0.8 | 5.2202
| 06B3B | Bin Discharger Silo #1 | 1 | FVNR | 480 |  | 3 |  | 3.6085 | 0.87 | 2.6101 | 0.8 | 2.0881
| 06B3B | Bin Discharger Silo #2 | 1 | FVNR | 480 |  | 3 |  | 3.6085 | 0.87 | 2.6101 | 0.8 | 2.0881
| 08B3A | Transfer Blower for Day Bins A | 3 | FVNR | 480 |  | 50 |  | 60.1424 | 0.25 | 12.5004 | 0.85 | 10.6253 | Only used to transfer to plant
| 08B3A | Transfer Blower for Day Bins B | 3 | FVNR | 480 |  | 50 |  | 60.1424 | 0 | 0 | 0.85 | 0 | Spare
| 08B3A | Air Cooler for Transfer Blower | 3 | FVNR | 480 |  | 1 |  | 1.2028 | 0.25 | 0.25001 | 0.8 | 0.20001 | Only used to transfer to plant
| 09B3B | Airlock Silo #1 | 1 | FVNR | 480 |  | 1 |  | 1.2028 | 0.25 | 0.25001 | 0.8 | 0.20001 | Only used to transfer to plant
| 09B3B | Airlock Silo #2 | 1 | FVNR | 480 |  | 1 |  | 1.2028 | 0.25 | 0.25001 | 0.8 | 0.20001 | Only used to transfer to plant
|  | Unloading Skid heater |  |  | 480 | 5000 |  | 5000 | 6.0142 | 0.1 | 0.50001 | 1 | 0.50001 | Only used for unloading
|  | Silo #1 Heater |  |  | 480 | 5000 |  | 5000 | 6.0142 | 1 | 5.0001 | 1 | 5.0001
|  | Silo #2 Heater |  |  | 480 | 5000 |  | 5000 | 6.0142 | 1 | 5.0001 | 1 | 5.0001
|  | Silo #1 Exhaust Fan | 1 | FVNR | 480 |  | 2 |  | 2.4057 | 0.87 | 1.7401 | 0.8 | 1.392
|  | Silo #2 Exhaust Fan | 1 | FVNR | 480 |  | 2 |  | 2.4057 | 0.87 | 1.7401 | 0.8 | 1.392
|  | Air Compressor | 3 | FVNR | 480 |  | 30 |  | 36.0855 | 0.87 | 26.1008 | 0.85 | 22.1857 | For continuous supply of fluidizing air
|  | Area Lighting |  | 100A BKR | 480 | 1500 |  | 1500 | 1.8043 | 1 | 1.5 | 0.9 | 1.35
|  | Receptacles |  |  | 480 | 1500 |  | 1500 | 1.8043 | 1 | 1.5 | 0.9 | 1.35
|  | Total | 25 |  |  |  | 276.5 |  | 354.2388 |  |  |  | 69.497
| 05B3A | Bin Vent Exhaust Fan #1 | 1 | FVNR | 480 |  | 3 |  | 3.6085 | 0.87 | 2.6101 | 0.8 | 2.0881
| 05B3A | Bin Vent Exhaust Fan #2 | 1 | FVNR | 480 |  | 3 |  | 3.6085 | 0.87 | 2.6101 | 0.8 | 2.0881
|  | Bin Discharger #1 | 1 | FVNR | 480 |  | 1.5 |  | 1.8043 | 0.87 | 1.305 | 0.8 | 1.044
|  | Bin Discharger #2 | 1 | FVNR | 480 |  | 1.5 |  | 1.8043 | 0.87 | 1.305 | 0.8 | 1.044
|  | Feeder #1 | 1 | FVNR | 480 |  | 1 |  | 1.2028 | 0.87 | 0.87003 | 0.8 | 0.69602
|  | Feeder #2 | 1 | FVNR | 480 |  | 2 |  | 2.4057 | 0.87 | 1.7401 | 0.8 | 1.392
|  | Feeder #3 | 1 | FVNR | 480 |  | 2 |  | 2.4057 | 0 | 0 | 0.8 | 0 | Spare
|  | Grinding Motor #1 | 3 | FVNR | 480 |  | 30 |  | 36.0855 | 0.87 | 26.1008 | 0.85 | 22.1857
|  | Grinding Motor #2 | 4 | FVNR | 480 |  | 60 |  | 72.1709 | 0.87 | 52.2015 | 0.85 | 44.3713
|  | Grinding Motor #3 | 3 | FVNR | 480 |  | 30 |  | 36.0855 | 0 | 0 | 0.85 | 0 | Spare
|  | Classifier Motor #1 | 1 | FVNR | 480 |  | 3 |  | 3.6085 | 0.87 | 2.6101 | 0.8 | 2.0881
|  | Classifier Motor #2 | 1 | FVNR | 480 |  | 6 |  | 7.2171 | 0.87 | 5.2202 | 0.8 | 4.1761
|  | Classifier Motor #3 | 1 | FVNR | 480 |  | 3 |  | 3.6085 | 0 | 0 | 0.8 | 0 | Spare
|  | Injection Blower Boiler #1 | 2 | FVNR | 480 |  | 25 |  | 30.0712 | 0.87 | 21.7506 | 0.85 | 18.488
|  | Backup Injection Blower Boiler #1 (25HP) | 2 | FVNR | 480 |  |  |  | 0 | 0.87 | 0 | 0.85 | 0 | Spare
|  | Injection Blower Boiler #2 | 2 | FVNR | 480 |  | 25 |  | 30.0712 | 0.87 | 21.7506 | 0.85 | 18.488
|  | Backup Injection Blower Boiler #2 (25HP) | 2 | FVNR | 480 |  |  |  | 0 | 0.87 | 0 | 0.85 | 0 | Spare
|  | Injection Blower Boiler #3 | 2 | FVNR | 480 |  | 25 |  | 30.0712 | 0.87 | 21.7506 | 0.85 | 18.488
|  | Backup Injection Blower Boiler #3 (25HP) | 2 | FVNR | 480 |  |  |  | 0 | 0.87 | 0 | 0.85 | 0 | Spare
|  | Injection Blower Boiler #5 | 4 | FVNR | 480 |  | 75 |  | 90.2136 | 0.87 | 65.2519 | 0.85 | 55.4641
|  | Backup Injection Blower Boiler #5 (75HP) | 4 | FVNR | 480 |  |  |  | 0 | 0.87 | 0 | 0.85 | 0 | Spare
|  | Air Cooler #1 | 1 | FVNR | 480 |  | 2 |  | 2.4057 | 0.87 | 1.7401 | 0.8 | 1.392
|  | Air Cooler #2 | 1 | FVNR | 480 |  | 2 |  | 2.4057 | 0.87 | 1.7401 | 0.8 | 1.392
|  | Air Cooler #3 | 1 | FVNR | 480 |  | 2 |  | 2.4057 | 0.87 | 1.7401 | 0.8 | 1.392
|  | Air Cooler #5 | 1 | FVNR | 480 |  | 2 |  | 2.4057 | 0.87 | 1.7401 | 0.8 | 1.392
|  | Exhaust Fan Mill #1 | 2 | FVNR | 480 |  | 15 |  | 18.0427 | 0.87 | 13.0504 | 0.8 | 10.4403
|  | Exhaust Fan Mill #2 | 2 | FVNR | 480 |  | 15 |  | 18.0427 | 0.87 | 13.0504 | 0.8 | 10.4403
|  | Exhaust Fan Mill #3 | 2 | FVNR | 480 |  | 15 |  | 18.0427 | 0.87 | 13.0504 | 0.8 | 10.4403
|  | Exhaust Fan Mill #4 | 2 | FVNR | 480 |  | 15 |  | 18.0427 | 0.87 | 13.0504 | 0.8 | 10.4403
|  | Airlock Mill #1 | 1 | FVNR | 480 |  | 0.25 |  | 0.30071 | 0.87 | 0.21751 | 0.8 | 0.17401
|  | Airlock Mill #2 | 1 | FVNR | 480 |  | 0.25 |  | 0.30071 | 0.87 | 0.21751 | 0.8 | 0.17401
|  | Airlock Mill #3 | 1 | FVNR | 480 |  | 0.25 |  | 0.30071 | 0.87 | 0.21751 | 0.8 | 0.17401
|  | Airlock Mill #4 | 1 | FVNR | 480 |  | 0.25 |  | 0.30071 | 0.87 | 0.21751 | 0.8 | 0.17401
|  | Area Lighting |  | 100A BKR | 480 | 1500 |  | 1500 | 1.8043 | 1 | 1.5 | 0.9 | 1.35
|  | Receptacles |  |  | 480 | 1500 |  | 1500 | 1.8043 | 1 | 1.5 | 0.9 | 1.35
|  | Total | 56 |  |  |  | 365 |  | 442.6482 |  |  |  | 242.8271
[10 empty] | Total |  |  | 312.3242