## Dry Sorbent Injection
Dry Sorbent Injection System - UAF
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 29.6 | <-- User Input (Conservative assumption based on a total heat input of 296 MMBtu/hour)
Retrofit Factor | B |  | 1 | <-- User Input (An "average" retrofit has a factor of 1.0. Proposed UAF boiler is not a retrofit, however modifications to existing equipment (e.g., ductwork and stack) and operating conditions (e.g., temperature and flowrate) may need to be modified. Retrofit of scrubbers on existing units can increase the capitical cost up to 30%. Therefore the Department assumed a retrofit factor of 0.7 for the dual fuel-fired boiler at UAF. https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Gross Heat Rate | C | (Btu/kWh) | 10000 | <-- User Input
SO2 Rate | D | (lb/MMBtu) | 0.2 | <-- User Input
Type of Coal | E |  | sub-bituminous | <-- User Input
Particulate Capture | F |  | Baghouse | <-- User Input
Milled Trona | G |  | TRUE | Based on in-line milling equipment
Removal Target | H | (%) | 80 | Maximum Removal Targets: Unmilled Trona with an ESP = 65% Milled Trona with an ESP = 80% Unmilled Trona with a Baghouse = 80% Milled Trona with Baghouse = 90%
Heat Input | J | (Btu/hr) | 296000000 | A*C*1000
NSR | K |  | 1.9695 | Unmilled Trona with an ESP = if(H<40,0.0350*H,0.352e^(0.0345*H)) Milled Trona with an ESP = if(H<40,0.0270*H,0.353e^(0.0280*H)) Unmilled Trona with an BGH = if(H<40,0.0215*H,0.295e^(0.0267*H)) Milled Trona with an BGH = if(H<40,0.0160*H,0.208e^(0.0281*H))
Trona Feed Rate | M | (ton/hr) | 0.14004 | (1.2011x10^-06)*K*A*C*D
Sorbent Waste Rate | N | (ton/hr) | 0.094327 | (0.7035-0.00073696*H/K)*M Based on a final reaction product of Na2SO4 and unreacted dry sorbent as Na2CO3.
Fly Ash Waste Rate | P | (ton/hr) | 0.54815 | (A*C)*Ash incoal*(1-Boiler Ash Removal)/(2*HHV) For Bituminous Coal: Ash in Coal = 0.12; Boiler Ash Removal = 0.2, HHV = 11,000 For PRB Coal: Ash in Coal = 0.06; Boiler Ash Removal = 0.2, HHV = 8,400 For Lignite Coal: Ash in Coal = 0.08; Boiler Ash Removal = 0.2, HHV = 7,200 <-- User Input (Usibelli Coal: Ash in Coal = 0.07; Boiler Ash Removal = 0.6; HHV = 7,560)
Aux Power | Q | (%) | 0.094623 | =if Milled Trona M*20/A else M*18/A
Trona Cost | R | ($/ton) | 451 | <-- User Input (based on delivered price paid by Healy)
Waste Disposal Cost | S | ($/ton) | 50
Aux Power Cost | T | ($/kWh) | 0.21 | <-- User Input (http://www.gvea.com/rates/rates)
Operating Labor Rate | U | ($/hr) | 60 | <-- User Input (Labor cost including all benefits)
IPM Model - Updates to Cost and Performance for APC Technologies - Dry Sorbent Injection for SO2 Control Cost Development Methodology, March 2013, prepared by Sargent & Lundy LLC for USEPA. https://www.epa.gov/sites/production/files/2015-07/documents/append5_4.pdf
Capital Cost Calculation (2012 dollars) |  |  |  | Comments
Includes - Equipment, installation, building, foundations, electrical, and retrofit difficulty factor of 0.7
Base Module (BM) ($) |  | = | 4300550.9906 | Base DSI module includes all equipment from unloading to injection
Unmilled Trona = if(M>25 then (682,000*B*M) else 6,833,000*B*(M^0.284)
Milled Trona = if(M>25 then (750,000*B*M) else 7,516,000*B*(M^0.284)
BM ($/kW) |  | = | 145.2889 | Base module cost per kW
Total Project Cost
A1 = 10% of BM |  | = | 215027.5495 | Engineering and construction management costs (CC Manual)
A2 = 10% of BM |  | = | 215027.5495 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc. (CC Manual)
A3 = 10% of BM |  | = | 215027.5495 | Contractor profit and fees (CC Manual)
CECC ($) - Excludes Owner's Costs = BM + A1 + A2 + A3 |  | = | 4945633.6392 | Capital, engineering, and construction costs subtotal
CECC ($/kW) - Excludes Owner's Costs |  | = | 167.0822 | Capital, engineering, and construction costst subtotal per kW
B1 = 5% of CECC |  | = | 247281.682 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
TPC ($) - Includes Owners Costs = CECC + B1 |  | = | 5192915.3211 | Total project cost without Allowance for Funds Used During Construction (AFUDC)
TPC ($/kW) - Include Owner's Costs |  | = | 175.4363 | Total project cost per kW without AFUDC
B2 = 0% of (CECC + B1) |  | = | 0 | AFUDC (Zero for less than 1 year engineering and construction cycle)
TPC ($) = CECC + B1 + B2 |  | = | 5192915.3211 | Total project cost
TPC ($/kW) |  | = | 175.4363 | Total project cost per kW
Dry Sorbent Injection System - UAF
Direct Annual Costs
Fixed Operating and Maintenance (O&M) Cost
FOMO ($/kW yr) = (1 additional operators)*(2080)*U/(A*1000) |  | = | 4.2162 | Fixed O&M additional operating labor costs
FOMM ($/kW yr) = BM*0.01/(B*A*1000) |  | = | 1.4529 | Fixed O&M additional maintenance material and labor costs
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  | = | 0.14392 | Fixed O&M additional administrative labor costs
FOM ($/kW yr) = FOMO + FOMM + FOMA |  | = | 5.813 | Total Fixed O&M costs ($/kW yr)
Variable O&M Cost
VOMR ($/MWh) = M*R/A |  | = | 2.1337 | Variable O&M costs for Trona reagent
VOMW ($/MWh) = (N+P)*S/A |  | = | 1.0853 | Variable O&M costs for waste disposal that includes both the sorbent and the fly ash waste not removed prior to the sorbent injection
VOMP ($/MWh) = Q*T*10 |  | = | 0.19871 | Variable O&M costs for additional auxiliary power required (Refer to Aux Power % above)
VOM ($/MWh) = VOMR + VOMW + VOMP |  | = | 3.4177 | Total Variable O&M Costs ($/MW yr)
Indirect Annual Costs
Overhead (60% of total labor and material costs) |  | = | 103239.3456 | CC Manual
Administrative charges (2% of total capital investment) |  | = | 103858.3064 | CC Manual
Property tax (1% of total capital investment) |  | = | 51929.1532 | CC Manual
Insurance (1% of total capital investment) |  | = | 51929.1532 | CC Manual
Capital Recovery Factor (CRF) = [ i (1+i)n ] / [ (1+i)n - 1 ]
i = Interest rate (%) | 5.5
n = Equipment life (years) | 15
CRF = | 0.099626 | = | 517347.2922 | CC Manual
TOTAL INDIRECT ANNUAL OPERATING COSTS |  | = | 828303.2506
TOTAL ANNUALIZED OPERATING COSTS (2012 $) |  | = | 1886569.5587
Composite CE Index for 2012 (cost year of equation) |  | = | 584.6
Composite CE Index for 2016 (cost year of review) |  | = | 536.4
TOTAL ANNUALIZED OPERATING COSTS (2016 $) |  | = | 1731022.7699
TOTAL UNCONTROLLED SO2 EMISSIONS, tons |  | = | 259.296
SO2 REMOVAL EFFICIENCY, % |  | = | 80
TOTAL SO2 REMOVED, tons |  | = | 207.4368
SO2 COST-EFFECTIVENESS, $/ton removed |  | = | 8344.8201

## Spray Dry Absorber
Spray Dry Absorber - UAF
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 29.6 | <-- User Input (Conservative assumption based on a total heat input of 296 MMBtu/hour)
Retrofit Factor | B |  | 1 | <-- User Input (An "average" retrofit has a factor of 1.0. Proposed UAF boiler is not a retrofit, however modifications to existing equipment (e.g., ductwork and stack) and operating conditions (e.g., temperature and flowrate) may need to be modified. Retrofit of scrubbers on existing units can increase the capitical cost up to 30%. Therefore the Department assumed a retrofit factor of 0.7 for the dual fuel-fired boiler at UAF. https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Gross Heat Rate | C | (Btu/kWh) | 10000 | <-- User Input
SO2 Rate | D | (lb/MMBtu) | 0.2 | <-- User Input (SDA FGD Estimation only valid up to 3lb/MMBtu SO2 Rate)
Type of Coal | E |  | sub-bituminous | <-- User Input
Coal Factor | F |  | 1.05 | Bituminous = 1, Sub-Bituminous = 1.05, Lignite = 1.07
Heat Rate Factor | G |  | 1 | C/10000
Heat Input | H | (Btu/hr) | 296000000 | A*C*1000
Lime Rate | K | (ton/hr) | 0.04012 | (0.6702*(D^2)+13.42*D)*A*G/2000 (Based on 95% SO2 Removal)
Waste Rate | L | (ton/hr) | 0.092802 | (0.8016*(D^2)+31.1917*D)*A*G/2000
Aux Power | M | (%) | 1.3664 | (0.000547*(D^2)+0.00649*D+1.3)*F*G
Makeup Water Rate | N | (1000 gph) | 1.7166 | (0.04898*(D^2)+0.5925*D+55.11)*A*F*G/1000
Lime Cost | P | ($/ton) | 80 | <-- User Input (https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Waste Disposal Cost | Q | ($/ton) | 30 | <-- User Input (https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Aux Power Cost | R | ($/kWh) | 0.21 | <-- User Input (http://www.gvea.com/rates/rates)
Makeup Water Cost | S | ($/1000 gal) | 7.17 | <-- User Input (http://www.newsminer.com/water-rates/article_11a2ba10-c211-562e-8da9-87dd16a7b104.html)
Operating Labor Rate | T | ($/hr) | 60 | Labor cost including all benefits
IPM Model - Updates to Cost and Performance for APC Technologies - SDA FGD for SO2 Control Cost Development Methodology, March 2013, prepared by Sargent & Lundy LLC for US EPA. https://www.epa.gov/sites/production/files/2015-07/documents/chapter_5_appendix_5-1b_sda_fgd.pdf
Capital Cost Calculation (2012 dollars) |  |  |  | Comments
Includes - Equipment, installation, building, foundations, electrical, and a retrofit difficulty factor of 0.7
BMR ($) = if(A>600 then (A*92,000) else 566,000*(A^0.716))*B*(F*G)^0.6*(D/4)^0.01 |  | = | 6396826.562 | Base module absorber island cost
BMF ($) = if(A>600 then (A*48,700) else 300,000*(A^0.716))*B*(D*G)^0.2 |  | = | 2459076.9499 | Base module reagent preparation and waste recycle/handling cost
BMB ($) = if(A>600 then (A*129,900) else 799,000*(A^0.716))*B*(F*G)^0.4 |  | = | 9214406.4261 | Base module balance of plan cost including: ID or booster fans, piping, ductwork, electrical, etc…
Base Module (BM) ($) |  | = | 18070309.9379 | Base DSI module includes all equipment from unloading to injection
BM ($/kW) |  | = | 610.4834 | Base module cost per kW
Total Project Cost
A1 = 10% of BM |  | = | 1807030.9938 | Engineering and construction management costs (CC Manual)
A2 = 10% of BM |  | = | 1807030.9938 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc. (CC Manual)
A3 = 10% of BM |  | = | 1807030.9938 | Contractor profit and fees (CC Manual)
CECC ($) - Excludes Owner's Costs = BM + A1 + A2 + A3 |  | = | 23491402.9193 | Capital, engineering, and construction costs subtotal
CECC ($/kW) - Excludes Owner's Costs |  | = | 793.6285 | Capital, engineering, and construction costst subtotal per kW
B1 = 5% of CECC |  | = | 1174570.146 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
TPC ($) - Includes Owners Costs = CECC + B1 |  | = | 24665973.0652 | Total project cost without Allowance for Funds Used During Construction (AFUDC)
TPC ($/kW) - Include Owner's Costs |  | = | 833.3099 | Total project cost per kW without AFUDC
B2 = 10% of (CECC + B1) |  | = | 2466597.3065 | AFUDC (Zero for less than 1 year engineering and construction cycle)
TPC ($) = CECC + B1 + B2 |  | = | 27132570.3718 | Total project cost
TPC ($/kW) |  | = | 916.6409 | Total project cost per kW
Spray Dry Absorber - UAF
Direct Annual Costs
Fixed O&M Cost
FOMO ($/kW yr) = (4 additional operators)*(2080)*T/(A*1000) |  | = | 16.8649 | Fixed O&M additional operating labor costs
FOMM ($/kW yr) = BM*0.015/(B*A*1000) |  | = | 9.1573 | Fixed O&M additional maintenance material and labor costs
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  | = | 0.61583 | Fixed O&M additional administrative labor costs
FOM ($/kW yr) = FOMO + FOMM + FOMA |  | = | 26.6379 | Total Fixed O&M costs ($/kW yr)
Variable O&M Cost
VOMR ($/MWh) = K*P/A |  | = | 0.10843 | Variable O&M costs for lime reagent
VOMW ($/MWh) = L*Q/A |  | = | 0.094056 | Variable O&M costs for waste disposal
VOMP ($/MWh) = M*R*10 |  | = | 2.8694 | Variable O&M costs for additional auxiliary power required (Refer to Aux Power % above)
VOMM ($/MWh) = N*S/A |  | = | 0.4158 | Variable O&M costs for makeup water
VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM |  | = | 3.4877 | Total Variable O&M Costs ($/MW yr)
Indirect Annual Costs
Overhead (60% of total labor and material costs) |  | = | 473089.9829 | CC Manual
Administrative charges (2% of total capital investment) |  | = | 542651.4074 | CC Manual
Property tax (1% of total capital investment) |  | = | 271325.7037 | CC Manual
Insurance (1% of total capital investment) |  | = | 271325.7037 | CC Manual
Capital Recovery Factor (CRF) = [ i (1+i)n ] / [ (1+i)n - 1 ]
i = Interest rate (%) | 5.5
n = Equipment life (years) | 15
CRF = | 0.099626 | = | 2703098.5378 | CC Manual
TOTAL INDIRECT ANNUAL OPERATING COSTS |  | = | 4261491.3356
TOTAL ANNUALIZED OPERATING COSTS (2012 $) |  | = | 5954321.618
Composite CE Index for 2012 (cost year of equation) |  | = | 584.6
Composite CE Index for 2016 (cost year of review) |  | = | 536.4
TOTAL ANNUALIZED OPERATING COSTS (2016 $) |  | = | 5463390.5506
TOTAL UNCONTROLLED SO2 EMISSIONS, tons |  | = | 259.296
SO2 REMOVAL EFFICIENCY, % |  | = | 90
TOTAL SO2 REMOVED, tons |  | = | 233.3664
SO2 COST-EFFECTIVENESS, $/ton removed |  | = | 23411.2132

## Wet Scrubber
Wet Scrubber - UAF
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 29.6 | <-- User Input (Conservative assumption based on a total heat input of 296 MMBtu/hr)
Retrofit Factor | B |  | 1 | <-- User Input (An "average" retrofit has a factor of 1.0 Proposed UAF boiler is not a retrofit, however modifications to existing equipment (e.g., ductwork and stack) and operating conditions (e.g., temperature and flowrate) may need to be modified. Retrofit of scrubbers on existing units can increase the capital cost up to 30%. Therefore the Department assumed a retrofit factor of 0.7 for the dual fuel-fired boiler at UAF. https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf) Sargent and Lundy has a drop down menu for selection of an additional waste water treatment plant facility, but no capital or operational cost are implemented so it is not reproduced here.
Gross Heat Rate | C | (Btu/kWh) | 10000 | <-- User Input
SO2 Rate | D | (lb/MMBtu) | 0.2 | <-- User Input
Type of Coal | E |  | sub-bituminous | <-- User Input
Coal Factor | F |  | 1.05 | Bituminous = 1, Sub-Bituminous = 1.05, Lignite = 1.07
Heat Rate Factor | G |  | 1 | C/10000
Heat Input | H | (Btu/hr) | 296000000 | A*C*1000
Limestone Rate | K | (ton/hr) | 0.051859 | 17.52*A*D*G/2000
Waste Rate | L | (ton/hr) | 0.093917 | 1.811*K
Aux Power | M | (%) | 1.1372 | (1.05e^(0.155*D))*F*G
Makeup Water Rate | N | (1000 gph) | 2.3315 | (1.674*D+74.68)*A*F*G/1000
Limestone Cost | P | ($/ton) | 20 | <-- User Input (https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Waste Disposal Cost | Q | ($/ton) | 30 | <-- User Input (https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Aux Power Cost | R | ($/kWh) | 0.21 | <-- User Input (http://www.gvea.com/rates/rates)
Makeup Water Cost | S | ($/1000 gal) | 7.17 | <-- User Input (http://www.newsminer.com/water-rates/article_11a2ba10-c211-562e-8da9-87dd16a7b104.html)
Operating Labor Rate | T | ($/hr) | 60 | Labor cost including all benefits
IPM Model - Updates to Cost and Performance for APC Technologies - Wet FGD for SO2 Control Cost Development Methodology, August 2010, prepared by Sargent & Lundy LLC for US EPA. https://www.epa.gov/sites/production/files/2015-07/documents/chapter_5_appendix_5-1a_wet_fgd.pdf
Capital Cost Calculation (2012 dollars) |  |  |  | Comments
Includes - Equipment, installation, building, foundations, electrical, minor physical/chemical waste water treatment, and a retrofit difficulty factor of 0.7
BMR ($) = 550,000*(B)*((F*G)^0.6)*((D/2)^0.02)*(A^0.716) |  | = | 6116755.6817 | Base absorber island cost
BMF ($) = 190,000*(B)*((D*G)^0.3)*(A^0.716) |  | = | 1325889.9073 | Base reagent preparation cost
BMW ($) = 100,000*(B)*((D*G)^0.45)*(A^0.716) |  | = | 548161.2898 | Base waste handling cost
BMB ($) = 1,010,000*(B)*((F*G)^0.4)*(A^0.716) |  | = | 11647747.7977 | Base balance of plan cost including: ID or booster fans, new wet chimney, piping, ductwork, minor waste water treatment, etc…
BMWW ($) = |  | = | 0 | Base wastewater treatment facility, beyond minor physical/chemcial treatment
Base Module (BM) ($) = BMR + BMF + BMW + BMB + BMWW |  | = | 19638554.6765 | Total base cost including retrofit factor
BM ($/kW) |  | = | 663.4647 | Base cost per kW
Total Project Cost
A1 = 10% of BM |  | = | 1963855.4677 | Engineering and construction management costs (CC Manual)
A2 = 10% of BM |  | = | 1963855.4677 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc. (CC Manual)
A3 = 10% of BM |  | = | 1963855.4677 | Contractor profit and fees (CC Manual)
CECC ($) - Excludes Owner's Costs = BM + A1 + A2 + A3 |  | = | 25530121.0795 | Capital, engineering, and construction costs subtotal
CECC ($/kW) - Excludes Owner's Costs = |  | = | 862.5041 | Capital, engineering, and construction costst subtotal per kW
B1 = 5% of CECC |  | = | 1276506.054 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
TPC ($) - Includes Owners Costs = CECC + B1 |  | = | 26806627.1334 | Total project cost without Allowance for Funds Used During Construction (AFUDC)
TPC ($/kW) - Include Owner's Costs = |  | = | 905.6293 | Total project cost per kW without AFUDC
B2 = 10% of (CECC + B1) |  | = | 2680662.7133 | AFUDC (based on a 3 year engineering and construction cycle)
TPC ($) - Includes Owner's Costs and AFUDC = CECC + B1 + B2 |  | = | 29487289.8468 | Total project cost
TPC ($/kW) - Includes Owner's Costs and AFUDC = |  | = | 996.1922 | Total project cost per kW
Wet Scrubber - UAF
Direct Annual Costs
Fixed O&M Cost
FOMO ($/kW yr) = (6 additional operators)*(2080)*T/(A*1000) |  | = | 25.2973 | Fixed O&M additional operating labor costs
FOMM ($/kW yr) = BM*0.015/(B*A*1000) |  | = | 9.952 | Fixed O&M additional maintenance material and labor costs
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  | = | 0.87834 | Fixed O&M additional administrative labor costs
FOMWW ($/kW yr) = |  |  | 0 | Fixed O&M costs for wastewater treatment facility
FOM ($/kW yr) = FOMO + FOMM + FOMA + FOMWW |  | = | 36.1276 | Total Fixed O&M costs ($/kW yr)
Variable O&M Cost
VOMR ($/MWh) = K*P/A |  | = | 0.03504 | Variable O&M costs for limestone reagent
VOMW ($/MWh) = L*Q/A |  | = | 0.095186 | Variable O&M costs for waste disposal
VOMP ($/MWh) = M*R*10 |  | = | 2.3881 | Variable O&M costs for additional auxiliary power required including additional fan power (Refer to Aux Power % above)
VOMM ($/MWh) = N*S/A |  | = | 0.56475 | Variable O&M costs for makeup water
VOMWW ($/MWh) = |  | = | 0 | Variable O&M costs for wastewater treatment facility
VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM + VOMWW |  | = | 3.0831 | Total Variable O&M Costs ($/MW yr)
Indirect Annual Costs
Overhead (60% of total labor and material costs) |  | = | 641626.356 | CC Manual
Administrative charges (2% of total capital investment) |  | = | 589745.7969 | CC Manual
Property tax (1% of total capital investment) |  | = | 294872.8985 | CC Manual
Insurance (1% of total capital investment) |  | = | 294872.8985 | CC Manual
Capital Recovery Factor (CRF) = [ i (1+i)n ] / [ (1+i)n - 1 ]
i = Interest rate (%) | 5.5
n = Equipment life (years) | 15
CRF = | 0.099626 | = | 2937688.8727 | CC Manual
TOTAL INDIRECT ANNUAL OPERATING COSTS |  | = | 4758806.8226
TOTAL ANNUALIZED OPERATING COSTS (2012 $) |  | = | 6627625.2574
Composite CE Index for 2012 (cost year of equation) |  | = | 584.6
Composite CE Index for 2016 (cost year of review) |  | = | 536.4
TOTAL ANNUALIZED OPERATING COSTS (2016 $) |  | = | 6081180.6159
TOTAL UNCONTROLLED SO2 EMISSIONS, tons |  | = | 259.296
SO2 REMOVAL EFFICIENCY, % |  | = | 99
TOTAL SO2 REMOVED, tons |  | = | 256.703
SO2 COST-EFFECTIVENESS, $/ton removed |  | = | 23689.5543 | Does not include costs associated with building and maintaining a wastewater treatment facility

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only