## 5-1 Available-SO2
Table 5-1. Summary of Available SO2 Emission Control Technology
Emission Unit |  | Available Emission Control Technology
1, 2 | Simple Cycle Gas Turbine | ULSD
Low Sulfur Fuel
Good Combustion Practices
5, 6 | Combined Cycle Gas Turbine | ULSD
LSR
Limited Operation
Good Combustion Practices
7 | Emergency Generator Engine | ULSD
Low Sulfur Fuel
Limited Operation
Good Combustion Practices
11, 12 | Propane-Fired Boiler | Low Sulfur Fuel
Good Combustion Practices

## 5-2 Feasible-SO2
Table 5-2. Summary of Technically Feasible SO2 Emission Control Technology
Emission Unit |  | Technically Feasible Control Technology
1, 2 | Simple Cycle Gas Turbine | ULSD
Low Sulfur Fuel
Good Combustion Practices
5, 6 | Combined Cycle Gas Turbine | ULSD
Good Combustion Practices and LSR
7 | Emergency Generator Engine | ULSD
Low Sulfur Fuel
Limited Operation
Good Combustion Practices
11, 12 | Propane-Fired Boiler | Low Sulfur Fuel
Good Combustion Practices

## 5-3 Ranking-SO2
Table 5-3. Ranking of Technically Feasible SO2 Emission Control Technology
Emission Unit |  | Emission Control Technology | Control Efficiency (pct.) | SO2 Emissions (tpy) | SO2 Emissions Reduction (tpy)
1 | Simple Cycle Turbine | ULSD (0.0015 wt. pct. S) | 99.7 | 4.4592 | 1481.9408
|  | Low Sulfur Fuel (0.05 wt. pct. S) | 90 | 148.64 | 1337.76
|  | Good Combustion Practices (0.50 wt. pct. S) (existing) | 0 | 1486.4 | 0
2 | Simple Cycle Turbine | Limited Operation + ULSD (0.0015 wt. pct. S) | 99.7 | 4.0683 | 1352.0317
|  | Limited Operation + Low Sulfur Fuel (0.05 wt. pct. S) | 90 | 135.61 | 1220.49
|  | Good Combustion Practices (0.50 wt. pct. S) (existing) | 0 | 1356.1 | 0
5, 6 | Combined Cycle Gas Turbines (per turbine) | ULSD (0.0015 wt. pct. S) | 50 | 3 | 3
|  | LSR (0.0030 wt. pct. S) + Good Combustion Practices (existing) | 0 | 6 | 0
7 | Emergency Generator Engine | ULSD (0.0015 wt. pct. S) + Limited Operation | 98.5 | 0.00015 | 0.00985
|  | Low Sulfur Fuel (0.05 wt. pct. S) + Limited Operation | 50 | 0.005 | 0.005
|  | Limited Operation (0.1 wt. pct. S) (existing) | 0 | 0.01 | 0
11, 12 | Propane-Fired Boiler | Low Sulfur Fuel (existing) | 0 | 0.0002 | 0

## 5-4 EU ID 1 ULSD CE
Table 5-4. Annualized Costs for ULSD on
the Diesel-fired Simple Cycle Gas Turbine (EU ID 1)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU ID 1 - GE Frame 7 CT) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities
| (a) | ULSD Costs: | 45282461.54 | GAL | 0.2668 | 12081360.7389 |  |  | 12081360.7389
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 12081360.7389
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.083679
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) (refer to Table 5-10) | [7 empty] | TIAC = | 1345052.1863
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 13426412.9251
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 1481.9408
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 9060.0198
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON ACTUAL HISTORIC RUN TIMES, AVOIDING 142.3 TONS PER YEAR)1 | [7 empty] | (TAC)/(TPY) = | 11842.953
COST EFFECTIVENESS ($ PER TON PM AVOIDED BASED ON 6 TONS SO2 AVOIDED = 1 TON PM AVOIDED)2 | [7 empty] | (TAC)/(TPY) = | 71057.718
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 5.5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 20 | years
1 | Annual average run hours for EU 1 from 2009-2016 is 833 hours, and the peak in the last four years has been 587 hours. 833 hours equates to 4,305,969 gallons of fuel, a TDAC of $1,148,832, and a TAC of $3,068,356. The capital cost of bulk fuel storage would be less and the TIAC for actuals is shown in Table 5-10.
2 | Alaska Department of Environmental Conservation, Amendments to State Air Quality Control Plan Vol. III: Appendix III.D.5.7, page 52. In reference to fuel oil emissions, "Ambient sampling and modeling in FNSB indicates that reduction of six tons of SOX emissions result in the same reduction in ambient PM2.5 concentration as the reduction of one ton of directly emitted PM2.5".
Note on E13: Author: Based on unlimited operation. 672 MMBtu/hr @ 8760 hrs/yr and HHV of 0.13 MMBtu/gallon.
Note on G13: Author: Difference in cost for delivery of ULSD compared to #2 fuel oil based on data provided by GVEA.

## 5-5 EU ID 2 ULSD CE
Table 5-5. Annualized Costs for ULSD on
the Diesel-fired Simple Cycle Gas Turbine (EU ID 2)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU ID 2 - GE Frame 7 CT) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities
| (a) | ULSD Costs: | 41312492.31 | GAL | 0.2668 | 11022172.9483 |  |  | 11022172.9483
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 11022172.9483
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.083679
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) (refer to Table 5-10) | [7 empty] | TIAC = | 1345052.1863
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 12367225.1346
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 1352.0317
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 9147.1414
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON ACTUALS, AVOIDING 422.3 TONS PER YEAR)1 | [7 empty] | (TAC)/(TPY) = | 9343.3112
COST EFFECTIVENESS ($ PER TON PM AVOIDED BASED ON 6 TONS SO2 AVOIDED = EQUIVALENT TO 1 TON PM AVOIDED)2 | [7 empty] | (TAC)/(TPY) = | 56059.8673
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 5.5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 20 | years
1 | Annual average run hours for EU 2 from 2009-2016 is 2472 hours, and the peak in the last four years has been 2873 hours. 2472 hours equates to 12,778,338 gallons of fuel, a TDAC of $3,409,261, and a TAC of $5,328,784. The capital cost of bulk fuel storage would be less and the TIAC for actuals is shown in Table 5-10.
2 | Alaska Department of Environmental Conservation, Amendments to State Air Quality Control Plan Vol. III: Appendix III.D.5.7, page 52. In reference to fuel oil emissions, "Ambient sampling and modeling in FNSB indicates that reduction of six tons of SOX emissions result in the same reduction in ambient PM2.5 concentration as the reduction of one ton of directly emitted PM2.5".
Note on E13: Author: Based on limited operations. 672 MMBtu/hr @ 7992 hrs/yr and HHV of 0.13 MMBtu/gal
Note on G13: Author: Difference in cost for delivery of ULSD compared to #2 fuel oil based on data provided by GVEA.

## 5-10 TCI ULSD EU1-2
Table 5-10. Capital Cost for New ULSD Storage Based on
Maximum Fuel Use and Actual Fuel Use
| North Pole EUs 1 and 2 Maximum Fuel Use | Zehnder EUs 1 and 2 Maximum Fuel Use | North Pole EUs 1 and 2 Actual Fuel Use | Zehnder EUs 1 and 2 Actual Fuel Use
Capital Cost Estimate | 30425000 |  | 21050000
Heat Input, MMBtu/day (combined for each set of combustion turbines) | 32256 | 12864 | 32256 | 12864
Percentage of Heat Input | 71.49% | 28.51% | 71.49% | 28.51%
Capital Cost (apportioned based on heat input ratio) | 21750638.2979 | 8674361.7021 | 15048510.6383 | 6001489.3617
Capital Cost (apportioned per combustion turbine) | 10875319.1489 | 4337180.8511 | 7524255.3191 | 3000744.6809
Capital Recovery (per combustion turbine) | 910039.4203 | 362932.3879 | 629624.6441 | 251100.3045
Administrative Charges, Property Taxes, Insurance (per combustion turbine) | 435012.766 | 173487.234 | 300970.2128 | 120029.7872
Total Annual Indirect Cost (per combustion turbine) | 1345052.1863 | 536419.6219 | 930594.8569 | 371130.0917
Capital recovery factor | 0.083679
Data Inputs for Capital Recovery Factor:
Annual Interest Rate (EPA OAQPS Control |  | 5.5 | pct.
Cost Manual)
Project Life (EPA OAQPS Control Cost |  | 20 | years
Manual)
Administrative Charges, Property Taxes |  | 4%
Insurance (percentage of total capital
cost)
Capital cost estimate for 1.27 million gallons of storage capacity.

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only