## Injection after Combination
Appendix III.D.7, Public Notice Draft May 10, 2019
Dry Sorbent Injection System 1
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 142.4 | <-- User Input
Retrofit Factor | B |  | 2 | <-- User Input (An "average" retrofit has a factor of 1.0.)
Gross Heat Rate | C | (Btu/kWh) | 3415 | <-- User Input
SO2 Rate | D | (lb/MMBtu) | 0.39 | <-- User Input
Type of Coal | E |  | sub-bituminous | <-- User Input
Particulate Capture | F |  | Baghouse | <-- User Input
Milled Trona | G |  | TRUE | Based on in-line milling equipment
Removal Target | H | (%) | 40 | Maximum Removal Targets: Unmilled Trona with an ESP = 65% Milled Trona with an ESP = 80% Unmilled Trona with a Baghouse = 80% Milled Trona with Baghouse = 90%
Heat Input | J | (Btu/hr) | 486000000 | A*C*1000 or User Input
NSR | K |  | 1.5 | 1.5 (to account for less than optimum mixing and residence time in the combined orientation and breaking the filter cake in all orientations)
Trona Feed Rate | M | (ton/hr) | 0.34148 | (1.2011x10^-06)*K*A*C*D
Sorbent Waste Rate | N | (ton/hr) | 0.24554 | (0.7387-0.00073696*H/K)*M Based on a final reaction product of Na2SO4 and unreacted dry sorbent as Na2CO3. Waste product adjusted for a maximum of 5% inert in the Trona sorbent.
Fly Ash Waste Rate Include in VOM? | P | (ton/hr) | 0.9 | (A*C)*Ash incoal*(1-Boiler Ash Removal)/(2*HHV) For Bituminous Coal: Ash in Coal = 0.12; Boiler Ash Removal = 0.2, HHV = 11,000 For PRB Coal: Ash in Coal = 0.06; Boiler Ash Removal = 0.2, HHV = 8,400 For Lignite Coal: Ash in Coal = 0.08; Boiler Ash Removal = 0.2, HHV = 7,200 Usibelli Coal: Ash in Coal = 0.07; Boiler Ash Removal = 0.6; HHV = 7,560
Aux Power Include in VOM? | Q | (%) | 0.047961 | =if Milled Trona M*20/A else M*18/A
Trona Cost | R | ($/ton) | 451 | <-- User Input (based on delivered price paid by Healy)
Waste Disposal Cost | S | ($/ton) | 50 | <-- User Input (Disposal cost with fly ash = $50. Without fly ash, the sorbent waste alone will be more difficult to dispose = $100)
Aux Power Cost | T | ($/kWh) | 0.09385 | <-- User Input
Operating Labor Rate | U | ($/hr) | 63 | <-- User Input (Labor cost including all benefits)
Location Adjusment Factor | LAF |  | 2.2 | Factor applied to Base Module Cost - Location Adjusment Factor for Fairbanks, AK from DoD Facilities Pricing Guide\2\/2/, UFC 3-701-01, Change 8, July 2015.
IPM Model - Updates to Cost and Performance for APC Technologies - Dry Sorbent Injection for SO2 Control Cost Development Methodology, March 2013, prepared by Sargent & Lundy LLC for USEPA.
Capital Cost Calculation (2012 dollars) |  |  |  | Comments
Includes - Equipment, installation, building, foundations, electrical, and retrofit difficulty
Base Module (BM) ($) |  | = | 26915857.3982 | Base DSI module includes all equipment from unloading to injection
Unmilled Trona = IF(M>25,(745000*B*M*LAF),(7500000*B*LAF*M^0.284)
Milled Trona = IF(M>25,(820000*B*M*LAF),(8300000*B*LAF*M^0.284)
BM ($/kW) |  | = | 189.0159 | Base module cost per kW
Total Project Cost
A1 = 5% of BM |  | = | 1345792.8699 | Engineering and construction management costs
A2 = 5% of BM |  | = | 1345792.8699 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc.
A3 = 5% of BM |  | = | 1345792.8699 | Contractor profit and fees
CECC ($) - Excludes Owner's Costs = BM + A1 + A2 + A3 |  | = | 30953236.008 | Capital, engineering, and construction costst subtotal
CECC ($/kW) - Excludes Owner's Costs |  | = | 217.3682 | Capital, engineering, and construction costst subtotal per kW
B1 = 5% of CECC |  | = | 1547661.8004 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
TPC ($) - Includes Owners Costs = CECC + B1 |  | = | 32500897.8084 | Total project cost without AFUDC
TPC ($/kW) - Include Owner's Costs |  | = | 228.2366 | Total project cost per kW without AFUDC
B2 = 0% of (CECC + B1) |  | = | 0 | AFUDC (Zero for less than 1 year engineering and construction cycle)
TPC ($) = CECC + B1 + B2 |  | = | 32500897.8084 | Total project cost
TPC ($/kW) |  | = | 228.2366 | Total project cost per kW
Direct Annual Costs
Fixed O&M Cost
FOMO ($/kW yr) = (2 additional operators)*(2080)*U/(A*1000) |  | = | 1.8404 | Fixed O&M additional operating labor costs
FOMM ($/kW yr) = BM*0.01/(B*A*1000) |  | = | 0.94508 | Fixed O&M additional maintenance material and labor costs
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  | = | 0.066554 | Fixed O&M additional administrative labor costs
FOM ($/kW yr) = FOMO + FOMM + FOMA |  | = | 2.8521 | Total Fixed O&M costs
Variable O&M Cost
VOMR ($/MWh) = M*R/A |  | = | 1.0815 | Variable O&M costs for Trona reagent
VOMW ($/MWh) = (N+P)*S/A |  | = | 0.40223 | Variable O&M costs for waste disposal that includes both the sorbent and the fly ash waste not removed prior to the sorbent injection
VOMP ($/MWh) = Q*T*10 |  | = | 0.045012 | Variable O&M costs for additional auxiliary power required (Refer to Aux Power % above)
VOM ($/MWh) = VOMR + VOMW + VOMP |  | = | 1.5288
Indirect Annual Costs
Overhead (80% of total operation and maintenance labor) |  | = | 324909.3107
Administrative charges (2% of total capital investment) |  | = | 650017.9562
Insurance (1% of total capital investment) |  | = | 325008.9781
Property tax (1% of total capital investment) |  | = | 325008.9781
Capital recovery |  | = | 5289521.1183
(16.275% of total capital investment: 10 yr at 10% interest)
TOTAL INDIRECT ANNUAL OPERATING COSTS |  | = | 6914466.3414
TOTAL ANNUALIZED OPERATING COSTS (2012 $) |  | = | 9227624.1291
Composite CE Index for 2012 (cost year of equation) |  | = | 584.6
Composite CE Index for 2015 (cost year of review) |  | = | 578.4
TOTAL ANNUALIZED OPERATING COSTS (2015 $) |  | = | 9129760.1715
TOTAL UNCONTROLLED SO2 EMISSIONS, tons |  | = | 830.1852
SO2 REMOVAL EFFICIENCY, % |  | = | 40
TOTAL SO2 REMOVED, tons |  | = | 332.0741
SO2 COST-EFFECTIVENESS, $/ton removed |  | = | 27493.143

## Large Boiler only
Appendix III.D.7, Public Notice Draft May 10, 2019
Dry Sorbent Injection System 1
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 74.6 | <-- User Input
Retrofit Factor | B |  | 2 | <-- User Input (An "average" retrofit has a factor of 1.0.)
Gross Heat Rate | C | (Btu/kWh) | 3415 | <-- User Input
SO2 Rate | D | (lb/MMBtu) | 0.32 | <-- User Input
Type of Coal | E |  | sub-bituminous | <-- User Input
Particulate Capture | F |  | Baghouse | <-- User Input
Milled Trona | G |  | TRUE | Based on in-line milling equipment
Removal Target | H | (%) | 40 | Maximum Removal Targets: Unmilled Trona with an ESP = 65% Milled Trona with an ESP = 80% Unmilled Trona with a Baghouse = 80% Milled Trona with Baghouse = 90%
Heat Input | J | (Btu/hr) | 255000000 | A*C*1000 or User Input
NSR | K |  | 1.5 | 1.5 (to account for deposition in the individual orientation)
Trona Feed Rate | M | (ton/hr) | 0.14701 | (1.2011x10^-06)*K*A*C*D
Sorbent Waste Rate | N | (ton/hr) | 0.10571 | (0.7387-0.00073696*H/K)*M Based on a final reaction product of Na2SO4 and unreacted dry sorbent as Na2CO3. Waste product adjusted for a maximum of 5% inert in the Trona sorbent.
Fly Ash Waste Rate Include in VOM? | P | (ton/hr) | 0.47222 | (A*C)*Ash incoal*(1-Boiler Ash Removal)/(2*HHV) For Bituminous Coal: Ash in Coal = 0.12; Boiler Ash Removal = 0.2, HHV = 11,000 For PRB Coal: Ash in Coal = 0.06; Boiler Ash Removal = 0.2, HHV = 8,400 For Lignite Coal: Ash in Coal = 0.08; Boiler Ash Removal = 0.2, HHV = 7,200 Usibelli Coal: Ash in Coal = 0.07; Boiler Ash Removal = 0.6; HHV = 7,560
Aux Power Include in VOM? | Q | (%) | 0.039414 | =if Milled Trona M*20/A else M*18/A
Trona Cost | R | ($/ton) | 451 | <-- User Input (based on delivered price paid by Healy)
Waste Disposal Cost | S | ($/ton) | 50 | <-- User Input (Disposal cost with fly ash = $50. Without fly ash, the sorbent waste alone will be more difficult to dispose = $100)
Aux Power Cost | T | ($/kWh) | 0.09385 | <-- User Input
Operating Labor Rate | U | ($/hr) | 63 | <-- User Input (Labor cost including all benefits)
Location Adjusment Factor | LAF |  | 2.2 | Factor applied to Base Module Cost - Location Adjusment Factor for Fairbanks, AK from DoD Facilities Pricing Guide\2\/2/, UFC 3-701-01, Change 8, July 2015.
IPM Model - Updates to Cost and Performance for APC Technologies - Dry Sorbent Injection for SO2 Control Cost Development Methodology, March 2013, prepared by Sargent & Lundy LLC for USEPA.
Capital Cost Calculation (2012 dollars) |  |  |  | Comments
Includes - Equipment, installation, building, foundations, electrical, and retrofit difficulty
Base Module (BM) ($) |  | = | 21186595.4968 | Base DSI module includes all equipment from unloading to injection
Unmilled Trona = IF(M>25,(745000*B*M*LAF),(7500000*B*LAF*M^0.284)
Milled Trona = IF(M>25,(820000*B*M*LAF),(8300000*B*LAF*M^0.284)
BM ($/kW) |  | = | 284.0026 | Base module cost per kW
Total Project Cost
A1 = 5% of BM |  | = | 1059329.7748 | Engineering and construction management costs
A2 = 5% of BM |  | = | 1059329.7748 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc.
A3 = 5% of BM |  | = | 1059329.7748 | Contractor profit and fees
CECC ($) - Excludes Owner's Costs = BM + A1 + A2 + A3 |  | = | 24364584.8214 | Capital, engineering, and construction costst subtotal
CECC ($/kW) - Excludes Owner's Costs |  | = | 326.603 | Capital, engineering, and construction costst subtotal per kW
B1 = 5% of CECC |  | = | 1218229.2411 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
TPC ($) - Includes Owners Costs = CECC + B1 |  | = | 25582814.0624 | Total project cost without AFUDC
TPC ($/kW) - Include Owner's Costs |  | = | 342.9332 | Total project cost per kW without AFUDC
B2 = 0% of (CECC + B1) |  | = | 0 | AFUDC (Zero for less than 1 year engineering and construction cycle)
TPC ($) = CECC + B1 + B2 |  | = | 25582814.0624 | Total project cost
TPC ($/kW) |  | = | 342.9332 | Total project cost per kW
Direct Annual Costs
Fixed O&M Cost
FOMO ($/kW yr) = (2 additional operators)*(2080)*U/(A*1000) |  | = | 3.5131 | Fixed O&M additional operating labor costs
FOMM ($/kW yr) = BM*0.01/(B*A*1000) |  | = | 1.42 | Fixed O&M additional maintenance material and labor costs
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  | = | 0.12243 | Fixed O&M additional administrative labor costs
FOM ($/kW yr) = FOMO + FOMM + FOMA |  | = | 5.0556 | Total Fixed O&M costs
Variable O&M Cost
VOMR ($/MWh) = M*R/A |  | = | 0.88879 | Variable O&M costs for Trona reagent
VOMW ($/MWh) = (N+P)*S/A |  | = | 0.38735 | Variable O&M costs for waste disposal that includes both the sorbent and the fly ash waste not removed prior to the sorbent injection
VOMP ($/MWh) = Q*T*10 |  | = | 0.03699 | Variable O&M costs for additional auxiliary power required (Refer to Aux Power % above)
VOM ($/MWh) = VOMR + VOMW + VOMP |  | = | 1.3131
Indirect Annual Costs
Overhead (80% of total operation and maintenance labor) |  | = | 301717.2586
Administrative charges (2% of total capital investment) |  | = | 511656.2812
Insurance (1% of total capital investment) |  | = | 255828.1406
Property tax (1% of total capital investment) |  | = | 255828.1406
Capital recovery |  | = | 4163602.9887
(16.275% of total capital investment: 10 yr at 10% interest)
TOTAL INDIRECT ANNUAL OPERATING COSTS |  | = | 5488632.8097
TOTAL ANNUALIZED OPERATING COSTS (2012 $) |  | = | 6723906.4051
Composite CE Index for 2012 (cost year of equation) |  | = | 584.6
Composite CE Index for 2015 (cost year of review) |  | = | 578.4
TOTAL ANNUALIZED OPERATING COSTS (2015 $) |  | = | 6652595.7316
TOTAL UNCONTROLLED SO2 EMISSIONS, tons |  | = | 357.408
SO2 REMOVAL EFFICIENCY, % |  | = | 40
TOTAL SO2 REMOVED, tons |  | = | 142.9632
SO2 COST-EFFECTIVENESS, $/ton removed |  | = | 46533.6236

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only