## SCR+Water Injection TCI
Capital Costs for SCR and Water Injection on the Simple Cycle Gas Turbines (EU IDs 1 and 2)
Shaded cells indicate user inputs.
Total Capital Investment Determination - Water Injection + SCR | [7 empty] | Date:
Project: |  | GVEA Zehnder PM2.5 BACT Analysis - Frame 5 CTs (EU ID 1 and 2, cost per turbine) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Water Injection1 | 1 | EA | 1250000 | 1250000
|  | SCR2,3 | 1 | EA | 3000000 | 3000000
|  | Reagent Prep/Water Treatment/Structure | 1 | EA | 2193500 | 2193500 |  | TOTAL = | 6443500
| (b) | Instrumentation
|  | Total Instrumentation4 |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | Injection System Freight |  | % MATL COST |  |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab |  | MH |  |  | 0
|  | Labor - onsite |  | MH |  |  | 0
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR | 0.5% | % |  | 15000
[8 empty] | TOTAL = | 15000
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 10 | Days | 1800 |  | 18000
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 8 | Days | 2500 |  | 20000
[8 empty] | TOTAL = | 38000
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope except SCR spares and SCR vendor rep. fees |  |  |  |  | PEMC = | 6496500
(2) | Direct Installation Costs5,6
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Functional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) | [7 empty] | DIC = | 7250000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 13746500
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 22% | % TDC |  |  | 3024230
(4) | Performance tests |  | 1 | EA | 10000 |  | 10000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 3034230
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs7 |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  | 30% | % PEMC |  |  | 1948950
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 1948950
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 18729680
Footnotes:
1 | For the water injection option, costs have been included for a water treatment system. Zehnder does not have any water treatment system, thus would need reverse osmosis, electro de-ionization, storage tanks, small pumps, and interconnecting piping. It is unlikely this equipment and reagent preparation equipment would fit inside the existing turbine building as it is all essential for normal maintenance and operation.
2 | Source of SCR Capital Costs: ATCO Emissions Management. These were supply-only costs given in a range for the Frame 5s. The highpoint of the range provided ($2 – $3 million) was used.
3 | Costs for reagent prep equipment and additional structures are discussed in a separately submitted CBI package.
4 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
5 | Construction costs associated directly with SCR installation were conservatively estimated at double the capital cost. This seems reasonable given the current footprint of the turbine building. Additional structure costs were included under part (1)(a) This should be viewed as an engineering estimate only.
6 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This is based on the assumption that some water treatment system work in addition to SCR treated water needs will be required to add water injection. This should be viewed as an engineering estimate only.
7 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
8 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements. However the reagent solutions will require continual heating to keep them in liquid form and a notable station load compared to the unit actual operation is expected.
Note on E28: Author: Cost of startup spares indicated as a percentage of equipment cost per data from similar project.
Note on E31: Author: days based on similar project
Note on E32: Author: days based on similar project
Note on K48: Author: The water injection installation costs would double the capital required due to new water treatment system. Assume that SCR installation costs are 2x the SCR equipment costs.
Note on E55: Author: Blended rate based on18% of SCR TDC that was used in similar project and 33% of water injection TDC based on Table 6-4 of EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines (EPA-453/R-93-007)
Note on E62: Author: Based on OAQPS Control Cost Manual standard contingency estimate.

## SCR+Water Injection CE
SCR and Water Injection on the Simple Cycle Gas Turbines (EU IDs 1 and 2)
Shaded cells indicate user inputs
Cost Effectiveness Determination - Water Injection + SCR | [7 empty] | Date:
Project: |  | GVEA Zehnder PM2.5 BACT Analysis - Frame 5 CTs (EU ID 1 and 2, cost per turbine) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 730 | MH | 105 |  | 76650 |  | 76650
(2) | Supervisory Labor |  | 183 | MH | 125 |  | 22875 |  | 22875
(3) | Maintenance Labor (water treatment) |  | 13950.8323 | 1000 GALS | 2.3704 |  | 33069.7289 |  | 33069.7289
(4) | Maintenance Labor (SCR system) |  | 365 | MH | 105 |  | 38325 |  | 38325
(5) | Maintenance Materials |  |  | LOT |  | 0 | Included in water treatment below |  | 0
(6) | Utilities
| a) | Water Use: | 10814.5987 | 1000 GALS | 1.3004 | 14062.8747 |  |  | 14062.8747
| b) | Water Pump Energy: | 33566.568 | kWh | 0.18 | 6041.9822 |  |  | 6041.9822
| c) | CT Fuel Use: | 17136350.365 | GALS
| d) | Fuel Penalty: | 437833.7518 | GALS | 1.7 | 744317.3781 |  |  | 744317.3781
| e) | Water Treatment Capacity: | 18136.082 | 1000 GALS | 6.6711 | 120987.9652 |  |  | 120987.9652
| f) | Water Waste Disposal: | 5259.4638 | 1000 GALS | 12.9359 | 68035.7705 |  |  | 68035.7705
| g) | Urea/DEF: | 17.7276 | TON | 356 | 6311.0256 |  |  | 6311.0256
| h) | SCR Energy Use8: |  | kWh | 0.18 | Excluded in this estimate. |  |  | 0
(7) | Catalyst Replacement Costs (every 3 years)
| (a) | Replacement of SCR Catalyst: % of total equipment cost | 30% | % total equip | 3000000 | 900000 |  |  | 284088.6672
| (b) | Replacement labor for SCR Catalyst | 180 | MH | 105 |  | 18900 |  | 5965.862
| (c) | Transport cost direct to site (SCR catalyst) | 13% | % replacement |  |  | 117000 |  | 36931.5267
| (d) | Transport cost for spent SCR catalyst | 13% | % replacement |  |  | 117000 |  | 36931.5267
Sinking Fund Factor [see inputs below]: |  |  | 0.31565
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 1494594.308
INDIRECT ANNUAL COSTS
(8) | Overhead |  | 30% | % WT Labor |  |  | 9920.9187 |  | 9920.9187
(9) | Administrative Charges, Property Taxes, Insurance |  | 4% | % total capital |  |  | 749187.2 |  | 749187.2
| Capital Recovery Factor [see inputs below] |  | 0.083679
(10) | Capital Recovery | [6 empty] | CRF * TCI = | 1567287.0742
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 2326395.1928
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 3820989.5008
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 981.35
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 3893.6052
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 5.5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 20 | years
|  | Catalyst Life | 3 | years
|  | Asset Utilization | 100 | %
Footnotes:
1 | For the water injection option, costs have been included for a water treatment system. Zehnder does not have any water treatment system, thus would need reverse osmosis, electro de-ionization, storage tanks, small pumps, and interconnecting piping. It is unlikely this equipment and reagent preparation equipment would fit inside the existing turbine building as it is all essential for normal maintenance and operation.
2 | Source of SCR Capital Costs: ATCO Emissions Management. These were supply-only costs given in a range for the Frame 5s. The highpoint of the range provided ($2 – $3 million) was used.
3 | Costs for reagent prep equipment and additional structures are discussed in a separately submitted CBI package.
4 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
5 | Construction costs associated directly with SCR installation were conservatively estimated at double the capital cost. This seems reasonable given the current footprint of the turbine building. Additional structure costs were included under part (1)(a) This should be viewed as an engineering estimate only.
6 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This is based on the assumption that some water treatment system work in addition to SCR treated water needs will be required to add water injection. This should be viewed as an engineering estimate only.
7 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
8 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements. However the reagent solutions will require continual heating to keep them in liquid form and a notable station load compared to the unit actual operation is expected.
Note on E10: Author: Have historically used 2 hours per day for operating.
Note on G10: Author: Labor cost from similar project
Note on G11: Author: Labor cost from similar project
Note on E12: Author: Water use x 1.29 to account for waste water labor as well. See table 6-5 of EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.
Note on G12: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 0.7 $/1000gal, Table 6-5, note g.
Note on E13: Author: Have historically used 1 hours per day for maintenance
Note on G13: Author: Labor cost from similar project
Note on E16: Author: used fuel/water ratio for similarly sized GE turbine in EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines (Table 6-2)
Note on G16: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 0.384 $/1000gal, Table 6-3
Note on E17: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Use water flow of 23.8 gal/min and formula in Table 6-5.
Note on G17: Author: Current rate GVEA charges to industrial users.
Note on E18: Author: Based on 268 MMBtu/hr and fuel HHV of 137 MMBtu/1000 gals. @ 8760 hours per year.
Note on E19: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Use 3.5% of annual fuel use and water/fuel ratio of 0.73 (Table 6-2).
Note on G19: Author: EIA Monthly energy pricing report (Dec 2015).
Note on E20: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Water use plus 30% design factor and 29% waste factor.
Note on G20: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 1.97 $/1000gal, Table 6-3
Note on E21: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. 29% waste water from treatment capacity.
Note on G21: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 3.82 $/1000gal, Table 6-3
Note on E22: Author: Based on SCR controlling emissions up to 929.7 tons/yr NOx after water injection, which controls up to 795.4 tons/yr based on a 77% CE alone. 2.2 moles urea to control 1 ton NOx, 50% urea solution.
Note on G22: Author: December 2015 price according to Farmer's Coop Association.
Note on E25: Author: Miratech indicated that catalyst makes up 30% of the SCR system cost
Note on E26: Author: Replacement labor from similar project
Note on G26: Author: Labor cost from similar project
Note on E27: Author: From similar project
Note on E28: Author: From similar project
Note on E35: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Assumes 30% of water treatment labor above.
Note on E36: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.
Note on E54: Author: Common replacement timeframe

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only