## SCR TCI
Table 3-8. UAF - Capital Costs for SCR on
the Mid-sized Diesel Boiler (EU ID 3)
Shaded cells indicate user inputs.
Total Capital Investment Determination - SCR
UAF - PM2.5 BACT Analysis (EU ID 3 - Zurn Boiler)
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Total SCR System | 1 | EA | 850000 | 850000
|  | (per Fuel Tech) | [5 empty] | TOTAL = | 850000
| (b) | Instrumentation
|  | NOx CEMs System | 1 | EA | 50000 | 50000
|  | NOx CEMS Certification Testing | 1 | EA | 10000 | 10000
[8 empty] | TOTAL = | 60000
| (c) | Freight
|  | SCR Freight | 1 |  | 20000
[8 empty] | TOTAL = | 20000
| (d) | Labor
|  | Labor - shop fab |  | MH |  |  | Included above
|  | Labor - onsite |  | MH |  |  | Included above
[8 empty] | TOTAL = | 0
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR | 0.5% | % |  | 4250
[8 empty] | TOTAL = | 4250
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | Included above
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | Included above
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope. |  |  |  |  | PEMC = | 934250
(2) | Direct Installation Costs
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  |  |  | 0
|  | Functional Checkout - onsite, enter % |  | % onsite fab labor |  |  |  |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) - 2 x SCR Equipment Capital | [7 empty] | DIC = | 1700000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 2634250
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  |  | % TDC |  |  | 0 |  | Included in PEMC above.
(4) | Performance tests |  | 1 | EA | 10000 |  | 10000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 10000
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  | 30% | % TDC |  |  | 790275
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 790275
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 3434525
Note on G13: Pacini, Lain: Fuel Tech (FTEK) proposal
Note on G16: Pacini, Lain: Based on engineering estimates/experience.
Note on G17: Pacini, Lain: Based on engineering estimates/experience.
Note on K47: Pacini, Lain: Assume installation of SCR requires 2 x the SCR equipment capital.
Note on E61: Pacini, Lain: Based on +/- 30% contingency included in FTEK proposal.

## SCR CE
Table 3-9. UAF - Annualized Costs for SCR on
the Mid-sized Diesel Boiler (EU ID 3)
Shaded cells indicate user inputs
Cost Effectiveness Determination - SCR
UAF - PM2.5 BACT Analysis (EU ID 3 - Zurn Boiler)
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 730 | MH | 105 |  | 76650 |  | 76650
(2) | Supervisory Labor |  | 182.5 | MH | 125 |  | 22812.5 |  | 22812.5
(3) | Maintenance Labor |  | 365 | MH | 105 |  | 38325 |  | 38325
(4) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(5) | Utilities
| (a) | Urea Solution: | 16.4894 | TON | 356 | 5870.2406 |  |  | 5870.2406
(50% Urea solution and 2.2 moles needed per ton of NOX removed.)
| (b) | Energy: | 376680 | kWh | 0.18 | 67802.4 |  |  | 67802.4
(6) | Annual RATA Testing |  | 1 | EA | 10000 | 10000 |  |  | 10000
(7) | Catalyst Replacement Costs (every 2 years)
(per FuelTech)
| (a) | Replacement of SCR Catalyst: % of total equipment cost | 30% | % total equip | 934250 | 280275 |  |  | 136386.8613
(per MiraTech)
| (b) | Replacement labor for SCR Catalyst | 180 | MH | 105 |  | 18900 |  | 9197.0803
| (c) | Transport cost direct to site (SCR catalyst) | 13% | % replacement |  |  | 36435.75 |  | 17730.292
| (d) | Transport cost for spent SCR catalyst | 13% | % replacement |  |  | 36435.75 |  | 17730.292
Sinking Fund Factor [see inputs below]: |  |  | 0.48662
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 402504.6662
INDIRECT ANNUAL COSTS
(8) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(9) | Administrative Charges and Insurance |  | 3% | % total capital |  |  | 103035.75 |  | 103035.75
| Capital Recovery Factor [see inputs below] |  | 0.083679
(10) | Capital Recovery | [6 empty] | CRF * TCI = | 287398.751
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 390434.501
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 792939.1672
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 124.92
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 6347.5758
Data Inputs for Capital Recovery Factor and Sinking Fund Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 5.5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 20 | years
|  | Catalyst Life (from vendor) | 2 | years
|  | Asset Utilization | 100 | %
Note on E10: Pacini, Lain: Have historically used 2 hours per day for operating.
Note on G10: Courtney Kimball: Based on similar project.
Note on E11: Pacini, Lain: Assumed to be half of maintenance labor.
Note on G11: Courtney Kimball: Based on similar project.
Note on E12: Pacini, Lain: Have historically used 1 hours per day for maintenance
Note on G12: Courtney Kimball: Based on similar project.
Note on E15: Pacini, Lain: 50% urea solution and 2.2 moles needed per ton NOx controlled.
Note on G15: Pacini, Lain: December 2015 price according to Farmer's Coop Association.
Note on E17: Pacini, Lain: 43 kW energy consumption based on 70 kW required for the 295.6 MMBtu/hr CFB boiler. Assuming that the ratio of the 180.9 MMBtu/hr to the 295.6 MMBtu/hr boiler would proportionally decrease the power consumption required by the SCR. Assume 8760 hours/yr.
Note on G17: Pacini, Lain: Current Per kW price based on GVEA data.
Note on C21: Pacini, Lain: Based on FTEK proposal
Note on E23: Pacini, Lain: Miratech indicated that catalyst makes up 30% of the SCR system cost
Note on E25: Courtney Kimball: Replacement labor based on similar project.
Note on G25: Courtney Kimball: Based on similar project.
Note on E26: Courtney Kimball: Based on similar project.
Note on E27: Courtney Kimball: Based on similar project.
Note on E35: Pacini, Lain: Percentage of total capital investment

## 5-22 (hidden)
Table 5-22. Point Thomson Project - Proposed VOC BACT and Associated
Emission Rate for Each Emission Unit Type
Emission Unit |  | Fuel | CO BACT
ID | Description |  | Description | Emission Rate
101 and 102 | Solar Taurus Turbine | Fuel Gas | Catalytic Oxidation | 25 ppm at ≥10 degrees F (in SoLoNOX mode)
103 and 104 | Solar Taurus Turbine | Dual Fuel-fired | Catalytic Oxidation | 100 ppm at ≥10 degrees F (in SoLoNOX mode)
105 | Waste Incinerator | ULSD | Good Combustion Practices | 1.0 g/hp-hr
106 through 109, 115, and 116 | Distillate-fired Engines | ULSD | Good Combustion Practices | 0.19 g/KW-hr
110 through 112 | Fine Water Mist Supply and Firewater Pumps | ULSD | Good Combustion Practices | 0.00247 lb/hp-hr
113 and 114 | Flares | Fuel Gas | None | 4.0 g/KW-hr (NOX and HC, combined)
Notes:
1 Emissions are on a per unit basis.
2 ULSD fired engines have NSPS Subpart IIII VOC emission limits.

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only