## User Input Sheet
CUECost
Coal Utility Environmental Cost
Version 1, November 25, 1998 (revised 2-9-00 as CUECost3.xls)
Developed for EPA
by Raytheon Engineers & Constructors and Eastern Research Group
| Current Date: | 2019-11-07 14:40
GoTo Buttons |  |  |  | Print Options
Inputs:
Calculations and Costs:
APC Technology Choices | [8 empty] | Description of Input
|  | Suggested | Default
Description | Units | Range | Values | Input 1 | Input 2 | Input 3 | Input 4 | Input 5
FGD Process | Integer | 1 or 2 | 1 | 1 | 2 | 2 | 2 | 1
(1 = LSFO, 2 = LSD)
Particulate Control | Integer | 1 or 2 | 1 | 1 | 1 | 1 | 1 | 1
(1 = Fabric Filter, 2 = ESP)
NOx Control | Integer | 1 - 4 | 1 | 1 | 1 | 2 | 2 | 3
(1 = SCR, 2 = SNCR, 3 = LNBs, 4 = NGR)
INPUTS | [8 empty] | Description of Input
Default
Description | Units | Range | Values | Input 1 | Input 2 | Input 3 | Input 4 | Input 5
General Plant Technical Inputs
Yellow are user entered values.
Location - State | Abbrev. | All States | PA | AK | AK | AK | AK | AK
MW Equivalent of Flue Gas to Control System | MW | 100-2000 | 500 | 150 | 150 | 79 | 22 | 22 | Gross Plant Generation (MW) minus auxiliary power requirements. Prior to control system retrofit.
Net Plant Heat Rate (w/o APC) | Btu/kWhr |  | 10500 | 11833 | 11833 | 11833 | 11833 | 11833 | 497 MMBtu/hr total heat input / 42 MW net output
Plant Capacity Factor | % | 40-90% | 65% | 65% | 65% | 65% | 65% | 65%
Percent Excess Air in Boiler | % |  | 120% | 120% | 120% | 120% | 120% | 120% | Excess O2.
Air Heater Inleakage | % |  | 12% | 12% | 12% | 12% | 12% | 12%
Air Heater Outlet Gas Temperature | °F |  | 300 | 300 | 300 | 300 | 300 | 300
Inlet Air Temperature | °F |  | 80 | 80 | 80 | 80 | 80 | 80
Ambient Absolute Pressure | In. of Hg |  | 29.4 | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
Pressure After Air Heater | In. of H2O |  | -12 | -12 | -12 | -12 | -12 | -12
Moisture in Air | lb/lb dry air |  | 0.013 | 0.013 | 0.013 | 0.013 | 0.013 | 0.013
Ash Split:
Fly Ash | % |  | 80% | 80% | 80% | 80% | 80% | 80%
Bottom Ash | % |  | 20% | 20% | 20% | 20% | 20% | 20%
Seismic Zone | Integer | 1-5 | 1 | 1 | 1 | 1 | 1 | 1 | See Map.
Retrofit Factor | Integer | 1.0-3.0 | 1.3 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
(1.0 = new, 1.3 = medium, 1.6 = difficult)
Select Coal | Integer | 1-8 | 1 | 8 | 8 | 8 | 8 | 8
Is Selected Coal a Powder River Basin Coal? | Yes / No | See Column K | Yes | No | No | No | No | No | This question is necessary for a correct SCA calculation.
Coals Available in Library
Coal 1, Wyoming PRB: 8,227 Btu, 0.37% S, 5.32% ash
Coal 2, Armstrong, PA: 13,100 Btu, 2.6% S, 9.1% ash
Coal 3, Jefferson, OH: 11,922 Btu, 3.43% S, 13% ash
Coal 4, Logan, WV: 12,058 Btu, 0.89% S, 16.6% ash
Coal 5, No. 6 Illinois: 10,100 Btu, 4% S, 16% ash
Coal 6, Rosebud, MT: 8,789 Btu, 0.56% S, 8.15% ash
Coal 7, Lignite, ND: 7,500 Btu, 0.94% S, 5.9% ash
Coal 8, "User Specified": 7,560 Btu, 0.3% S, 7% ash
Economic Inputs
Cost Basis -Year Dollars | Year |  | 1998 | 2015 | 2015 | 2015 | 2015 | 2015 | Date of Startup.
Sevice Life (levelization period) | Years |  | 30 | 30 | 30 | 30 | 30 | 30
Inflation Rate | % |  | 3% | 3% | 3% | 3% | 3% | 3%
After Tax Discount Rate (current $'s) | % |  | 9.2% | 9.2% | 9.2% | 9.2% | 9.2% | 9.2%
AFDC Rate (current $'s) | % |  | 10.8% | 10.8% | 10.8% | 10.8% | 10.8% | 10.8%
First-year Carrying Charge (current $'s) | % |  | 22.3% | 22.3% | 22.3% | 22.3% | 22.3% | 22.3%
Levelized Carrying Charge (current $'s) | % |  | 16.9% | 16.9% | 16.9% | 16.9% | 16.9% | 16.9%
First-year Carrying Charge (constant $'s) | % |  | 15.7% | 15.7% | 15.7% | 15.7% | 15.7% | 15.7%
Levelized Carrying Charge (constant $'s) | % |  | 11.7% | 11.7% | 11.7% | 11.7% | 11.7% | 11.7%
Sales Tax | % |  | 6% | 6% | 6% | 6% | 6% | 6%
Escalation Rates:
Consumables (O&M) | % |  | 3% | 3% | 3% | 3% | 3% | 3%
Capital Costs:
Is Chem. Eng. Cost Index available? | Yes / No |  | Yes | Yes | Yes | Yes | Yes | Yes
If "Yes" input cost basis CE Plant Index. | Integer |  | 388 | 578.4 | 578.4 | 578.4 | 578.4 | 578.4 | The default CE Index value is the published January 1998 value.
If "No" input escalation rate. | % |  | 3% | 3% | 3% | 3% | 3% | 3%
Construction Labor Rate | $/hr |  | 35 | 60 | 60 | 60 | 60 | 60
Prime Contractor's Markup | % |  | 3% | 3% | 3% | 3% | 3% | 3% | Percent of Total Process Capital. (covers construction labor fee).
Operating Labor Rate | $/hr |  | 30 | 63 | 63 | 63 | 63 | 63
Power Cost | Mills/kWh |  | 25 | 25 | 25 | 25 | 25 | 25
Steam Cost | $/1000 lbs |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Limestone Forced Oxidation (LSFO) Inputs
SO2 Removal Required | % | 90-98% | 95% | 50% | 95% | 95% | 95% | 95%
L/G Ratio | gal / 1000 acf | 95-160 | 125 | 125 | 125 | 125 | 125 | 125
Design Scrubber with Dibasic Acid Addition? | Integer | 1 or 2 | 2 | 2 | 1 | 1 | 1 | 1
(1 = yes, 2 = no)
Adiabatic Saturation Temperature | °F | 100-170 | 127 | 127 | 127 | 127 | 127 | 127
Reagent Feed Ratio | Factor | 1.0-2.0 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
(Mole CaCO3 / Mole SO2 removed)
Scrubber Slurry Solids Concentration | Wt. % |  | 15% | 15% | 15% | 15% | 15% | 15%
Stacking, Landfill, Wallboard | Integer | 1,2,3 | 1 | 1 | 1 | 1 | 1 | 1
(1 = stacking, 2 = landfill, 3 = wallboard)
Number of Absorbers | Integer | 1-6 | 1 | 1 | 1 | 1 | 1 | 1
(Max. Capacity = 700 MW per absorber)
Absorber Material | Integer | 1 or 2 | 1 | 1 | 1 | 1 | 1 | 1
(1 = alloy, 2 = RLCS)
Absorber Pressure Drop | in. H2O |  | 6 | 6 | 6 | 6 | 6 | 6
Reheat Required ? | Integer | 1 or 2 | 1 | 1 | 1 | 1 | 1 | 1
(1 = yes, 2 = no)
Amount of Reheat | °F | 0-50 | 25 | 25 | 25 | 25 | 25 | 25
Reagent Bulk Storage | Days |  | 60 | 60 | 60 | 60 | 60 | 60
Reagent Cost (delivered) | $/ton |  | 15 | 15 | 15 | 15 | 15 | 15
Landfill Disposal Cost | $/ton |  | 30 | 30 | 30 | 30 | 30 | 30
Stacking Disposal Cost | $/ton |  | 6 | 6 | 6 | 6 | 6 | 6
Credit for Gypsum Byproduct | $/ton |  | 2 | 2 | 2 | 2 | 2 | 2
Maintenance Factors by Area (% of Installed Cost)
Reagent Feed | % |  | 5% | 5% | 5% | 5% | 5% | 5%
SO2 Removal | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Flue Gas Handling | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Waste / Byproduct | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Support Equipment | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Contingency by Area (% of Installed Cost)
Reagent Feed | % |  | 20% | 20% | 20% | 20% | 20% | 20%
SO2 Removal | % |  | 20% | 20% | 20% | 20% | 20% | 20%
Flue Gas Handling | % |  | 20% | 20% | 20% | 20% | 20% | 20%
Waste / Byproduct | % |  | 20% | 20% | 20% | 20% | 20% | 20%
Support Equipment | % |  | 20% | 20% | 20% | 20% | 20% | 20%
General Facilities by Area (% of Installed Cost)
Reagent Feed | % |  | 10% | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Support Equipment | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Engineering Fees by Area (% of Installed Cost)
Reagent Feed | % |  | 10% | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Support Equipment | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Indicates user inputs specific to Aurora.
Lime Spray Dryer (LSD) Inputs
SO2 Removal Required | % | 90-95% | 90% | 90% | 90% | 90% | 90% | 90%
Adiabatic Saturation Temperature | °F | 100-170 | 127 | 127 | 127 | 127 | 127 | 127
Flue Gas Approach to Saturation | °F | 10.-50 | 20 | 20 | 20 | 20 | 20 | 20
Spray Dryer Outlet Temperature | °F | 110-220 | 147 | 147 | 147 | 147 | 147 | 147
Reagent Feed Ratio | Factor | Calc. Based on %S | 0.9 | 0.91837 | 0.91837 | 0.91837 | 0.91837 | 0.91837
(Mole CaO / Mole Inlet SO2)
Recycle Rate | Factor | Calculated | 30 | 30 | 30 | 30 | 30 | 30
(lb recycle / lb lime feed)
Recycle Slurry Solids Concentration | Wt. % | 10-50 | 35% | 35% | 35% | 35% | 35% | 35%
Number of Absorbers | Integer | 1-7 | 2 | 1 | 1 | 1 | 1 | 1
(Max. Capacity = 300 MW per spray dryer)
Absorber Material | Integer | 1 or 2 | 1 | 1 | 1 | 1 | 1 | 1
(1 = alloy, 2 = RLCS)
Spray Dryer Pressure Drop | in. H2O |  | 5 | 5 | 5 | 5 | 5 | 5
Reagent Bulk Storage | Days |  | 60 | 60 | 60 | 60 | 60 | 60
Reagent Cost (delivered) | $/ton |  | 65 | 65 | 65 | 65 | 65 | 65
Dry Waste Disposal Cost | $/ton |  | 30 | 30 | 30 | 30 | 30 | 30
Maintenance Factors by Area (% of Installed Cost)
Reagent Feed | % |  | 5% | 5% | 5% | 5% | 5% | 5%
SO2 Removal | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Flue Gas Handling | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Waste / Byproduct | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Support Equipment | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Contingency by Area (% of Installed Cost)
Reagent Feed | % |  | 20% | 20% | 20% | 20% | 20% | 20%
SO2 Removal | % |  | 20% | 20% | 20% | 20% | 20% | 20%
Flue Gas Handling | % |  | 20% | 20% | 20% | 20% | 20% | 20%
Waste / Byproduct | % |  | 20% | 20% | 20% | 20% | 20% | 20%
Support Equipment | % |  | 20% | 20% | 20% | 20% | 20% | 20%
General Facilities by Area (% of Installed Cost)
Reagent Feed | % |  | 10% | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Support Equipment | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Engineering Fees by Area (% of Installed Cost)
Reagent Feed | % |  | 10% | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Support Equipment | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Particulate Control Inputs
Outlet Particulate Emission Limit | lbs/MMBtu |  | 0.03 | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Fabric Filter:
Pressure Drop | in. H2O |  | 6 | 6 | 6 | 6 | 6 | 6
Type (1 = Reverse Gas, 2 = Pulse Jet) | Integer |  | 2 | 2 | 2 | 2 | 2 | 2
Gas-to-Cloth Ratio | ACFM/ft2 |  | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Bag Material (RGFF fiberglass only) | Integer |  | 2 | 2 | 2 | 2 | 2 | 2
(1 = Fiberglass, 2 = Nomex, 3 = Ryton)
Bag Diameter | inches | 5 - 14 | 6 | 6 | 6 | 6 | 6 | 6
Bag Length | feet | 15 - 35 | 20 | 20 | 20 | 20 | 20 | 20
Bag Reach |  |  | 3 | 3 | 3 | 3 | 3 | 3
Compartments out of Service | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Bag Life | Years | 1 - 10 | 5 | 5 | 5 | 5 | 5 | 5
Maintenance (% of installed cost) | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Contingency (% of installed cost) | % |  | 20% | 20% | 20% | 20% | 20% | 20%
General Facilities (% of installed cost) | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Engineering Fees (% of installed cost) | % |  | 10% | 10% | 10% | 10% | 10% | 10%
ESP:
Strength of the electric field in the ESP = E | kV/cm |  | 10 | 10 | 10 | 10 | 10 | 10
Plate Spacing | in. |  | 12 | 12 | 12 | 12 | 12 | 12
Plate Height | ft. |  | 36 | 36 | 36 | 36 | 36 | 36
Pressure Drop | in. H2O |  | 3 | 3 | 3 | 3 | 3 | 3
Maintenance (% of installed cost) | % |  | 5% | 5% | 5% | 5% | 5% | 5%
Contingency (% of installed cost) | % |  | 20% | 20% | 20% | 20% | 20% | 20%
General Facilities (% of installed cost) | % |  | 10% | 10% | 10% | 10% | 10% | 10%
Engineering Fees (% of installed cost) | % |  | 10% | 10% | 10% | 10% | 10% | 10%
NOx Control Inputs
See Source Keys @ bottom of
Selective Catalytic Reduction (SCR) Inputs | [10 empty] | Constants_CC Sheet.
[10 empty] | IAPCS name | Range Source | Default Source
NH3/NOX Stoichiometric Ratio | NH3/NOX | 0.7-1.0 | 0.9 | D | D | D | D | D | IAPCS Names and a list of sources are contained in columns L, M, and N. | NH3:NOX ratio
NOX Reduction Efficiency | Fraction | 0.60-0.90 | 0.7 | D | D | D | D | D | " | n | b | c
Inlet NOx | lbs/MMBtu |  | 0.9 | 0.36 | 0.36 | 0.29 | 0.44 | 0.44 | " | NOx
Space Velocity (Calculated if zero) | 1/hr |  | 0 | D | D | D | D | D | " | SV | i | i
Overall Catalyst Life | years | 2-5 | 3 | D | D | D | D | D | " | N | d | c
Ammonia Cost | $/ton |  | 205.66 | D | D | D | D | D | " | UCNH3 | d | a
Catalyst Cost | $/ft3 |  | 356.34 | D | D | D | D | D | " | UCCAT | d | a
Solid Waste Disposal Cost | $/ton |  | 11.48 | D | D | D | D | D | " | UCWASTE |  | a
Maintenance (% of installed cost) | % |  | 1.5% | D | D | D | D | D | " |  |  | a
Contingency (% of installed cost) | % |  | 20% | D | D | D | D | D | " |  |  | f
General Facilities (% of installed cost) | % |  | 5% | D | D | D | D | D | " |  |  | f
Engineering Fees (% of installed cost) | % |  | 10% | D | D | D | D | D | " |  |  | f
Number of Reactors | integer |  | 2 | 1 | 1 | 1 | 1 | 1 | " | Nr,tot
Number of Air Preheaters | integer |  | 1 | D | D | D | D | D | " | Nt,aph
Selective NonCatalytic Reduction (SNCR) Inputs
Reagent | integer | 1:Urea 2:Ammonia | 1 | D | D | D | D | D | " |  | -- | --
Number of Injector Levels | integer |  | 3 | D | D | D | D | D | " | NIL |  | f
Number of Injectors | integer |  | 18 | D | D | D | D | D
Number of Lance Levels | integer |  | 0 | D | D | D | D | D | " | NLL |  | f
Number of Lances | integer |  | 0 | D | D | D | D | D
Steam or Air Injection for Ammonia | integer | 1: Steam, 2: Air | 1 | D | D | D | D | D | " |  |  | --
NOX Reduction Efficiency | fraction | 0.30-0.70 | 0.5 | D | D | D | D | D | " | n | b | c
Inlet NOx | lbs/MMBtu |  | 0.9 | 0.36 | 0.36 | 0.29 | 0.44 | 0.44 | " | NOx
NH3/NOX Stoichiometric Ratio | NH3/NOX | 0.8-2.0 | 1.2 | D | D | D | D | D | " | NH3:NOX ratio
Urea/NOX Stoichiometric Ratio | Urea/NOX | 0.8-2.0 | 1.2 | D | D | D | D | D | Urea provides 2 moles of Ammonia for every mole of Urea. | UREA:NOX ratio | f | c
Urea Cost | $/ton |  | 224.95 | D | D | D | D | D | " | UCUREA |  | g
Ammonia Cost | $/ton |  | 205.66 | D | D | D | D | D | " | UCNH3 |  | a
Water Cost | $/1,000 gal |  | 0.407 | D | D | D | D | D | " | UCH2O |  | a
Maintenance (% of installed cost) | % |  | 1.5% | D | D | D | D | D | " |  |  | a
Contingency (% of installed cost) | % |  | 20% | D | D | D | D | D | " |  |  | e
General Facilities (% of installed cost) | % |  | 5% | D | D | D | D | D | " |  |  | e
Engineering Fees (% of installed cost) | % |  | 10% | D | D | D | D | D | " |  |  | e
Low NOX Burner Technology Inputs
NOX Reduction Efficiency | fraction | 0.15-0.60 | 0.35 | D | D | D | D | D | " | n | i | g
Boiler Type | T:T-fired, W:Wall |  | T | D | D | D | D | D | "
Retrofit Difficulty | L:Low, A:Average, H:High |  | A | H | H | H | H | A | "
Maintenance Labor (% of installed cost) | % |  | 0.8% | D | D | D | D | D | " |  |  | g
Maintenance Materials (% of installed cost) | % |  | 1.2% | D | D | D | D | D | " |  |  | g
Natural Gas Reburning Inputs
NOX Reduction Efficiency | fraction | 0.55-0.65 | 0.61 | D | D | D | D | D | " | n | i
Gas Reburn Fraction | fraction | 0.08 - 0.20 | 0.15 | D | D | D | D | D | " |  |  | i
Waste Disposal Cost | $/ton |  | 11.48 | D | D | D | D | D | " | UCWASTE |  | a
Natural Gas Cost | $/MMBtu |  | 2.31 | D | D | D | D | D | " | UCGAS |  | a
Maintenance (% of installed cost) | % |  | 1.5% | D | D | D | D | D | " |  |  | a
Contingency (% of installed cost) | % |  | 20% | D | D | D | D | D | " |  |  | e
General Facilities (% of installed cost) | % |  | 2% | D | D | D | D | D | " |  |  | e
Engineering Fees (% of installed cost) | % |  | 10% | D | D | D | D | D | " |  |  | e
Note on A103: Year $'s CE Annual Index Value January 1, 1998 CE Index = 388 See Chemical Engineering Magazine for current year.
Default Values will be selected when "D" is input.
APC Technology Choices
General Plant Technical Inputs
Economic Inputs
LSFO Inputs
LSD Inputs
Particulate Control Inputs
NOx Control Inputs
Cost Summary
SCR Calculations
SNCR Calculations
Low NOx Burner Calculations
Natural Gas Reburning Calculations
LSFO Material Balances
LSFO Cost Calculations
LSD Material Balances
LSD Cost Calculations
Fabric Filter Calculations
ESP Calculations
Fuel and Combustion Calculations
Coal Analysis Library
Cost Summary
Input Summary
NOx Control Calculations
Particulate Control Calculations
LSFO Calculations
LSD Calculations
Combustion Calculations
Coal Analysis Library
Print ALL

## Input & Calculation Summary
CUECost
Coal Utility Environmental Cost
Version 1, November 25, 1998 (revised 2-9-00 as CUECost3.xls)
APC Technology Choices
Description | Units | Input 1 | Input 2 | Input 3 | Input 4 | Input 5
FGD Process | Integer | 1 | 2 | 2 | 2 | 1
(1 = LSFO, 2 = LSD)
Particulate Control | Integer | 1 | 1 | 1 | 1 | 1
(1 = Fabric Filter, 2 = ESP)
NOx Control | Integer | 1 | 1 | 2 | 2 | 3
(1 = SCR, 2 = SNCR, 3 = LNBs, 4 = NGR)
INPUTS
Description | Units | Input 1 | Input 2 | Input 3 | Input 4 | Input 5
General Plant Technical Inputs |  |  | Combined Exhaust | one Large Boiler | one Small Boiler | one Small Boiler
Location - State | Abbrev. | AK | AK | AK | AK | AK
MW Equivalent of Flue Gas to Control System | MW | 150 | 150 | 79 | 22 | 22
Net Plant Heat Rate | Btu/kWhr | 11833 | 11833 | 11833 | 11833 | 11833
Plant Capacity Factor | % | 65% | 65% | 65% | 65% | 65%
Total Air Downstream of Economizer | % | 120% | 120% | 120% | 120% | 120%
Air Heater Leakage | % | 12% | 12% | 12% | 12% | 12%
Air Heater Outlet Gas Temperature | °F | 300 | 300 | 300 | 300 | 300
Inlet Air Temperature | °F | 80 | 80 | 80 | 80 | 80
Ambient Absolute Pressure | In. of Hg | 29.4 | 29.4 | 29.4 | 29.4 | 29.4
Pressure After Air Heater | In. of H2O | -12 | -12 | -12 | -12 | -12
Moisture in Air | lb/lb dry air | 0.013 | 0.013 | 0.013 | 0.013 | 0.013
Ash Split:
Fly Ash | % | 80% | 80% | 80% | 80% | 80%
Bottom Ash | % | 20% | 20% | 20% | 20% | 20%
Seismic Zone | Integer | 1 | 1 | 1 | 1 | 1
Retrofit Factor | Integer | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
(1.0 = new, 1.3 = medium, 1.6 = difficult)
Select Coal | Integer | 8 | 8 | 8 | 8 | 8
Is Selected Coal a Powder River Basin Coal? | Yes / No | No | No | No | No | No
Economic Inputs
Cost Basis -Year Dollars | Year | 2015 | 2015 | 2015 | 2015 | 2015
Sevice Life (levelization period) | Years | 30 | 30 | 30 | 30 | 30
Inflation Rate | % | 3% | 3% | 3% | 3% | 3%
After Tax Discount Rate (current $'s) | % | 9.2% | 9.2% | 9.2% | 9.2% | 9.2%
AFDC Rate (current $'s) | % | 10.8% | 10.8% | 10.8% | 10.8% | 10.8%
First-year Carrying Charge (current $'s) | % | 22.3% | 22.3% | 22.3% | 22.3% | 22.3%
Levelized Carrying Charge (current $'s) | % | 16.9% | 16.9% | 16.9% | 16.9% | 16.9%
First-year Carrying Charge (constant $'s) | % | 15.7% | 15.7% | 15.7% | 15.7% | 15.7%
Levelized Carrying Charge (constant $'s) | % | 11.7% | 11.7% | 11.7% | 11.7% | 11.7%
Sales Tax | % | 6% | 6% | 6% | 6% | 6%
Escalation Rates:
Consumables (O&M) | % | 3% | 3% | 3% | 3% | 3%
Capital Costs:
Is Chem. Eng. Cost Index available? | Yes / No | Yes | Yes | Yes | Yes | Yes
If "Yes" input cost basis CE Plant Index. | Integer | 578.4 | 578.4 | 578.4 | 578.4 | 578.4
If "No" input escalation rate. | % | 3% | 3% | 3% | 3% | 3%
Construction Labor Rate | $/hr | 60 | 60 | 60 | 60 | 60
Prime Contractor's Markup | % | 3% | 3% | 3% | 3% | 3%
Operating Labor Rate | $/hr | 63 | 63 | 63 | 63 | 63
Power Cost | Mills/kWh | 25 | 25 | 25 | 25 | 25
Steam Cost | $/1000 lbs | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Limestone Forced Oxidation (LSFO) Inputs
SO2 Removal Required | % | 50% | 95% | 95% | 95% | 95%
L/G Ratio | gal / 1000 acf | 125 | 125 | 125 | 125 | 125
Design Scrubber with Dibasic Acid Addition? | Integer | 2 | 1 | 1 | 1 | 1
(1 = yes, 2 = no)
Adiabatic Saturation Temperature | °F | 127 | 127 | 127 | 127 | 127
Reagent Feed Ratio | Factor | 1.05 | 1.05 | 1.05 | 1.05 | 1.05
(Mole CaCO3 / Mole SO2 removed)
Scrubber Slurry Solids Concentration | Wt. % | 15% | 15% | 15% | 15% | 15%
Stacking, Landfill, Wallboard | Integer | 1 | 1 | 1 | 1 | 1
(1 = stacking, 2 = lanfill, 3 = wallboard)
Number of Absorbers | Integer | 1 | 1 | 1 | 1 | 1
(Max. Capacity = 700 MW per absorber)
Absorber Material | Integer | 1 | 1 | 1 | 1 | 1
(1 = alloy, 2 = RLCS)
Absorber Pressure Drop | in. H2O | 6 | 6 | 6 | 6 | 6
Reheat Required ? | Integer | 1 | 1 | 1 | 1 | 1
(1 = yes, 2 = no)
Amount of Reheat | °F | 25 | 25 | 25 | 25 | 25
Reagent Bulk Storage | Days | 60 | 60 | 60 | 60 | 60
Reagent Cost (delivered) | $/ton | 15 | 15 | 15 | 15 | 15
Landfill Disposal Cost | $/ton | 30 | 30 | 30 | 30 | 30
Stacking Disposal Cost | $/ton | 6 | 6 | 6 | 6 | 6
Credit for Gypsum Byproduct | $/ton | 2 | 2 | 2 | 2 | 2
Maintenance Factors by Area (% of Installed Cost)
Reagent Feed | % | 5% | 5% | 5% | 5% | 5%
SO2 Removal | % | 5% | 5% | 5% | 5% | 5%
Flue Gas Handling | % | 5% | 5% | 5% | 5% | 5%
Waste / Byproduct | % | 5% | 5% | 5% | 5% | 5%
Support Equipment | % | 5% | 5% | 5% | 5% | 5%
Contingency by Area (% of Installed Cost)
Reagent Feed | % | 20% | 20% | 20% | 20% | 20%
SO2 Removal | % | 20% | 20% | 20% | 20% | 20%
Flue Gas Handling | % | 20% | 20% | 20% | 20% | 20%
Waste / Byproduct | % | 20% | 20% | 20% | 20% | 20%
Support Equipment | % | 20% | 20% | 20% | 20% | 20%
General Facilities by Area (% of Installed Cost)
Reagent Feed | % | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % | 10% | 10% | 10% | 10% | 10%
Support Equipment | % | 10% | 10% | 10% | 10% | 10%
Engineering Fees by Area (% of Installed Cost)
Reagent Feed | % | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % | 10% | 10% | 10% | 10% | 10%
Support Equipment | % | 10% | 10% | 10% | 10% | 10%
Lime Spray Dryer (LSD) Inputs
SO2 Removal Required | % | 90% | 90% | 90% | 90% | 90%
Adiabatic Saturation Temperature | °F | 127 | 127 | 127 | 127 | 127
Flue Gas Approach to Saturation | °F | 20 | 20 | 20 | 20 | 20
Spray Dryer Outlet Temperature | °F | 147 | 147 | 147 | 147 | 147
Reagent Feed Ratio | Factor | 0.91837 | 0.91837 | 0.91837 | 0.91837 | 0.91837
(Mole CaO / Mole Inlet SO2)
Recycle Rate | Factor | 30 | 30 | 30 | 30 | 30
(lb recycle / lb lime feed)
Recycle Slurry Solids Concentration | Wt. % | 35% | 35% | 35% | 35% | 35%
Number of Absorbers | Integer | 1 | 1 | 1 | 1 | 1
(Max. Capacity = 300 MW per spray dryer)
Absorber Material | Integer | 1 | 1 | 1 | 1 | 1
(1 = alloy, 2 = RLCS)
Spray Dryer Pressure Drop | in. H2O | 5 | 5 | 5 | 5 | 5
Reagent Bulk Storage | Days | 60 | 60 | 60 | 60 | 60
Reagent Cost (delivered) | $/ton | 65 | 65 | 65 | 65 | 65
Dry Waste Disposal Cost | $/ton | 30 | 30 | 30 | 30 | 30
Maintenance Factors by Area (% of Installed Cost)
Reagent Feed | % | 5% | 5% | 5% | 5% | 5%
SO2 Removal | % | 5% | 5% | 5% | 5% | 5%
Flue Gas Handling | % | 5% | 5% | 5% | 5% | 5%
Waste / Byproduct | % | 5% | 5% | 5% | 5% | 5%
Support Equipment | % | 5% | 5% | 5% | 5% | 5%
Contingency by Area (% of Installed Cost)
Reagent Feed | % | 20% | 20% | 20% | 20% | 20%
SO2 Removal | % | 20% | 20% | 20% | 20% | 20%
Flue Gas Handling | % | 20% | 20% | 20% | 20% | 20%
Waste / Byproduct | % | 20% | 20% | 20% | 20% | 20%
Support Equipment | % | 20% | 20% | 20% | 20% | 20%
General Facilities by Area (% of Installed Cost)
Reagent Feed | % | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % | 10% | 10% | 10% | 10% | 10%
Support Equipment | % | 10% | 10% | 10% | 10% | 10%
Engineering Fees by Area (% of Installed Cost)
Reagent Feed | % | 10% | 10% | 10% | 10% | 10%
SO2 Removal | % | 10% | 10% | 10% | 10% | 10%
Flue Gas Handling | % | 10% | 10% | 10% | 10% | 10%
Waste / Byproduct | % | 10% | 10% | 10% | 10% | 10%
Support Equipment | % | 10% | 10% | 10% | 10% | 10%
Particulate Control Inputs
Outlet Particulate Emission Limit | lbs/MMBtu | 0.03 | 0.03 | 0.03 | 0.03 | 0.03
Fabric Filter:
Pressure Drop | in. H2O | 6 | 6 | 6 | 6 | 6
Type (1 = Reverse Gas, 2 = Pulse Jet) | Integer | 2 | 2 | 2 | 2 | 2
Gas-to-Cloth Ratio | ACFM/ft2 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
Bag Material (RGFF fiberglass only) | Integer | 2 | 2 | 2 | 2 | 2
(1 = Fiberglass, 2 = Nomex, 3 = Ryton)
Bag Diameter | inches | 6 | 6 | 6 | 6 | 6
Bag Length | feet | 20 | 20 | 20 | 20 | 20
Bag Reach |  | 3 | 3 | 3 | 3 | 3
Compartments out of Service | % | 10% | 10% | 10% | 10% | 10%
Bag Life | Years | 5 | 5 | 5 | 5 | 5
Maintenance (% of installed cost) | % | 5% | 5% | 5% | 5% | 5%
Contingency (% of installed cost) | % | 20% | 20% | 20% | 20% | 20%
General Facilities (% of installed cost) | % | 10% | 10% | 10% | 10% | 10%
Engineering Fees (% of installed cost) | % | 10% | 10% | 10% | 10% | 10%
ESP:
Strength of the electric field in the ESP = E | kV/cm | 10 | 10 | 10 | 10 | 10
Plate Spacing | in. | 12 | 12 | 12 | 12 | 12
Plate Height | ft. | 36 | 36 | 36 | 36 | 36
Pressure Drop | in. H2O | 3 | 3 | 3 | 3 | 3
Maintenance (% of installed cost) | % | 5% | 5% | 5% | 5% | 5%
Contingency (% of installed cost) | % | 20% | 20% | 20% | 20% | 20%
General Facilities (% of installed cost) | % | 10% | 10% | 10% | 10% | 10%
Engineering Fees (% of installed cost) | % | 10% | 10% | 10% | 10% | 10%
NOx Control Inputs
Selective Catalytic Reduction (SCR) Inputs
NH3/NOX Stoichiometric Ratio | NH3/NOX | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NOX Reduction Efficiency | Fraction | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Inlet NOx | lbs/MMBtu | 0.36 | 0.36 | 0.29 | 0.44 | 0.44
Space Velocity (Calculated if zero) | 1/hr | 0 | 0 | 0 | 0 | 0
Overall Catalyst Life | years | 3 | 3 | 3 | 3 | 3
Ammonia Cost | $/ton | 205.66 | 205.66 | 205.66 | 205.66 | 205.66
Catalyst Cost | $/ft3 | 356.34 | 356.34 | 356.34 | 356.34 | 356.34
Solid Waste Disposal Cost | $/ton | 11.48 | 11.48 | 11.48 | 11.48 | 11.48
Maintenance (% of installed cost) | % | 1.5% | 1.5% | 1.5% | 1.5% | 1.5%
Contingency (% of installed cost) | % | 20% | 20% | 20% | 20% | 20%
General Facilities (% of installed cost) | % | 5% | 5% | 5% | 5% | 5%
Engineering Fees (% of installed cost) | % | 10% | 10% | 10% | 10% | 10%
Number of Reactors | integer | 1 | 1 | 1 | 1 | 1
Number of Air Preheaters | integer | 1 | 1 | 1 | 1 | 1
Selective NonCatalytic Reduction (SNCR) Inputs
Reagent | 1:Urea 2:Ammonia | 1 | 1 | 1 | 1 | 1
Number of Injector Levels | integer | 3 | 3 | 3 | 3 | 3
Number of Injectors | integer | 18 | 18 | 18 | 18 | 18
Number of Lance Levels | integer | 0 | 0 | 0 | 0 | 0
Number of Lances | integer | 0 | 0 | 0 | 0 | 0
Steam or Air Injection for Ammonia | integer | 1 | 1 | 1 | 1 | 1
NOX Reduction Efficiency | Fraction | 0.5 | 0.5 | 0.5 | 0.5 | 0.5
Inlet NOx | lbs/MMBtu | 0.36 | 0.36 | 0.29 | 0.44 | 0.44
NH3/NOX Stoichiometric Ratio | NH3/NOX | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Urea/NOX Stoichiometric Ratio | Urea/NOX | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
Urea Cost | $/ton | 224.95 | 224.95 | 224.95 | 224.95 | 224.95
Ammonia Cost | $/ton | 205.66 | 205.66 | 205.66 | 205.66 | 205.66
Water Cost | $/1,000 gal | 0.407 | 0.407 | 0.407 | 0.407 | 0.407
Maintenance (% of installed cost) | % | 1.5% | 1.5% | 1.5% | 1.5% | 1.5%
Contingency (% of installed cost) | % | 20% | 20% | 20% | 20% | 20%
General Facilities (% of installed cost) | % | 5% | 5% | 5% | 5% | 5%
Engineering Fees (% of installed cost) | % | 10% | 10% | 10% | 10% | 10%
Low NOX Burner Technology Inputs
NOX Reduction Efficiency | fraction | 0.35 | 0.35 | 0.35 | 0.35 | 0.35
Boiler Type | T:T-fired, W:Wall | T | T | T | T | T
Retrofit Difficulty | L:Low, A:Average, H:High | H | H | H | H | A
Maintenance Labor (% of installed cost) | % | 0.8% | 0.8% | 0.8% | 0.8% | 0.8%
Maintenance Materials (% of installed cost) | % | 1.2% | 1.2% | 1.2% | 1.2% | 1.2%
Natural Gas Reburning Inputs
NOX Reduction Efficiency | fraction | 0.61 | 0.61 | 0.61 | 0.61 | 0.61
Gas Reburn Fraction | fraction | 0.15 | 0.15 | 0.15 | 0.15 | 0.15
Waste Disposal Cost | $/ton | 11.48 | 11.48 | 11.48 | 11.48 | 11.48
Natural Gas Cost | $/MMBtu | 2.31 | 2.31 | 2.31 | 2.31 | 2.31
Maintenance (% of installed cost) | % | 1.5% | 1.5% | 1.5% | 1.5% | 1.5%
Contingency (% of installed cost) | % | 20% | 20% | 20% | 20% | 20%
General Facilities (% of installed cost) | % | 2% | 2% | 2% | 2% | 2%
Engineering Fees (% of installed cost) | % | 10% | 10% | 10% | 10% | 10%
SUMMARY OF COSTS
Description | Units | Input 1 | Input 2 | Input 3 | Input 4 | Input 5
APC Technologies
NOx Control |  | SCR | SCR | SNCR | SNCR | LNCFS and LNBs
Particulate Control |  | PJFF | PJFF | PJFF | PJFF | PJFF
SO2 Control |  | LSFO | LSD | LSD | LSD | LSFO
|  | Combined Exhaust | Combined Exhaust | one Large Boiler | one Small Boiler | one Small Boiler
NOx Control Costs |  | SCR | SCR | SNCR | SNCR | LNCFS and LNBs
Total Capital Requirement (TCR) | $ | 16131899.2296 | 33115791.307 | 3275232.6805 | 2268399.7903 | 1882494.9368
| $/kW | 107.546 | 220.7719 | 41.4586 | 103.1091 | 85.568
First Year Costs
Fixed O&M | $ | 344867.0125 | 536499.6427 | 183943.1635 | 169911.4345 | 42167.8866
| $/kW-Yr | 2.2991 | 3.5767 | 2.3284 | 7.7232 | 1.9167
| Mills/kWH | 0.40378 | 0.62815 | 0.40892 | 1.3564 | 0.33662
| $/ton NOx removed | 1154.2435 | 502.7887 | 458.2389 | 1519.9709 | 538.8855
Variable O&M | $ | 633871.1865 | 1938182.1546 | 139517.3762 | 61314.491 | 0
| $/kW-Yr | 4.2258 | 12.9212 | 1.766 | 2.787 | 0
| Mills/kWH | 0.74215 | 2.2693 | 0.31016 | 0.48947 | 0
| $/ton NOx removed | 2121.5184 | 1816.3965 | 347.5654 | 548.499 | 0
Fixed Charges | $ | 3597413.5282 | 7384821.4615 | 730376.8877 | 505853.1532 | 419796.3709
| $/kW-Yr | 23.9828 | 49.2321 | 9.2453 | 22.9933 | 19.0817
| Mills/kWH | 4.2119 | 8.6463 | 1.6237 | 4.0382 | 3.3512
| $/ton NOx removed | 12040.2683 | 6920.7963 | 1819.5135 | 4525.1934 | 5364.7973
TOTAL | $ | 4576151.7271 | 9859503.2588 | 1053837.4274 | 737079.0787 | 461964.2575
| $/kW-Yr | 30.5077 | 65.73 | 13.3397 | 33.5036 | 20.9984
| Mills/kWH | 5.3579 | 11.5437 | 2.3428 | 5.884 | 3.6878
| $/ton NOx removed | 15316.0303 | 9239.9815 | 2625.3178 | 6593.6633 | 5903.6828
Levelized Current Dollars
Fixed O&M | $/kW-Yr | 3.1287 | 4.8672 | 3.1685 | 10.5099 | 2.6083
| Mills/kWH | 0.54947 | 0.85479 | 0.55647 | 1.8458 | 0.45808
| $/ton NOx removed | 1570.7125 | 684.2027 | 623.5786 | 2068.4 | 733.3237
Variable O&M | $/kW-Yr | 5.7505 | 17.5834 | 2.4033 | 3.7926 | 0
| Mills/kWH | 1.0099 | 3.0881 | 0.42207 | 0.66607 | 0
| $/ton NOx removed | 2886.9952 | 2471.7805 | 472.9724 | 746.4059 | 0
Fixed Charges | $/kW-Yr | 18.1753 | 37.3105 | 7.0065 | 17.4254 | 14.461
| Mills/kWH | 3.192 | 6.5526 | 1.2305 | 3.0603 | 2.5397
| $/ton NOx removed | 9124.6876 | 5244.9084 | 1378.9138 | 3429.4066 | 4065.6984
TOTAL | $/kW-Yr | 27.0545 | 59.761 | 12.5783 | 31.728 | 17.0693
| Mills/kWH | 4.7514 | 10.4954 | 2.209 | 5.5722 | 2.9978
| $/ton NOx removed | 13582.3953 | 8400.8916 | 2475.4648 | 6244.2125 | 4799.0221
Levelized Constant Dollars
Fixed O&M | $/kW-Yr | 2.2991 | 3.5767 | 2.3284 | 7.7232 | 1.9167
| Mills/kWH | 0.40378 | 0.62815 | 0.40892 | 1.3564 | 0.33662
| $/ton NOx removed | 1154.2435 | 502.7887 | 458.2389 | 1519.9709 | 538.8855
Variable O&M | $/kW-Yr | 4.2258 | 12.9212 | 1.766 | 2.787 | 0
| Mills/kWH | 0.74215 | 2.2693 | 0.31016 | 0.48947 | 0
| $/ton NOx removed | 2121.5184 | 1816.3965 | 347.5654 | 548.499 | 0
Fixed Charges | $/kW-Yr | 12.5829 | 25.8303 | 4.8507 | 12.0638 | 10.0115
| Mills/kWH | 3.1388 | 6.4434 | 1.21 | 3.0093 | 2.4974
| $/ton NOx removed | 8972.684 | 5157.5361 | 1355.9432 | 3372.2779 | 3997.97
TOTAL | $/kW-Yr | 19.1078 | 42.3282 | 8.9451 | 22.574 | 11.9282
| Mills/kWH | 4.2848 | 9.3409 | 1.9291 | 4.8552 | 2.834
| $/ton NOx removed | 12248.446 | 7476.7213 | 2161.7475 | 5440.7478 | 4536.8554
Particulate Control Costs |  | PJFF | PJFF | PJFF | PJFF | PJFF
Total Capital Requirement (TCR) | $ | 17565252.1726 | 40384436.3567 | 25619606.446 | 11083014.6045 | 11569915.946
| $/kW | 117.1017 | 269.2296 | 324.2988 | 503.7734 | 525.9053
First Year Costs
Fixed O&M | $ | 503415.4427 | 1157407.1756 | 734251.0881 | 317636.2428 | 331590.7054
| $/kW-Yr | 3.3561 | 7.716 | 9.2943 | 14.438 | 15.0723
| Mills/kWH | 0.58941 | 1.3551 | 1.6323 | 2.5357 | 2.6471
| $/ton PM removed | 45.9201 | 8.4646 | 10.196 | 15.8387 | 57.7455
Variable O&M | $ | 312466.1331 | 1064939.3812 | 565461.9481 | 163387.7455 | 186500.0305
| $/kW-Yr | 2.0831 | 7.0996 | 7.1577 | 7.4267 | 8.4773
| Mills/kWH | 0.36584 | 1.2469 | 1.2571 | 1.3043 | 1.4888
| $/ton PM removed | 28.5023 | 7.7884 | 7.8522 | 8.1472 | 32.4784
Fixed Charges | $ | 3917051.2345 | 9005729.3075 | 5713172.2375 | 2471512.2568 | 2580091.256
| $/kW-Yr | 26.1137 | 60.0382 | 72.3186 | 112.3415 | 117.2769
| Mills/kWH | 4.5862 | 10.5441 | 12.7008 | 19.7298 | 20.5966
| $/ton PM removed | 357.3024 | 65.8628 | 79.3346 | 123.2402 | 449.3146
TOTAL | $ | 4732932.8103 | 11228075.8643 | 7012885.2737 | 2952536.2451 | 3098181.9918
| $/kW-Yr | 31.5529 | 74.8538 | 88.7707 | 134.2062 | 140.8265
| Mills/kWH | 5.5414 | 13.1461 | 15.5902 | 23.5698 | 24.7324
| $/ton PM removed | 431.7248 | 82.1158 | 97.3828 | 147.2262 | 539.5384
Levelized Current Dollars
Fixed O&M | $/kW-Yr | 4.567 | 10.5001 | 12.6479 | 19.6475 | 20.5106
| Mills/kWH | 0.80208 | 1.8441 | 2.2213 | 3.4506 | 3.6021
| $/ton PM removed | 62.4888 | 11.5188 | 13.8749 | 21.5536 | 78.5809
Variable O&M | $/kW-Yr | 2.8347 | 9.6612 | 9.7404 | 10.1064 | 11.536
| Mills/kWH | 0.49784 | 1.6967 | 1.7106 | 1.7749 | 2.026
| $/ton PM removed | 38.7863 | 10.5985 | 10.6853 | 11.0869 | 44.1971
Fixed Charges | $/kW-Yr | 19.7902 | 45.4998 | 54.8065 | 85.1377 | 88.878
| Mills/kWH | 3.4756 | 7.9908 | 9.6253 | 14.9522 | 15.6091
| $/ton PM removed | 270.7807 | 49.914 | 60.1235 | 93.3973 | 340.512
TOTAL | $/kW-Yr | 27.1919 | 65.6612 | 77.1947 | 114.8916 | 120.9246
| Mills/kWH | 4.7755 | 11.5316 | 13.5572 | 20.1777 | 21.2372
| $/ton PM removed | 372.0559 | 72.0313 | 84.6838 | 126.0377 | 463.29
Levelized Constant Dollars
Fixed O&M | $/kW-Yr | 3.3561 | 7.716 | 9.2943 | 14.438 | 15.0723
| Mills/kWH | 0.58941 | 1.3551 | 1.6323 | 2.5357 | 2.6471
| $/ton PM removed | 45.9201 | 8.4646 | 10.196 | 15.8387 | 57.7455
Variable O&M | $/kW-Yr | 2.0831 | 7.0996 | 7.1577 | 7.4267 | 8.4773
| Mills/kWH | 0.36584 | 1.2469 | 1.2571 | 1.3043 | 1.4888
| $/ton PM removed | 28.5023 | 7.7884 | 7.8522 | 8.1472 | 32.4784
Fixed Charges | $/kW-Yr | 13.7009 | 31.4999 | 37.943 | 58.9415 | 61.5309
| Mills/kWH | 3.4177 | 7.8577 | 9.465 | 14.7031 | 15.349
| $/ton PM removed | 266.2699 | 49.0825 | 59.122 | 91.8415 | 334.8395
TOTAL | $/kW-Yr | 19.1401 | 46.3155 | 54.395 | 80.8062 | 85.0805
| Mills/kWH | 4.373 | 10.4597 | 12.3543 | 18.5431 | 19.4849
| $/ton PM removed | 340.6923 | 65.3354 | 77.1701 | 115.8274 | 425.0634
|  |  | Combined Exhaust | one Large Boiler | one Small Boiler | one Small Boiler
SO2 Control Costs |  | LSFO | LSD | LSD | LSD | LSFO
Total Capital Requirement (TCR) | $ | 88476054.2608 | 86902657.4054 | 71352927.1568 | 48861936.7657 | 76889228.4311
| $/kW | 589.8404 | 579.351 | 903.2016 | 2220.9971 | 3494.9649
First Year Costs
Fixed O&M | $ | 5133155.9871 | 4701167.3033 | 3546131.7183 | 2086959.6609 | 3165254.2993
| $/kW-Yr | 34.221 | 31.3411 | 44.8877 | 94.8618 | 143.8752
| Mills/kWH | 6.01 | 5.5042 | 7.8833 | 16.66 | 25.2679
| $/ton SO2 removed | 18603.9856 | 1303.7728 | 1867.305 | 3946.1979 | 5670.1208
Variable O&M | $ | 621703.4526 | 1807847.6941 | 952133.1189 | 265150.9951 | 173779.1151
| $/kW-Yr | 4.1447 | 12.0523 | 12.0523 | 12.0523 | 7.8991
| Mills/kWH | 0.7279 | 2.1167 | 2.1167 | 2.1167 | 1.3873
| $/ton SO2 removed | 2253.2263 | 501.3697 | 501.3697 | 501.3697 | 311.3016
Fixed Charges | $ | 19730160.1001 | 19379292.6014 | 15911702.756 | 10896211.8988 | 17146297.9401
| $/kW-Yr | 131.5344 | 129.1953 | 201.414 | 495.2824 | 779.3772
| Mills/kWH | 23.1005 | 22.6897 | 35.373 | 86.9832 | 136.8769
| $/ton SO2 removed | 71507.5901 | 5374.4514 | 8378.7079 | 20603.4687 | 30715.2513
TOTAL | $ | 25485019.5399 | 25888307.5989 | 20409967.5932 | 13248322.5548 | 20485331.3545
| $/kW-Yr | 169.9001 | 172.5887 | 258.354 | 602.1965 | 931.1514
| Mills/kWH | 29.8384 | 30.3106 | 45.373 | 105.7598 | 163.532
| $/ton SO2 removed | 92364.802 | 7179.594 | 10747.3825 | 25051.0363 | 36696.6736
Levelized Current Dollars
Fixed O&M | $/kW-Yr | 46.5685 | 42.6495 | 61.0839 | 129.0894 | 195.7876
| Mills/kWH | 8.1785 | 7.4902 | 10.7278 | 22.6711 | 34.3849
| $/ton SO2 removed | 25316.5922 | 1774.1943 | 2541.0576 | 5370.0473 | 7715.9884
Variable O&M | $/kW-Yr | 5.6402 | 16.401 | 16.401 | 16.401 | 10.7492
| Mills/kWH | 0.99054 | 2.8804 | 2.8804 | 2.8804 | 1.8878
| $/ton SO2 removed | 3066.2253 | 682.2716 | 682.2716 | 682.2716 | 423.624
Fixed Charges | $/kW-Yr | 99.683 | 97.9103 | 152.6411 | 375.3485 | 590.6491
| Mills/kWH | 17.5067 | 17.1954 | 26.8074 | 65.92 | 103.7318
| $/ton SO2 removed | 54191.8508 | 4073.0148 | 6349.7831 | 15614.288 | 23277.4774
TOTAL | $/kW-Yr | 151.8917 | 156.9608 | 230.126 | 520.8389 | 797.1858
| Mills/kWH | 26.6757 | 27.566 | 40.4155 | 91.4715 | 140.0045
| $/ton SO2 removed | 82574.6683 | 6529.4807 | 9573.1123 | 21666.6068 | 31417.0898
Levelized Constant Dollars
Fixed O&M | $/kW-Yr | 34.221 | 31.3411 | 44.8877 | 94.8618 | 143.8752
| Mills/kWH | 6.01 | 5.5042 | 7.8833 | 16.66 | 25.2679
| $/ton SO2 removed | 18603.9856 | 1303.7728 | 1867.305 | 3946.1979 | 5670.1208
Variable O&M | $/kW-Yr | 4.1447 | 12.0523 | 12.0523 | 12.0523 | 7.8991
| Mills/kWH | 0.7279 | 2.1167 | 2.1167 | 2.1167 | 1.3873
| $/ton SO2 removed | 2253.2263 | 501.3697 | 501.3697 | 501.3697 | 311.3016
Fixed Charges | $/kW-Yr | 69.0113 | 67.7841 | 105.6746 | 259.8567 | 408.9109
| Mills/kWH | 17.215 | 16.9089 | 26.3608 | 64.8219 | 102.0038
| $/ton SO2 removed | 53289.0958 | 4005.1645 | 6244.0052 | 15354.1773 | 22889.7095
TOTAL | $/kW-Yr | 107.3771 | 111.1775 | 162.6146 | 366.7708 | 560.6851
| Mills/kWH | 23.953 | 24.5298 | 36.3608 | 83.5985 | 128.6589
| $/ton SO2 removed | 74146.3077 | 5810.307 | 8612.6799 | 19801.7449 | 28871.1319
Note on A60: Year $'s CE Annual Index Value January 1, 1998 CE Index = 388 See Chemical Engineering Magazine for current year.

## NOX Cost & Tech. Results (hidden)
SCR (high-dust) - Preliminary |  | Case1 | Case2 | Case3 | Case4 | Case5 |  | Equations (bold indicates existing cuecost model parameter, blue indicates new input value from NOX User Input Sheet, normal text parameters are calculated on this sheet)
Ammonia Injection Rate | lb/hr | 212.896 | 212.896 | 90.3231 | 38.1636 | 38.1636 | NH3= 3.702 x 10-4 * NH3:NOX ratio * BSIZE * HTR * NOx | =3.702x10^4*NH3:NOX ratio * BSIZE(MW) * HTR (Btu/kWh) * NOX(lb/10^6 Btu)
Space Velocity | 1/hr | 2839.6346 | 2839.6346 | 2839.6346 | 2839.6346 | 2839.6346 | If SV is not input then SV =6131.06/3 * (n)^-0.241 * (NH3:NOx ratio)^-2.306 | = 6131.06 / 3 * (NOX reduction eff) ^ -0.241 * (NH3:NOX ratio) ^-2.306
Gross Catalyst Volume | ft3 | 3870.0218 | 13821.117 | 7279.1216 | 2027.0972 | 2027.0972 | CV = Q/SV | = flue gas volume flow rate (scfm) * 60min/hr / space velocity (1/hr)
SCR Capital Costs |  | Case1 | Case2 | Case3 | Case4 | Case5
Cost Basis (Year) |  | 2015 | 2015 | 2015 | 2015 | 2015
Reactor Housing and Installation | $ | 1715007.2521 | 3195947.9758 | 2335773.4795 | 1250074.1265 | 1250074.1265 | DCr=18.65* Nr,tot * (CV/Nr,tot)^0.489*1000*Retrofit Factor | DCr=18.65* Number of Reactors * (Gross Catalyst Volume/Number of Reactors)^0.489*1000*Retrofit Factor
Ammonia Handling and Injection | $ | 1089521.3339 | 1089521.3339 | 720699.199 | 475788.4209 | 475788.4209 | DCnh3=50.8(NH3 (lb/hr))^0.482*1000*Retrofit Factor | DCnh3=50.8(Ammonia Injection Rate (lb/hr))^0.482*1000*Retrofit Factor
Flue Gas Handling:Ductwork and Fans | $ | 2107853.2637 | 5099225.4133 | 3267759.4414 | 1345668.9055 | 1345668.9055 | DCfgh=143.66*(Gfg)^0.694*Retrofit Factor*1989 CI/1982 CI (Note: IAPCS Eqution used) | DCfgh=143.66*(Flue gas (SCFM) * (750+460)/(70+460) )^0.694*Retrofit Factor*108.7/91.8, Gfg = flue gas ACFM, assume maximum operating SCR temperature, 750 deg F; atmospheric pressure
Air Preheater Modifications | $ | 430750.5453 | 1192585.7722 | 714033.0096 | 256776.1963 | 256776.1963 | Dcaph,mod=1370*Nt,aph(UAt,aph/4.4/10^6/Nt,aph)^0.8 *1000*Retrofit Factor | Dcaph,mod = 1370*No. air preheaters * (SCFM economizer exit*60(m/hr)*7.9 *(Tair heater outlet-725)*(ln(125/(Tair heater outlet-Tinlet air temperature))/0.7302/530/(125-Tair heater outlet+Tinlet air)/4.4/10^6/No. air preheaters)^0.8 *1000*Retrofit Factor,
Misc. Other Direct Capital Costs | $ | 384597.9245 | 384597.9245 | 313472.3819 | 232277.5076 | 232277.5076 | DCmisc=(100+300 * (BSIZE/550)^0.6) * 1,000*Retrofit Factor | DCmisc=(100+300 * (BSIZE(MW)/550)^0.6) * 1,000*Retrofit Factor
Equipment Capital Cost Subtotal | $ | 5727730.3196 | 10961878.4197 | 7351737.5115 | 3560585.1568 | 3560585.1568 | =sum(Direct Capital Costs) | capital costs=SUM(direct capital costs)
Instruments & Controls | $ | 114554.6064 | 219237.5684 | 147034.7502 | 71211.7031 | 71211.7031 | =0.02*Equipment Capital Cost Subtotal | =0.02*capital costs
Taxes | $ | 343663.8192 | 657712.7052 | 441104.2507 | 213635.1094 | 213635.1094 | =Equipment Capital Cost Subtotal * Sales Tax % | =capital costs*(Sales Tax)
Freight | $ | 286386.516 | 548093.921 | 367586.8756 | 178029.2578 | 178029.2578 | =0.05 * Equipment Capital Cost Subtotal | =0.05*capital costs
Total Direct Cost |  | 6472335.2611 | 12386922.6142 | 8307463.3879 | 4023461.2272 | 4023461.2272
Total Direct Cost with Retrofit Factor | $ | 10355736.4178 | 19819076.1828 | 13291941.4207 | 6437537.9635 | 6437537.9635 |  | Total Direct Cost with Retrofit Factor= Total Direct Cost*Def_RetroFact
General Facilities | $ | 517786.8209 | 990953.8091 | 664597.071 | 321876.8982 | 321876.8982 | =Total Direct Cost with Retrofit Factor * General Facilities (%) | =Total Direct Cost with Retrofit Factor*(General Facilities)
Engineering Fees | $ | 1035573.6418 | 1981907.6183 | 1329194.1421 | 643753.7963 | 643753.7963 | =Total Direct Cost with Retrofit Factor * Engineering (%) | =Total Direct Cost with Retrofit Factor*(Engineering Fees)
Contingency | $ | 2071147.2836 | 3963815.2366 | 2658388.2841 | 1287507.5927 | 1287507.5927 | =Total Direct Cost with Retrofit Factor * Contingency (%) | =Total Direct Cost with Retrofit Factor*(Contingency)
Total Plant Cost (TPC) | $ | 13980244.164 | 26755752.8467 | 17944120.918 | 8690676.2507 | 8690676.2507 |  | Total Plant Cost (TPC)=SUM(four lines above)
Total Plant Cost (TPC) w/ Prime Contractor's Markup | $ | 14399651.4889 | 27558425.4321 | 18482444.5455 | 8951396.5382 | 8951396.5382
Total Cash Expended (TCE) | $ | 14399651.4889 | 27558425.4321 | 18482444.5455 | 8951396.5382 | 8951396.5382 |  | Total Cash Expended (TCE)=Total Plant Cost (TPC)*VLOOKUP(2,Constants_CC!AFDC / TCE FACTORS FOR CASE 1,3)
Allow. for Funds During Constr. (AFDC) | $ | 0 | 0 | 0 | 0 | 0 |  | Allow. for Funds During Constr. (AFDC)=Total Plant Cost (TPC)*VLOOKUP(2,Constants_CC!AFDC / TCE FACTORS FOR CASE 1,2)
Total Plant Investment (TPI) | $ | 14399651.4889 | 27558425.4321 | 18482444.5455 | 8951396.5382 | 8951396.5382 |  | Total Plant Investment (TPI)=Total Cash Expended (TCE)+Allow. for Funds During Constr. (AFDC)
Preproduction Costs | $ | 332713.179 | 611858.0438 | 408123.7818 | 200415.7363 | 200415.7363 | =0.02*TPI+(Op. Lab,$/yr+Maint.,$/yr)/12+(Ammonia,$/yr)/(12*CF) | =0.02*TPI+(Op. Lab,$/yr+Maint.,$/yr)/12+(Ammonia,$/yr)/(12*CF)
Inventory Capital
Initial Ammonia(60 days) | $ | 20491.0037 | 20491.0037 | 8693.4981 | 3673.2022 | 3673.2022 | =NH3(lb/hr) * 24(hours/day) * UCNH3($/ton) / 2000(lb/ton) * 60days * CF | =60*24/2000*Ammonia Injection rate (lb/hr)*Ammonia Cost ($/ton)*CF
Initial Catalyst | $ | 1379043.558 | 4925016.8273 | 2593842.1957 | 722335.8013 | 722335.8013 | DCcat=CV (cf)* UC cat($/cf) | DCcat=Gross Catalyst Volume (cf)* UC cat($/cf)
Total Capital Requirement (TCR) | $ | 16131899.2296 | 33115791.307 | 21493104.0211 | 9877821.278 | 9877821.278 |  | Total Capital Requirement (TCR)=SUM(Total Plant Investment (TPI), Preproduction Costs, Inventory Capital)
| $/kW | 107.546 | 220.7719 | 272.0646 | 448.9919 | 448.9919 |  | =Total Capital Requirement (TCR)/(BSIZE(MW)*1000)
SCR O&M Costs |  | Case1 | Case2 | Case3 | Case4 | Case5 |  | Equations (bold indicates existing cuecost model parameter, blue indicates new input value from NOX User Input Sheet, normal text parameters are calculated on this sheet)
Cost Basis (Year) |  | 2015 | 2015 | 2015 | 2015 | 2015
Ammonia | $/yr | 124653.6061 | 124653.6061 | 52885.4466 | 22345.3131 | 22345.3131 | =(8,760/2,000) * (NH3 * CF * UCNH3) | = (8,760/2,000) * (NH3 Injection rate (lb/hr) * Capacity Factor * Cost rate NH3($/ton))
Catalyst Replacement | $/yr | 459681.186 | 1641672.2758 | 864614.0652 | 240778.6004 | 240778.6004 | = CV * UCCAT/ N | = catalyst volume (ft3) * Catalyst cost rate ($/ft3) / catalyst life (yr)
Catalyst Disposal | $/yr | 355.4228 | 1269.3314 | 668.5145 | 186.1686 | 186.1686 | = 48 / 2,000 * Catalyst Replacement Cost * UCWASTE/UCCAT | = 48 / 2,000 * waste disposal rate ($/ton)* Catalyst Replacement Cost($/yr) / Catalyst cost rate ($/ft3)
Electricity | $/yr | 33109.5295 | 154515.4993 | 74701.4411 | 10625.3662 | 10625.3662 | = [-545,133 + 5.801*Qfg] * (CF/0.628) * UCELEC | = [-545,133 + 5.801* flue gas flow rate (acfm)] * (Capacity Factor/0.628) * electricity rate (mills/kWh)*$/1000mills
High-dust SCR Steam | $/yr | 16071.4421 | 16071.4421 | 6788.4131 | 2838.1244 | 2838.1244 | = [-14.91 + 33.29 * NH3 *CF] * UCSTEAM | = [-14.91 + 33.29 * Ammonia Injection Rate (lb/hr) * Capacity Factor] * Steam Rate ($/MMBtu)
Operating Labor | $/yr | 135163.35 | 135163.35 | 111174.651 | 91916.118 | 91916.118 | = (1,341 + 5.363 * BSIZE) * UCOL | = (1,341 + 5.363 * BSIZE(MW) ) * Operating Labor Wage ($/labor-hr)
Maintenance | $/yr | 209703.6625 | 401336.2927 | 269161.8138 | 130360.1438 | 130360.1438 | = Maintenance Cost % * TPC | =Maintenance(% capital cost/year) * total plant cost ($)
Total O&M Costs | $/yr | 978738.1989 | 2474681.7973 | 1379994.3453 | 499049.8346 | 499049.8346
SNCR - Preliminary |  | Case1 | Case2 | Case3 | Case4 | Case5 |  | Equations (bold indicates existing cuecost model parameter, blue indicates new input value from NOX User Input Sheet, normal text parameters are calculated on this sheet)
Number of Wall Injectors | integer | 18 | 18 | 18 | 18 | 18 | Ni = (8.6 + 0.03* BSIZE - 0.013*n)* NIL | = (8.6 + 0.03* BSIZE (MW) - 0.013* NOX Reduction Eff.)* No. Injection Levels
Number of Lances | integer | 0 | 0 | 0 | 0 | 0 | Nl = (2 + 0.013 BSIZE)* NLL | = (2 + 0.013 BSIZE(MW))* No. Lance Levels
Urea Injection Rate | lb/hr | 498.406 | 498.406 | 211.4533 | 89.3439 | 89.3439 | UREA = 6.5*10^-4 * UREA:NOX * BSIZE * HTR * NOx | = 6.5^10-4 * UREA:NOX ratio * BSIZE(MW)* HTR (Btu/kWh) * NOX(lb/10^6 Btu)
Ammonia Injection Rate | lb/hr | 283.8614 | 283.8614 | 120.4308 | 50.8848 | 50.8848 | NH3 = 3.702 x 10-4 * NH3:NOX ratio * BSIZE * HTR * NOx | =3.702x10^4*NH3:NOX ratio * BSIZE(MW) * HTR (Btu/kWh) * NOX(lb/10^6 Btu)
SNCR Capital Costs |  | Case1 | Case2 | Case3 | Case4 | Case5
Cost Basis (Year) |  | 2015 | 2015 | 2015 | 2015 | 2015
Urea Based SNCR Costs
Urea Storage & Handling | $ | 305336.9713 | 305336.9713 | 213551.0238 | 149101.2278 | 149101.2278 | =If Urea based, then = 38143*(UREA/8.7)^0.417*(0.915), else 0 | =(38143*(UREA injection rate (lb/hour)/8.7)^0.417)*(0.915)
Urea Injection | $ | 453454.3183 | 453454.3183 | 453454.3183 | 453454.3183 | 453454.3183 | =If Urea based, then = (117809+10477*Ni+53111*Nl)*(0.915), else 0 | =(117809+10477*No. Injectors+53111*No. lances)*(0.915)
Controls/Miscellaneous | $ | 189651.7798 | 189651.7798 | 178513.5523 | 169571.5951 | 169571.5951 | =If Urea based, then = (96082+106*BSIZE+898*Ni+2433*Nl)*(0.915), else 0 | =(96082+106*BSIZE(MW)+898*No. injectors+2433*No. lances)*(0.915)
Air Heater Modifications | $ | 352088.5828 | 940668.2759 | 573405.9038 | 213719.6013 | 213719.6013 | =If Urea based, then = 11.2*(Economizer Outlet (ACFM))^0.772*(0.915), else 0 | ACFM AirHeater Inlet = Economizer outlet (wet lb/hour)*0.7302(atm-cf/lbmol/d R)*(678+460)d R/29(lb/lbmol)/1atm; 678 d F is average from Acid Rain Study
Ammonia Based SNCR Costs
Ammonia Storage, Handling, Injection, Controls | $ | 0 | 0 | 0 | 0 | 0 | =If Amonia based then = 63822*(BSIZE)^0.6*(0.655), else 0 | =(63822*(BSIZE(MW))^0.6)*(0.655)
Air Heater Modifications | $ | 0 | 0 | 0 | 0 | 0 | =If Amonia based then = 11.2*(Economizer Outlet (ACFM))^0.772*(0.655), else 0 | ACFM AirHeater Inlet = Economizer outlet (wet lb/hour)*0.7302(atm-cf/lbmol/d R)*(678+460)d R/29(lb/lbmol)/1atm; 678 d F is average from Acid Rain Study
Total Direct Cost | $ | 1300531.6522 | 1889111.3453 | 1418924.7982 | 985846.7424 | 985846.7424 |  | Total Direct Cost=Installation+Purchased Equipment Cost Subtotal
Total Direct Cost with Retrofit Factor | $ | 2080850.6435 | 3022578.1524 | 2270279.6771 | 1577354.7879 | 1577354.7879 |  | Total Direct Cost with Retrofit Factor= Total Direct Cost*Def_RetroFact
General Facilities | $ | 104042.5322 | 151128.9076 | 113513.9839 | 78867.7394 | 78867.7394 |  | =Total Direct Cost with Retrofit Factor*(General Facilities)
Engineering Fees | $ | 208085.0643 | 302257.8152 | 227027.9677 | 157735.4788 | 157735.4788 |  | =Total Direct Cost with Retrofit Factor*(Engineering Fees)
Contingency | $ | 416170.1287 | 604515.6305 | 454055.9354 | 315470.9576 | 315470.9576 |  | =Total Direct Cost with Retrofit Factor*(Contingency)
Total Plant Cost (TPC) | $ | 2809148.3687 | 4080480.5058 | 3064877.5641 | 2129428.9636 | 2129428.9636 |  | Total Plant Cost (TPC)=SUM(four lines above)
Total Plant Cost (TPC) w/ Prime Contractor's Markup | $ | 2893422.8198 | 4202894.921 | 3156823.891 | 2193311.8325 | 2193311.8325
Total Cash Expended (TCE) | $ | 2893422.8198 | 4202894.921 | 3156823.891 | 2193311.8325 | 2193311.8325 |  | Total Cash Expended (TCE)=Total Plant Cost (TPC)*VLOOKUP(2,Constants_CC!AFDC / TCE FACTORS FOR CASE 1,3)
Allow. for Funds During Constr. (AFDC) | $ | 0 | 0 | 0 | 0 | 0 |  | Allow. for Funds During Constr. (AFDC)=Total Plant Cost (TPC)*VLOOKUP(2,Constants_CC!AFDC / TCE FACTORS FOR CASE 1,2)
Total Plant Investment (TPI) | $ | 2893422.8198 | 4202894.921 | 3156823.891 | 2193311.8325 | 2193311.8325 |  | Total Plant Investment (TPI)=Total Cash Expended (TCE)+Allow. for Funds During Constr. (AFDC)
Preproduction Costs | $ | 114120.7642 | 141899.3714 | 96147.7004 | 65682.1375 | 65682.1375 |  | =0.02*TPI+(Op. Lab,$/yr+Maint.,$/yr)/12+(Reagent,$/yr+Water,$/yr)/(12*CF)
Inventory Capital | $ | 52470.4849 | 52470.4849 | 22261.0891 | 9405.8203 | 9405.8203 |  | IF UREA =60*24/2000*Urea Injection rate (lb/hr)*Urea Cost ($/ton); IF AMMONIA =60*24/2000*Ammonia Injection rate (lb/hr)*Ammonia Cost ($/ton)*CF
Total Capital Requirement (TCR) | $ | 3060014.0689 | 4397264.7773 | 3275232.6805 | 2268399.7903 | 2268399.7903 |  | Total Capital Requirement (TCR)=SUM(Total Plant Investment (TPI), Preproduction Costs, Inventory Capital)
| $/kW | 20.4001 | 29.3151 | 41.4586 | 103.1091 | 103.1091 |  | =Total Capital Requirement (TCR)/(BSIZE(MW)*1000)
SNCR O&M Costs |  | Case1 | Case2 | Case3 | Case4 | Case5
Cost Basis (Year) |  | 2015 | 2015 | 2015 | 2015 | 2015
Operating and Supervisory Labor | $/yr | 137970 | 137970 | 137970 | 137970 | 137970 | = 0.25* 8,760 *UCOL | = 0.25 * 8,760 * supervisory and labor wage rate ($/hr)
Maintenance Labor and Materials | $/yr | 42137.2255 | 61207.2076 | 45973.1635 | 31941.4345 | 31941.4345 | =Maintenance Cost %* TPC | = Maintenance(% capital cost/year) * total plant cost ($)
Reagent | $/yr | 319195.4497 | 319195.4497 | 135421.6251 | 57218.7399 | 57218.7399 | IF UREA =Urea *8760* CF/2,000 * UCUREA*(1+ Esc. Consumables O&M)^(Cost Basis year-1998); IF AMMONIA = NH3 *8760* CF/2,000 * UCHN3 | (IF UREA =Injection rate of pure Urea(lb/hr) *8760* CF/2,000 * Urea cost rate ($/ton)*(1+ Esc. Consumables O&M)^(Cost Basis year-1998); IF AMMONIA = Injection rate of ammonia (lb/hr) *8760* CF/2,000 * Ammonia cost rate ($/ton))
Electricity | $/yr | 1592.8965 | 1592.8965 | 1592.8965 | 1592.8965 | 1592.8965 | IF UREA (5.97 + 0.29* NI + 0.87* NL) *8760* CF*UCELEC*(1+ Esc. Consumables O&M)^(Cost Basis year-1998); IF AMMONIA Steam ((BSIZE* 0.12 * 8,760 * CF)*UCELEC; if Ammonia Air:(BSIZE *4.23 * 8,760 * CF))*UCELE | (IF UREA = (5.97 + 0.29* No. Wall Injectors + 0.87* No. Lances) * 8760* CF * Electricity cost ($/kWh); IF AMMONIA and steam = ((BSIZE* 0.12 * 8,760 * CF)* Electricity cost ($/kWh)), IF AMMONIA and air = (BSIZE *4.23 * 8,760 * CF))*UCELE
Water | $/yr | 2502.8546 | 2502.8546 | 2502.8546 | 2502.8546 | 2502.8546 | IF AMMONIA = (1.0 * NI + 2.5* NL) *60 *8760* CF/1,000 * UCH2O | IF AMMONIA = (1.0 * No. Wall Injectors + 2.5* No. Lances) *60 *8760* CF/1,000 * Water cost rate ($/1000 gal)
Steam (for steam atomization) | $/yr | 0 | 0 | 0 | 0 | 0 | IF UREA and Steam = BSIZE * 99.2 * 8,760* CF/1,000*UCSTEAM | IF UREAand steam =BSIZE(MW) * 99.2 * 8,760* CF/1,000 * Steam atomization cost rate ($/1000 lb)
Total O&M Costs | $/yr | 503398.4264 | 522468.4085 | 323460.5397 | 231225.9255 | 231225.9255
Low NOX Burner Technology Capital Costs |  | Case1 | Case2 | Case3 | Case4 | Case5
Cost Basis (Year) |  | 2015 | 2015 | 2015 | 2015 | 2015
Total Capital Requirement with Retrofit (TCR) | $ | 22156487.7519 | 22156487.7519 | 18034907.5032 | 11964465.5489 | 1882494.9368 | IF(Boiler Type="T",IF(RD="H",57.04*(300/BSIZE)^0.679, IF(RD="L",11.71,21.2*(300/BSIZE)^0.35)), IF(Boiler Type="W",IF(RD="H",27.72*(300/BSIZE)^0.573, IF(RD="L",6.53*(300/BSIZE)^0.857,15.37*(300/BSIZE)^0.35))),0)*1000*BSIZE*388/357.6
| $/kW | 147.7099 | 147.7099 | 228.29 | 543.8393 | 85.568 |  | =Total Capital Requirement (TCR)/(BSIZE(MW)*1000)
Low NOX Burner Technology O&M Costs |  | Case1 | Case2 | Case3 | Case4 | Case5 |  | Equations (bold indicates existing cuecost model parameter, blue indicates new input value from NOX User Input Sheet, normal text parameters are calculated on this sheet)
Cost Basis (Year) |  | 2015 | 2015 | 2015 | 2015 | 2015
Maintenance Labor | $/yr | 177251.902 | 177251.902 | 144279.26 | 95715.7244 | 15059.9595 | =0.008 * TPC | =0.008/yr * Total Plant Costs ($)
Maintenance Materials | $/yr | 265877.853 | 265877.853 | 216418.89 | 143573.5866 | 22589.9392 | =0.012 * TPC | =0.012/yr * Total Plant Costs ($)
Control, Administration, Overhead | $/yr | 53175.5706 | 53175.5706 | 43283.778 | 28714.7173 | 4517.9878 | =0.3*Maintenance Labor Cost | =0.3*Maintenance Labor Cost($/year)
Total O&M Costs | $/yr | 496305.3256 | 496305.3256 | 403981.9281 | 268004.0283 | 42167.8866
Natural Gas Reburning - Preliminary |  | Case1 | Case2 | Case3 | Case4 | Case5
Fraction of heat input as reburn fuel | fraction | 0.15 | 0.15 | 0.15 | 0.15 | 0.15 | if(input>0,input, if(NOx=0,0.15,RBFRAC =(n - 0.48) / 0.86 | RBFRAC =(Nox Reduction Efficiency - 0.48) / 0.86
Bottom Ash Rate | tons/yr | 131.0147 | 467.8965 | 246.4255 | 68.6248 | 68.6248 | BA = BAF * ASH * (500/HHV) * Qin * 8,760 * CF/2,000 | BA = Bottom ash Factor * percent ash in coal (%wt) * (500/HHV) * boiler heat input (MMBtu/hr) * 8,760 * CF/2,000
Natural Gas Reburning Capital Costs |  | Case1 | Case2 | Case3 | Case4 | Case5
Cost Basis (Year) |  | 2015 | 2015 | 2015 | 2015 | 2015
Gas Pipeline from Fenceline to Boiler | $ | 913808.9195 | 913808.9195 | 692973.6644 | 515683.3893 | 515683.3893 | =372.7*EXP(.00264*MW)*1000 replaced by 1923*MW+276519 (nk 1/24/00) | =372.7*EXP(.00624*MW Output)*1000
Fuel Injectors, Overfire Air Ports and Associated Piping, Valves, Windbox and Control Dampers | $ | 2488045.9936 | 2488045.9936 | 1918523.228 | 1306349.1118 | 1306349.1118 | =(BSIZE/500)^0.214*(BSIZE*3237.657+1504675) | =(BSIZE/500)^0.214*(BSIZE*m+b), m= 3237.657, b= 1504675
Total Direct Cost | $ | 3401854.9131 | 3401854.9131 | 2611496.8924 | 1822032.5011 | 1822032.5011 |  | Total Direct Cost=Installation+Purchased Equipment Cost Subtotal
Total Direct Cost with Retrofit Factor | $ | 5442967.8609 | 5442967.8609 | 4178395.0279 | 2915252.0017 | 2915252.0017 |  | Total Direct Cost with Retrofit Factor= Total Direct Cost*Def_RetroFact
General Facilities | $ | 108859.3572 | 108859.3572 | 83567.9006 | 58305.04 | 58305.04 |  | =Total Direct Cost with Retrofit Factor*(General Facilities)
Engineering Fees | $ | 544296.7861 | 544296.7861 | 417839.5028 | 291525.2002 | 291525.2002 |  | =Total Direct Cost with Retrofit Factor*(Engineering Fees)
Contingency | $ | 1088593.5722 | 1088593.5722 | 835679.0056 | 583050.4003 | 583050.4003 |  | =Total Direct Cost with Retrofit Factor*(Contingency)
Total Plant Cost (TPC) | $ | 7184717.5764 | 7184717.5764 | 5515481.4368 | 3848132.6422 | 3848132.6422 |  | Total Plant Cost (TPC)=SUM(four lines above)
Total Plant Cost (TPC) w/ Prime Contractor's Markup | $ | 7400259.1037 | 7400259.1037 | 5680945.8799 | 3963576.6215 | 3963576.6215
Total Cash Expended (TCE) | $ | 7400259.1037 | 7400259.1037 | 5680945.8799 | 3963576.6215 | 3963576.6215 |  | Total Cash Expended (TCE)=Total Plant Cost (TPC)*VLOOKUP(2,Constants_CC!AFDC / TCE FACTORS FOR CASE 1,3)
Allow. for Funds During Constr. (AFDC) | $ | 0 | 0 | 0 | 0 | 0 |  | Allow. for Funds During Constr. (AFDC)=Total Plant Cost (TPC)*VLOOKUP(2,Constants_CC!AFDC / TCE FACTORS FOR CASE 1,2)
Total Plant Investment (TPI) | $ | 7400259.1037 | 7400259.1037 | 5680945.8799 | 3963576.6215 | 3963576.6215 |  | Total Plant Investment (TPI)=Total Cash Expended (TCE)+Allow. for Funds During Constr. (AFDC)
Preproduction Costs | $ | 154543.5094 | 148284.5177 | 115929.1502 | 82804.0424 | 82804.0424 |  | =0.02*TPI+(Maint.,$/yr)/12+(Waste Disp.,$/yr)/(12*CF)
Inventory Capital | $ | 0 | 0 | 0 | 0 | 0 |  | 0
Total Capital Requirement (TCR) | $ | 7554802.6131 | 7548543.6213 | 5796875.0301 | 4046380.6639 | 4046380.6639 |  | Total Capital Requirement (TCR)=SUM(Total Plant Investment (TPI), Preproduction Costs, Inventory Capital)
| $/kW | 50.3654 | 50.3236 | 73.3782 | 183.9264 | 183.9264 |  | =Total Capital Requirement (TCR)/(BSIZE(MW)*1000)
Natural Gas Reburning O&M Costs |  | Case1 | Case2 | Case3 | Case4 | Case5
Cost Basis (Year) |  | 2015 | 2015 | 2015 | 2015 | 2015
Electrical Consumption Savings | $/yr | -15239.1146 | -54423.8761 | -28663.2414 | -7982.1685 | -7982.1685 | =9.51 * 10^7 * Qin * CF * RBFRAC/HHV * UCELEC | =9.51 * 10^7 * boiler heat input(MMBtu/hr) * CF * Fraction of heat input as reburn fuel / HHV(Btu/lb) * Electricity Rate($/kW)
Maintenance | $/yr | 107669.6995 | 107669.6995 | 82663.4326 | 57690.0452 | 57690.0452 | =Maintenance (% capital cost)*TPC-1387.5*RBFRAC*(BSIZE/500)^0.6 | =Maintenance(% capital cost) * Total Plant Cost($) - 1387.5 * Fraction of heat input as reburn fuel * (BSIZE(MW) / 500)^0.6
Waste Disposal Savings | $/yr | -18986.3512 | -67806.4871 | -35711.4165 | -9944.9514 | -9944.9514 | = [BA * RBFRAC + 4.336 * RBFRAC *PPHPRT * CF] * UCWASTE | = [Bottom ash rate(tons/year) * fraction of heat input as reburn fuel + 4.336 * fraction of heat input as reburn fuel * fly ash rate (ton/hr) * 2000 * CF] * Waste Disposal Rate($/ton)
Natural Gas Consumption | $/yr | 343835.037 | 1227947.684 | 646719.1135 | 180098.9936 | 180098.9936 | = Qin * RBFRAC * 8,760 * CF * UCGAS | = boiler heat input(MMBtu/hr) * fraction of heat input as reburn fuel * 8,760 * CF * Unit cost of gas ($/mmBtu)
Total O&M Costs |  | 417279.2707 | 1213387.0203 | 665007.8882 | 219861.9189 | 219861.9189
Note on A51: Assumes user input cost is current cost (cost basis).
Note on A52: Assumes user input cost is current cost (cost basis).
Note on A53: Assumes user input cost is current cost (cost basis).
Note on A54: Assumes user input cost is current cost (cost basis).
Note on A55: Assumes user input cost is current cost (cost basis).
Note on A56: Assumes user input cost is current cost (cost basis).
Note on A95: Assumes user input cost is current cost (cost basis).
Note on A105: Assumes user input cost is current cost (cost basis).
Note on A107: Assumes user input cost is current cost (cost basis).
Note on A108: Assumes user input cost is current cost (cost basis).
Note on A109: Assumes user input cost is current cost (cost basis).
Note on A110: Assumes user input cost is current cost (cost basis).

## LSFO Cost & Tech. Results
LSFO Material Balance - Preliminary |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Flue Gas, Downstream of ID Fans
Temperature | °F |  | 295 | 295 | 295 | 295 | 295
Pressure | in. H2O |  | 10 | 10 | 10 | 10 | 10
Flow Rate | SCFM |  | 205105.5902 | 732569.9506 | 385820.174 | 107443.5927 | 107443.5927
Flow Rate | ACFM |  | 295677.9476 | 1056064.7283 | 556194.0902 | 154889.4935 | 154889.4935
CO2 | lb/hr |  | 167773.1629 | 599172.9887 | 315564.4407 | 87878.705 | 87878.705
N2 | lb/hr |  | 662514.4698 | 2366056.4549 | 1246123.0663 | 347021.6134 | 347021.6134
SO2 | lb/hr |  | 193.83 | 1407.2582 | 741.156 | 206.3979 | 206.3979
O2 | lb/hr |  | 52552.2095 | 187681.1755 | 98845.4191 | 27526.5724 | 27526.5724
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 149.9231 | 535.4247 | 281.9904 | 78.529 | 78.529
H2O | lb/hr |  | 59658.7384 | 213060.9208 | 112212.085 | 31248.935 | 31248.935
Fly Ash | lb/hr |  | 14.91 | 53.2485 | 28.0442 | 7.8098 | 7.8098
Total (gas only) | lb/hr |  | 942842.3336 | 3367914.223 | 1773768.1574 | 493960.7527 | 493960.7527
Flue Gas, to Absorber
Temperature | °F |  | 295 | 295 | 295 | 295 | 295
Pressure | in. H2O |  | 10 | 10 | 10 | 10 | 10
Flow Rate | SCFM |  | 205105.5902 | 732569.9506 | 385820.174 | 107443.5927 | 107443.5927
Flow Rate | ACFM |  | 295677.9476 | 1056064.7283 | 556194.0902 | 154889.4935 | 154889.4935
CO2 | lb/hr |  | 167773.1629 | 599172.9887 | 315564.4407 | 87878.705 | 87878.705
N2 | lb/hr |  | 662514.4698 | 2366056.4549 | 1246123.0663 | 347021.6134 | 347021.6134
SO2 | lb/hr |  | 193.83 | 1407.2582 | 741.156 | 206.3979 | 206.3979
O2 | lb/hr |  | 52552.2095 | 187681.1755 | 98845.4191 | 27526.5724 | 27526.5724
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 149.9231 | 535.4247 | 281.9904 | 78.529 | 78.529
H2O | lb/hr |  | 59658.7384 | 213060.9208 | 112212.085 | 31248.935 | 31248.935
Fly Ash | lb/hr |  | 14.91 | 53.2485 | 28.0442 | 7.8098 | 7.8098
Total (gas only) | lb/hr |  | 942842.3336 | 3367914.223 | 1773768.1574 | 493960.7527 | 493960.7527
Flue Gas, from Absorbers (total)
Temperature | °F |  | 127 | 127 | 127 | 127 | 127
Pressure | in. H2O |  | 4 | 4 | 4 | 4 | 4
Flow Rate | SCFM |  | 213946.1899 | 765041.9075 | 402922.0713 | 112206.1464 | 112206.1464
Flow Rate | ACFM |  | 243352.1669 | 870193.6039 | 458301.9647 | 127628.3952 | 127628.3952
CO2 | lb/hr |  | 167839.7417 | 600091.412 | 316048.1436 | 88013.4071 | 88013.4071
N2 | lb/hr |  | 662835.5056 | 2370484.9889 | 1248455.4275 | 347671.1317 | 347671.1317
SO2 | lb/hr |  | 96.915 | 70.3629 | 37.0578 | 10.3199 | 10.3199
O2 | lb/hr |  | 52624.8218 | 188682.8266 | 99372.9553 | 27673.4812 | 27673.4812
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 149.9231 | 535.4247 | 281.9904 | 78.529 | 78.529
H2O | lb/hr |  | 84551.9879 | 301995.3028 | 159050.8595 | 44292.6444 | 44292.6444
Fly Ash | lb/hr |  | 14.91 | 53.2485 | 28.0442 | 7.8098 | 7.8098
Total (gas only) | lb/hr |  | 968098.8952 | 3461860.3178 | 1823246.434 | 507739.5133 | 507739.5133
Heat Capacities
O2 | Btu/lbmol°F |  | 7.2129 | 7.2129 | 7.2129 | 7.2129 | 7.2129
CO2 | Btu/lbmol°F |  | 9.3543 | 9.3543 | 9.3543 | 9.3543 | 9.3543
N2 | Btu/lbmol°F |  | 6.9989 | 6.9989 | 6.9989 | 6.9989 | 6.9989
H2O | Btu/lbmol°F |  | 8.0694 | 8.0694 | 8.0694 | 8.0694 | 8.0694
NO | Btu/lbmol°F |  | 7.1644 | 7.1644 | 7.1644 | 7.1644 | 7.1644
SO2 | Btu/lbmol°F |  | 9.8301 | 9.8301 | 9.8301 | 9.8301 | 9.8301
HCl | Btu/lbmol°F |  | 6.951 | 6.951 | 6.951 | 6.951 | 6.951
O2 | Btu/lb°F |  | 0.22541 | 0.22541 | 0.22541 | 0.22541 | 0.22541
CO2 | Btu/lb°F |  | 0.21255 | 0.21255 | 0.21255 | 0.21255 | 0.21255
N2 | Btu/lb°F |  | 0.24978 | 0.24978 | 0.24978 | 0.24978 | 0.24978
H2O | Btu/lb°F |  | 0.44792 | 0.44792 | 0.44792 | 0.44792 | 0.44792
NO | Btu/lb°F |  | 0.23874 | 0.23874 | 0.23874 | 0.23874 | 0.23874
SO2 | Btu/lb°F |  | 0.15344 | 0.15344 | 0.15344 | 0.15344 | 0.15344
HCl | Btu/lb°F |  | 0.19064 | 0.19064 | 0.19064 | 0.19064 | 0.19064
Reheated Gas Temperature: | °C |  | 66.6667 | 66.6667 | 66.6667 | 66.6667 | 66.6667
| K |  | 339.6667 | 339.6667 | 339.6667 | 339.6667 | 339.6667
FGD Outlet Temperature: | °C |  | 52.7778 | 52.7778 | 52.7778 | 52.7778 | 52.7778
| K |  | 325.7778 | 325.7778 | 325.7778 | 325.7778 | 325.7778
Total Btu/hr | Btu/hr |  | 6275627.7915 | 22439925.17 | 11818360.5896 | 3291189.0249 | 3291189.0249
Hot Reheat Air
Temperature | °F |  | 440 | 440 | 440 | 440 | 440
Pressure | in. H2O |  | 1 | 1 | 1 | 1 | 1
Flow Rate | SCFM |  | 19267.1724 | 68894.1285 | 36284.241 | 10104.4722 | 10104.4722
Flow Rate | ACFM |  | 33852.2694 | 121046.4381 | 63751.1241 | 17753.4776 | 17753.4776
N2 | lb/hr |  | 66105.564 | 236375.381 | 124491.034 | 34668.3892 | 34668.3892
O2 | lb/hr |  | 19935.7792 | 71284.8832 | 37543.3718 | 10455.1162 | 10455.1162
H2O | lb/hr |  | 1133.27 | 4052.2629 | 2134.1918 | 594.3319 | 594.3319
Total | lb/hr |  | 87174.6132 | 311712.5271 | 164168.5976 | 45717.8373 | 45717.8373
Heat Capacities of Hot Reheat Air
O2 | Btu/lbmol°F |  | 7.3317 | 7.3317 | 7.3317 | 7.3317 | 7.3317
N2 | Btu/lbmol°F |  | 7.113 | 7.113 | 7.113 | 7.113 | 7.113
H2O | Btu/lbmol°F |  | 8.3379 | 8.3379 | 8.3379 | 8.3379 | 8.3379
O2 | Btu/lb°F |  | 0.22912 | 0.22912 | 0.22912 | 0.22912 | 0.22912
N2 | Btu/lb°F |  | 0.25385 | 0.25385 | 0.25385 | 0.25385 | 0.25385
H2O | Btu/lb°F |  | 0.46282 | 0.46282 | 0.46282 | 0.46282 | 0.46282
Heated Temperature: | °C |  | 226.6667 | 226.6667 | 226.6667 | 226.6667 | 226.6667
| K |  | 499.6667 | 499.6667 | 499.6667 | 499.6667 | 499.6667
FGD Outlet Temperature: | °C |  | 66.6667 | 66.6667 | 66.6667 | 66.6667 | 66.6667
| K |  | 339.6667 | 339.6667 | 339.6667 | 339.6667 | 339.6667
Heat Capacities of Inlet Reheat Air
O2 | Btu/lbmol°F |  | 7.3043 | 7.3043 | 7.3043 | 7.3043 | 7.3043
N2 | Btu/lbmol°F |  | 7.0867 | 7.0867 | 7.0867 | 7.0867 | 7.0867
H2O | Btu/lbmol°F |  | 8.276 | 8.276 | 8.276 | 8.276 | 8.276
O2 | Btu/lb°F |  | 0.22827 | 0.22827 | 0.22827 | 0.22827 | 0.22827
N2 | Btu/lb°F |  | 0.25291 | 0.25291 | 0.25291 | 0.25291 | 0.25291
H2O | Btu/lb°F |  | 0.45938 | 0.45938 | 0.45938 | 0.45938 | 0.45938
Heated Temperature: | °C |  | 226.6667 | 226.6667 | 226.6667 | 226.6667 | 226.6667
| K |  | 499.6667 | 499.6667 | 499.6667 | 499.6667 | 499.6667
Inlet Air Temperature: | °C |  | 26.6667 | 26.6667 | 26.6667 | 26.6667 | 26.6667
| K |  | 299.6667 | 299.6667 | 299.6667 | 299.6667 | 299.6667
Required Heat | Btu/hr |  | 7844534.7393 | 28049906.4625 | 14772950.7369 | 4113986.2812 | 4113986.2812
Oxidation Air (total)
Temperature | °F |  | 60 | 60 | 60 | 60 | 60
Pressure | in. H2O |  | 0 | 0 | 0 | 0 | 0
Flow Rate | SCFM |  | 93.5442 | 1290.3969 | 679.609 | 189.2582 | 189.2582
Flow Rate | ACFM |  | 95.1987 | 1313.2202 | 691.6293 | 192.6056 | 192.6056
N2 | lb/hr |  | 321.0359 | 4428.5339 | 2332.3612 | 649.5183 | 649.5183
O2 | lb/hr |  | 96.8164 | 1335.5347 | 703.3816 | 195.8784 | 195.8784
H2O | lb/hr |  | 5.4321 | 74.9329 | 39.4647 | 10.9902 | 10.9902
Total (gas only) | lb/hr |  | 423.2843 | 5839.0015 | 3075.2075 | 856.3869 | 856.3869
Limestone to Ball Mill
Temperature | °F |  | 80 | 80 | 80 | 80 | 80
Wt.% Solids | wt. % |  | 100% | 100% | 100% | 100% | 100%
Inerts | lb/hr |  | 7.8409 | 108.1618 | 56.9652 | 15.8637 | 15.8637
CaCO3 | lb/hr |  | 158.9873 | 2193.1527 | 1155.0604 | 321.6624 | 321.6624
Total | lb/hr |  | 166.8282 | 2301.3145 | 1212.0256 | 337.5261 | 337.5261
Limestone Slurry to Limestone Slurry Tank
Temperature | °F |  | 90 | 90 | 90 | 90 | 90
Flow Rate | GPM |  | 0.59534 | 8.2124 | 4.3252 | 1.2045 | 1.2045
Wt.% Solids | wt. % |  | 40% | 40% | 40% | 40% | 40%
Inerts | lb/hr |  | 7.8409 | 108.1618 | 56.9652 | 15.8637 | 15.8637
CaCO3 | lb/hr |  | 158.9873 | 2193.1527 | 1155.0604 | 321.6624 | 321.6624
H2O | lb/hr |  | 250.2424 | 3451.9717 | 1818.0384 | 506.2892 | 506.2892
Total | lb/hr |  | 417.0706 | 5753.2862 | 3030.0641 | 843.8153 | 843.8153
Limestone Slurry to Reaction Mix Tank (total)
Temperature | °F |  | 68 | 68 | 68 | 68 | 68
Flow Rate | GPM |  | 1.3891 | 19.1623 | 10.0921 | 2.8105 | 2.8105
Wt.% Solids | wt. % |  | 20% | 20% | 20% | 20% | 20%
Inerts | lb/hr |  | 7.8409 | 108.1618 | 56.9652 | 15.8637 | 15.8637
CaCO3 | lb/hr |  | 158.9873 | 2193.1527 | 1155.0604 | 321.6624 | 321.6624
H2O | lb/hr |  | 667.313 | 9205.258 | 4848.1025 | 1350.1045 | 1350.1045
Total | lb/hr |  | 834.1412 | 11506.5725 | 6060.1282 | 1687.6306 | 1687.6306
Slurry to Absorber
Temperature | °F |  | 126 | 126 | 126 | 126 | 126
Flow Rate | GPM |  | 30047.4055 | 60169.3991 | 31689.2169 | 8824.8452 | 8824.8452
Wt.% Solids | wt. % |  | 15% | 15% | 15% | 15% | 15%
CaSO3*1/2H2O | lb/hr |  | 0 | 0 | 0 | 0 | 0
CaSO4*2H2O | lb/hr |  | 2448767.7202 | 4903614.1292 | 2582570.1081 | 719196.739 | 719196.739
Inerts | lb/hr |  | 73716.8303 | 147616.6512 | 77744.7696 | 21650.4422 | 21650.4422
CaCl2 | lb/hr |  | 0 | 0 | 0 | 0 | 0
CaCO3 | lb/hr |  | 71177.446 | 142531.5791 | 75066.6317 | 20904.6316 | 20904.6316
H2O | lb/hr |  | 14697417.9799 | 29431320.0376 | 15500495.2198 | 4316593.6055 | 4316593.6055
Total | lb/hr |  | 17291079.9764 | 34625082.3972 | 18235876.7292 | 5078345.4183 | 5078345.4183
Slurry from Rxn Tank to Thickener
Temperature | °F |  | 126 | 126 | 126 | 126 | 126
Flow Rate | GPM |  | 3.196 | 44.0874 | 23.2193 | 6.4661 | 6.4661
Wt.% Solids | wt. % |  | 15% | 15% | 15% | 15% | 15%
CaSO3*1/2H2O | lb/hr |  | 0 | 0 | 0 | 0 | 0
CaSO4*2H2O | lb/hr |  | 260.4644 | 3592.9797 | 1892.3027 | 526.9704 | 526.9704
Inerts | lb/hr |  | 7.8409 | 108.1618 | 56.9652 | 15.8637 | 15.8637
CaCl2 | lb/hr |  | 0 | 0 | 0 | 0 | 0
CaCO3 | lb/hr |  | 7.5708 | 104.4358 | 55.0029 | 15.3173 | 15.3173
H2O | lb/hr |  | 1563.2982 | 21564.9384 | 11357.5342 | 3162.8576 | 3162.8576
Total | lb/hr |  | 1839.1743 | 25370.5158 | 13361.805 | 3721.009 | 3721.009
LSFO Equipment Capital Costs |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 2015 | 2015 | 2015 | 2015 | 2015
Sizing Criteria
Reagent Feed System | $ | kpph Reag. | 10628589.0202 | 10841638.2832 | 10733739.4249 | 10645871.0526 | 10645871.0526
Ball Mill & Hydroclone System | $ | TPH Reag. | 2767929.7805 | 2803651.0252 | 2785407.5015 | 2770782.3489 | 2770782.3489
DBA Acid Tank (pump, heater, agitator) | $ | gpm DBA | 0 | 173856.2573 | 145005.6641 | 100986.2204 | 100986.2204
SO2 Removal System | $ | kpph SO2 | 2850322.3506 | 2912746.3287 | 2878580.3345 | 2850973.0951 | 2850973.0951
Absorber Tower | $ | kACFM | 8477990.7924 | 17378086.3258 | 12106088.7237 | 5888160.0433 | 5888160.0433 |  |  | Calculated Number of Spray Pumps
Spray Pumps | $ | slurry gpm | 629404.2863 | 1259738.5916 | 649660.0067 | 303471.1611 | 303471.1611 | 1 | 2 | 1 | 1 | 1
Flue Gas Handling System | $ | * | 4823010.579 | 7724400.1009 | 5894666.9884 | 4210189.2372 | 4210189.2372
ID Fans | $ | ACFM | 973101.0298 | 2325052.0666 | 1499365.4503 | 625225.441 | 625225.441 |  |  | Calculated No. of ID Fans and Flue Gas Flow per Fan
Waste / Byproduct Handling System | $ | kpph SO2 | 120817.6464 | 124040.1816 | 122273.4001 | 120851.1145 | 120851.1145 | 156215.5295 | 557950.6759 | 293854.0226 | 81832.7658 | 81832.7658
Thickener System | $ | TPH solids | 172634.5443 | 196361.8513 | 184253.1337 | 174532.0506 | 174532.0506 | 2 | 2 | 2 | 2 | 2
Support Equipment | $ | MW | 2167145.1696 | 2167145.1696 | 1980684.3446 | 1820207.674 | 1820207.674
Chimney | $ | ACFM | 3768538.6103 | 5766957.8146 | 4655513.4848 | 3037979.4812 | 3037979.4812
TOTAL | $ |  | 37379483.8094 | 53673673.9963 | 43635238.4573 | 32549228.92 | 32549228.92
* Based on flue gas flow and reheat temperature.
Capital Costs with Retrofit Factors
Reagent Feed System | $ |  | 17005742.4323 | 17346621.2531 | 17173983.0798 | 17033393.6842 | 17033393.6842
Ball Mill & Hydroclone System | $ |  | 4428687.6489 | 4485841.6403 | 4456652.0024 | 4433251.7582 | 4433251.7582
DBA Acid Tank (pump, heater, agitator) | $ |  | 0 | 278170.0116 | 232009.0625 | 161577.9527 | 161577.9527
SO2 Removal System | $ |  | 4560515.761 | 4660394.1259 | 4605728.5352 | 4561556.9521 | 4561556.9521
Absorber Tower | $ |  | 13564785.2679 | 27804938.1213 | 19369741.958 | 9421056.0693 | 9421056.0693
Spray Pumps | $ |  | 1007046.858 | 2015581.7466 | 1039456.0108 | 485553.8577 | 485553.8577
Flue Gas Handling System | $ |  | 7716816.9265 | 12359040.1614 | 9431467.1815 | 6736302.7795 | 6736302.7795
ID Fans | $ |  | 1556961.6476 | 3720083.3065 | 2398984.7204 | 1000360.7057 | 1000360.7057
Waste / Byproduct Handling System | $ |  | 193308.2342 | 198464.2905 | 195637.4401 | 193361.7832 | 193361.7832
Thickener System | $ |  | 276215.2709 | 314178.9621 | 294805.014 | 279251.281 | 279251.281
Support Equipment | $ |  | 3467432.2713 | 3467432.2713 | 3169094.9514 | 2912332.2784 | 2912332.2784
Chimney | $ |  | 6029661.7765 | 9227132.5033 | 7448821.5757 | 4860767.17 | 4860767.17
TOTAL | $ |  | 59807174.0951 | 85877878.3941 | 69816381.5317 | 52078766.2721 | 52078766.2721
General Facilities
Reagent Feed System | $ |  | 1700574.2432 | 1734662.1253 | 1717398.308 | 1703339.3684 | 1703339.3684
Ball Mill & Hydroclone System | $ |  | 442868.7649 | 448584.164 | 445665.2002 | 443325.1758 | 443325.1758
DBA Acid Tank (pump, heater, agitator) | $ |  | 0 | 27817.0012 | 23200.9062 | 16157.7953 | 16157.7953
SO2 Removal System | $ |  | 456051.5761 | 466039.4126 | 460572.8535 | 456155.6952 | 456155.6952
Absorber Tower | $ |  | 1356478.5268 | 2780493.8121 | 1936974.1958 | 942105.6069 | 942105.6069
Spray Pumps | $ |  | 100704.6858 | 201558.1747 | 103945.6011 | 48555.3858 | 48555.3858
Flue Gas Handling System | $ |  | 771681.6926 | 1235904.0161 | 943146.7181 | 673630.2779 | 673630.2779
ID Fans | $ |  | 155696.1648 | 372008.3307 | 239898.472 | 100036.0706 | 100036.0706
Waste / Byproduct Handling System | $ |  | 19330.8234 | 19846.4291 | 19563.744 | 19336.1783 | 19336.1783
Thickener System | $ |  | 27621.5271 | 31417.8962 | 29480.5014 | 27925.1281 | 27925.1281
Support Equipment | $ |  | 346743.2271 | 346743.2271 | 316909.4951 | 291233.2278 | 291233.2278
Chimney | $ |  | 602966.1776 | 922713.2503 | 744882.1576 | 486076.717 | 486076.717
TOTAL | $ |  | 5980717.4095 | 8587787.8394 | 6981638.1532 | 5207876.6272 | 5207876.6272
Engineering Fees
Reagent Feed System | $ |  | 1700574.2432 | 1734662.1253 | 1717398.308 | 1703339.3684 | 1703339.3684
Ball Mill & Hydroclone System | $ |  | 442868.7649 | 448584.164 | 445665.2002 | 443325.1758 | 443325.1758
DBA Acid Tank (pump, heater, agitator) | $ |  | 0 | 27817.0012 | 23200.9062 | 16157.7953 | 16157.7953
SO2 Removal System | $ |  | 456051.5761 | 466039.4126 | 460572.8535 | 456155.6952 | 456155.6952
Absorber Tower | $ |  | 1356478.5268 | 2780493.8121 | 1936974.1958 | 942105.6069 | 942105.6069
Spray Pumps | $ |  | 100704.6858 | 201558.1747 | 103945.6011 | 48555.3858 | 48555.3858
Flue Gas Handling System | $ |  | 771681.6926 | 1235904.0161 | 943146.7181 | 673630.2779 | 673630.2779
ID Fans | $ |  | 155696.1648 | 372008.3307 | 239898.472 | 100036.0706 | 100036.0706
Waste / Byproduct Handling System | $ |  | 19330.8234 | 19846.4291 | 19563.744 | 19336.1783 | 19336.1783
Thickener System | $ |  | 27621.5271 | 31417.8962 | 29480.5014 | 27925.1281 | 27925.1281
Support Equipment | $ |  | 346743.2271 | 346743.2271 | 316909.4951 | 291233.2278 | 291233.2278
Chimney | $ |  | 602966.1776 | 922713.2503 | 744882.1576 | 486076.717 | 486076.717
TOTAL | $ |  | 5980717.4095 | 8587787.8394 | 6981638.1532 | 5207876.6272 | 5207876.6272
Contingency
Reagent Feed System | $ |  | 3401148.4865 | 3469324.2506 | 3434796.616 | 3406678.7368 | 3406678.7368
Ball Mill & Hydroclone System | $ |  | 885737.5298 | 897168.3281 | 891330.4005 | 886650.3516 | 886650.3516
DBA Acid Tank (pump, heater, agitator) | $ |  | 0 | 55634.0023 | 46401.8125 | 32315.5905 | 32315.5905
SO2 Removal System | $ |  | 912103.1522 | 932078.8252 | 921145.707 | 912311.3904 | 912311.3904
Absorber Tower | $ |  | 2712957.0536 | 5560987.6243 | 3873948.3916 | 1884211.2139 | 1884211.2139
Spray Pumps | $ |  | 201409.3716 | 403116.3493 | 207891.2022 | 97110.7715 | 97110.7715
Flue Gas Handling System | $ |  | 1543363.3853 | 2471808.0323 | 1886293.4363 | 1347260.5559 | 1347260.5559
ID Fans | $ |  | 311392.3295 | 744016.6613 | 479796.9441 | 200072.1411 | 200072.1411
Waste / Byproduct Handling System | $ |  | 38661.6468 | 39692.8581 | 39127.488 | 38672.3566 | 38672.3566
Thickener System | $ |  | 55243.0542 | 62835.7924 | 58961.0028 | 55850.2562 | 55850.2562
Support Equipment | $ |  | 693486.4543 | 693486.4543 | 633818.9903 | 582466.4557 | 582466.4557
Chimney | $ |  | 1205932.3553 | 1845426.5007 | 1489764.3151 | 972153.434 | 972153.434
TOTAL | $ |  | 11961434.819 | 17175575.6788 | 13963276.3063 | 10415753.2544 | 10415753.2544
Total Plant Cost (TPC) | $ |  | 83730043.7331 | 120229029.7518 | 97742934.1444 | 72910272.7809 | 72910272.7809
Total Plant Cost (TPC) w/ Prime Contractor's Markup | $ |  | 86241945.0451 | 123835900.6443 | 100675222.1687 | 75097580.9643 | 75097580.9643
Total Cash Expended (TCE) | $ |  | 86241945.0451 | 123835900.6443 | 100675222.1687 | 75097580.9643 | 75097580.9643
Allow. for Funds During Constr. (AFDC) | $ |  | 0 | 0 | 0 | 0 | 0
Total Plant Investment (TPI) | $ |  | 86241945.0451 | 123835900.6443 | 100675222.1687 | 75097580.9643 | 75097580.9643
Preproduction Costs | $ |  | 2232307.4707 | 3158641.7988 | 2495826.6251 | 1788002.1846 | 1788002.1846
Inventory Capital | $ |  | 1801.745 | 24854.1965 | 13089.8768 | 3645.2822 | 3645.2822
Total Capital Requirement (TCR) | $ |  | 88476054.2608 | 127019396.6397 | 103184138.6707 | 76889228.4311 | 76889228.4311
| $/kW |  | 589.8404 | 846.796 | 1306.1283 | 3494.9649 | 3494.9649
Maintenance Cost by Area |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
TPC w/o Retrofit Factor
Reagent Feed System | $ |  | 15305168.1891 | 15611959.1278 | 15456584.7718 | 15330054.3158 | 15330054.3158
Ball Mill & Hydroclone System | $ |  | 3985818.884 | 4037257.4763 | 4010986.8022 | 3989926.5824 | 3989926.5824
DBA Acid Tank (pump, heater, agitator) | $ |  | 0 | 250353.0105 | 208808.1562 | 145420.1574 | 145420.1574
SO2 Removal System | $ |  | 4104464.1849 | 4194354.7133 | 4145155.6816 | 4105401.2569 | 4105401.2569
Absorber Tower | $ |  | 12208306.7411 | 25024444.3091 | 17432767.7622 | 8478950.4624 | 8478950.4624
Spray Pumps | $ |  | 906342.1722 | 1814023.5719 | 935510.4097 | 436998.472 | 436998.472
Flue Gas Handling System | $ |  | 6945135.2338 | 11123136.1453 | 8488320.4633 | 6062672.5015 | 6062672.5015
ID Fans | $ |  | 1401265.4828 | 3348074.9759 | 2159086.2484 | 900324.6351 | 900324.6351
Waste / Byproduct Handling System | $ |  | 173977.4108 | 178617.8615 | 176073.6961 | 174025.6049 | 174025.6049
Thickener System | $ |  | 248593.7438 | 282761.0659 | 265324.5126 | 251326.1529 | 251326.1529
Support Equipment | $ |  | 3120689.0442 | 3120689.0442 | 2852185.4563 | 2621099.0506 | 2621099.0506
Chimney | $ |  | 5426695.5988 | 8304419.253 | 6703939.4182 | 4374690.453 | 4374690.453
TOTAL | $ |  | 53826456.6856 | 77290090.5547 | 62834743.3785 | 46870889.6449 | 46870889.6449
First Year Maintenance Costs
Reagent Feed System | $ |  | 765258.4095 | 780597.9564 | 772829.2386 | 766502.7158 | 766502.7158
Ball Mill & Hydroclone System | $ |  | 199290.9442 | 201862.8738 | 200549.3401 | 199496.3291 | 199496.3291
DBA Acid Tank (pump, heater, agitator) | $ |  | 0 | 12517.6505 | 10440.4078 | 7271.0079 | 7271.0079
SO2 Removal System | $ |  | 205223.2092 | 199231.8489 | 196894.8949 | 195006.5597 | 195006.5597
Absorber Tower | $ |  | 610415.3371 | 1188661.1047 | 828056.4687 | 402750.147 | 402750.147
Spray Pumps | $ |  | 45317.1086 | 86166.1197 | 44436.7445 | 20757.4274 | 20757.4274
Flue Gas Handling System | $ |  | 347256.7617 | 556156.8073 | 424416.0232 | 303133.6251 | 303133.6251
ID Fans | $ |  | 70063.2741 | 167403.7488 | 107954.3124 | 45016.2318 | 45016.2318
Waste / Byproduct Handling System | $ |  | 8698.8705 | 8930.8931 | 8803.6848 | 8701.2802 | 8701.2802
Thickener System | $ |  | 12429.6872 | 14138.0533 | 13266.2256 | 12566.3076 | 12566.3076
Support Equipment | $ |  | 156034.4522 | 156034.4522 | 142609.2728 | 131054.9525 | 131054.9525
Chimney | $ |  | 271334.7799 | 415220.9627 | 335196.9709 | 218734.5226 | 218734.5226
TOTAL | $ |  | 2691322.8343 | 3786922.4712 | 3085453.5843 | 2310991.1068 | 2310991.1068
LSFO O&M Data and Costs |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 2015 | 2015 | 2015 | 2015 | 2015
Parameters
Reagent Required | lbs/hr |  | 166.8282 | 2301.3145 | 1212.0256 | 337.5261 | 337.5261
| lbs/MMBtu |  | 0.33567 | 1.2966 | 1.2966 | 1.2966 | 1.2966
DBA Required | lbs/hr |  | 0 | 13.369 | 7.041 | 1.9608 | 1.9608
Percent SO2 Removal | % |  | 50% | 95% | 95% | 95% | 95%
FGD Sludge to Disposal | lbs/hr, dry |  | 275.8761 | 3805.5774 | 2004.2707 | 558.1513 | 558.1513
Steam to FGD System | lbs/hr |  | 9173.3924 | 32801.5371 | 17275.4762 | 4810.8921 | 4810.8921
Total FGD Power Consumption | kW |  | 3000 | 2469.3 | 1300.498 | 362.164 | 362.164
FGD Byproduct | lbs/hr |  | 0 | 0 | 0 | 0 | 0
Fixed O&M Costs
Number of Operators |  |  | 12.4382 | 12.4382 | 8.0546 | 3.3868 | 3.3868
(40 hrs/week)
Operating Labor Cost ** | $/yr |  | 1629903.3944 | 1629903.3944 | 1055476.6913 | 443803.2767 | 443803.2767
Maint. Labor & Matls. Cost | $/yr |  | 2691322.8343 | 3786922.4712 | 3085453.5843 | 2310991.1068 | 2310991.1068
Admin. & Support Labor | $/yr |  | 811929.7584 | 943401.7149 | 686897.4375 | 410459.9158 | 410459.9158
TOTAL | $/yr |  | 5133155.9871 | 6360227.5805 | 4827827.7131 | 3165254.2993 | 3165254.2993
Variable Operating Costs **
Reagent Costs | $/yr |  | 7124.4 | 98277.6354 | 51759.5546 | 14414.0532 | 14414.0532
DBA Costs | $/yr |  | 0 | 16366.4063 | 8619.6406 | 2400.4063 | 2400.4063
Disposal Costs | $/yr |  | 4712.5163 | 65006.8727 | 34236.9529 | 9534.3413 | 9534.3413
Credit for Byproduct | $/yr |  | 0 | 0 | 0 | 0 | 0
Steam Costs | $/yr |  | 182816.5363 | 653701.8335 | 344282.9656 | 95876.2689 | 95876.2689
Power Costs | $/yr |  | 427050 | 351504.855 | 185125.8903 | 51554.0454 | 51554.0454
TOTAL | $/yr |  | 621703.4526 | 1184857.6029 | 624025.0042 | 173779.1151 | 173779.1151
** These costs assume inputs are in current dollars (no escalation included).
Intermediate Material Balance Calcs. |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Sulfite Reaction
SO2 | lbmole/hr |  | 1.5128 | 20.8685 | 10.9907 | 3.0607 | 3.0607
CaCO3 | lbmole/hr |  | 1.5128 | 20.8685 | 10.9907 | 3.0607 | 3.0607
H2O | lbmole/hr |  | 0.75641 | 10.4343 | 5.4954 | 1.5304 | 1.5304
CaSO3*1/2H2O | lbmole/hr |  | 1.5128 | 20.8685 | 10.9907 | 3.0607 | 3.0607
CO2 | lbmole/hr |  | 1.5128 | 20.8685 | 10.9907 | 3.0607 | 3.0607
SO2 | lb/hr |  | 96.915 | 1336.8953 | 704.0982 | 196.078 | 196.078
CaCO3 | lb/hr |  | 151.4165 | 2088.7169 | 1100.0576 | 306.3451 | 306.3451
H2O | lb/hr |  | 13.6269 | 187.9767 | 99.001 | 27.5699 | 27.5699
CaSO3*1/2H2O | lb/hr |  | 195.3796 | 2695.1663 | 1419.4542 | 395.2911 | 395.2911
CO2 | lb/hr |  | 66.5789 | 918.4232 | 483.7029 | 134.7021 | 134.7021
Sulfate Reaction
CaSO3*1/2H2O | lbmole/hr |  | 1.5128 | 20.8685 | 10.9907 | 3.0607 | 3.0607
O2 | lbmole/hr |  | 0.75641 | 10.4343 | 5.4954 | 1.5304 | 1.5304
H2O | lbmole/hr |  | 2.2692 | 31.3028 | 16.4861 | 4.5911 | 4.5911
CaSO4*2H2O | lbmole/hr |  | 1.5128 | 20.8685 | 10.9907 | 3.0607 | 3.0607
CaSO3*1/2H2O | lb/hr |  | 195.3796 | 2695.1663 | 1419.4542 | 395.2911 | 395.2911
O2 | lb/hr |  | 24.2041 | 333.8837 | 175.8454 | 48.9696 | 48.9696
H2O | lb/hr |  | 40.8807 | 563.93 | 297.0031 | 82.7097 | 82.7097
CaSO4*2H2O | lb/hr |  | 260.4644 | 3592.9797 | 1892.3027 | 526.9704 | 526.9704
Water in Absorber
Mole Fraction H2O in Absorber | % |  | 0.13886 | 0.13886 | 0.13886 | 0.13886 | 0.13886
Moles H2O in Absorber | lbmole |  | 4693.3329 | 16763.2308 | 8828.6349 | 2458.6072 | 2458.6072
DBA Feed Calculations
SO2 Removed | lbs/hr |  | 96.915 | 1336.8953 | 704.0982 | 196.078 | 196.078
DBA Added | lbs/hr |  | 0 | 13.369 | 7.041 | 1.9608 | 1.9608
DBA Added | GPM |  | 0 | 0.017811 | 0.0093805 | 0.0026123 | 0.0026123

## LSD Cost & Tech. Results (hidden)
LSD Material Balance - Preliminary |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Flue Gas, Downstream of Air Heater
Temperature | °F |  | 300 | 300 | 300 | 300 | 300
Pressure | in. H2O |  | -12 | -12 | -12 | -12 | -12
Flow Rate | SCFM |  | 205105.5902 | 732569.9506 | 385820.174 | 107443.5927 | 107443.5927
Flow Rate | ACFM |  | 314500.1388 | 1123291.427 | 591600.1515 | 164749.4093 | 164749.4093
CO2 | lb/hr |  | 167773.1629 | 599172.9887 | 315564.4407 | 87878.705 | 87878.705
N2 | lb/hr |  | 662514.4698 | 2366056.4549 | 1246123.0663 | 347021.6134 | 347021.6134
SO2 | lb/hr |  | 193.83 | 1407.2582 | 741.156 | 206.3979 | 206.3979
O2 | lb/hr |  | 52552.2095 | 187681.1755 | 98845.4191 | 27526.5724 | 27526.5724
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 149.9231 | 535.4247 | 281.9904 | 78.529 | 78.529
H2O | lb/hr |  | 59658.7384 | 213060.9208 | 112212.085 | 31248.935 | 31248.935
Fly Ash | lb/hr |  | 3865.5765 | 13805.2416 | 7270.7606 | 2024.7688 | 2024.7688
Total (gas only) | lb/hr |  | 942842.3336 | 3367914.223 | 1773768.1574 | 493960.7527 | 493960.7527
Flue Gas, to Spray Dryer
Temperature | °F |  | 300 | 300 | 300 | 300 | 300
Pressure | in. H2O |  | -12 | -12 | -12 | -12 | -12
Flow Rate | SCFM |  | 205105.5902 | 732569.9506 | 385820.174 | 107443.5927 | 107443.5927
Flow Rate | ACFM |  | 314500.1388 | 1123291.427 | 591600.1515 | 164749.4093 | 164749.4093
CO2 | lb/hr |  | 167773.1629 | 599172.9887 | 315564.4407 | 87878.705 | 87878.705
N2 | lb/hr |  | 662514.4698 | 2366056.4549 | 1246123.0663 | 347021.6134 | 347021.6134
SO2 | lb/hr |  | 193.83 | 1407.2582 | 741.156 | 206.3979 | 206.3979
O2 | lb/hr |  | 52552.2095 | 187681.1755 | 98845.4191 | 27526.5724 | 27526.5724
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 149.9231 | 535.4247 | 281.9904 | 78.529 | 78.529
H2O | lb/hr |  | 59658.7384 | 213060.9208 | 112212.085 | 31248.935 | 31248.935
Fly Ash | lb/hr |  | 3865.5765 | 13805.2416 | 7270.7606 | 2024.7688 | 2024.7688
Total (gas only) | lb/hr |  | 942842.3336 | 3367914.223 | 1773768.1574 | 493960.7527 | 493960.7527
Flue Gas, from Spray Dryers (total)
Temperature | °F |  | 147 | 147 | 147 | 147 | 147
Pressure | in. H2O |  | -17 | -17 | -17 | -17 | -17
Flow Rate | SCFM |  | 213716.3106 | 763020.8395 | 404279.7748 | 116276.3848 | 116276.3848
Flow Rate | ACFM |  | 265145.9267 | 946637.4701 | 501567.406 | 144257.6363 | 144257.6363
CO2 | lb/hr |  | 167773.1629 | 599172.9887 | 315564.4407 | 87878.705 | 87878.705
N2 | lb/hr |  | 662514.4698 | 2366056.4549 | 1246123.0663 | 347021.6134 | 347021.6134
SO2 | lb/hr |  | 54.2724 | 394.0323 | 207.5237 | 57.7914 | 57.7914
O2 | lb/hr |  | 52543.496 | 187617.9134 | 98812.101 | 27517.294 | 27517.294
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 149.9231 | 535.4247 | 281.9904 | 78.529 | 78.529
H2O | lb/hr |  | 84188.8933 | 299972.503 | 164882.0559 | 56429.1618 | 56429.1618
Fly Ash | lb/hr |  | 8390.1553 | 48080.8966 | 25322.6055 | 7051.8648 | 7051.8648
Total (gas only) | lb/hr |  | 967224.2175 | 3453749.3171 | 1825871.178 | 518983.0945 | 518983.0945
Flue Gas Downstream of Particulate Control Device
Temperature | °F |  | 147 | 147 | 147 | 147 | 147
Pressure | in. H2O |  | -23 | -23 | -23 | -23 | -23
Flow Rate | SCFM |  | 213652.5778 | 762649.7159 | 404084.3164 | 116221.9534 | 116221.9534
Flow Rate | ACFM |  | 269282.2857 | 961224.3426 | 509297.615 | 146483.1998 | 146483.1998
CO2 | lb/hr |  | 167773.1629 | 599172.9887 | 315564.4407 | 87878.705 | 87878.705
N2 | lb/hr |  | 662514.4698 | 2366056.4549 | 1246123.0663 | 347021.6134 | 347021.6134
SO2 | lb/hr |  | 19.383 | 140.7258 | 74.1156 | 20.6398 | 20.6398
O2 | lb/hr |  | 52541.3177 | 187602.0978 | 98803.7715 | 27514.9743 | 27514.9743
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 149.9231 | 535.4247 | 281.9904 | 78.529 | 78.529
H2O | lb/hr |  | 84018.4649 | 298995.9405 | 164367.733 | 56285.9326 | 56285.9326
Fly Ash | lb/hr |  | 14.91 | 53.2485 | 28.0442 | 7.8098 | 7.8098
Total (gas only) | lb/hr |  | 967016.7213 | 3452503.6326 | 1825215.1175 | 518800.3941 | 518800.3941
Flue Gas Downstream of ID Fans
Temperature | °F |  | 152 | 152 | 152 | 152 | 152
Pressure | in. H2O |  | 1 | 1 | 1 | 1 | 1
Flow Rate | SCFM |  | 213652.5778 | 762649.7159 | 404084.3164 | 116221.9534 | 116221.9534
Flow Rate | ACFM |  | 255262.4031 | 911179.2668 | 482781.6013 | 138856.715 | 138856.715
CO2 | lb/hr |  | 167773.1629 | 599172.9887 | 315564.4407 | 87878.705 | 87878.705
N2 | lb/hr |  | 662514.4698 | 2366056.4549 | 1246123.0663 | 347021.6134 | 347021.6134
SO2 | lb/hr |  | 19.383 | 140.7258 | 74.1156 | 20.6398 | 20.6398
O2 | lb/hr |  | 52541.3177 | 187602.0978 | 98803.7715 | 27514.9743 | 27514.9743
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 149.9231 | 535.4247 | 281.9904 | 78.529 | 78.529
H2O | lb/hr |  | 84018.4649 | 298995.9405 | 164367.733 | 56285.9326 | 56285.9326
Fly Ash | lb/hr |  | 14.91 | 53.2485 | 28.0442 | 7.8098 | 7.8098
Total (gas only) | lb/hr |  | 967016.7213 | 3452503.6326 | 1825215.1175 | 518800.3941 | 518800.3941
Lime to Ball Mill
Temperature | °F |  | 60 | 60 | 60 | 60 | 60
Wt.% Solids | wt. % |  | 100% | 100% | 100% | 100% | 100%
Inerts | lb/hr |  | 17.3138 | 125.7029 | 66.2035 | 18.4364 | 18.4364
CaO | lb/hr |  | 155.8242 | 1131.3258 | 595.8316 | 165.9278 | 165.9278
Total | lb/hr |  | 173.138 | 1257.0286 | 662.0351 | 184.3642 | 184.3642
Water to Ball Mill
Temperature | °F |  | 60 | 60 | 60 | 60 | 60
Flow Rate | GPM |  | 1.1408 | 8.2824 | 4.3621 | 1.2148 | 1.2148
Wt.% Solids | wt. % |  | 0% | 0% | 0% | 0% | 0%
H2O | lb/hr |  | 570.8486 | 4144.515 | 2182.7779 | 607.8622 | 607.8622
Total | lb/hr |  | 570.8486 | 4144.515 | 2182.7779 | 607.8622 | 607.8622
Lime Slurry to Head Tanks (Total)
Temperature | °F |  | 110 | 110 | 110 | 110 | 110
Flow Rate | GPM |  | 1.1437 | 8.3034 | 4.3731 | 1.2178 | 1.2178
Wt.% Solids | wt. % |  | 30% | 30% | 30% | 30% | 30%
Ca(OH)2 | lb/hr |  | 205.8821 | 1494.76 | 787.2403 | 219.2315 | 219.2315
Inerts | lb/hr |  | 17.3138 | 125.7029 | 66.2035 | 18.4364 | 18.4364
H2O | lb/hr |  | 520.7905 | 3781.08 | 1991.3688 | 554.5584 | 554.5584
Total | lb/hr |  | 743.9864 | 5401.5428 | 2844.8125 | 792.2263 | 792.2263
Lime Slurry from Head Tank
Temperature | °F |  | 110 | 110 | 110 | 110 | 110
Flow Rate | GPM |  | 22.7587 | 165.8362 | 87.3405 | 24.3227 | 24.3227
Wt.% Solids | wt. % |  | 35.24% | 35.69% | 35.69% | 35.69% | 35.69%
CaSO3*1/2H2O | lb/hr |  | 308.977 | 4192.2523 | 2208.1254 | 615.0257 | 615.0257
CaSO4*2H2O | lb/hr |  | 137.3011 | 1862.925 | 981.232 | 273.301 | 273.301
Flyash / Inerts | lb/hr |  | 4651.9094 | 30929.1662 | 16289.2122 | 4536.1607 | 4536.1607
Ca(OH)2 | lb/hr |  | 215.2652 | 1592.7608 | 838.7053 | 233.4879 | 233.4879
CaCl2 | lb/hr |  | 114.1938 | 1608.5454 | 847.2455 | 235.9815 | 235.9815
H2O | lb/hr |  | 9974.1246 | 72414.8426 | 38138.4838 | 10620.8436 | 10620.8436
Total | lb/hr |  | 15401.7711 | 112600.4923 | 59303.0041 | 16514.8004 | 16514.8004
Lime Slurry to Atomizer
Temperature | °F |  | 104 | 104 | 104 | 104 | 104
Flow Rate | GPM |  | 50.7124 | 193.1143 | 114.752 | 52.2191 | 52.2191
Wt.% Solids | wt. % |  | 18.11% | 31.6% | 28.65% | 18.96% | 18.96%
CaSO3*1/2H2O | lb/hr |  | 308.977 | 4192.2523 | 2208.1254 | 615.0257 | 615.0257
CaSO4*2H2O | lb/hr |  | 137.3011 | 1862.925 | 981.232 | 273.301 | 273.301
Flyash / Inerts | lb/hr |  | 4651.9094 | 30929.1662 | 16289.2122 | 4536.1607 | 4536.1607
Ca(OH)2 | lb/hr |  | 215.2652 | 1592.7608 | 838.7053 | 233.4879 | 233.4879
CaCl2 | lb/hr |  | 114.1938 | 1608.5454 | 847.2455 | 235.9815 | 235.9815
H2O | lb/hr |  | 24544.2746 | 86984.9926 | 52708.6338 | 25190.9936 | 25190.9936
Total | lb/hr |  | 29971.9211 | 127170.6423 | 73873.1541 | 31084.9504 | 31084.9504
Solids from Spray Dryers (Total)
Temperature | °F |  | 150 | 150 | 150 | 150 | 150
Wt.% Solids | wt. % |  | 98% | 98% | 98% | 98% | 98%
CaSO3*1/2H2O | lb/hr |  | 51.9998 | 572.4456 | 301.5179 | 83.9822 | 83.9822
CaSO4*2H2O | lb/hr |  | 23.1073 | 254.3795 | 133.9865 | 37.3195 | 37.3195
Flyash / Inerts | lb/hr |  | 851.7483 | 4473.4395 | 2355.9899 | 656.0875 | 656.0875
Ca(OH)2 | lb/hr |  | 5.3841 | 42.0573 | 22.1286 | 6.1514 | 6.1514
CaCl2 | lb/hr |  | 0 | 0 | 0 | 0 | 0
H2O | lb/hr |  | 19.0253 | 109.027 | 57.4209 | 15.9906 | 15.9906
Total | lb/hr |  | 951.2648 | 5451.3488 | 2871.0437 | 799.5312 | 799.5312
Baghouse/ESP Solids to Recycle
Particulate Removal Efficiency | % |  | 99.82% | 99.89% | 99.89% | 99.89% | 99.89%
Temperature | °F |  | 150 | 150 | 150 | 150 | 150
Wt.% Solids | wt. % |  | 98% | 98% | 98% | 98% | 98%
CaSO3*1/2H2O | lb/hr |  | 256.9772 | 3619.8067 | 1906.6075 | 531.0435 | 531.0435
CaSO4*2H2O | lb/hr |  | 114.1938 | 1608.5454 | 847.2455 | 235.9815 | 235.9815
Flyash / Inerts | lb/hr |  | 3782.8473 | 26330.0239 | 13867.0188 | 3861.6368 | 3861.6368
Ca(OH)2 | lb/hr |  | 3.999 | 55.9435 | 29.3365 | 8.105 | 8.105
CaCl2 | lb/hr |  | 114.1938 | 1608.5454 | 847.2455 | 235.9815 | 235.9815
H2O | lb/hr |  | 84.8575 | 645.1902 | 339.8002 | 94.6279 | 94.6279
Total | lb/hr |  | 4242.8748 | 32259.5098 | 16990.0085 | 4731.3948 | 4731.3948
Recycle Solids to Slurry Tank
Temperature | °F |  | 150 | 150 | 150 | 150 | 150
Wt.% Solids | wt. % |  | 98% | 98% | 98% | 98% | 98%
CaSO3*1/2H2O | lb/hr |  | 308.977 | 4192.2523 | 2208.1254 | 615.0257 | 615.0257
CaSO4*2H2O | lb/hr |  | 137.3011 | 1862.925 | 981.232 | 273.301 | 273.301
Flyash / Inerts | lb/hr |  | 4634.5956 | 30803.4634 | 16223.0087 | 4517.7243 | 4517.7243
Ca(OH)2 | lb/hr |  | 9.3831 | 98.0008 | 51.4651 | 14.2565 | 14.2565
CaCl2 | lb/hr |  | 114.1938 | 1608.5454 | 847.2455 | 235.9815 | 235.9815
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
Total | lb/hr |  | 5308.3334 | 39319.404 | 20708.2977 | 5766.9075 | 5766.9075
Blowdown Water to Recycle Solids Tank
Temperature | °F |  | 60 | 60 | 60 | 60 | 60
Flow Rate | GPM |  | 18.684 | 135.6506 | 71.4426 | 19.8954 | 19.8954
Wt.% Solids | wt. % |  | 0% | 0% | 0% | 0% | 0%
H2O | lb/hr |  | 9349.4513 | 67879.5455 | 35749.8939 | 9955.6667 | 9955.6667
Total | lb/hr |  | 9349.4513 | 67879.5455 | 35749.8939 | 9955.6667 | 9955.6667
Recycle Slurry to Head Tanks (Total)
Temperature | °F |  | 110 | 110 | 110 | 110 | 110
Flow Rate | GPM |  | 21.6979 | 158.6863 | 83.5749 | 23.2741 | 23.2741
Wt.% Solids | wt. % |  | 35% | 35% | 35% | 35% | 35%
CaSO3*1/2H2O | lb/hr |  | 308.977 | 4192.2523 | 2208.1254 | 615.0257 | 615.0257
CaSO4*2H2O | lb/hr |  | 137.3011 | 1862.925 | 981.232 | 273.301 | 273.301
Flyash / Inerts | lb/hr |  | 4634.5956 | 30803.4634 | 16223.0087 | 4517.7243 | 4517.7243
Ca(OH)2 | lb/hr |  | 9.3831 | 98.0008 | 51.4651 | 14.2565 | 14.2565
CaCl2 | lb/hr |  | 114.1938 | 1608.5454 | 847.2455 | 235.9815 | 235.9815
H2O | lb/hr |  | 9453.334 | 68633.7626 | 36147.115 | 10066.2852 | 10066.2852
Total | lb/hr |  | 14657.7847 | 107198.9495 | 56458.1916 | 15722.5741 | 15722.5741
Dry Solids
Temperature | °F |  | 100 | 100 | 100 | 100 | 100
Wt.% Solids | wt. % |  | 98% | 98% | 98% | 98% | 98%
CaSO3*1/2H2O | lb/hr |  | 262.8478 | 1909.0708 | 1005.5367 | 280.0701 | 280.0701
CaSO4*2H2O | lb/hr |  | 116.8025 | 848.3401 | 446.8337 | 124.4557 | 124.4557
Flyash / Inerts | lb/hr |  | 3869.265 | 13886.3432 | 7313.4071 | 2036.6109 | 2036.6109
Ca(OH)2 | lb/hr |  | 4.0903 | 29.5044 | 15.4719 | 4.2746 | 4.2746
CaCl2 | lb/hr |  | 0 | 0 | 0 | 0 | 0
H2O | lb/hr |  | 86.796 | 340.2706 | 179.2092 | 49.9064 | 49.9064
Total | lb/hr |  | 4339.8017 | 17013.529 | 8960.4586 | 2495.3176 | 2495.3176
Solids to Landfill
Temperature | °F |  | 100 | 100 | 100 | 100 | 100
Wt.% Solids | wt. % |  | 80% | 80% | 80% | 80% | 80%
CaSO3*1/2H2O | lb/hr |  | 262.8478 | 1909.0708 | 1005.5367 | 280.0701 | 280.0701
CaSO4*2H2O | lb/hr |  | 116.8025 | 848.3401 | 446.8337 | 124.4557 | 124.4557
Flyash / Inerts | lb/hr |  | 3869.265 | 13886.3432 | 7313.4071 | 2036.6109 | 2036.6109
Ca(OH)2 | lb/hr |  | 4.0903 | 29.5044 | 15.4719 | 4.2746 | 4.2746
CaCl2 | lb/hr |  | 0 | 0 | 0 | 0 | 0
H2O | lb/hr |  | 1063.2514 | 4168.3146 | 2195.3124 | 611.3528 | 611.3528
Total | lb/hr |  | 5316.2571 | 20841.573 | 10976.5618 | 3056.764 | 3056.764
LSD Equipment Capital Costs |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 2015 | 2015 | 2015 | 2015 | 2015
Sizing Criteria
Reagent Feed System | $ | * | 5768432.0187 | 6142653.1814 | 5952565.6948 | 5773559.5892 | 5773559.5892
SO2 Removal System | $ | Wt. % S | 1986228.3749 | 1986228.3749 | 1986228.3749 | 1986228.3749 | 1986228.3749
Spray Dryers | $ | kACFM | 6774551.1507 | 13483826.7267 | 10138424.1963 | 4494492.3953 | 4494492.3953
Flue Gas Handling System | $ | kACFM | 1644748.4252 | 3346868.6278 | 2344722.814 | 1167561.691 | 1167561.691 |  |  | Calculated No. of ID Fans and Flue Gas Flow per Fan
ID Fans | $ | ACFM | 706203.7214 | 1686671.616 | 1092173.9985 | 465600.9529 | 465600.9529 | 269282.2857 | 961224.3426 | 509297.615 | 146483.1998 | 146483.1998
Waste / Byproduct Handling System | $ | kpph SO2 | 1551268.9311 | 1551268.9311 | 1551268.9311 | 1551268.9311 | 1551268.9311 | 1 | 1 | 1 | 1 | 1
Support Equipment | $ | MW | 2583567.7528 | 2583567.7528 | 2326703.6654 | 2107317.6292 | 2107317.6292
Chimney | $ | ACFM | 3829146.1288 | 5856265.3758 | 4737109.1574 | 3124727.2399 | 3124727.2399
TOTAL | $ |  | 24844146.5037 | 36637350.5865 | 30129196.8324 | 20670756.8035 | 20670756.8035
* Based on lbs/hr of lime feed and GPM of lime slurry.
Capital Costs with Retrofit Factors
Reagent Feed System | $ |  | 9229491.2299 | 9828245.0902 | 9524105.1117 | 9237695.3427 | 9237695.3427
SO2 Removal System | $ |  | 3177965.3999 | 3177965.3999 | 3177965.3999 | 3177965.3999 | 3177965.3999
Spray Dryers | $ |  | 10839281.8411 | 21574122.7628 | 16221478.7141 | 7191187.8324 | 7191187.8324
Flue Gas Handling System | $ |  | 2631597.4804 | 5354989.8045 | 3751556.5024 | 1868098.7055 | 1868098.7055
ID Fans | $ |  | 1129925.9542 | 2698674.5856 | 1747478.3975 | 744961.5247 | 744961.5247
Waste / Byproduct Handling System | $ |  | 2482030.2898 | 2482030.2898 | 2482030.2898 | 2482030.2898 | 2482030.2898
Support Equipment | $ |  | 4133708.4045 | 4133708.4045 | 3722725.8647 | 3371708.2067 | 3371708.2067
Chimney | $ |  | 6126633.8061 | 9370024.6012 | 7579374.6518 | 4999563.5839 | 4999563.5839
TOTAL | $ |  | 39750634.4058 | 58619760.9384 | 48206714.9318 | 33073210.8855 | 33073210.8855
General Facilities
Reagent Feed System | $ |  | 922949.123 | 982824.509 | 952410.5112 | 923769.5343 | 923769.5343
SO2 Removal System | $ |  | 317796.54 | 317796.54 | 317796.54 | 317796.54 | 317796.54
Spray Dryers | $ |  | 1083928.1841 | 2157412.2763 | 1622147.8714 | 719118.7832 | 719118.7832
Flue Gas Handling System | $ |  | 263159.748 | 535498.9804 | 375155.6502 | 186809.8706 | 186809.8706
ID Fans | $ |  | 112992.5954 | 269867.4586 | 174747.8398 | 74496.1525 | 74496.1525
Waste / Byproduct Handling System | $ |  | 248203.029 | 248203.029 | 248203.029 | 248203.029 | 248203.029
Support Equipment | $ |  | 413370.8404 | 413370.8404 | 372272.5865 | 337170.8207 | 337170.8207
Chimney | $ |  | 612663.3806 | 937002.4601 | 757937.4652 | 499956.3584 | 499956.3584
TOTAL | $ |  | 3975063.4406 | 5861976.0938 | 4820671.4932 | 3307321.0886 | 3307321.0886
Engineering Fees
Reagent Feed System | $ |  | 922949.123 | 982824.509 | 952410.5112 | 923769.5343 | 923769.5343
SO2 Removal System | $ |  | 317796.54 | 317796.54 | 317796.54 | 317796.54 | 317796.54
Spray Dryers | $ |  | 1083928.1841 | 2157412.2763 | 1622147.8714 | 719118.7832 | 719118.7832
Flue Gas Handling System | $ |  | 263159.748 | 535498.9804 | 375155.6502 | 186809.8706 | 186809.8706
ID Fans | $ |  | 112992.5954 | 269867.4586 | 174747.8398 | 74496.1525 | 74496.1525
Waste / Byproduct Handling System | $ |  | 248203.029 | 248203.029 | 248203.029 | 248203.029 | 248203.029
Support Equipment | $ |  | 413370.8404 | 413370.8404 | 372272.5865 | 337170.8207 | 337170.8207
Chimney | $ |  | 612663.3806 | 937002.4601 | 757937.4652 | 499956.3584 | 499956.3584
TOTAL | $ |  | 3975063.4406 | 5861976.0938 | 4820671.4932 | 3307321.0886 | 3307321.0886
Contingency
Reagent Feed System | $ |  | 1845898.246 | 1965649.018 | 1904821.0223 | 1847539.0685 | 1847539.0685
SO2 Removal System | $ |  | 635593.08 | 635593.08 | 635593.08 | 635593.08 | 635593.08
Spray Dryers | $ |  | 2167856.3682 | 4314824.5526 | 3244295.7428 | 1438237.5665 | 1438237.5665
Flue Gas Handling System | $ |  | 526319.4961 | 1070997.9609 | 750311.3005 | 373619.7411 | 373619.7411
ID Fans | $ |  | 225985.1908 | 539734.9171 | 349495.6795 | 148992.3049 | 148992.3049
Waste / Byproduct Handling System | $ |  | 496406.058 | 496406.058 | 496406.058 | 496406.058 | 496406.058
Support Equipment | $ |  | 826741.6809 | 826741.6809 | 744545.1729 | 674341.6413 | 674341.6413
Chimney | $ |  | 1225326.7612 | 1874004.9202 | 1515874.9304 | 999912.7168 | 999912.7168
TOTAL | $ |  | 7950126.8812 | 11723952.1877 | 9641342.9864 | 6614642.1771 | 6614642.1771
Total Plant Cost (TPC) | $ |  | 55650888.1682 | 82067665.3138 | 67489400.9045 | 46302495.2397 | 46302495.2397
Total Plant Cost (TPC) w/ Prime Contractor's Markup | $ |  | 57320414.8132 | 84529695.2732 | 69514082.9317 | 47691570.0969 | 47691570.0969
Total Cash Expended (TCE) | $ |  | 57320414.8132 | 84529695.2732 | 69514082.9317 | 47691570.0969 | 47691570.0969
Allow. for Funds During Constr. (AFDC) | $ |  | 0 | 0 | 0 | 0 | 0
Total Plant Investment (TPI) | $ |  | 57320414.8132 | 84529695.2732 | 69514082.9317 | 47691570.0969 | 47691570.0969
Preproduction Costs | $ |  | 1528792.4976 | 2314133.1928 | 1807860.9837 | 1161738.4243 | 1161738.4243
Inventory Capital | $ |  | 8102.8578 | 58828.9394 | 30983.2414 | 8628.2444 | 8628.2444
Total Capital Requirement (TCR) | $ |  | 58857310.1686 | 86902657.4054 | 71352927.1568 | 48861936.7657 | 48861936.7657
| $/kW |  | 392.3821 | 579.351 | 903.2016 | 2220.9971 | 2220.9971
Maintenance Cost by Area |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
TPC w/o Retrofit Factor
Reagent Feed System | $ |  | 8306542.1069 | 8845420.5812 | 8571694.6005 | 8313925.8084 | 8313925.8084
SO2 Removal System | $ |  | 2860168.8599 | 2860168.8599 | 2860168.8599 | 2860168.8599 | 2860168.8599
Spray Dryers | $ |  | 9755353.657 | 19416710.4865 | 14599330.8427 | 6472069.0492 | 6472069.0492
Flue Gas Handling System | $ |  | 2368437.7324 | 4819490.824 | 3376400.8521 | 1681288.835 | 1681288.835
ID Fans | $ |  | 1016933.3588 | 2428807.127 | 1572730.5578 | 670465.3722 | 670465.3722
Waste / Byproduct Handling System | $ |  | 2233827.2608 | 2233827.2608 | 2233827.2608 | 2233827.2608 | 2233827.2608
Support Equipment | $ |  | 3720337.564 | 3720337.564 | 3350453.2782 | 3034537.386 | 3034537.386
Chimney | $ |  | 5513970.4255 | 8433022.1411 | 6821437.1867 | 4499607.2255 | 4499607.2255
TOTAL | $ |  | 35775570.9653 | 52757784.8446 | 43386043.4386 | 29765889.797 | 29765889.797
First Year Maintenance Costs
Reagent Feed System | $ |  | 415327.1053 | 442271.0291 | 428584.73 | 415696.2904 | 415696.2904
SO2 Removal System | $ |  | 143008.443 | 143008.443 | 143008.443 | 143008.443 | 143008.443
Spray Dryers | $ |  | 487767.6829 | 970835.5243 | 729966.5421 | 323603.4525 | 323603.4525
Flue Gas Handling System | $ |  | 118421.8866 | 240974.5412 | 168820.0426 | 84064.4417 | 84064.4417
ID Fans | $ |  | 50846.6679 | 121440.3564 | 78636.5279 | 33523.2686 | 33523.2686
Waste / Byproduct Handling System | $ |  | 111691.363 | 111691.363 | 111691.363 | 111691.363 | 111691.363
Support Equipment | $ |  | 186016.8782 | 186016.8782 | 167522.6639 | 151726.8693 | 151726.8693
Chimney | $ |  | 275698.5213 | 421651.1071 | 341071.8593 | 224980.3613 | 224980.3613
TOTAL | $ |  | 1788778.5483 | 2637889.2422 | 2169302.1719 | 1488294.4898 | 1488294.4898
LSD O&M Data and Costs |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 2015 | 2015 | 2015 | 2015 | 2015
Parameters
Reagent Required | lbs/hr |  | 173.138 | 1257.0286 | 662.0351 | 184.3642 | 184.3642
| lbs/MMBtu |  | 0.34837 | 0.70821 | 0.70821 | 0.70821 | 0.70821
Percent SO2 Removal | % |  | 90% | 90% | 90% | 90% | 90%
FGD Solids - dry | lbs/hr |  | 4253.0057 | 16673.2584 | 8781.2494 | 2445.4112 | 2445.4112
- wetted | lbs/hr |  | 5316.2571 | 20841.573 | 10976.5618 | 3056.764 | 3056.764
Fresh Water to FGD | gpm |  | 1.1408 | 8.2824 | 4.3621 | 1.2148 | 1.2148
Blowdown Water to FGD | gpm |  | 49.7523 | 172.4175 | 104.5886 | 50.1344 | 50.1344
Total FGD Power Consumption | kW |  | 1050 | 1050 | 553 | 154 | 154
Fixed O&M Costs
Number of Operators |  |  | 10.2537 | 10.2537 | 6.5542 | 2.4659 | 2.4659
(40 hrs/week)
Operating Labor Cost ** | $/yr |  | 1343639.5016 | 1343639.5016 | 858856.3737 | 323130.6402 | 323130.6402
Maint. Labor & Matls. Cost | $/yr |  | 1788778.5483 | 2637889.2422 | 2169302.1719 | 1488294.4898 | 1488294.4898
Admin. & Support Labor | $/yr |  | 617745.2763 | 719638.5595 | 517973.1727 | 275534.5308 | 275534.5308
TOTAL | $/yr |  | 3750163.3261 | 4701167.3033 | 3546131.7183 | 2086959.6609 | 2086959.6609
Variable Operating Costs **
Reagent Costs | $/yr |  | 32040.05 | 232619.4312 | 122512.9004 | 34117.5166 | 34117.5166
Disposal Costs | $/yr |  | 363249.216 | 1424063.0026 | 750006.5147 | 208862.5737 | 208862.5737
Credit for Byproduct | $/yr |  | 0 | 0 | 0 | 0 | 0
Steam Costs | $/yr |  | 0 | 0 | 0 | 0 | 0
Fresh Water Costs | $/yr |  | 233.8426 | 1697.7603 | 894.1538 | 249.0048 | 249.0048
Power Costs | $/yr |  | 149467.5 | 149467.5 | 78719.55 | 21921.9 | 21921.9
TOTAL | $/yr |  | 544990.6086 | 1807847.6941 | 952133.1189 | 265150.9951 | 265150.9951
** These costs assume inputs are in current dollars (no escalation included).
Intermediate Material Balance Calcs. |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
FGD Reactions in Spray Dryer (80% of SO2 Removal)
Sulfite Reaction | 60%
SO2 | lbmole/hr |  | 1.6338 | 11.8621 | 6.2474 | 1.7398 | 1.7398
Ca(OH)2 | lbmole/hr |  | 1.6338 | 11.8621 | 6.2474 | 1.7398 | 1.7398
H2O | lbmole/hr |  | 0.81692 | 5.9311 | 3.1237 | 0.86989 | 0.86989
CaSO3*1/2H2O | lbmole/hr |  | 1.6338 | 11.8621 | 6.2474 | 1.7398 | 1.7398
SO2 | lb/hr |  | 104.6682 | 759.9194 | 400.2242 | 111.4549 | 111.4549
Ca(OH)2 | lb/hr |  | 121.0587 | 878.9189 | 462.8973 | 128.9081 | 128.9081
H2O | lb/hr |  | 14.7171 | 106.8499 | 56.2743 | 15.6713 | 15.6713
CaSO3*1/2H2O | lb/hr |  | 211.0099 | 1531.9892 | 806.8477 | 224.6918 | 224.6918
Sulfate Reaction | 20%
Ca(OH)2 | lbmole/hr |  | 0.54461 | 3.954 | 2.0825 | 0.57992 | 0.57992
SO2 | lbmole/hr |  | 0.54461 | 3.954 | 2.0825 | 0.57992 | 0.57992
O2 | lbmole/hr |  | 0.27231 | 1.977 | 1.0412 | 0.28996 | 0.28996
H2O | lbmole/hr |  | 0.54461 | 3.954 | 2.0825 | 0.57992 | 0.57992
CaSO4*2H2O | lbmole/hr |  | 0.54461 | 3.954 | 2.0825 | 0.57992 | 0.57992
Ca(OH)2 | lb/hr |  | 40.3529 | 292.973 | 154.2991 | 42.9694 | 42.9694
SO2 | lb/hr |  | 34.8894 | 253.3065 | 133.4081 | 37.1516 | 37.1516
O2 | lb/hr |  | 8.7135 | 63.2622 | 33.3181 | 9.2785 | 9.2785
H2O | lb/hr |  | 9.8114 | 71.2333 | 37.5162 | 10.4475 | 10.4475
CaSO4*2H2O | lb/hr |  | 93.7672 | 680.7751 | 358.5416 | 99.847 | 99.847
FGD Reactions in Particulate Control (20% of SO2 Removal)
Sulfite Reaction | 15%
SO2 | lbmole/hr |  | 0.40846 | 2.9655 | 1.5618 | 0.43494 | 0.43494
Ca(OH)2 | lbmole/hr |  | 0.40846 | 2.9655 | 1.5618 | 0.43494 | 0.43494
H2O | lbmole/hr |  | 0.20423 | 1.4828 | 0.78092 | 0.21747 | 0.21747
CaSO3*1/2H2O | lbmole/hr |  | 0.40846 | 2.9655 | 1.5618 | 0.43494 | 0.43494
SO2 | lb/hr |  | 26.1671 | 189.9799 | 100.0561 | 27.8637 | 27.8637
Ca(OH)2 | lb/hr |  | 30.2647 | 219.7297 | 115.7243 | 32.227 | 32.227
H2O | lb/hr |  | 3.6793 | 26.7125 | 14.0686 | 3.9178 | 3.9178
CaSO3*1/2H2O | lb/hr |  | 52.7525 | 382.9973 | 201.7119 | 56.1729 | 56.1729
Sulfate Reaction | 5%
Ca(OH)2 | lbmole/hr |  | 0.13615 | 0.98851 | 0.52061 | 0.14498 | 0.14498
SO2 | lbmole/hr |  | 0.13615 | 0.98851 | 0.52061 | 0.14498 | 0.14498
O2 | lbmole/hr |  | 0.068077 | 0.49425 | 0.26031 | 0.072491 | 0.072491
H2O | lbmole/hr |  | 0.13615 | 0.98851 | 0.52061 | 0.14498 | 0.14498
CaSO4*2H2O | lbmole/hr |  | 0.13615 | 0.98851 | 0.52061 | 0.14498 | 0.14498
Ca(OH)2 | lb/hr |  | 10.0882 | 73.2432 | 38.5748 | 10.7423 | 10.7423
SO2 | lb/hr |  | 8.7224 | 63.3266 | 33.352 | 9.2879 | 9.2879
O2 | lb/hr |  | 2.1784 | 15.8155 | 8.3295 | 2.3196 | 2.3196
H2O | lb/hr |  | 2.4528 | 17.8083 | 9.379 | 2.6119 | 2.6119
CaSO4*2H2O | lb/hr |  | 23.4418 | 170.1938 | 89.6354 | 24.9618 | 24.9618
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 519.9977 | 5724.4556 | 3015.1789 | 839.8221 | 839.8221
CaSO4*2H2O | lb/hr |  | 231.0731 | 2543.7952 | 1339.865 | 373.1945 | 373.1945
Inerts | lb/hr |  | 8517.4833 | 44734.3947 | 23559.8986 | 6560.8747 | 6560.8747
Ca(OH)2 | lb/hr |  | 53.8407 | 420.5728 | 221.2858 | 61.5141 | 61.5141
H2O | lb/hr
TOTAL | lb/hr |  | 9322.3948 | 53423.2184 | 28136.2284 | 7835.4054 | 7835.4054
Spray Dryer Solids Removal
CaSO3*1/2H2O | lb/hr |  | 51.9998 | 572.4456 | 301.5179 | 83.9822 | 83.9822
CaSO4*2H2O | lb/hr |  | 23.1073 | 254.3795 | 133.9865 | 37.3195 | 37.3195
Inerts | lb/hr |  | 851.7483 | 4473.4395 | 2355.9899 | 656.0875 | 656.0875
Ca(OH)2 | lb/hr |  | 5.3841 | 42.0573 | 22.1286 | 6.1514 | 6.1514
H2O | lb/hr |  | 19.0253 | 109.027 | 57.4209 | 15.9906 | 15.9906
TOTAL | lb/hr |  | 932.2395 | 5342.3218 | 2813.6228 | 783.5405 | 783.5405
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 520.7504 | 5535.0074 | 2915.373 | 812.0128 | 812.0128
CaSO4*2H2O | lb/hr |  | 231.4076 | 2459.6095 | 1295.5139 | 360.8368 | 360.8368
Inerts | lb/hr |  | 7665.7349 | 40260.9552 | 21203.9088 | 5904.7872 | 5904.7872
Ca(OH)2 | lb/hr |  | 8.1037 | 85.5426 | 44.8581 | 12.3933 | 12.3933
H2O | lb/hr
TOTAL | lb/hr |  | 8425.9967 | 48341.1147 | 25459.6537 | 7090.0302 | 7090.0302
Components of Baghouse/ESP Solids
CaSO3*1/2H2O | lb/hr |  | 519.825 | 5528.8775 | 2912.1442 | 811.1135 | 811.1135
CaSO4*2H2O | lb/hr |  | 230.9964 | 2456.8855 | 1294.0791 | 360.4372 | 360.4372
Inerts | lb/hr |  | 7652.1123 | 40216.3671 | 21180.4259 | 5898.2478 | 5898.2478
Ca(OH)2 | lb/hr |  | 8.0893 | 85.4479 | 44.8084 | 12.3796 | 12.3796
H2O | lb/hr |  | 171.6535 | 985.4608 | 519.0093 | 144.5342 | 144.5342
TOTAL | lb/hr |  | 8582.6765 | 49273.0388 | 25950.4671 | 7226.7124 | 7226.7124
Total Waste Solids Out
CaSO3*1/2H2O | lb/hr |  | 263.7624 | 1914.9866 | 1008.5596 | 280.8647 | 280.8647
CaSO4*2H2O | lb/hr |  | 117.209 | 850.9689 | 448.1769 | 124.8088 | 124.8088
Inerts | lb/hr |  | 3882.8903 | 13930.9445 | 7336.9641 | 2043.2052 | 2043.2052
Ca(OH)2 | lb/hr |  | 4.1176 | 29.8952 | 15.7448 | 4.3846 | 4.3846
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 4267.9794 | 16726.7951 | 8809.4454 | 2453.2633 | 2453.2633
CaSO3*1/2H2O | wt. % |  | 6.18% | 11.45% | 11.45% | 11.45% | 11.45%
CaSO4*2H2O | wt. % |  | 2.746% | 5.087% | 5.087% | 5.087% | 5.087%
Inerts | wt. % |  | 90.98% | 83.29% | 83.29% | 83.29% | 83.29%
Ca(OH)2 | wt. % |  | 0.09648% | 0.1787% | 0.1787% | 0.1787% | 0.1787%
H2O | wt. % |  | NA | NA | NA | NA | NA
TOTAL | wt. % |  | 100% | 100% | 100% | 100% | 100%
Waste Out Gas Stream
CaSO3*1/2H2O | lb/hr |  | 0.92144 | 6.0962 | 3.2107 | 0.89411 | 0.89411
CaSO4*2H2O | lb/hr |  | 0.40946 | 2.709 | 1.4267 | 0.39732 | 0.39732
Inerts | lb/hr |  | 13.5647 | 44.3481 | 23.3567 | 6.5044 | 6.5044
Ca(OH)2 | lb/hr |  | 0.014385 | 0.095169 | 0.050122 | 0.013958 | 0.013958
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 14.91 | 53.2485 | 28.0442 | 7.8098 | 7.8098
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 262.841 | 1908.8903 | 1005.3489 | 279.9706 | 279.9706
CaSO4*2H2O | lb/hr |  | 116.7995 | 848.2599 | 446.7502 | 124.4115 | 124.4115
Inerts | lb/hr |  | 3869.3256 | 13886.5964 | 7313.6074 | 2036.7008 | 2036.7008
Ca(OH)2 | lb/hr |  | 4.1033 | 29.8 | 15.6947 | 4.3707 | 4.3707
H2O | lb/hr |  | 86.7973 | 340.2765 | 179.2123 | 49.9072 | 49.9072
TOTAL | lb/hr |  | 4339.8667 | 17013.8231 | 8960.6135 | 2495.3607 | 2495.3607
ITERATION 1
Assumed Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 314.5794 | 4231.024 | 2228.3393 | 620.5502 | 620.5502
CaSO4*2H2O | lb/hr |  | 139.7907 | 1880.1541 | 990.2145 | 275.7559 | 275.7559
Inerts | lb/hr |  | 4630.9757 | 30779.4121 | 16210.4904 | 4514.3138 | 4514.3138
Ca(OH)2 | lb/hr |  | 4.911 | 66.0513 | 34.787 | 9.6875 | 9.6875
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
TOTAL | lb/hr |  | 5194.1396 | 37710.8586 | 19861.0522 | 5530.9259 | 5530.9259
Composition of Recycle Slurry to Head Tanks
CaSO3*1/2H2O | lb/hr |  | 314.5794 | 4231.024 | 2228.3393 | 620.5502 | 620.5502
CaSO4*2H2O | lb/hr |  | 139.7907 | 1880.1541 | 990.2145 | 275.7559 | 275.7559
Inerts | lb/hr |  | 4630.9757 | 30779.4121 | 16210.4904 | 4514.3138 | 4514.3138
Ca(OH)2 | lb/hr |  | 4.911 | 66.0513 | 34.787 | 9.6875 | 9.6875
H2O | lb/hr |  | 9453.334 | 68633.7626 | 36147.115 | 10066.2852 | 10066.2852
TOTAL | lb/hr |  | 14543.5908 | 105590.404 | 55610.9461 | 15486.5926 | 15486.5926
Composition of Slurry from Head Tank
CaSO3*1/2H2O | lb/hr |  | 314.5794 | 4231.024 | 2228.3393 | 620.5502 | 620.5502
CaSO4*2H2O | lb/hr |  | 139.7907 | 1880.1541 | 990.2145 | 275.7559 | 275.7559
Inerts | lb/hr |  | 4648.2895 | 30905.1149 | 16276.6939 | 4532.7502 | 4532.7502
Ca(OH)2 | lb/hr |  | 210.7931 | 1560.8113 | 822.0273 | 228.919 | 228.919
H2O | lb/hr |  | 9974.1246 | 72414.8426 | 38138.4838 | 10620.8436 | 10620.8436
TOTAL | lb/hr |  | 15287.5773 | 110991.9468 | 58455.7587 | 16278.8189 | 16278.8189
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 525.5894 | 5763.0132 | 3035.187 | 845.2419 | 845.2419
CaSO4*2H2O | lb/hr |  | 233.5579 | 2560.9292 | 1348.756 | 375.6029 | 375.6029
Inerts | lb/hr |  | 8513.8661 | 44710.3565 | 23547.4544 | 6557.519 | 6557.519
Ca(OH)2 | lb/hr |  | 49.3815 | 388.9194 | 204.8309 | 57.0415 | 57.0415
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 9322.3948 | 53423.2184 | 28136.2284 | 7835.4054 | 7835.4054
Composition of Solids from Spray Dryers
CaSO3*1/2H2O | lb/hr |  | 52.5589 | 576.3013 | 303.5187 | 84.5242 | 84.5242
CaSO4*2H2O | lb/hr |  | 23.3558 | 256.0929 | 134.8756 | 37.5603 | 37.5603
Inerts | lb/hr |  | 851.3866 | 4471.0357 | 2354.7454 | 655.7519 | 655.7519
Ca(OH)2 | lb/hr |  | 4.9381 | 38.8919 | 20.4831 | 5.7042 | 5.7042
H2O | lb/hr |  | 19.0253 | 109.027 | 57.4209 | 15.9906 | 15.9906
TOTAL | lb/hr |  | 951.2648 | 5451.3488 | 2871.0437 | 799.5312 | 799.5312
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 525.7829 | 5569.7092 | 2933.3802 | 816.8907 | 816.8907
CaSO4*2H2O | lb/hr |  | 233.6439 | 2475.03 | 1303.5158 | 363.0044 | 363.0044
Inerts | lb/hr |  | 7662.4795 | 40239.3209 | 21192.709 | 5901.7671 | 5901.7671
Ca(OH)2 | lb/hr |  | 4.0904 | 57.0545 | 30.0487 | 8.368 | 8.368
H2O | lb/hr
TOTAL | lb/hr |  | 8425.9967 | 48341.1147 | 25459.6537 | 7090.0302 | 7090.0302
CaSO3*1/2H2O | wt % |  | 6.24% | 11.52% | 11.52% | 11.52% | 11.52%
CaSO4*2H2O | wt % |  | 2.773% | 5.12% | 5.12% | 5.12% | 5.12%
Inerts | wt % |  | 90.94% | 83.24% | 83.24% | 83.24% | 83.24%
Ca(OH)2 | wt % |  | 0.04855% | 0.118% | 0.118% | 0.118% | 0.118%
H2O | wt %
TOTAL | wt % |  | 100% | 100% | 100% | 100% | 100%
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 265.3919 | 1921.0729 | 1011.7651 | 281.7574 | 281.7574
CaSO4*2H2O | lb/hr |  | 117.9331 | 853.6735 | 449.6014 | 125.2054 | 125.2054
Inerts | lb/hr |  | 3867.6797 | 13879.1213 | 7309.6705 | 2035.6045 | 2035.6045
Ca(OH)2 | lb/hr |  | 2.0647 | 19.6789 | 10.3642 | 2.8862 | 2.8862
H2O | lb/hr |  | 86.7973 | 340.2765 | 179.2123 | 49.9072 | 49.9072
TOTAL | lb/hr |  | 4339.8667 | 17013.8231 | 8960.6135 | 2495.3607 | 2495.3607
Solids Out Stack
CaSO3*1/2H2O | lb/hr |  | 0.93039 | 6.1351 | 3.2312 | 0.89982 | 0.89982
CaSO4*2H2O | lb/hr |  | 0.41344 | 2.7263 | 1.4358 | 0.39986 | 0.39986
Inerts | lb/hr |  | 13.5589 | 44.3242 | 23.3441 | 6.5009 | 6.5009
Ca(OH)2 | lb/hr |  | 0.0072381 | 0.062846 | 0.033099 | 0.0092175 | 0.0092175
H2O | lb/hr
TOTAL | lb/hr |  | 14.91 | 53.2485 | 28.0442 | 7.8098 | 7.8098
Composition of Baghouse/ESP Solids to Recycle
CaSO3*1/2H2O | lb/hr |  | 259.4606 | 3642.5012 | 1918.384 | 534.2335 | 534.2335
CaSO4*2H2O | lb/hr |  | 115.2974 | 1618.6303 | 852.4786 | 237.3991 | 237.3991
Inerts | lb/hr |  | 3781.2408 | 26315.8754 | 13859.6944 | 3859.6617 | 3859.6617
Ca(OH)2 | lb/hr |  | 2.0185 | 37.3128 | 19.6514 | 5.4725 | 5.4725
H2O | lb/hr |  | 84.8575 | 645.1902 | 339.8002 | 94.6279 | 94.6279
TOTAL | lb/hr |  | 4242.8748 | 32259.5098 | 16990.0085 | 4731.3948 | 4731.3948
Calculated Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 312.0196 | 4218.8025 | 2221.9027 | 618.7577 | 618.7577
CaSO4*2H2O | lb/hr |  | 138.6532 | 1874.7232 | 987.3542 | 274.9594 | 274.9594
Inerts | lb/hr |  | 4632.6274 | 30786.911 | 16214.4398 | 4515.4136 | 4515.4136
Ca(OH)2 | lb/hr |  | 6.9567 | 76.2047 | 40.1345 | 11.1767 | 11.1767
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
TOTAL | lb/hr |  | 5194.1396 | 37710.8586 | 19861.0522 | 5530.9259 | 5530.9259
ITERATION 2
Assumed Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 309.4597 | 4206.581 | 2215.466 | 616.9652 | 616.9652
CaSO4*2H2O | lb/hr |  | 137.5156 | 1869.2923 | 984.4939 | 274.1629 | 274.1629
Inerts | lb/hr |  | 4634.4761 | 30795.7372 | 16219.0883 | 4516.7081 | 4516.7081
Ca(OH)2 | lb/hr |  | 8.8054 | 85.0309 | 44.7829 | 12.4712 | 12.4712
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
TOTAL | lb/hr |  | 5194.1396 | 37710.8586 | 19861.0522 | 5530.9259 | 5530.9259
Composition of Recycle Slurry to Head Tanks
CaSO3*1/2H2O | lb/hr |  | 309.4597 | 4206.581 | 2215.466 | 616.9652 | 616.9652
CaSO4*2H2O | lb/hr |  | 137.5156 | 1869.2923 | 984.4939 | 274.1629 | 274.1629
Inerts | lb/hr |  | 4634.4761 | 30795.7372 | 16219.0883 | 4516.7081 | 4516.7081
Ca(OH)2 | lb/hr |  | 8.8054 | 85.0309 | 44.7829 | 12.4712 | 12.4712
H2O | lb/hr |  | 9453.334 | 68633.7626 | 36147.115 | 10066.2852 | 10066.2852
TOTAL | lb/hr |  | 14543.5908 | 105590.404 | 55610.9461 | 15486.5926 | 15486.5926
Composition of Slurry from Head Tank
CaSO3*1/2H2O | lb/hr |  | 309.4597 | 4206.581 | 2215.466 | 616.9652 | 616.9652
CaSO4*2H2O | lb/hr |  | 137.5156 | 1869.2923 | 984.4939 | 274.1629 | 274.1629
Inerts | lb/hr |  | 4651.7899 | 30921.4401 | 16285.2918 | 4535.1445 | 4535.1445
Ca(OH)2 | lb/hr |  | 214.6875 | 1579.7909 | 832.0232 | 231.7027 | 231.7027
H2O | lb/hr |  | 9974.1246 | 72414.8426 | 38138.4838 | 10620.8436 | 10620.8436
TOTAL | lb/hr |  | 15287.5773 | 110991.9468 | 58455.7587 | 16278.8189 | 16278.8189
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 520.4697 | 5738.5703 | 3022.3137 | 841.657 | 841.657
CaSO4*2H2O | lb/hr |  | 231.2828 | 2550.0674 | 1343.0355 | 374.0099 | 374.0099
Inerts | lb/hr |  | 8517.3664 | 44726.6817 | 23556.0524 | 6559.9133 | 6559.9133
Ca(OH)2 | lb/hr |  | 53.2759 | 407.899 | 214.8268 | 59.8252 | 59.8252
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 9322.3948 | 53423.2184 | 28136.2284 | 7835.4054 | 7835.4054
Composition of Solids from Spray Dryers
CaSO3*1/2H2O | lb/hr |  | 52.047 | 573.857 | 302.2314 | 84.1657 | 84.1657
CaSO4*2H2O | lb/hr |  | 23.1283 | 255.0067 | 134.3035 | 37.401 | 37.401
Inerts | lb/hr |  | 851.7366 | 4472.6682 | 2355.6052 | 655.9913 | 655.9913
Ca(OH)2 | lb/hr |  | 5.3276 | 40.7899 | 21.4827 | 5.9825 | 5.9825
H2O | lb/hr |  | 19.0253 | 109.027 | 57.4209 | 15.9906 | 15.9906
TOTAL | lb/hr |  | 951.2648 | 5451.3488 | 2871.0437 | 799.5312 | 799.5312
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 521.1752 | 5547.7106 | 2921.7942 | 813.6642 | 813.6642
CaSO4*2H2O | lb/hr |  | 231.5963 | 2465.2544 | 1298.3673 | 361.5706 | 361.5706
Inerts | lb/hr |  | 7665.6298 | 40254.0135 | 21200.4471 | 5903.922 | 5903.922
Ca(OH)2 | lb/hr |  | 7.5954 | 74.1362 | 39.0451 | 10.8733 | 10.8733
H2O | lb/hr
TOTAL | lb/hr |  | 8425.9967 | 48341.1147 | 25459.6537 | 7090.0302 | 7090.0302
CaSO3*1/2H2O | wt % |  | 6.185% | 11.48% | 11.48% | 11.48% | 11.48%
CaSO4*2H2O | wt % |  | 2.749% | 5.1% | 5.1% | 5.1% | 5.1%
Inerts | wt % |  | 90.98% | 83.27% | 83.27% | 83.27% | 83.27%
Ca(OH)2 | wt % |  | 0.09014% | 0.1534% | 0.1534% | 0.1534% | 0.1534%
H2O | wt %
TOTAL | wt % |  | 100% | 100% | 100% | 100% | 100%
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 263.0661 | 1913.4853 | 1007.7689 | 280.6445 | 280.6445
CaSO4*2H2O | lb/hr |  | 116.8996 | 850.3018 | 447.8256 | 124.7109 | 124.7109
Inerts | lb/hr |  | 3869.2699 | 13884.189 | 7312.3395 | 2036.3477 | 2036.3477
Ca(OH)2 | lb/hr |  | 3.8338 | 25.5706 | 13.4672 | 3.7504 | 3.7504
H2O | lb/hr |  | 86.7973 | 340.2765 | 179.2123 | 49.9072 | 49.9072
TOTAL | lb/hr |  | 4339.8667 | 17013.8231 | 8960.6135 | 2495.3607 | 2495.3607
Solids Out Stack
CaSO3*1/2H2O | lb/hr |  | 0.92223 | 6.1109 | 3.2184 | 0.89626 | 0.89626
CaSO4*2H2O | lb/hr |  | 0.40982 | 2.7155 | 1.4302 | 0.39828 | 0.39828
Inerts | lb/hr |  | 13.5645 | 44.3404 | 23.3526 | 6.5033 | 6.5033
Ca(OH)2 | lb/hr |  | 0.01344 | 0.081662 | 0.043009 | 0.011977 | 0.011977
H2O | lb/hr
TOTAL | lb/hr |  | 14.91 | 53.2485 | 28.0442 | 7.8098 | 7.8098
Composition of Baghouse/ESP Solids to Recycle
CaSO3*1/2H2O | lb/hr |  | 257.1868 | 3628.1144 | 1910.8069 | 532.1234 | 532.1234
CaSO4*2H2O | lb/hr |  | 114.287 | 1612.2372 | 849.1116 | 236.4614 | 236.4614
Inerts | lb/hr |  | 3782.7954 | 26325.4841 | 13864.755 | 3861.071 | 3861.071
Ca(OH)2 | lb/hr |  | 3.7482 | 48.4839 | 25.5348 | 7.111 | 7.111
H2O | lb/hr |  | 84.8575 | 645.1902 | 339.8002 | 94.6279 | 94.6279
TOTAL | lb/hr |  | 4242.8748 | 32259.5098 | 16990.0085 | 4731.3948 | 4731.3948
Calculated Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 309.2338 | 4201.9714 | 2213.0383 | 616.2891 | 616.2891
CaSO4*2H2O | lb/hr |  | 137.4152 | 1867.2439 | 983.4151 | 273.8624 | 273.8624
Inerts | lb/hr |  | 4634.532 | 30798.1523 | 16220.3602 | 4517.0623 | 4517.0623
Ca(OH)2 | lb/hr |  | 9.0757 | 89.2738 | 47.0175 | 13.0935 | 13.0935
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
TOTAL | lb/hr |  | 5194.1396 | 37710.8586 | 19861.0522 | 5530.9259 | 5530.9259
ITERATION 3
Assumed Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 309.2338 | 4197.3618 | 2210.6106 | 616.2891 | 616.2891
CaSO4*2H2O | lb/hr |  | 137.4152 | 1865.1955 | 982.3363 | 273.8624 | 273.8624
Inerts | lb/hr |  | 4634.532 | 30801.4813 | 16222.1135 | 4517.0623 | 4517.0623
Ca(OH)2 | lb/hr |  | 9.0757 | 92.6028 | 48.7708 | 13.0935 | 13.0935
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
TOTAL | lb/hr |  | 5194.1396 | 37710.8586 | 19861.0522 | 5530.9259 | 5530.9259
Composition of Recycle Slurry to Head Tanks
CaSO3*1/2H2O | lb/hr |  | 309.2338 | 4197.3618 | 2210.6106 | 616.2891 | 616.2891
CaSO4*2H2O | lb/hr |  | 137.4152 | 1865.1955 | 982.3363 | 273.8624 | 273.8624
Inerts | lb/hr |  | 4634.532 | 30801.4813 | 16222.1135 | 4517.0623 | 4517.0623
Ca(OH)2 | lb/hr |  | 9.0757 | 92.6028 | 48.7708 | 13.0935 | 13.0935
H2O | lb/hr |  | 9453.334 | 68633.7626 | 36147.115 | 10066.2852 | 10066.2852
TOTAL | lb/hr |  | 14543.5908 | 105590.404 | 55610.9461 | 15486.5926 | 15486.5926
Composition of Slurry from Head Tank
CaSO3*1/2H2O | lb/hr |  | 309.2338 | 4197.3618 | 2210.6106 | 616.2891 | 616.2891
CaSO4*2H2O | lb/hr |  | 137.4152 | 1865.1955 | 982.3363 | 273.8624 | 273.8624
Inerts | lb/hr |  | 4651.8458 | 30927.1842 | 16288.317 | 4535.4988 | 4535.4988
Ca(OH)2 | lb/hr |  | 214.9579 | 1587.3628 | 836.0111 | 232.325 | 232.325
H2O | lb/hr |  | 9974.1246 | 72414.8426 | 38138.4838 | 10620.8436 | 10620.8436
TOTAL | lb/hr |  | 15287.5773 | 110991.9468 | 58455.7587 | 16278.8189 | 16278.8189
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 520.2437 | 5729.3511 | 3017.4582 | 840.9809 | 840.9809
CaSO4*2H2O | lb/hr |  | 231.1824 | 2545.9706 | 1340.8779 | 373.7095 | 373.7095
Inerts | lb/hr |  | 8517.4224 | 44732.4258 | 23559.0776 | 6560.2675 | 6560.2675
Ca(OH)2 | lb/hr |  | 53.5463 | 415.4709 | 218.8147 | 60.4475 | 60.4475
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 9322.3948 | 53423.2184 | 28136.2284 | 7835.4054 | 7835.4054
Composition of Solids from Spray Dryers
CaSO3*1/2H2O | lb/hr |  | 52.0244 | 572.9351 | 301.7458 | 84.0981 | 84.0981
CaSO4*2H2O | lb/hr |  | 23.1182 | 254.5971 | 134.0878 | 37.3709 | 37.3709
Inerts | lb/hr |  | 851.7422 | 4473.2426 | 2355.9078 | 656.0268 | 656.0268
Ca(OH)2 | lb/hr |  | 5.3546 | 41.5471 | 21.8815 | 6.0447 | 6.0447
H2O | lb/hr |  | 19.0253 | 109.027 | 57.4209 | 15.9906 | 15.9906
TOTAL | lb/hr |  | 951.2648 | 5451.3488 | 2871.0437 | 799.5312 | 799.5312
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 520.9718 | 5539.4133 | 2917.4243 | 813.0557 | 813.0557
CaSO4*2H2O | lb/hr |  | 231.506 | 2461.5673 | 1296.4255 | 361.3003 | 361.3003
Inerts | lb/hr |  | 7665.6801 | 40259.1832 | 21203.1698 | 5904.2408 | 5904.2408
Ca(OH)2 | lb/hr |  | 7.8388 | 80.9509 | 42.6341 | 11.4334 | 11.4334
H2O | lb/hr
TOTAL | lb/hr |  | 8425.9967 | 48341.1147 | 25459.6537 | 7090.0302 | 7090.0302
CaSO3*1/2H2O | wt % |  | 6.183% | 11.46% | 11.46% | 11.47% | 11.47%
CaSO4*2H2O | wt % |  | 2.748% | 5.092% | 5.092% | 5.096% | 5.096%
Inerts | wt % |  | 90.98% | 83.28% | 83.28% | 83.28% | 83.28%
Ca(OH)2 | wt % |  | 0.09303% | 0.1675% | 0.1675% | 0.1613% | 0.1613%
H2O | wt %
TOTAL | wt % |  | 100% | 100% | 100% | 100% | 100%
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 262.9635 | 1910.6234 | 1006.2617 | 280.4346 | 280.4346
CaSO4*2H2O | lb/hr |  | 116.8539 | 849.03 | 447.1558 | 124.6177 | 124.6177
Inerts | lb/hr |  | 3869.2953 | 13885.9721 | 7313.2786 | 2036.4577 | 2036.4577
Ca(OH)2 | lb/hr |  | 3.9567 | 27.9211 | 14.7051 | 3.9435 | 3.9435
H2O | lb/hr |  | 86.7973 | 340.2765 | 179.2123 | 49.9072 | 49.9072
TOTAL | lb/hr |  | 4339.8667 | 17013.8231 | 8960.6135 | 2495.3607 | 2495.3607
Solids Out Stack
CaSO3*1/2H2O | lb/hr |  | 0.92187 | 6.1018 | 3.2136 | 0.89559 | 0.89559
CaSO4*2H2O | lb/hr |  | 0.40966 | 2.7115 | 1.428 | 0.39798 | 0.39798
Inerts | lb/hr |  | 13.5646 | 44.3461 | 23.3556 | 6.5036 | 6.5036
Ca(OH)2 | lb/hr |  | 0.013871 | 0.089169 | 0.046962 | 0.012594 | 0.012594
H2O | lb/hr
TOTAL | lb/hr |  | 14.91 | 53.2485 | 28.0442 | 7.8098 | 7.8098
Composition of Baghouse/ESP Solids to Recycle
CaSO3*1/2H2O | lb/hr |  | 257.0865 | 3622.6881 | 1907.9491 | 531.7255 | 531.7255
CaSO4*2H2O | lb/hr |  | 114.2424 | 1609.8259 | 847.8416 | 236.2846 | 236.2846
Inerts | lb/hr |  | 3782.8202 | 26328.865 | 13866.5356 | 3861.2795 | 3861.2795
Ca(OH)2 | lb/hr |  | 3.8682 | 52.9406 | 27.882 | 7.4772 | 7.4772
H2O | lb/hr |  | 84.8575 | 645.1902 | 339.8002 | 94.6279 | 94.6279
TOTAL | lb/hr |  | 4242.8748 | 32259.5098 | 16990.0085 | 4731.3948 | 4731.3948
Calculated Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 309.1109 | 4195.6232 | 2209.6949 | 615.8236 | 615.8236
CaSO4*2H2O | lb/hr |  | 137.3606 | 1864.4229 | 981.9294 | 273.6556 | 273.6556
Inerts | lb/hr |  | 4634.5625 | 30802.1076 | 16222.4433 | 4517.3062 | 4517.3062
Ca(OH)2 | lb/hr |  | 9.2229 | 94.4877 | 49.7635 | 13.522 | 13.522
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
TOTAL | lb/hr |  | 5194.1396 | 37710.8586 | 19861.0522 | 5530.9259 | 5530.9259
ITERATION 4
Assumed Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 309.1109 | 4193.8846 | 2209.6949 | 615.8236 | 615.8236
CaSO4*2H2O | lb/hr |  | 137.3606 | 1863.6503 | 981.9294 | 273.6556 | 273.6556
Inerts | lb/hr |  | 4634.5625 | 30803.3632 | 16222.4433 | 4517.3062 | 4517.3062
Ca(OH)2 | lb/hr |  | 9.2229 | 95.7433 | 49.7635 | 13.522 | 13.522
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
TOTAL | lb/hr |  | 5194.1396 | 37710.8586 | 19861.0522 | 5530.9259 | 5530.9259
Composition of Recycle Slurry to Head Tanks
CaSO3*1/2H2O | lb/hr |  | 309.1109 | 4193.8846 | 2209.6949 | 615.8236 | 615.8236
CaSO4*2H2O | lb/hr |  | 137.3606 | 1863.6503 | 981.9294 | 273.6556 | 273.6556
Inerts | lb/hr |  | 4634.5625 | 30803.3632 | 16222.4433 | 4517.3062 | 4517.3062
Ca(OH)2 | lb/hr |  | 9.2229 | 95.7433 | 49.7635 | 13.522 | 13.522
H2O | lb/hr |  | 9453.334 | 68633.7626 | 36147.115 | 10066.2852 | 10066.2852
TOTAL | lb/hr |  | 14543.5908 | 105590.404 | 55610.9461 | 15486.5926 | 15486.5926
Composition of Slurry from Head Tank
CaSO3*1/2H2O | lb/hr |  | 309.1109 | 4193.8846 | 2209.6949 | 615.8236 | 615.8236
CaSO4*2H2O | lb/hr |  | 137.3606 | 1863.6503 | 981.9294 | 273.6556 | 273.6556
Inerts | lb/hr |  | 4651.8763 | 30929.066 | 16288.6468 | 4535.7427 | 4535.7427
Ca(OH)2 | lb/hr |  | 215.105 | 1590.5033 | 837.0038 | 232.7535 | 232.7535
H2O | lb/hr |  | 9974.1246 | 72414.8426 | 38138.4838 | 10620.8436 | 10620.8436
TOTAL | lb/hr |  | 15287.5773 | 110991.9468 | 58455.7587 | 16278.8189 | 16278.8189
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 520.1208 | 5725.8739 | 3016.5426 | 840.5154 | 840.5154
CaSO4*2H2O | lb/hr |  | 231.1278 | 2544.4254 | 1340.471 | 373.5026 | 373.5026
Inerts | lb/hr |  | 8517.4528 | 44734.3077 | 23559.4074 | 6560.5114 | 6560.5114
Ca(OH)2 | lb/hr |  | 53.6934 | 418.6114 | 219.8074 | 60.876 | 60.876
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 9322.3948 | 53423.2184 | 28136.2284 | 7835.4054 | 7835.4054
Composition of Solids from Spray Dryers
CaSO3*1/2H2O | lb/hr |  | 52.0121 | 572.5874 | 301.6543 | 84.0515 | 84.0515
CaSO4*2H2O | lb/hr |  | 23.1128 | 254.4425 | 134.0471 | 37.3503 | 37.3503
Inerts | lb/hr |  | 851.7453 | 4473.4308 | 2355.9407 | 656.0511 | 656.0511
Ca(OH)2 | lb/hr |  | 5.3693 | 41.8611 | 21.9807 | 6.0876 | 6.0876
H2O | lb/hr |  | 19.0253 | 109.027 | 57.4209 | 15.9906 | 15.9906
TOTAL | lb/hr |  | 951.2648 | 5451.3488 | 2871.0437 | 799.5312 | 799.5312
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 520.8612 | 5536.2838 | 2916.6002 | 812.6368 | 812.6368
CaSO4*2H2O | lb/hr |  | 231.4568 | 2460.1767 | 1296.0593 | 361.1141 | 361.1141
Inerts | lb/hr |  | 7665.7075 | 40260.8769 | 21203.4667 | 5904.4603 | 5904.4603
Ca(OH)2 | lb/hr |  | 7.9712 | 83.7773 | 43.5276 | 11.819 | 11.819
H2O | lb/hr
TOTAL | lb/hr |  | 8425.9967 | 48341.1147 | 25459.6537 | 7090.0302 | 7090.0302
CaSO3*1/2H2O | wt % |  | 6.182% | 11.45% | 11.46% | 11.46% | 11.46%
CaSO4*2H2O | wt % |  | 2.747% | 5.089% | 5.091% | 5.093% | 5.093%
Inerts | wt % |  | 90.98% | 83.28% | 83.28% | 83.28% | 83.28%
Ca(OH)2 | wt % |  | 0.0946% | 0.1733% | 0.171% | 0.1667% | 0.1667%
H2O | wt %
TOTAL | wt % |  | 100% | 100% | 100% | 100% | 100%
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 262.9076 | 1909.544 | 1005.9774 | 280.2901 | 280.2901
CaSO4*2H2O | lb/hr |  | 116.8291 | 848.5504 | 447.0295 | 124.5534 | 124.5534
Inerts | lb/hr |  | 3869.3091 | 13886.5562 | 7313.381 | 2036.5334 | 2036.5334
Ca(OH)2 | lb/hr |  | 4.0235 | 28.896 | 15.0133 | 4.0766 | 4.0766
H2O | lb/hr |  | 86.7973 | 340.2765 | 179.2123 | 49.9072 | 49.9072
TOTAL | lb/hr |  | 4339.8667 | 17013.8231 | 8960.6135 | 2495.3607 | 2495.3607
Solids Out Stack
CaSO3*1/2H2O | lb/hr |  | 0.92168 | 6.0983 | 3.2127 | 0.89513 | 0.89513
CaSO4*2H2O | lb/hr |  | 0.40957 | 2.7099 | 1.4276 | 0.39777 | 0.39777
Inerts | lb/hr |  | 13.5647 | 44.348 | 23.356 | 6.5039 | 6.5039
Ca(OH)2 | lb/hr |  | 0.014105 | 0.092282 | 0.047946 | 0.013019 | 0.013019
H2O | lb/hr
TOTAL | lb/hr |  | 14.91 | 53.2485 | 28.0442 | 7.8098 | 7.8098
Composition of Baghouse/ESP Solids to Recycle
CaSO3*1/2H2O | lb/hr |  | 257.0319 | 3620.6415 | 1907.4101 | 531.4515 | 531.4515
CaSO4*2H2O | lb/hr |  | 114.2181 | 1608.9164 | 847.6021 | 236.1629 | 236.1629
Inerts | lb/hr |  | 3782.8337 | 26329.9727 | 13866.7297 | 3861.423 | 3861.423
Ca(OH)2 | lb/hr |  | 3.9336 | 54.789 | 28.4663 | 7.7295 | 7.7295
H2O | lb/hr |  | 84.8575 | 645.1902 | 339.8002 | 94.6279 | 94.6279
TOTAL | lb/hr |  | 4242.8748 | 32259.5098 | 16990.0085 | 4731.3948 | 4731.3948
Calculated Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 309.044 | 4193.2289 | 2209.0644 | 615.503 | 615.503
CaSO4*2H2O | lb/hr |  | 137.3309 | 1863.3589 | 981.6492 | 273.5131 | 273.5131
Inerts | lb/hr |  | 4634.579 | 30803.4034 | 16222.6705 | 4517.4742 | 4517.4742
Ca(OH)2 | lb/hr |  | 9.3029 | 96.6502 | 50.4471 | 13.8171 | 13.8171
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
TOTAL | lb/hr |  | 5194.1396 | 37710.8586 | 19861.0522 | 5530.9259 | 5530.9259
ITERATION 5
Assumed Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 309.044 | 4193.2289 | 2209.0644 | 615.503 | 615.503
CaSO4*2H2O | lb/hr |  | 137.3309 | 1863.3589 | 981.6492 | 273.5131 | 273.5131
Inerts | lb/hr |  | 4634.579 | 30803.4034 | 16222.6705 | 4517.4742 | 4517.4742
Ca(OH)2 | lb/hr |  | 9.3029 | 96.6502 | 50.4471 | 13.8171 | 13.8171
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
TOTAL | lb/hr |  | 5194.1396 | 37710.8586 | 19861.0522 | 5530.9259 | 5530.9259
Composition of Recycle Slurry to Head Tanks
CaSO3*1/2H2O | lb/hr |  | 309.044 | 4193.2289 | 2209.0644 | 615.503 | 615.503
CaSO4*2H2O | lb/hr |  | 137.3309 | 1863.3589 | 981.6492 | 273.5131 | 273.5131
Inerts | lb/hr |  | 4634.579 | 30803.4034 | 16222.6705 | 4517.4742 | 4517.4742
Ca(OH)2 | lb/hr |  | 9.3029 | 96.6502 | 50.4471 | 13.8171 | 13.8171
H2O | lb/hr |  | 9453.334 | 68633.7626 | 36147.115 | 10066.2852 | 10066.2852
TOTAL | lb/hr |  | 14543.5908 | 105590.404 | 55610.9461 | 15486.5926 | 15486.5926
Composition of Slurry from Head Tank
CaSO3*1/2H2O | lb/hr |  | 309.044 | 4193.2289 | 2209.0644 | 615.503 | 615.503
CaSO4*2H2O | lb/hr |  | 137.3309 | 1863.3589 | 981.6492 | 273.5131 | 273.5131
Inerts | lb/hr |  | 4651.8928 | 30929.1063 | 16288.874 | 4535.9106 | 4535.9106
Ca(OH)2 | lb/hr |  | 215.185 | 1591.4102 | 837.6873 | 233.0485 | 233.0485
H2O | lb/hr |  | 9974.1246 | 72414.8426 | 38138.4838 | 10620.8436 | 10620.8436
TOTAL | lb/hr |  | 15287.5773 | 110991.9468 | 58455.7587 | 16278.8189 | 16278.8189
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 520.0539 | 5725.2181 | 3015.9121 | 840.1948 | 840.1948
CaSO4*2H2O | lb/hr |  | 231.0981 | 2544.134 | 1340.1908 | 373.3601 | 373.3601
Inerts | lb/hr |  | 8517.4694 | 44734.3479 | 23559.6345 | 6560.6794 | 6560.6794
Ca(OH)2 | lb/hr |  | 53.7734 | 419.5183 | 220.491 | 61.171 | 61.171
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 9322.3948 | 53423.2184 | 28136.2284 | 7835.4054 | 7835.4054
Composition of Solids from Spray Dryers
CaSO3*1/2H2O | lb/hr |  | 52.0054 | 572.5218 | 301.5912 | 84.0195 | 84.0195
CaSO4*2H2O | lb/hr |  | 23.1098 | 254.4134 | 134.0191 | 37.336 | 37.336
Inerts | lb/hr |  | 851.7469 | 4473.4348 | 2355.9635 | 656.0679 | 656.0679
Ca(OH)2 | lb/hr |  | 5.3773 | 41.9518 | 22.0491 | 6.1171 | 6.1171
H2O | lb/hr |  | 19.0253 | 109.027 | 57.4209 | 15.9906 | 15.9906
TOTAL | lb/hr |  | 951.2648 | 5451.3488 | 2871.0437 | 799.5312 | 799.5312
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 520.801 | 5535.6936 | 2916.0328 | 812.3483 | 812.3483
CaSO4*2H2O | lb/hr |  | 231.4301 | 2459.9144 | 1295.8071 | 360.9859 | 360.9859
Inerts | lb/hr |  | 7665.7224 | 40260.9131 | 21203.6711 | 5904.6114 | 5904.6114
Ca(OH)2 | lb/hr |  | 8.0432 | 84.5936 | 44.1428 | 12.0846 | 12.0846
H2O | lb/hr
TOTAL | lb/hr |  | 8425.9967 | 48341.1147 | 25459.6537 | 7090.0302 | 7090.0302
CaSO3*1/2H2O | wt % |  | 6.181% | 11.45% | 11.45% | 11.46% | 11.46%
CaSO4*2H2O | wt % |  | 2.747% | 5.089% | 5.09% | 5.091% | 5.091%
Inerts | wt % |  | 90.98% | 83.29% | 83.28% | 83.28% | 83.28%
Ca(OH)2 | wt % |  | 0.09546% | 0.175% | 0.1734% | 0.1704% | 0.1704%
H2O | wt %
TOTAL | wt % |  | 100% | 100% | 100% | 100% | 100%
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 262.8773 | 1909.3404 | 1005.7817 | 280.1906 | 280.1906
CaSO4*2H2O | lb/hr |  | 116.8156 | 848.4599 | 446.9425 | 124.5092 | 124.5092
Inerts | lb/hr |  | 3869.3166 | 13886.5687 | 7313.4515 | 2036.5855 | 2036.5855
Ca(OH)2 | lb/hr |  | 4.0599 | 29.1775 | 15.2255 | 4.1681 | 4.1681
H2O | lb/hr |  | 86.7973 | 340.2765 | 179.2123 | 49.9072 | 49.9072
TOTAL | lb/hr |  | 4339.8667 | 17013.8231 | 8960.6135 | 2495.3607 | 2495.3607
Solids Out Stack
CaSO3*1/2H2O | lb/hr |  | 0.92157 | 6.0977 | 3.2121 | 0.89481 | 0.89481
CaSO4*2H2O | lb/hr |  | 0.40952 | 2.7096 | 1.4274 | 0.39763 | 0.39763
Inerts | lb/hr |  | 13.5647 | 44.348 | 23.3562 | 6.504 | 6.504
Ca(OH)2 | lb/hr |  | 0.014233 | 0.093181 | 0.048624 | 0.013311 | 0.013311
H2O | lb/hr
TOTAL | lb/hr |  | 14.91 | 53.2485 | 28.0442 | 7.8098 | 7.8098
Composition of Baghouse/ESP Solids to Recycle
CaSO3*1/2H2O | lb/hr |  | 257.0022 | 3620.2555 | 1907.039 | 531.2628 | 531.2628
CaSO4*2H2O | lb/hr |  | 114.2049 | 1608.7449 | 847.4372 | 236.079 | 236.079
Inerts | lb/hr |  | 3782.8411 | 26329.9964 | 13866.8634 | 3861.5219 | 3861.5219
Ca(OH)2 | lb/hr |  | 3.9691 | 55.3228 | 28.8687 | 7.9031 | 7.9031
H2O | lb/hr |  | 84.8575 | 645.1902 | 339.8002 | 94.6279 | 94.6279
TOTAL | lb/hr |  | 4242.8748 | 32259.5098 | 16990.0085 | 4731.3948 | 4731.3948
Calculated Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 309.0076 | 4192.7773 | 2208.6302 | 615.2823 | 615.2823
CaSO4*2H2O | lb/hr |  | 137.3147 | 1863.1583 | 981.4563 | 273.415 | 273.415
Inerts | lb/hr |  | 4634.588 | 30803.4311 | 16222.8269 | 4517.5898 | 4517.5898
Ca(OH)2 | lb/hr |  | 9.3465 | 97.2747 | 50.9178 | 14.0202 | 14.0202
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
TOTAL | lb/hr |  | 5194.1396 | 37710.8586 | 19861.0522 | 5530.9259 | 5530.9259
ITERATION 6
Assumed Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 309.0076 | 4192.7773 | 2208.6302 | 615.2823 | 615.2823
CaSO4*2H2O | lb/hr |  | 137.3147 | 1863.1583 | 981.4563 | 273.415 | 273.415
Inerts | lb/hr |  | 4634.588 | 30803.4311 | 16222.8269 | 4517.5898 | 4517.5898
Ca(OH)2 | lb/hr |  | 9.3465 | 97.2747 | 50.9178 | 14.0202 | 14.0202
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
TOTAL | lb/hr |  | 5194.1396 | 37710.8586 | 19861.0522 | 5530.9259 | 5530.9259
Composition of Recycle Slurry to Head Tanks
CaSO3*1/2H2O | lb/hr |  | 309.0076 | 4192.7773 | 2208.6302 | 615.2823 | 615.2823
CaSO4*2H2O | lb/hr |  | 137.3147 | 1863.1583 | 981.4563 | 273.415 | 273.415
Inerts | lb/hr |  | 4634.588 | 30803.4311 | 16222.8269 | 4517.5898 | 4517.5898
Ca(OH)2 | lb/hr |  | 9.3465 | 97.2747 | 50.9178 | 14.0202 | 14.0202
H2O | lb/hr |  | 9453.334 | 68633.7626 | 36147.115 | 10066.2852 | 10066.2852
TOTAL | lb/hr |  | 14543.5908 | 105590.404 | 55610.9461 | 15486.5926 | 15486.5926
Composition of Slurry from Head Tank
CaSO3*1/2H2O | lb/hr |  | 309.0076 | 4192.7773 | 2208.6302 | 615.2823 | 615.2823
CaSO4*2H2O | lb/hr |  | 137.3147 | 1863.1583 | 981.4563 | 273.415 | 273.415
Inerts | lb/hr |  | 4651.9018 | 30929.134 | 16289.0304 | 4536.0263 | 4536.0263
Ca(OH)2 | lb/hr |  | 215.2286 | 1592.0346 | 838.158 | 233.2517 | 233.2517
H2O | lb/hr |  | 9974.1246 | 72414.8426 | 38138.4838 | 10620.8436 | 10620.8436
TOTAL | lb/hr |  | 15287.5773 | 110991.9468 | 58455.7587 | 16278.8189 | 16278.8189
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 520.0175 | 5724.7666 | 3015.4779 | 839.9741 | 839.9741
CaSO4*2H2O | lb/hr |  | 231.0819 | 2543.9334 | 1339.9978 | 373.262 | 373.262
Inerts | lb/hr |  | 8517.4784 | 44734.3756 | 23559.7909 | 6560.795 | 6560.795
Ca(OH)2 | lb/hr |  | 53.817 | 420.1428 | 220.9617 | 61.3742 | 61.3742
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 9322.3948 | 53423.2184 | 28136.2284 | 7835.4054 | 7835.4054
Composition of Solids from Spray Dryers
CaSO3*1/2H2O | lb/hr |  | 52.0018 | 572.4767 | 301.5478 | 83.9974 | 83.9974
CaSO4*2H2O | lb/hr |  | 23.1082 | 254.3933 | 133.9998 | 37.3262 | 37.3262
Inerts | lb/hr |  | 851.7478 | 4473.4376 | 2355.9791 | 656.0795 | 656.0795
Ca(OH)2 | lb/hr |  | 5.3817 | 42.0143 | 22.0962 | 6.1374 | 6.1374
H2O | lb/hr |  | 19.0253 | 109.027 | 57.4209 | 15.9906 | 15.9906
TOTAL | lb/hr |  | 951.2648 | 5451.3488 | 2871.0437 | 799.5312 | 799.5312
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 520.7683 | 5535.2872 | 2915.642 | 812.1496 | 812.1496
CaSO4*2H2O | lb/hr |  | 231.4155 | 2459.7338 | 1295.6335 | 360.8976 | 360.8976
Inerts | lb/hr |  | 7665.7305 | 40260.9381 | 21203.8118 | 5904.7155 | 5904.7155
Ca(OH)2 | lb/hr |  | 8.0824 | 85.1556 | 44.5664 | 12.2674 | 12.2674
H2O | lb/hr
TOTAL | lb/hr |  | 8425.9967 | 48341.1147 | 25459.6537 | 7090.0302 | 7090.0302
CaSO3*1/2H2O | wt % |  | 6.18% | 11.45% | 11.45% | 11.45% | 11.45%
CaSO4*2H2O | wt % |  | 2.746% | 5.088% | 5.089% | 5.09% | 5.09%
Inerts | wt % |  | 90.98% | 83.29% | 83.28% | 83.28% | 83.28%
Ca(OH)2 | wt % |  | 0.09592% | 0.1762% | 0.175% | 0.173% | 0.173%
H2O | wt %
TOTAL | wt % |  | 100% | 100% | 100% | 100% | 100%
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 262.8607 | 1909.2003 | 1005.6469 | 280.1221 | 280.1221
CaSO4*2H2O | lb/hr |  | 116.8083 | 848.3976 | 446.8826 | 124.4788 | 124.4788
Inerts | lb/hr |  | 3869.3207 | 13886.5773 | 7313.5001 | 2036.6214 | 2036.6214
Ca(OH)2 | lb/hr |  | 4.0796 | 29.3714 | 15.3716 | 4.2312 | 4.2312
H2O | lb/hr |  | 86.7973 | 340.2765 | 179.2123 | 49.9072 | 49.9072
TOTAL | lb/hr |  | 4339.8667 | 17013.8231 | 8960.6135 | 2495.3607 | 2495.3607
Solids Out Stack
CaSO3*1/2H2O | lb/hr |  | 0.92151 | 6.0972 | 3.2116 | 0.8946 | 0.8946
CaSO4*2H2O | lb/hr |  | 0.4095 | 2.7094 | 1.4272 | 0.39753 | 0.39753
Inerts | lb/hr |  | 13.5647 | 44.3481 | 23.3563 | 6.5041 | 6.5041
Ca(OH)2 | lb/hr |  | 0.014302 | 0.0938 | 0.049091 | 0.013513 | 0.013513
H2O | lb/hr
TOTAL | lb/hr |  | 14.91 | 53.2485 | 28.0442 | 7.8098 | 7.8098
Composition of Baghouse/ESP Solids to Recycle
CaSO3*1/2H2O | lb/hr |  | 256.986 | 3619.9897 | 1906.7835 | 531.1329 | 531.1329
CaSO4*2H2O | lb/hr |  | 114.1977 | 1608.6268 | 847.3237 | 236.0213 | 236.0213
Inerts | lb/hr |  | 3782.8451 | 26330.0127 | 13866.9555 | 3861.59 | 3861.59
Ca(OH)2 | lb/hr |  | 3.9885 | 55.6904 | 29.1457 | 8.0227 | 8.0227
H2O | lb/hr |  | 84.8575 | 645.1902 | 339.8002 | 94.6279 | 94.6279
TOTAL | lb/hr |  | 4242.8748 | 32259.5098 | 16990.0085 | 4731.3948 | 4731.3948
Calculated Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 308.9878 | 4192.4664 | 2208.3313 | 615.1303 | 615.1303
CaSO4*2H2O | lb/hr |  | 137.3059 | 1863.0201 | 981.3234 | 273.3475 | 273.3475
Inerts | lb/hr |  | 4634.5929 | 30803.4502 | 16222.9345 | 4517.6695 | 4517.6695
Ca(OH)2 | lb/hr |  | 9.3702 | 97.7047 | 51.2419 | 14.1601 | 14.1601
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
TOTAL | lb/hr |  | 5194.1396 | 37710.8586 | 19861.0522 | 5530.9259 | 5530.9259
ITERATION 7
Assumed Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 308.9878 | 4192.4664 | 2208.3313 | 615.1303 | 615.1303
CaSO4*2H2O | lb/hr |  | 137.3059 | 1863.0201 | 981.3234 | 273.3475 | 273.3475
Inerts | lb/hr |  | 4634.5929 | 30803.4502 | 16222.9345 | 4517.6695 | 4517.6695
Ca(OH)2 | lb/hr |  | 9.3702 | 97.7047 | 51.2419 | 14.1601 | 14.1601
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
TOTAL | lb/hr |  | 5194.1396 | 37710.8586 | 19861.0522 | 5530.9259 | 5530.9259
Composition of Recycle Slurry to Head Tanks
CaSO3*1/2H2O | lb/hr |  | 308.9878 | 4192.4664 | 2208.3313 | 615.1303 | 615.1303
CaSO4*2H2O | lb/hr |  | 137.3059 | 1863.0201 | 981.3234 | 273.3475 | 273.3475
Inerts | lb/hr |  | 4634.5929 | 30803.4502 | 16222.9345 | 4517.6695 | 4517.6695
Ca(OH)2 | lb/hr |  | 9.3702 | 97.7047 | 51.2419 | 14.1601 | 14.1601
H2O | lb/hr |  | 9453.334 | 68633.7626 | 36147.115 | 10066.2852 | 10066.2852
TOTAL | lb/hr |  | 14543.5908 | 105590.404 | 55610.9461 | 15486.5926 | 15486.5926
Composition of Slurry from Head Tank
CaSO3*1/2H2O | lb/hr |  | 308.9878 | 4192.4664 | 2208.3313 | 615.1303 | 615.1303
CaSO4*2H2O | lb/hr |  | 137.3059 | 1863.0201 | 981.3234 | 273.3475 | 273.3475
Inerts | lb/hr |  | 4651.9067 | 30929.1531 | 16289.1381 | 4536.1059 | 4536.1059
Ca(OH)2 | lb/hr |  | 215.2523 | 1592.4647 | 838.4822 | 233.3916 | 233.3916
H2O | lb/hr |  | 9974.1246 | 72414.8426 | 38138.4838 | 10620.8436 | 10620.8436
TOTAL | lb/hr |  | 15287.5773 | 110991.9468 | 58455.7587 | 16278.8189 | 16278.8189
Solids in Spray Dryer
CaSO3*1/2H2O | lb/hr |  | 519.9977 | 5724.4556 | 3015.1789 | 839.8221 | 839.8221
CaSO4*2H2O | lb/hr |  | 231.0731 | 2543.7952 | 1339.865 | 373.1945 | 373.1945
Inerts | lb/hr |  | 8517.4833 | 44734.3947 | 23559.8986 | 6560.8747 | 6560.8747
Ca(OH)2 | lb/hr |  | 53.8407 | 420.5728 | 221.2858 | 61.5141 | 61.5141
H2O | lb/hr |  | NA | NA | NA | NA | NA
TOTAL | lb/hr |  | 9322.3948 | 53423.2184 | 28136.2284 | 7835.4054 | 7835.4054
Composition of Solids from Spray Dryers
CaSO3*1/2H2O | lb/hr |  | 51.9998 | 572.4456 | 301.5179 | 83.9822 | 83.9822
CaSO4*2H2O | lb/hr |  | 23.1073 | 254.3795 | 133.9865 | 37.3195 | 37.3195
Inerts | lb/hr |  | 851.7483 | 4473.4395 | 2355.9899 | 656.0875 | 656.0875
Ca(OH)2 | lb/hr |  | 5.3841 | 42.0573 | 22.1286 | 6.1514 | 6.1514
H2O | lb/hr |  | 19.0253 | 109.027 | 57.4209 | 15.9906 | 15.9906
TOTAL | lb/hr |  | 951.2648 | 5451.3488 | 2871.0437 | 799.5312 | 799.5312
Solids in Baghouse/ESP
CaSO3*1/2H2O | lb/hr |  | 520.7504 | 5535.0074 | 2915.373 | 812.0128 | 812.0128
CaSO4*2H2O | lb/hr |  | 231.4076 | 2459.6095 | 1295.5139 | 360.8368 | 360.8368
Inerts | lb/hr |  | 7665.7349 | 40260.9552 | 21203.9088 | 5904.7872 | 5904.7872
Ca(OH)2 | lb/hr |  | 8.1037 | 85.5426 | 44.8581 | 12.3933 | 12.3933
H2O | lb/hr
TOTAL | lb/hr |  | 8425.9967 | 48341.1147 | 25459.6537 | 7090.0302 | 7090.0302
CaSO3*1/2H2O | wt % |  | 6.18% | 11.45% | 11.45% | 11.45% | 11.45%
CaSO4*2H2O | wt % |  | 2.746% | 5.088% | 5.088% | 5.089% | 5.089%
Inerts | wt % |  | 90.98% | 83.29% | 83.28% | 83.28% | 83.28%
Ca(OH)2 | wt % |  | 0.09618% | 0.177% | 0.1762% | 0.1748% | 0.1748%
H2O | wt %
TOTAL | wt % |  | 100% | 100% | 100% | 100% | 100%
Dry Solids
CaSO3*1/2H2O | lb/hr |  | 262.8517 | 1909.1038 | 1005.5541 | 280.0749 | 280.0749
CaSO4*2H2O | lb/hr |  | 116.8043 | 848.3547 | 446.8414 | 124.4578 | 124.4578
Inerts | lb/hr |  | 3869.323 | 13886.5833 | 7313.5335 | 2036.6461 | 2036.6461
Ca(OH)2 | lb/hr |  | 4.0904 | 29.5049 | 15.4722 | 4.2746 | 4.2746
H2O | lb/hr |  | 86.7973 | 340.2765 | 179.2123 | 49.9072 | 49.9072
TOTAL | lb/hr |  | 4339.8667 | 17013.8231 | 8960.6135 | 2495.3607 | 2495.3607
Solids Out Stack
CaSO3*1/2H2O | lb/hr |  | 0.92148 | 6.0969 | 3.2113 | 0.89444 | 0.89444
CaSO4*2H2O | lb/hr |  | 0.40948 | 2.7093 | 1.427 | 0.39747 | 0.39747
Inerts | lb/hr |  | 13.5647 | 44.3481 | 23.3564 | 6.5042 | 6.5042
Ca(OH)2 | lb/hr |  | 0.01434 | 0.094227 | 0.049412 | 0.013651 | 0.013651
H2O | lb/hr
TOTAL | lb/hr |  | 14.91 | 53.2485 | 28.0442 | 7.8098 | 7.8098
Composition of Baghouse/ESP Solids to Recycle
CaSO3*1/2H2O | lb/hr |  | 256.9772 | 3619.8067 | 1906.6075 | 531.0435 | 531.0435
CaSO4*2H2O | lb/hr |  | 114.1938 | 1608.5454 | 847.2455 | 235.9815 | 235.9815
Inerts | lb/hr |  | 3782.8473 | 26330.0239 | 13867.0188 | 3861.6368 | 3861.6368
Ca(OH)2 | lb/hr |  | 3.999 | 55.9435 | 29.3365 | 8.105 | 8.105
H2O | lb/hr |  | 84.8575 | 645.1902 | 339.8002 | 94.6279 | 94.6279
TOTAL | lb/hr |  | 4242.8748 | 32259.5098 | 16990.0085 | 4731.3948 | 4731.3948
Calculated Composition of Recycle Solids to Slurry Tank
CaSO3*1/2H2O | lb/hr |  | 308.977 | 4192.2523 | 2208.1254 | 615.0257 | 615.0257
CaSO4*2H2O | lb/hr |  | 137.3011 | 1862.925 | 981.232 | 273.301 | 273.301
Inerts | lb/hr |  | 4634.5956 | 30803.4634 | 16223.0087 | 4517.7243 | 4517.7243
Ca(OH)2 | lb/hr |  | 9.3831 | 98.0008 | 51.4651 | 14.2565 | 14.2565
H2O | lb/hr |  | 103.8828 | 754.2172 | 397.221 | 110.6185 | 110.6185
TOTAL | lb/hr |  | 5194.1396 | 37710.8586 | 19861.0522 | 5530.9259 | 5530.9259

## FF ESP Cost & Tech. Results (hidden)
Fabric Filter - Preliminary |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Flue Gas, Upstream of Fabric Filter
Temperature | °F |  | 300 | 147 | 147 | 147 | 300
Pressure | in. H2O |  | -12 | -17 | -17 | -17 | -12
Flow Rate | SCFM |  | 205105.5902 | 763020.8395 | 404279.7748 | 116276.3848 | 107443.5927
Flow Rate | ACFM |  | 314500.1388 | 946637.4701 | 501567.406 | 144257.6363 | 164749.4093
CO2 | lb/hr |  | 167773.1629 | 599172.9887 | 315564.4407 | 87878.705 | 87878.705
N2 | lb/hr |  | 662514.4698 | 2366056.4549 | 1246123.0663 | 347021.6134 | 347021.6134
SO2 | lb/hr |  | 193.83 | 394.0323 | 207.5237 | 57.7914 | 206.3979
O2 | lb/hr |  | 52552.2095 | 187617.9134 | 98812.101 | 27517.294 | 27526.5724
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 149.9231 | 535.4247 | 281.9904 | 78.529 | 78.529
H2O | lb/hr |  | 59658.7384 | 299972.503 | 164882.0559 | 56429.1618 | 31248.935
Fly Ash | lb/hr |  | 3865.5765 | 48080.8966 | 25322.6055 | 7051.8648 | 2024.7688
Total (gas only) | lb/hr |  | 942842.3336 | 3453749.3171 | 1825871.178 | 518983.0945 | 493960.7527
Total Fabric Required | Ft2 |  | 89857.1825 | 270467.8486 | 143304.9731 | 41216.4675 | 47071.2598
Surface Area per Bag | Ft2 |  | 31.416 | 31.416 | 31.416 | 31.416 | 31.416
Required No. of Bags (no spare compartments) |  |  | 2860.2363 | 8609.2389 | 4561.5283 | 1311.9578 | 1498.3212
Final No. of Bags |  |  | 3146.2599 | 9470.1628 | 5017.6811 | 1443.1536 | 1648.1534
No. of Casings |  |  | 1 | 1 | 1 | 1 | 1
Fabric Filter Dimensions (per Casing) | Ft2 |  | 3088.8406 | 9297.3323 | 4926.1085 | 1416.8161 | 1618.0746
Length | Ft |  | 78.5982 | 136.3623 | 99.2583 | 53.2319 | 56.8872
Width | Ft |  | 39.2991 | 68.1811 | 49.6292 | 26.6159 | 28.4436
Capital Cost |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 2015 | 2015 | 2015 | 2015 | 2015
Fabric Filter | $ |  | 2771941.0443 | 6053260.12 | 3858901.997 | 1595393.8976 | 1752891.7338
Bags | $ |  | 247077.0985 | 743695.8226 | 394040.5872 | 113331.4546 | 129430.1687
Ash Handling System | $ |  | 393404.188 | 1176540.7431 | 773448.5652 | 449839.3519 | 360800.017
ID Fan(s) | $ |  | 398530.5498 | 788300.8995 | 532032.4946 | 246003.4751 | 267084.2575
Equipment Cost Subtotal | $ |  | 3810952.8807 | 8761797.5852 | 5558423.644 | 2404568.1792 | 2510206.177
Instruments & Controls | $ |  | 76219.0576 | 175235.9517 | 111168.4729 | 48091.3636 | 50204.1235
Taxes | $ |  | 228657.1728 | 525707.8551 | 333505.4186 | 144274.0908 | 150612.3706
Freight | $ |  | 190547.644 | 438089.8793 | 277921.1822 | 120228.409 | 125510.3088
Purchased Equipment Cost Subtotal | $ |  | 4306376.7552 | 9900831.2713 | 6281018.7177 | 2717162.0425 | 2836532.98
Installation | $ |  | 2885272.426 | 6633556.9518 | 4208282.5408 | 1820498.5685 | 1900477.0966
Total Direct Cost | $ |  | 7191649.1812 | 16534388.2231 | 10489301.2585 | 4537660.611 | 4737010.0766
Total Direct Cost with Retrofit Factor | $ |  | 11506638.6899 | 26455021.1569 | 16782882.0136 | 7260256.9776 | 7579216.1225
General Facilities | $ |  | 1150663.869 | 2645502.1157 | 1678288.2014 | 726025.6978 | 757921.6123
Engineering Fees | $ |  | 1150663.869 | 2645502.1157 | 1678288.2014 | 726025.6978 | 757921.6123
Contingency | $ |  | 2301327.738 | 5291004.2314 | 3356576.4027 | 1452051.3955 | 1515843.2245
Total Plant Cost (TPC) | $ |  | 16109294.1659 | 37037029.6196 | 23496034.819 | 10164359.7686 | 10610902.5716
Total Plant Cost (TPC) w/ Prime Contractor's Markup | $ |  | 16592572.9909 | 38148140.5082 | 24200915.8636 | 10469290.5617 | 10929229.6487
Total Cash Expended (TCE) | $ |  | 16350933.5784 | 37592585.0639 | 23848475.3413 | 10316825.1652 | 10770066.1101
Allow. for Funds During Constr. (AFDC) | $ |  | 869901.885 | 1999999.5995 | 1268785.8802 | 548875.4275 | 572988.7389
Total Plant Investment (TPI) | $ |  | 17220835.4633 | 39592584.6634 | 25117261.2216 | 10865700.5927 | 11343054.849
Preproduction Costs | $ |  | 344416.7093 | 791851.6933 | 502345.2244 | 217314.0119 | 226861.097
Inventory Capital | $ |  | 0 | 0 | 0 | 0 | 0
Total Capital Requirement (TCR) | $ |  | 17565252.1726 | 40384436.3567 | 25619606.446 | 11083014.6045 | 11569915.946
| $/kW |  | 117.1017 | 269.2296 | 324.2988 | 503.7734 | 525.9053
O&M Data and Costs |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 2015 | 2015 | 2015 | 2015 | 2015
Power Required Excluding ID Fan(s) | kW |  | 141.7431 | 409.3499 | 222.0473 | 67.0649 | 76.1796
ID Fan Power for FF Delta P | kW |  | 317.6108 | 956.0005 | 506.5283 | 145.6845 | 166.3789
Total Power | kW |  | 459.3539 | 1365.3504 | 728.5756 | 212.7494 | 242.5585
Power Cost ** | $/yr |  | 65389.0346 | 321243.5586 | 171421.3609 | 50056.2909 | 57069.8618
Maintenance Costs | $/yr |  | 503415.4427 | 1157407.1756 | 734251.0881 | 317636.2428 | 331590.7054
Periodic Replacement Items | $/yr |  | 247077.0985 | 743695.8226 | 394040.5872 | 113331.4546 | 129430.1687
First Year Cost. Bags Replaced Every |  |  | 5 Years | 5 Years | 5 Years | 5 Years | 5 Years
** These costs assume inputs are in current dollars (no escalation included).
ESP |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Flue Gas, Upstream of ESP
Temperature | °F |  | 300 | 147 | 147 | 147 | 300
Pressure | in. H2O |  | -12 | -17 | -17 | -17 | -12
Flow Rate | SCFM |  | 205105.5902 | 763020.8395 | 404279.7748 | 116276.3848 | 107443.5927
Flow Rate | ACFM |  | 314500.1388 | 946637.4701 | 501567.406 | 144257.6363 | 164749.4093
CO2 | lb/hr |  | 167773.1629 | 599172.9887 | 315564.4407 | 87878.705 | 87878.705
N2 | lb/hr |  | 662514.4698 | 2366056.4549 | 1246123.0663 | 347021.6134 | 347021.6134
SO2 | lb/hr |  | 193.83 | 394.0323 | 207.5237 | 57.7914 | 206.3979
O2 | lb/hr |  | 52552.2095 | 187617.9134 | 98812.101 | 27517.294 | 27526.5724
HCl | lb/hr |  | 0 | 0 | 0 | 0 | 0
Other Gases | lb/hr |  | 149.9231 | 535.4247 | 281.9904 | 78.529 | 78.529
H2O | lb/hr |  | 59658.7384 | 299972.503 | 164882.0559 | 56429.1618 | 31248.935
Fly Ash | lb/hr |  | 3865.5765 | 48080.8966 | 25322.6055 | 7051.8648 | 2024.7688
Total (gas only) | lb/hr |  | 942842.3336 | 3453749.3171 | 1825871.178 | 518983.0945 | 493960.7527
Inlet Particulate Loading | lb/hr |  | 3865.5765 | 48080.8966 | 25322.6055 | 7051.8648 | 2024.7688
| gr/ft3 |  | 1.434 | 5.9256 | 5.8901 | 5.7031 | 1.4338
Overall PM Collection Efficiency | % | h | 99.61% | 99.89% | 99.89% | 99.89% | 99.61%
ESP Requirements
k | dimensionless |  | 0.52718 | 0.49759 | 0.49598 | 0.48585 | 0.52144 | k = power factor in modified Deustch-Anderson equation
E | kV/cm |  | 10 | 10 | 10 | 10 | 10 | E = the strength of the electric field in the ESP
Ash Composition
Na2O | wt% in Ash |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3 | weight percent of Na2O in the flyash -- from coal library
Fe | wt% in Ash |  | 7 | 7 | 7 | 7 | 7 | weight percent of Fe2O3 in the flyash -- from coal library
MgO | wt% in Ash |  | 22.2 | 22.2 | 22.2 | 22.2 | 22.2 | weight percent of MgO in the flyash -- from coal library
CaO | wt% in Ash |  | 0 | 0 | 0 | 0 | 0 | weight percent of CaO in the flyash -- from coal library
Flue Gas Composition
H2O | Vol% |  | 10.2141 | 14.0232 | 14.58 | 17.5552 | 10.2141 | volume percent of H2O in flue gas on a wet basis -- from CUECost combustion calculations
SO2 | ppm |  | 93.3215 | 51.8004 | 51.6047 | 50.5594 | 189.7164 | volume percent of SO2 in flue gas on a wet basis -- from CUECost combustion calculations
SO3 | ppm |  | 0.69058 | 0.38332 | 0.38188 | 0.37414 | 1.4039 | volume percent of SO3 in flue gas: SO3 = 0.74%* SO2
Flue Gas Temperature
TF | °F |  | 300 | 147 | 147 | 147 | 300 | flue gas temperature in the ESP (degrees F)
TC | °C |  | 148.8889 | 63.8889 | 63.8889 | 63.8889 | 148.8889 | flue gas temperature in the ESP (degrees C)
TK | Kelvin |  | 422.0389 | 337.0389 | 337.0389 | 337.0389 | 422.0389 | flue gas temperature in the ESP (Kelvin); note: the temperature in Kelvin is used in resistivity calculations
Resistivity Calculations
Volume Resistivity
rv1 | Log10(ohm-cm) |  | 10.2863 | 10.2863 | 10.2863 | 10.2863 | 10.2863 | rv1 = 8.9434 - 1.8916 * Log10(Na2O) - 0.9696 * Log10(Fe) + 1.237 * (Log10(MgO + CaO) - Log10(2.5))
rv2 | Log10(ohm-cm) |  | 10.0463 | 10.0463 | 10.0463 | 10.0463 | 10.0463 | rv2 = rv1 + (E - 2.0) * (-0.03); note: 0.03 is a correction factor for the electric field
iv | Log10(ohm-cm) |  | 3.1111 | 3.1111 | 3.1111 | 3.1111 | 3.1111 | iv = rv2 - 4334.5 / 625
rv | Log10(ohm-cm) |  | 13.3814 | 15.9716 | 15.9716 | 15.9716 | 13.3814 | rv = iv + 4334.5 / TK
rv(TK=1000/2.4) | Log10(ohm-cm) |  | 13.5139 | 13.5139 | 13.5139 | 13.5139 | 13.5139 | rv = iv + 4334.5 / (1000/2.4)
Volume Resistivity | ohm-cm |  | 2.4068e+13 | 9366793523271820 | 9366793523271820 | 9366793523271820 | 2.4068e+13 | volume resistivity = 10^rv
Surface Resistivity
rs1 | Log10(ohm-cm) |  | 11.9415 | 11.9415 | 11.9415 | 11.9415 | 11.9415 | rs1 = 10.7737 - 2.2334 * Log10(Na2O)
rs2 | Log10(ohm-cm) |  | 11.7861 | 11.2985 | 11.2273 | 10.8464 | 11.7861 | rs2 = rs1 + (H2O - 9.0) * (-0.128)
rs3 | Log10(ohm-cm) |  | 11.1029 | 10.6153 | 10.5441 | 10.1632 | 11.1029 | rs3: if (MgO + CaO) > 10.0 then rs3 = rs2 + 0.56 - 0.056 * (MgO + CaO) else rs3 = rs2
rs4 | Log10(ohm-cm) |  | 10.8629 | 10.3753 | 10.3041 | 9.9232 | 10.8629 | rs4 = rs3 + (E - 2.0) * (-0.03)
rs4(with E=12) | Log10(ohm-cm) |  | 10.8029 | 10.3153 | 10.2441 | 9.8632 | 10.8029 | rs4(with E = 12.0) = rs3 + (12.0 - 2.0) * (-0.03)
rs0 | Log10(ohm-cm) |  | 12.1025 | 12.0996 | 12.0992 | 12.0969 | 12.1025 | rs0 = rs4(with E = 12.0) + Log10(Exp(1)) * 7.3895E-4 * Exp(2303.3 / 385) * H2O
rs | Log10(ohm-cm) |  | 11.3337 | 7.9195 | 7.7531 | 6.864 | 11.3337 | rs = rs0 - Log10(Exp(1)) * 7.3895E-4 * Exp(2303.3 / TK) * H2O
Surface Resistivity | ohm-cm |  | 215646558628.1513 | 83082452.6986 | 56635540.813 | 7310872.7098 | 215646558628.1513 | surface resistivity = 10^rs
rvs1 | ohm-cm |  | 213731538381.2948 | 83082451.9616 | 56635540.4706 | 7310872.7041 | 213731538381.2948 | rvs1 = 10^(rv + rs) / (10^rv + 10^rs); note: combined volume and surface resistivity
rs2(with H2O=10) | Log10(ohm-cm) |  | 11.8135 | 11.8135 | 11.8135 | 11.8135 | 11.8135 | rs2(with H2O = 10) = rs1 + (10 - 9.0) * (-0.128)
rs3(with H2O=10) | Log10(ohm-cm) |  | 11.1303 | 11.1303 | 11.1303 | 11.1303 | 11.1303 | rs3(with H2O = 10): if (MgO + CaO) > 10.0 then rs3 = rs2(with H2O=10) + 0.56 - 0.056 * (MgO + CaO) else rs3 = rs2(with H2O=10)
rs4(with H2O = 10) | Log10(ohm-cm) |  | 10.8903 | 10.8903 | 10.8903 | 10.8903 | 10.8903 | rs4(with H2O = 10) = rs3(with H2O = 10) + (E - 2.0) * (-0.03)
rs4(with H2O = 10, E = 12) | Log10(ohm-cm) |  | 10.8303 | 10.8303 | 10.8303 | 10.8303 | 10.8303 | rs4(with H2O = 10, with E = 12.0) = rs3(with H2O=10) + (12.0 - 2.0) * (-0.03)
rs0(with H2O = 10) | Log10(ohm-cm) |  | 12.1027 | 12.1027 | 12.1027 | 12.1027 | 12.1027 | rs0 = rs4(with H2O = 10, with E = 12.0) + Log10(Exp(1)) * 7.3895E-4 * Exp(2303.3 / 385) * 10
rs(with H2O = 10, TK = 1000/2.4) | Log10(ohm-cm) |  | 11.2951 | 11.2951 | 11.2951 | 11.2951 | 11.2951 | rs(with H2O = 10, T = 1000/2.4) = rs0 (with H2O = 10) - Log10(Exp(1)) * 7.3895E-4 * Exp(2303.3 / (1000/2.4)) * 10
rvs1(with H2O=10, TK = 1000/2.4) | ohm-cm |  | 196124667602.5675 | 196124667602.5675 | 196124667602.5675 | 196124667602.5675 | 196124667602.5675 | rvs1 = 10^(rv + rs) / (10^rv + 10^rs)
rvs2 | Log10(ohm-cm) |  | 11.5325 | 11.5325 | 11.5325 | 11.5325 | 11.5325 | rvs2 = Log10(rvs1(with H2O = 10 and TK = 1000/2.4)) + (-8) * (-0.03)
Acid Resistivity
ia1 | Log10(ohm-cm) |  | 0.2915 | 0.2915 | 0.2915 | 0.2915 | 0.2915 | ia1: if ((MgO + CaO) < 5 and Fe < 1) then ia1 = 2.6354 else ia1 = 0.2915
ra1 | Log10(ohm-cm) |  | 9.1358 | 9.1358 | 9.1358 | 9.1358 | 9.1358 | ra1 = ia1 + 0.7669 * rvs2
sa |  |  | -2.0502 | -2.0502 | -2.0502 | -2.0502 | -2.0502 | sa: if ((MgO + CaO) < 5 and Fe < 1) then sa = -5.0 else sa = -2.0502
ia2 | Log10(ohm-cm) |  | 10.3701 | 10.3701 | 10.3701 | 10.3701 | 10.3701 | ia2 = ra1 - sa*Log10(4)
ra2 | Log10(ohm-cm) |  | 10.6998 | 11.2239 | 11.2273 | 11.2455 | 10.0681 | ra2 = ia2 + sa*Log10(SO3)
acid_v | index value |  | 1 | 1 | 1 | 1 | 1 | acid_v: if SO3 < 2.75 then acid_v = 1, else if SO3 > 6.5 then acid_v = 3, else acid_v = 2
atom_v | index value |  | 3 | 3 | 3 | 3 | 3 | atom_v: if (Na2O > 1 and (MgO + CaO) > 5) then atom_v = 1, else if (Fe < 1 and (MgO + CaO) < 3 then atom_v = 2, else atom_v = 3
sa1 |  |  | -4.85 | -4.85 | -4.85 | -4.85 | -4.85 | sa1 = Lookup (acid_v, atom_v); note: the lookup table is located below
ia3 | Log10(ohm-cm) |  | 22.3398 | 22.8639 | 22.8673 | 22.8855 | 21.7081 | ia3 = ra2 - sa1 * 2.4
ra3 | Log10(ohm-cm) |  | 10.848 | 8.4739 | 8.4773 | 8.4955 | 10.2162 | ra3 = ia3 + sa1 * 1000 / TK
ra | Log10(ohm-cm) |  | 10.1944 | 8.3902 | 8.3927 | 8.4066 | 9.7143 | ra = 1.95 + 0.76 * ra3
Acid Resistivity | ohm-cm |  | 15647529931.6813 | 245558056.1065 | 247010259.6922 | 255013428.6074 | 5180160488.7314 | acid resistivity = 10^ra
Total Resistivity
rvsa | ohm-cm |  | 14580103881.1544 | 62078669.2431 | 46071967.9045 | 7107121.6241 | 5057581097.9198 | rvsa = 10^(rv + rs + ra)/(10^rv * 10^rs + 10^rv * 10^ra + 10^rs * 10_ra)
Migration Velocity
wk | 1000ft/minute |  | 0.045589 | 0.063687 | 0.064675 | 0.070872 | 0.049099 | wk = 0.1232972 - 0.003323934*ln(rvsa)
Specific Collection Area
SCA | ft2/1000acfm |  | 567.7438 | 740.8945 | 738.7892 | 730.7964 | 546.3716 | SCA = (-ln(1 - h))^(1/k) / wk
Total Collector Plate Area | ft2 |  | 178555.4926 | 701358.5381 | 370552.5968 | 105422.9677 | 90014.3932
ESP Footprint Area | ft2 |  | 4959.8748 | 19482.1816 | 10293.1277 | 2928.4158 | 2500.3998
Capital Cost |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 2015 | 2015 | 2015 | 2015 | 2015
ESP | $ |  | 2445092.4999 | 6572184.3697 | 3716940.4147 | 1214997.4551 | 1368787.9317
Ash Handling System | $ |  | 393404.188 | 1176540.7431 | 773448.5652 | 449839.3519 | 360800.017
ID Fan(s) | $ |  | 398530.5498 | 788300.8995 | 532032.4946 | 246003.4751 | 267084.2575
Equipment Cost Subtotal | $ |  | 3237027.2377 | 8537026.0123 | 5022421.4744 | 1910840.2821 | 1996672.2062
Instruments & Controls | $ |  | 64740.5448 | 170740.5202 | 100448.4295 | 38216.8056 | 39933.4441
Taxes | $ |  | 194221.6343 | 512221.5607 | 301345.2885 | 114650.4169 | 119800.3324
Freight | $ |  | 161851.3619 | 426851.3006 | 251121.0737 | 95542.0141 | 99833.6103
Purchased Equipment Cost Subtotal | $ |  | 3657840.7786 | 9646839.3939 | 5675336.2661 | 2159249.5188 | 2256239.5931
Installation | $ |  | 2962851.0307 | 7813939.9091 | 4597022.3756 | 1748992.1102 | 1827554.0704
Total Direct Cost | $ |  | 6620691.8093 | 17460779.303 | 10272358.6417 | 3908241.6291 | 4083793.6634
Total Direct Cost with Retrofit Factor | $ |  | 10593106.8949 | 27937246.8848 | 16435773.8267 | 6253186.6065 | 6534069.8615
General Facilities | $ |  | 1059310.6895 | 2793724.6885 | 1643577.3827 | 625318.6607 | 653406.9862
Engineering Fees | $ |  | 1059310.6895 | 2793724.6885 | 1643577.3827 | 625318.6607 | 653406.9862
Contingency | $ |  | 2118621.379 | 5587449.377 | 3287154.7653 | 1250637.3213 | 1306813.9723
Total Plant Cost (TPC) | $ |  | 14830349.6529 | 39112145.6387 | 23010083.3573 | 8754461.2491 | 9147697.8061
Total Plant Cost (TPC) w/ Prime Contractor's Markup | $ |  | 15275260.1425 | 40285510.0079 | 23700385.8581 | 9017095.0866 | 9422128.7403
Total Cash Expended (TCE) | $ |  | 15052804.8977 | 39698827.8233 | 23355234.6077 | 8885778.1679 | 9284913.2732
Allow. for Funds During Constr. (AFDC) | $ |  | 800838.8813 | 2112055.8645 | 1242544.5013 | 472740.9075 | 493975.6815
Total Plant Investment (TPI) | $ |  | 15853643.7789 | 41810883.6878 | 24597779.109 | 9358519.0753 | 9778888.9547
Preproduction Costs | $ |  | 317072.8756 | 836217.6738 | 491955.5822 | 187170.3815 | 195577.7791
Inventory Capital | $ |  | 0 | 0 | 0 | 0 | 0
Total Capital Requirement (TCR) | $ |  | 16170716.6545 | 42647101.3616 | 25089734.6912 | 9545689.4568 | 9974466.7338
| $/kW |  | 107.8048 | 284.314 | 317.5916 | 433.895 | 453.3849
O&M Data and Costs |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
Cost Basis (Year) |  |  | 2015 | 2015 | 2015 | 2015 | 2015
Power Required Excluding ID Fan(s) | kW |  | 76.4412 | 216.3424 | 114.8404 | 33.2546 | 39.8653
ID Fan Power for FF Delta P | kW |  | 158.8054 | 478.0003 | 253.2642 | 72.8422 | 83.1895
Total Power | kW |  | 235.2466 | 694.3426 | 368.1046 | 106.0968 | 123.0548
Power Cost ** | $/yr |  | 33487.358 | 163366.9198 | 86608.6999 | 24962.763 | 28952.6824
Maintenance Costs | $/yr |  | 463448.4267 | 1222254.5512 | 719065.1049 | 273576.914 | 285865.5564
** These costs assume inputs are in current dollars (no escalation included).
Note on D130: ERG - Morrisville: The sum of MgO wt% and CaO wt% is used in resistivity calculations. IAPCS calls this quantity "Alkalinity Content"
Note on E130: ERG - Morrisville: The sum of MgO wt% and CaO wt% is used in resistivity calculations. IAPCS calls this quantity "Alkalinity Content"
Note on F130: ERG - Morrisville: The sum of MgO wt% and CaO wt% is used in resistivity calculations. IAPCS calls this quantity "Alkalinity Content"
Note on G130: ERG - Morrisville: The sum of MgO wt% and CaO wt% is used in resistivity calculations. IAPCS calls this quantity "Alkalinity Content"
Note on H130: ERG - Morrisville: The sum of MgO wt% and CaO wt% is used in resistivity calculations. IAPCS calls this quantity "Alkalinity Content"
Note on D131: ERG - Morrisville: The sum of MgO wt% and CaO wt% is used in resistivity calculations. IAPCS calls this quantity "Alkalinity Content"
Note on E131: ERG - Morrisville: The sum of MgO wt% and CaO wt% is used in resistivity calculations. IAPCS calls this quantity "Alkalinity Content"
Note on F131: ERG - Morrisville: The sum of MgO wt% and CaO wt% is used in resistivity calculations. IAPCS calls this quantity "Alkalinity Content"
Note on G131: ERG - Morrisville: The sum of MgO wt% and CaO wt% is used in resistivity calculations. IAPCS calls this quantity "Alkalinity Content"
Note on H131: ERG - Morrisville: The sum of MgO wt% and CaO wt% is used in resistivity calculations. IAPCS calls this quantity "Alkalinity Content"
Note on D191: ERG - Morrisville: This "effective migration velocity" is calculated based on an empirical log-linear relationship with total resistivity.
Note on E191: ERG - Morrisville: This "effective migration velocity" is calculated based on an empirical log-linear relationship with total resistivity.
Note on F191: ERG - Morrisville: This "effective migration velocity" is calculated based on an empirical log-linear relationship with total resistivity.
Note on G191: ERG - Morrisville: This "effective migration velocity" is calculated based on an empirical log-linear relationship with total resistivity.
Note on H191: ERG - Morrisville: This "effective migration velocity" is calculated based on an empirical log-linear relationship with total resistivity.
Note on D194: ERG - Morrisville: SCA is calculated using a modified Deutsch-Anderson equation, and represents the performance of an ESP.
Note on E194: ERG - Morrisville: SCA is calculated using a modified Deutsch-Anderson equation, and represents the performance of an ESP.
Note on F194: ERG - Morrisville: SCA is calculated using a modified Deutsch-Anderson equation, and represents the performance of an ESP.
Note on G194: ERG - Morrisville: SCA is calculated using a modified Deutsch-Anderson equation, and represents the performance of an ESP.
Note on H194: ERG - Morrisville: SCA is calculated using a modified Deutsch-Anderson equation, and represents the performance of an ESP.

## Constants_CC
PRELIMINARY VERSION
|  |  | Coal 1, Wyoming PRB: 8,227 Btu, 0.37% S, 5.32% ash | Coal 2, Armstrong, PA: 13,100 Btu, 2.6% S, 9.1% ash | Coal 3, Jefferson, OH: 11,922 Btu, 3.43% S, 13% ash | Coal 4, Logan, WV: 12,058 Btu, 0.89% S, 16.6% ash | Coal 5, No. 6 Illinois: 10,100 Btu, 4% S, 16% ash | Coal 6, Rosebud, MT: 8,789 Btu, 0.56% S, 8.15% ash | Coal 7, Lignite, ND: 7,500 Btu, 0.94% S, 5.9% ash | Coal 8, "User Specified": 7,560 Btu, 0.3% S, 7% ash
COAL ANALYSIS LIBRARY
| Index Number |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8
1 | Coal Name |  | Wyoming PRB | Armstrong, PA | Jefferson, OH | Logan, WV | No. 6 Illinois | Rosebud, MT | Lignite, ND | "User Specified" |  |  |  |  | 1
2 | Coal Cost | $/MMBtu | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
3 | PROXIMATE ANALYSIS (ASTM, as rec'd) | [11 empty] | SCA |  | 567.7438
4 | Moisture - Enter below in Ultimate Analysis | [11 empty] | Total Collection Plate Area |  | 178555.4926
5 | Volatile Matter | wt% | 31.39 | 36.2 | 37.2 | 35.4 | 33 | 36.4 | 42 | 36
6 | Fixed Carbon | wt% | 33.05 | 48.7 | 44.8 | 43 | 39 | 30.3 | 20.1 | 26.5
7 | Ash - Enter below in Ultimate Analysis | [13 empty] | Current | Previous | Raytheon
8 |  |  | 100 | 100 | 100 | 100 | 100 | 100.05 | 100 | 98.5 |  |  |  |  | SCA | SCA | SCA
9
10 | COAL ULTIMATE ANALYSIS (ASTM, as rec'd) | [10 empty] | Coal 1, Wyoming PRB: 8,227 Btu, 0.37% S, 5.32% ash |  | 1 | 0 | 477 | 619
11 | Moisture | wt% | 30.24 | 6 | 5 | 5 | 12 | 25.2 | 32 | 29 | http://www.usibelli.com/Coal-data.php | Coal 2, Armstrong, PA: 13,100 Btu, 2.6% S, 9.1% ash |  | 2 | 0 | 483 | 301
12 | Carbon | wt% | 48.18 | 71.55 | 65.72 | 65.99 | 55.35 | 51.52 | 45.06 | 70 |  | Coal 3, Jefferson, OH: 11,922 Btu, 3.43% S, 13% ash |  | 3 | 0 | 523 | 348
13 | Hydrogen | wt% | 3.31 | 4.88 | 4.53 | 4.75 | 4 | 3.29 | 2.8 | 5 |  | Coal 4, Logan, WV: 12,058 Btu, 0.89% S, 16.6% ash |  | 4 | 0 | 544 | 624
14 | Nitrogen | wt% | 0.7 | 1.4 | 1.21 | 0.7 | 1.08 | 0.69 | 1.5 | 0.8 |  | Coal 5, No. 6 Illinois: 10,100 Btu, 4% S, 16% ash |  | 5 | 0 | 556 | 327
15 | Chlorine | wt% | 0.01 | 0 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0 |  | Coal 6, Rosebud, MT: 8,789 Btu, 0.56% S, 8.15% ash |  | 6 | 0 | 508 | 530
16 | Sulfur | wt% | 0.37 | 2.6 | 3.43 | 0.89 | 4 | 0.56 | 0.94 | 0.3 |  | Coal 7, Lignite, ND: 7,500 Btu, 0.94% S, 5.9% ash |  | 7 | 0 | 494 | 411
17 | Ash | wt% | 5.32 | 9.1 | 13 | 16.6 | 16 | 8.15 | 5.9 | 7
18 | Oxygen | wt% | 11.87 | 4.47 | 7.01 | 5.97 | 7.47 | 10.49 | 11.7 | 0
19 | TOTAL | wt% | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 112.1
20
21 | Modified Mott Spooner HHV (Btu/lb) - calc | Btu/lb | 8227 | 13100 | 11922 | 12058 | 10100 | 8789 | 7500 | 7560
22
23 | COAL ASH ANALYSIS (ASTM, as rec'd)
24 | SiO2 | wt% | 35.51 | 46.92 | 51.35 | 50.68 | 50.82 | 27 | 29.8 | 44.4
25 | Al2O3 | wt% | 17.11 | 21 | 30 | 29 | 19.06 | 19 | 10 | 18
26 | TiO2 | wt% | 1.26 | 2.4 | 1.8 | 1.7 | 0.83 | 1.08 | 0.4 | 0.8
27 | Fe2O3 | wt% | 6.07 | 20.2 | 9 | 9 | 20 | 9 | 9 | 7
28 | CaO | wt% | 26.67 | 3.25 | 4.5 | 5.5 | 3.43 | 18.5 | 21.4 | 19.1
29 | MgO | wt% | 5.3 | 2.65 | 2 | 1 | 3.07 | 2.4 | 10.5 | 3.1
30 | Na2O | wt% | 1.68 | 0.9 | 0.4 | 0.4 | 0.6 | 2.8 | 4.4 | 0.3
31 | K2O | wt% | 2.87 | 0.3 | 0.2 | 0.9 | 0.37 | 0.45 | 0.49 | 1.2
32 | P2O5 | wt% | 0.97 | 0 | 0.16 | 0.6 | 0.17 | 0.42 | 0 | 0.07
33 | SO3 | wt% | 1.56 | 1.38 | 0.59 | 1.22 | 1.22 | 18.85 | 14.01 | 5.1
34 | Other Unaccounted for | wt% | 1 | 1 | 0 | 0 | 0.43 | 0.5 | 0 | 0.93
35 | TOTAL | wt% | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100
36
LIMESTONE ANALYSIS
| CaCO3 = | wt% | 1: 95.3
| CaO = | wt%
| Ca(OH)2 = | wt%
| CaSO4 = | wt% | 1: 0
| MgCO3 = | wt% | 1: 1.32
| MgO = | wt%
| Mg(OH)2 = | wt%
| SiO2 = | wt% | 1: 0.77
| Al2O3 = | wt% | 1: 0.25
| Fe2O3 = | wt% | 1: 0.09
| Na2O = | wt% | 1: 0.03
| K2O = | wt% | 1: 0.06
| TiO2 = | wt%
| P2O5 = | wt%
| SO3 = | wt%
| CO2 = | wt%
| H2O = | wt%
| Unknown = | wt% | 1: 2.18
| TOTAL = | wt% | 1: 100
LIME ANALYSIS
| CaCO3 = | wt% | 1: 0
| CaO = | wt% | 1: 90
| Ca(OH)2 = | wt%
| CaSO4 = | wt% | 1: 0
| MgCO3 = | wt% | 1: 0
| MgO = | wt% | 1: 5
| Mg(OH)2 = | wt%
| SiO2 = | wt% | 1: 1.26
| Al2O3 = | wt% | 1: 3
| Fe2O3 = | wt% | 1: 0.2
| Na2O = | wt% | 1: 0.1
| K2O = | wt% | 1: 0.02
| TiO2 = | wt%
| P2O5 = | wt%
| SO3 = | wt%
| CO2 = | wt%
| H2O = | wt%
| Unknown = | wt% | 1: 0.42
| TOTAL = | wt% | 1: 100
| Recycle Rate Lookup Table | % S | 1: lb recyle/lb lime
|  | 0 | 1: 30
|  | 0.4801 | 1: 28.5
|  | 0.5001 | 1: 23.5
|  | 0.5501 | 1: 19.5
|  | 0.6001 | 1: 16.5
|  | 0.6501 | 1: 14.5
|  | 0.7001 | 1: 12.5
|  | 0.7501 | 1: 11.25
|  | 0.8001 | 1: 10
|  | 0.8501 | 1: 9
|  | 0.9001 | 1: 8.25
|  | 0.9501 | 1: 7.5
|  | 1.0001 | 1: 5.5
|  | 1.2001 | 1: 4.25
|  | 1.4001 | 1: 3.3
|  | 1.6001 | 1: 2.75
|  | 1.8001 | 1: 2.25
|  | 2.0001 | 1: 1.85
|  | 2.2001 | 1: 1.6
|  | 2.4001 | 1: 1.4
|  | 2.6001 | 1: 1.2
2.8001 | bar: 1
|  | 3.0001 | 1: 0.66
|  | 3.5001 | 1: 0.49
|  | 4.0001 | 1: 0.34
|  | 4.5001 | 1: 0.3
MOLECULAR WEIGHTS
|  | Variable | 1: Molecular
| Description | Name | 1: Weight
| Air | Air_MolWt | 1: 28.8555
| H2O | H2O_MolWt | 1: 18.0153
| C | C_MolWt | 1: 12.0112
| H2 | H2_MolWt | 1: 2.0159
| N2 | N2_MolWt | 1: 28.02
| Cl2 | Cl2_MolWt | 1: 70.906
| S | S_MolWt | 1: 32.064
| Ash | Ash_MolWt | bar: 1
| O2 | O2_MolWt | 1: 31.9988
| Ca | Ca_MolWt | 1: 40.08
| Mg | Mg_MolWt | 1: 24.312
| CO2 | CO2_MolWt | 1: 44.01
| NO2 | NO2_MolWt | 1: 46.0088
| NO | NO_MolWt | 1: 30.0094
| HCl | HCl_MolWt | 1: 36.461
| SO2 | SO2_MolWt | 1: 64.0628
| SO3 | SO3_MolWt | 1: 80.0622
| CaCO3 | CaCO3_MolWt | 1: 100.0894
| CaSO4 | CaSO4_MolWt | 1: 136.1416
| CaO | CaO_MolWt | 1: 56.0794
| Ca(OH)2 | Ca_OH_2_MolWt | 1: 74.0947
| CaSO3*½H2O | CaSO3halfH2O_MolWt | 1: 129.1499
| CaSO4*2 H2O (gypsum) | CaSO4_2H2O_MolWt | 1: 172.1723
| Na | Na_MolWt | 1: 22.99
| Na2CO3 | Na2CO3_MolWt | 1: 105.9894
| H2SO4 | H2SO4_MolWt | 1: 98.0775
| CH4 | CH4_MolWt | 1: 16.043
| CaCl2 | CaCl2_MolWt | 1: 110.99
WATER SATURATION PRESSURES
|  | Pressure | 1: Pressure
| Temperature, °F | " HgA | 1: psia
| 120 | 3.4456 | 1: 1.6924
| 121 | 3.5425 | 1: 1.74
| 122 | 3.6419 | 1: 1.7888
| 123 | 3.7435 | 1: 1.8387
| 124 | 3.8473 | 1: 1.8897
| 125 | 3.9538 | 1: 1.942
| 126 | 4.0627 | 1: 1.9955
| 127 | 4.1743 | 1: 2.0503
| 128 | 4.2885 | 1: 2.1064
| 129 | 4.4053 | 1: 2.1638
| 130 | 4.5259 | 1: 2.223
| 131 | 4.648 | 1: 2.283
| 132 | 4.7732 | 1: 2.3445
| 133 | 4.9013 | 1: 2.4074
| 134 | 5.0322 | 1: 2.4717
| 135 | 5.1662 | 1: 2.5375
| 136 | 5.303 | 1: 2.6047
| 137 | 5.4431 | 1: 2.6735
| 138 | 5.5862 | 1: 2.7438
| 139 | 5.7326 | 1: 2.8157
| 140 | 5.8822 | 1: 2.8892
| 141 | 6.0351 | 1: 2.9643
| 142 | 6.1915 | 1: 3.0411
| 143 | 6.3511 | 1: 3.1195
| 144 | 6.5144 | 1: 3.1997
| 145 | 6.6811 | 1: 3.2816
SATURATION (ASME)
|  | Saturation | 1: Water; 2: Steam
|  | Temperature | 1: Enthalpy; 2: Enthalpy
| Pressure (psia) | (°F) | 1: (Btu/lb); 3: Index
| 300 | 417.35 | 1: 393.99; 2: 1202.9; 3: 0
| 400 | 444.6 | 1: 424.18; 2: 1204.6; 3: 1
| 500 | 467.01 | 1: 449.52; 2: 1204.7; 3: 2
| 600 | 486.2 | 1: 471.7; 2: 1203.7; 3: 3
| 1500 | 596.2 | 1: 611.68; 2: 1170.1; 3: 4
| 1600 | 604.87 | 1: 624.2; 2: 1164.5; 3: 5
| 1700 | 613.13 | 1: 636.45; 2: 1158.6; 3: 6
| 1800 | 621.02 | 1: 648.49; 2: 1152.3; 3: 7
| 1900 | 628.56 | 1: 660.36; 2: 1145.6; 3: 8
| 2400 | 662.11 | 1: 718.95; 2: 1103.7; 3: 9
| 2500 | 668.11 | 1: 731.71; 2: 1093.3; 3: 10
| 2600 | 673.91 | 1: 744.5; 2: 1082; 3: 11
| 2700 | 679.53 | 1: 757.3; 2: 1069.7; 3: 12
| 2800 | 684.96 | 1: 770.7; 2: 1055.8; 3: 13
| 2900 | 690.22 | 1: 785.1; 2: 1039.8; 3: 14
| 3000 | 695.33 | 1: 801.84; 2: 1020.3; 3: 15
| 3100 | 700.28 | 1: 824; 2: 993.3; 3: 16
| 3200 | 705.08 | 1: 875.5; 2: 931.6; 3: 17
| 3208.2 | 705.47 | 1: 906; 2: 906; 3: 18
| 3300 | 730 | 1: 1104.1; 2: 1104.1; 3: 19
| 3400 | 730 | 1: 1079.3; 2: 1079.3; 3: 20
| 3500 | 730 | 1: 1048.6; 2: 1048.6; 3: 21
| 4000 | 770 | 1: 1099.9; 2: 1099.9; 3: 22
Heat Capacity Results; Used in Efficiency Calculations
|  | Case 1 | 1: Case 2; 2: Case 3; 3: Case 4; 4: Case 5
| O2 - Based on °K | 7.2514 | 1: 7.2514; 2: 7.2514; 3: 7.2514; 4: 7.2514
| CO2 - Based on °K | 9.6671 | 1: 9.6671; 2: 9.6671; 3: 9.6671; 4: 9.6671
| N2 - Based on °K | 7.036 | 1: 7.036; 2: 7.036; 3: 7.036; 4: 7.036
| H2O - Based on °C | 8.1566 | 1: 8.1566; 2: 8.1566; 3: 8.1566; 4: 8.1566
| NO - Based on °C | 7.2156 | 1: 7.2156; 2: 7.2156; 3: 7.2156; 4: 7.2156
| SO2 - Based on °C | 10.0536 | 1: 10.0536; 2: 10.0536; 3: 10.0536; 4: 10.0536
| HCl - Based on °C | 6.9536 | 1: 6.9536; 2: 6.9536; 3: 6.9536; 4: 6.9536
| STACK OUTLET TEMP, °C | 148.8889 | 1: 148.8889; 2: 148.8889; 3: 148.8889; 4: 148.8889
| STACK OUTLET TEMP, °K | 421.8889 | 1: 421.8889; 2: 421.8889; 3: 421.8889; 4: 421.8889
| REFERENCE TEMP, °C | 26.6667 | 1: 26.6667; 2: 26.6667; 3: 26.6667; 4: 26.6667
| REFERENCE TEMP, °K | 299.6667 | 1: 299.6667; 2: 299.6667; 3: 299.6667; 4: 299.6667
ESP Section Lookup Table
| Efficiency | No. of Sections
| 0 | 2
| 0.965 | 3
| 0.99 | 4
| 0.998 | 5
| 0.999 | 6
ESP SCA Ratio Lookup Table
| No. of Sections | SCA Ratio (Avg.)
| 2 | 2.6
| 3 | 2.65
| 4 | 2.89
| 5 | 2.96
| 6 | 3.09
Lookup Table for Acid Resistivity Calculations
Atom_v
| Acid_v | 1 | 1: 2; 2: 3
| 1 | -4.74 | 1: -4.85; 2: -4.85
| 2 | -28.39 | 1: -28.39; 2: -28.39
| 3 | -8.67 | 1: -9.71; 2: -10.59
CONSTANTS
Variable
| Description | Name | 1: Value
| Degree Kelvin Conversion | degK | 1: 460
| " H2O / " Hg Conversion | inH2O_inHg | 1: 13.615
| Standard Atmospheric Pressure, " Hg | SAPress_inHg | 1: 29.92
| Standard Atmospheric Temperature, deg. F | SATemp_degF | 1: 70
| cubic feet per mole @ 60 deg F | cubft_60 | 1: 379.63
| cubic feet per mole @ 69 deg F | cubft_69 | 1: 386
| cubic feet per mole @ 70 deg F | cubft_70 | 1: 386.704
| kW per Horsepower | kW_Hp | 1: 0.746
Chemical Engineering Cost Index
| Year | Index
| 1979 | 238.7
| 1980 | 261.2
| 1981 | 297
| 1982 | 314
| 1983 | 317
| 1984 | 322.7
| 1985 | 325.3
| 1986 | 318.4
| 1987 | 323.8
| 1988 | 342.5
| 1989 | 355.4
| 1990 | 357.6
| 1991 | 361.3
| 1992 | 358.2
| 1993 | 359.2
| 1994 | 368.1
| 1995 | 381.1
| 1996 | 381.7
| 1997 | 386.5
| FUEL AND COMBUSTION CALCULATIONS |  |  | Case1 | Case 2 | Case 3 | Case 4 | Case 5
FUEL ANALYSIS FOR SPECIFIED COALS
PROXIMATE ANALYSIS (wt. %)
| Moisture | wt% |  | 29 | 29 | 29 | 29 | 29
| Volatile Matter | wt% |  | 36 | 36 | 36 | 36 | 36
| Fixed Carbon | wt% |  | 26.5 | 26.5 | 26.5 | 26.5 | 26.5
| Ash | wt% |  | 7 | 7 | 7 | 7 | 7
| TOTAL |  |  | 98.5 | 98.5 | 98.5 | 98.5 | 98.5
COAL ULTIMATE ANALYSIS (wt. %)
| Moisture | wt% |  | 29 | 29 | 29 | 29 | 29
| Carbon | wt% |  | 70 | 70 | 70 | 70 | 70
| Hydrogen | wt% |  | 5 | 5 | 5 | 5 | 5
| Nitrogen | wt% |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| Chlorine | wt% |  | 0 | 0 | 0 | 0 | 0
| Sulfur | wt% |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| Ash | wt% |  | 7 | 7 | 7 | 7 | 7
| Oxygen | wt% |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  |  | 112.1 | 112.1 | 112.1 | 112.1 | 112.1
HIGHER HEATING VALUE (HHV)
| Modified Mott Spooner - calc | Btu/lb |  | 7560 | 7560 | 7560 | 7560 | 7560
| COAL COST | $/MMBtu |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
COAL ASH ANALYSIS (ASTM, as rec'd)
| SiO2 | wt% |  | 44.4 | 44.4 | 44.4 | 44.4 | 44.4
| Al2O3 | wt% |  | 18 | 18 | 18 | 18 | 18
| TiO2 | wt% |  | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
| Fe2O3 | wt% |  | 7 | 7 | 7 | 7 | 7
| CaO | wt% |  | 19.1 | 19.1 | 19.1 | 19.1 | 19.1
| MgO | wt% |  | 3.1 | 3.1 | 3.1 | 3.1 | 3.1
| Na2O | wt% |  | 0.3 | 0.3 | 0.3 | 0.3 | 0.3
| K2O | wt% |  | 1.2 | 1.2 | 1.2 | 1.2 | 1.2
| P2O5 | wt% |  | 0.07 | 0.07 | 0.07 | 0.07 | 0.07
| SO3 | wt% |  | 5.1 | 5.1 | 5.1 | 5.1 | 5.1
| Other Unaccounted for | wt% |  | 0.93 | 0.93 | 0.93 | 0.93 | 0.93
| TOTAL | wt% |  | 100 | 100 | 100 | 100 | 100
PROXIMATE ANALYSIS (lbs/MMBtu)
| Moisture | lbs/MMBtu |  | 38.3598 | 38.3598 | 38.3598 | 38.3598 | 38.3598
| Volatile Matter | lbs/MMBtu |  | 47.619 | 47.619 | 47.619 | 47.619 | 47.619
| Fixed Carbon | lbs/MMBtu |  | 35.0529 | 35.0529 | 35.0529 | 35.0529 | 35.0529
| Ash | lbs/MMBtu |  | 9.2593 | 9.2593 | 9.2593 | 9.2593 | 9.2593
| TOTAL | lbs/MMBtu |  | 130.291 | 130.291 | 130.291 | 130.291 | 130.291
COAL ULTIMATE ANALYSIS (lbs/MMBtu)
| Moisture | lbs/MMBtu |  | 38.3598 | 38.3598 | 38.3598 | 38.3598 | 38.3598
| Carbon | lbs/MMBtu |  | 92.5926 | 92.5926 | 92.5926 | 92.5926 | 92.5926
| Hydrogen | lbs/MMBtu |  | 6.6138 | 6.6138 | 6.6138 | 6.6138 | 6.6138
| Nitrogen | lbs/MMBtu |  | 1.0582 | 1.0582 | 1.0582 | 1.0582 | 1.0582
| Chlorine | lbs/MMBtu |  | 0 | 0 | 0 | 0 | 0
| Sulfur | lbs/MMBtu |  | 0.39683 | 0.39683 | 0.39683 | 0.39683 | 0.39683
| Ash | lbs/MMBtu |  | 9.2593 | 9.2593 | 9.2593 | 9.2593 | 9.2593
| Oxygen | lbs/MMBtu |  | 0 | 0 | 0 | 0 | 0
| TOTAL | lbs/MMBtu |  | 148.2804 | 148.2804 | 148.2804 | 148.2804 | 148.2804
COAL ULTIMATE ANALYSIS (lbmoles/MMBtu)
| Moisture | lbmoles/MMBtu |  | 2.1293 | 2.1293 | 2.1293 | 2.1293 | 2.1293
| Carbon | lbmoles/MMBtu |  | 7.7089 | 7.7089 | 7.7089 | 7.7089 | 7.7089
| Hydrogen | lbmoles/MMBtu |  | 3.2807 | 3.2807 | 3.2807 | 3.2807 | 3.2807
| Nitrogen | lbmoles/MMBtu |  | 0.037766 | 0.037766 | 0.037766 | 0.037766 | 0.037766
| Chlorine | lbmoles/MMBtu |  | 0 | 0 | 0 | 0 | 0
| Sulfur | lbmoles/MMBtu |  | 0.012376 | 0.012376 | 0.012376 | 0.012376 | 0.012376
| Ash | lbmoles/MMBtu |  | 9.2593 | 9.2593 | 9.2593 | 9.2593 | 9.2593
| Oxygen | lbmoles/MMBtu |  | 0 | 0 | 0 | 0 | 0
Flue Gas, Downstream Of Economizer
Flue Gas (lb-moles/MMBtu)
| CO2 | lbmoles/MMBtu |  | 7.6703 | 7.6703 | 7.6703 | 7.6703 | 7.6703
| NOx | lbmoles/MMBtu |  | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0.010052
| HCl | lbmoles/MMBtu |  | 0 | 0 | 0 | 0 | 0
| SO2 | lbmoles/MMBtu |  | 0.012376 | 0.012376 | 0.012376 | 0.012376 | 0.012376
| Total O2 Req'd - * | lbmoles/MMBtu |  | 11.1998 | 11.1998 | 11.1998 | 11.1998 | 11.1998
| N2 | lbmoles/MMBtu |  | 42.1651 | 42.1651 | 42.1651 | 42.1651 | 42.1651
| O2 | lbmoles/MMBtu |  | 1.8666 | 1.8666 | 1.8666 | 1.8666 | 1.8666
| H20 | lbmoles/MMBtu |  | 6.5205 | 6.5205 | 6.5205 | 6.5205 | 6.5205
| Total Dry | lbmoles/MMBtu |  | 51.7245 | 51.7245 | 51.7245 | 51.7245 | 51.7245
| Total Wet | lbmoles/MMBtu |  | 58.245 | 58.245 | 58.245 | 58.245 | 58.245
Wet Flue Gas PPMV & % Vol
| % O2 | % Vol |  | 3.2048 | 3.2048 | 3.2048 | 3.2048 | 3.2048
| % CO2 | % Vol |  | 13.1691 | 13.1691 | 13.1691 | 13.1691 | 13.1691
| % N2 | % Vol |  | 72.3926 | 72.3926 | 72.3926 | 72.3926 | 72.3926
| NOx | ppmv |  | 172.5822 | 172.5822 | 172.5822 | 172.5822 | 172.5822
| HCL | ppmv |  | 0 | 0 | 0 | 0 | 0
| SO2 | ppmv |  | 212.4823 | 212.4823 | 212.4823 | 212.4823 | 212.4823
| % H2O | % Vol |  | 11.195 | 11.195 | 11.195 | 11.195 | 11.195
Dry Flue Gas PPMV & % Vol
| % O2 | % Vol |  | 3.6088 | 3.6088 | 3.6088 | 3.6088 | 3.6088
| % CO2 | % Vol |  | 14.8292 | 14.8292 | 14.8292 | 14.8292 | 14.8292
| % N2 | % Vol |  | 81.5186 | 81.5186 | 81.5186 | 81.5186 | 81.5186
| NOx | ppmv |  | 194.3383 | 194.3383 | 194.3383 | 194.3383 | 194.3383
| HCL | ppmv |  | 0 | 0 | 0 | 0 | 0
| SO2 | ppmv |  | 239.2683 | 239.2683 | 239.2683 | 239.2683 | 239.2683
| % H2O | % Vol |  | 0 | 0 | 0 | 0 | 0
Flue Gas, Air & Ash Downstream Of Economizer
Flue Gas (lbs/MMBtu)
| O2 | lbs/MMBtu |  | 59.7298 | 59.7298 | 59.7298 | 59.7298 | 59.7298
| CO2 | lbs/MMBtu |  | 337.5718 | 337.5718 | 337.5718 | 337.5718 | 337.5718
| N2 | lbs/MMBtu |  | 1181.4669 | 1181.4669 | 1181.4669 | 1181.4669 | 1181.4669
| NOx | lbs/MMBtu |  | 0.30166 | 0.30166 | 0.30166 | 0.30166 | 0.30166
| HCl | lbs/MMBtu |  | 0 | 0 | 0 | 0 | 0
| SO2 | lbs/MMBtu |  | 0.79284 | 0.79284 | 0.79284 | 0.79284 | 0.79284
| H2O | lbs/MMBtu |  | 117.4693 | 117.4693 | 117.4693 | 117.4693 | 117.4693
| Gas Dry | lbs/MMBtu |  | 1579.863 | 1579.863 | 1579.863 | 1579.863 | 1579.863
| Gas Wet | lbs/MMBtu |  | 1697.3323 | 1697.3323 | 1697.3323 | 1697.3323 | 1697.3323
| % H2O | wt% |  | 6.9208 | 6.9208 | 6.9208 | 6.9208 | 6.9208
| Theoretical Wet Air | lbs/MMBtu |  | 1299.1121 | 1299.1121 | 1299.1121 | 1299.1121 | 1299.1121
| Actual Total Wet Air | lbs/MMBtu |  | 1558.9345 | 1558.9345 | 1558.9345 | 1558.9345 | 1558.9345
| Mol Wt Wet, Lb/Lb-Mol | lbs/lb-mole |  | 29.1412 | 29.1412 | 29.1412 | 29.1412 | 29.1412
| Total Ash | lbs/MMBtu |  | 9.7222 | 9.7222 | 9.7222 | 9.7222 | 9.7222
| Fly Ash | lbs/MMBtu |  | 7.7778 | 7.7778 | 7.7778 | 7.7778 | 7.7778
| Bottom Ash | lbs/MMBtu |  | 1.9444 | 1.9444 | 1.9444 | 1.9444 | 1.9444
| NOx - Flue Gas | lbs/MMBtu |  | 0.30166 | 0.30166 | 0.30166 | 0.30166 | 0.30166
| Carbon Loss | lbmoles/MMBtu |  | 0.038544 | 0.038544 | 0.038544 | 0.038544 | 0.038544
* - Theoretical + Excess O2 Required for Combustion, Not O2 in Flue Gas
Gases, Downstream Of Air Heater
Flue Gas (lb-moles/MMBtu)
| CO2 | lbmoles/MMBtu |  | 7.6703 | 7.6703 | 7.6703 | 7.6703 | 7.6703
| NOx | lbmoles/MMBtu |  | 0.010052 | 0.010052 | 0.010052 | 0.010052 | 0.010052
| HCl | lbmoles/MMBtu |  | 0 | 0 | 0 | 0 | 0
| SO2 | lbmoles/MMBtu |  | 0.012376 | 0.012376 | 0.012376 | 0.012376 | 0.012376
| N2 | lbmoles/MMBtu |  | 47.5741 | 47.5741 | 47.5741 | 47.5741 | 47.5741
| O2 | lbmoles/MMBtu |  | 3.3045 | 3.3045 | 3.3045 | 3.3045 | 3.3045
| H2O | lbmoles/MMBtu |  | 6.6631 | 6.6631 | 6.6631 | 6.6631 | 6.6631
| Total Dry Flue Gas | lbmoles/MMBtu |  | 58.5714 | 58.5714 | 58.5714 | 58.5714 | 58.5714
| Total Wet Flue Gas | lbmoles/MMBtu |  | 65.2344 | 65.2344 | 65.2344 | 65.2344 | 65.2344
| Dry Air Addition | lbmoles/MMBtu |  | 6.8468 | 6.8468 | 6.8468 | 6.8468 | 6.8468
| Wet Air Addition | lbmoles/MMBtu |  | 6.9894 | 6.9894 | 6.9894 | 6.9894 | 6.9894
Wet Flue Gas PPMV & % Vol
| % O2 | % Vol |  | 5.0655 | 5.0655 | 5.0655 | 5.0655 | 5.0655
| % CO2 | % Vol |  | 11.7581 | 11.7581 | 11.7581 | 11.7581 | 11.7581
| % N2 | % Vol |  | 72.9279 | 72.9279 | 72.9279 | 72.9279 | 72.9279
| PPMV NOx | ppmv |  | 154.0913 | 154.0913 | 154.0913 | 154.0913 | 154.0913
| PPMV HCL | ppmv |  | 0 | 0 | 0 | 0 | 0
| PPMV SO2 | ppmv |  | 189.7164 | 189.7164 | 189.7164 | 189.7164 | 189.7164
| % H2O | % Vol |  | 10.2141 | 10.2141 | 10.2141 | 10.2141 | 10.2141
| TOTAL |  |  | 100 | 100 | 100 | 100 | 100
Dry Flue Gas PPMV & % Vol
| % O2 | % Vol |  | 5.6418 | 5.6418 | 5.6418 | 5.6418 | 5.6418
| % CO2 | % Vol |  | 13.0957 | 13.0957 | 13.0957 | 13.0957 | 13.0957
| % N2 | % Vol |  | 81.2242 | 81.2242 | 81.2242 | 81.2242 | 81.2242
| NOx | ppmv |  | 171.6207 | 171.6207 | 171.6207 | 171.6207 | 171.6207
| HCL | ppmv |  | 0 | 0 | 0 | 0 | 0
| SO2 | ppmv |  | 211.2985 | 211.2985 | 211.2985 | 211.2985 | 211.2985
| % H2O | % Vol |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  |  | 100 | 100 | 100 | 100 | 100
Flue Gas & Air Downstream Of Air Heater
Flue Gas (lbs/MMBtu)
| O2 | lbs/MMBtu |  | 105.7389 | 105.7389 | 105.7389 | 105.7389 | 105.7389
| CO2 | lbs/MMBtu |  | 337.5718 | 337.5718 | 337.5718 | 337.5718 | 337.5718
| N2 | lbs/MMBtu |  | 1333.0271 | 1333.0271 | 1333.0271 | 1333.0271 | 1333.0271
| NOx | lbs/MMBtu |  | 0.30166 | 0.30166 | 0.30166 | 0.30166 | 0.30166
| HCl | lbs/MMBtu |  | 0 | 0 | 0 | 0 | 0
| SO2 | lbs/MMBtu |  | 0.39 | 0.79284 | 0.79284 | 0.79284 | 0.79284
| H2O | lbs/MMBtu |  | 120.0377 | 120.0377 | 120.0377 | 120.0377 | 120.0377
| Gas Dry | lbs/MMBtu |  | 1777.0294 | 1777.4322 | 1777.4322 | 1777.4322 | 1777.4322
| Gas Wet | lbs/MMBtu |  | 1897.0671 | 1897.4699 | 1897.4699 | 1897.4699 | 1897.4699
| Wt % H2O | wt% |  | 6.3275 | 6.3262 | 6.3262 | 6.3262 | 6.3262
| Total Wet Air | lbs/MMBtu |  | 1759.0719 | 1759.0719 | 1759.0719 | 1759.0719 | 1759.0719
| Mol Wt Wet, Lb/Lb-Mol | lbs/lb-mole |  | 29.0808 | 29.0869 | 29.0869 | 29.0869 | 29.0869
Boiler Losses & Efficiencies
| Dry Gas | % |  | 9.5269 | 9.5269 | 9.5269 | 9.5269 | 9.5269
| Moisture | % |  | 11.1369 | 11.1369 | 11.1369 | 11.1369 | 11.1369
| Carbon | % |  | 0.65278 | 0.65278 | 0.65278 | 0.65278 | 0.65278
| Radiation | % |  | 0.22174 | 0.22174 | 0.25681 | 0.34415 | 0.34415
| Manufacturers Margin | % |  | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
| Ash Losses | % |  | 0 | 0 | 0 | 0 | 0
| Total Losses | % |  | 23.0383 | 23.0383 | 23.0734 | 23.1607 | 23.1607
| Boiler Efficiency | % |  | 76.9617 | 76.9617 | 76.9266 | 76.8393 | 76.8393
Coal Flow Rates
| Btu Input Rate to Boiler | MMBtu/hr |  | 497 | 1774.95 | 934.807 | 260.326 | 260.326
| Coal Input Rate to Boiler | tons/hr |  | 32.8704 | 117.3909 | 61.8259 | 17.2173 | 17.2173
| Coal Input Rate to Boiler | lbs/MMBtu |  | 132.2751 | 132.2751 | 132.2751 | 132.2751 | 132.2751
Economizer Outlet
| Flue Gas | SCFM/MMBtu |  | 22111.5647 | 22111.5647 | 22111.5647 | 22111.5647 | 22111.5647
| Flue Gas | SCFM |  | 183157.4612 | 654115.3636 | 344500.7582 | 95936.92 | 95936.92
| Wet Flue Gas | lb/hr |  | 843574.1351 | 3012679.9016 | 1586678.0815 | 441859.7189 | 441859.7189
| Wet Air | SCFM |  | 169888.8743 | 606728.8882 | 319543.8811 | 88986.9036 | 88986.9036
| Wet Air | lb/hr |  | 774790.4664 | 2767030.8618 | 1457302.9205 | 405831.1931 | 405831.1931
| Total Air | % |  | 120% | 120% | 120% | 120% | 120%
| Excess Air | % |  | 20% | 20% | 20% | 20% | 20%
Air Heater Outlet
| Flue Gas | SCFM/MMBtu |  | 24764.9525 | 24764.9525 | 24764.9525 | 24764.9525 | 24764.9525
| Flue Gas | SCFM |  | 205136.3565 | 732609.2072 | 385840.8491 | 107449.3504 | 107449.3504
| Wet Flue Gas | lb/hr |  | 942842.3336 | 3367914.223 | 1773768.1574 | 493960.7527 | 493960.7527
| Wet Air | SCFM |  | 191699.3502 | 684621.2507 | 360567.192 | 100411.1168 | 100411.1168
| Wet Air | lb/hr |  | 874258.7149 | 3122264.5997 | 1644392.6892 | 457932.1413 | 457932.1413
| Wet Air Leakage | SCFM |  | 21810.4759 | 77892.3625 | 41023.3109 | 11424.2132 | 11424.2132
| Wet Air Leakage | lb/hr |  | 99468.2486 | 355233.738 | 187089.7687 | 52100.9482 | 52100.9482
| Equivalent Total Air | % |  | 135.4% | 135.4% | 135.4% | 135.4% | 135.4%
| Equivalent Excess Air | % |  | 35.41% | 35.41% | 35.41% | 35.41% | 35.41%
| Flue Gas Temperature | °F |  | 300 | 300 | 300 | 300 | 300
| Pressure | in. H2O |  | -12 | -12 | -12 | -12 | -12
| Flue Gas | ACFM |  | 314547.3145 | 1123351.6214 | 591631.854 | 164758.2378 | 164758.2378
Ash Parameters
| Fly Ash | tons/hr |  | 1.9328 | 6.9026 | 3.6354 | 1.0124 | 1.0124
| Bottom Ash | tons/hr |  | 0.48318 | 1.7256 | 0.90882 | 0.25309 | 0.25309
| Total Ash | tons/hr |  | 2.416 | 8.6282 | 4.5442 | 1.2655 | 1.2655
| ECONOMIC FACTORS |  |  | CASE 1 | CASE 2 | CASE 3 | CASE 4 | CASE 5
| Construction Period | Years | bar: 2 to 6
Current Dollars
| P/A Factor |  |  | 10.0942 | 10.0942 | 10.0942 | 10.0942 | 10.0942
| A/P (Annuity) Factor |  |  | 0.099067 | 0.099067 | 0.099067 | 0.099067 | 0.099067
P/AE (Present Worth) Factors
| Consumables (O&M) |  |  | 13.7363 | 13.7363 | 13.7363 | 13.7363 | 13.7363
| Capital Costs |  |  | 13.7363 | 13.7363 | 13.7363 | 13.7363 | 13.7363
Levelization Factors
| Consumables (O&M) |  |  | 1.3608 | 1.3608 | 1.3608 | 1.3608 | 1.3608
| Capital Costs |  |  | 1.3608 | 1.3608 | 1.3608 | 1.3608 | 1.3608
Constant Dollars
| P/A Factor |  |  | 13.7363 | 13.7363 | 13.7363 | 13.7363 | 13.7363
| A/P (Annuity) Factor |  |  | 0.0728 | 0.0728 | 0.0728 | 0.0728 | 0.0728
P/AE (Present Worth) Factors
| Consumables (O&M) |  |  | 13.7363 | 13.7363 | 13.7363 | 13.7363 | 13.7363
| Capital Costs |  |  | 13.7363 | 13.7363 | 13.7363 | 13.7363 | 13.7363
Levelization Factors
Consumables (O&M) | bar: 2 to 6
Capital Costs | bar: 2 to 6
| Z = (1 + i) / (1 + e) |  |  | 1.0757 | 1.0757 | 1.0757 | 1.0757 | 1.0757
AFDC / TCE FACTORS FOR CASE 1
|  |  | AFDC | TCE
| Unit Size, MW | Years | 1: Factor; 2: Factor
| 0 | 1 | 1: 0; 2: 1
| 160 | 2 | 1: 0.052427; 2: 0.98544
| 400 | 3 | 1: 0.10648; 2: 0.97116
| 725 | 4 | 1: 0.16228; 2: 0.95715
| 1300 | 5 | 1: 0.21995; 2: 0.94342
| 2000 | 6 | 1: 0.2796; 2: 0.92995
AFDC / TCE FACTORS FOR CASE 2
|  |  | AFDC | TCE
| Unit Size, MW | Years | 1: Factor; 2: Factor
| 0 | 1 | 1: 0; 2: 1
| 160 | 2 | 1: 0.052427; 2: 0.98544
| 400 | 3 | 1: 0.10648; 2: 0.97116
| 725 | 4 | 1: 0.16228; 2: 0.95715
| 1300 | 5 | 1: 0.21995; 2: 0.94342
| 2000 | 6 | 1: 0.2796; 2: 0.92995
AFDC / TCE FACTORS FOR CASE 3
|  |  | AFDC | TCE
| Unit Size, MW | Years | 1: Factor; 2: Factor
| 0 | 1 | 1: 0; 2: 1
| 160 | 2 | 1: 0.052427; 2: 0.98544
| 400 | 3 | 1: 0.10648; 2: 0.97116
| 725 | 4 | 1: 0.16228; 2: 0.95715
| 1300 | 5 | 1: 0.21995; 2: 0.94342
| 2000 | 6 | 1: 0.2796; 2: 0.92995
AFDC / TCE FACTORS FOR CASE 4
|  |  | AFDC | TCE
| Unit Size, MW | Years | 1: Factor; 2: Factor
| 0 | 1 | 1: 0; 2: 1
| 160 | 2 | 1: 0.052427; 2: 0.98544
| 400 | 3 | 1: 0.10648; 2: 0.97116
| 725 | 4 | 1: 0.16228; 2: 0.95715
| 1300 | 5 | 1: 0.21995; 2: 0.94342
| 2000 | 6 | 1: 0.2796; 2: 0.92995
AFDC / TCE FACTORS FOR CASE 5
|  |  | AFDC | TCE
| Unit Size, MW | Years | 1: Factor; 2: Factor
| 0 | 1 | 1: 0; 2: 1
| 160 | 2 | 1: 0.052427; 2: 0.98544
| 400 | 3 | 1: 0.10648; 2: 0.97116
| 725 | 4 | 1: 0.16228; 2: 0.95715
| 1300 | 5 | 1: 0.21995; 2: 0.94342
| 2000 | 6 | 1: 0.2796; 2: 0.92995
Source Key for Nox Defaults
a | Table 2-1, "Cost Estimates for Selected Applications of NOX control Technologies on Stationary Combustion Boilers: Draft Report" March 1996. EPA, Acid Rain Division, Cost year 1995
b | Table 1-5, "Cost Estimates for Selected Applications of NOX control Technologies on Stationary Combustion Boilers: Draft Report" March 1996. EPA, Acid Rain Division
c | Section 3.0, "Cost Estimates for Selected Applications of NOX control Technologies on Stationary Combustion Boilers: Draft Report" March 1996. EPA, Acid Rain Division, Cost year 1995
d | Pg. B4-21-25 "Investigation of Performance and cost of NOX controls as Applied to Group 2 Boilers: Revised Draft Report", EPA, Acid Rain Division, August 1996
e | Table B2-1 "Investigation of Performance and cost of NOX controls as Applied to Group 2 Boilers: Revised Draft Report", EPA, Acid Rain Division, August 1996
f | Pg. B4-17-19 "Investigation of Performance and cost of NOX controls as Applied to Group 2 Boilers: Revised Draft Report", EPA, Acid Rain Division, August 1996
g | IAPCS default for cost year 06/96
h | "Development of the Integrated Environmental Control Model:Performance Models of Selective Reduction(SCR) Nox Control Systems; Quarterly Progress Report" Center for Energy and Environmental Studies, Carnegie Mellon University, July 1994
i | IAPCS equations
Note on B422: All the carbon loss is assumed to be included in the flyash.