## Dry Sorbent Injection
Four Boilers Dry Sorbent Injection System - Chena Power Plant
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 27.5 | <-- User Input (Gross Output based on sum of turbines rated size; 20MW, 5MW, and 2.5 MW)
Retrofit Factor | B |  | 1.5 | <-- User Input (An "average" retrofit has a factor of 1.0. Site-specific considerations provided by Aurora in 12/22/17 BACT Addendum)
Gross Heat Rate | C | (Btu/kWh) | 18000 | <-- User Input (Heat Rate is higher because district heating is not included in unit size, cell D4)
SO2 Rate | D | (lb/MMBtu) | 0.301 | E.F. is average from two most recent SO2 source tests accepted by the Department which occurred on November 19, 2011 and July 12, 2019
Type of Coal | E |  | sub-bituminous | <-- User Input
Particulate Capture | F |  | Baghouse | <-- User Input
Milled Trona | G |  | TRUE | Based on in-line milling equipment
Removal Target | H | (%) | 80 | Maximum Removal Targets: Unmilled Trona with an ESP = 65% Milled Trona with an ESP = 80% Unmilled Trona with a Baghouse = 80% Milled Trona with Baghouse = 90%
Heat Input | J | (Btu/hr) | 495000000 | A*C*1000
NSR | K |  | 1.9695 | Unmilled Trona with an ESP = if(H<40,0.0350*H,0.352e^(0.0345*H)) Milled Trona with an ESP = if(H<40,0.0270*H,0.353e^(0.0280*H)) Unmilled Trona with an BGH = if(H<40,0.0215*H,0.295e^(0.0267*H)) Milled Trona with an BGH = if(H<40,0.0160*H,0.208e^(0.0281*H))
Trona Feed Rate | M | (ton/hr) | 0.35246 | (1.2011x10^-06)*K*A*C*D
Sorbent Waste Rate | N | (ton/hr) | 0.2374 | (0.7035-0.00073696*H/K)*M Based on a final reaction product of Na2SO4 and unreacted dry sorbent as Na2CO3.
Fly Ash Waste Rate | P | (ton/hr) | 0.91667 | (A*C)*Ash incoal*(1-Boiler Ash Removal)/(2*HHV) For Bituminous Coal: Ash in Coal = 0.12; Boiler Ash Removal = 0.2, HHV = 11,000 For PRB Coal: Ash in Coal = 0.06; Boiler Ash Removal = 0.2, HHV = 8,400 For Lignite Coal: Ash in Coal = 0.08; Boiler Ash Removal = 0.2, HHV = 7,200 <-- User Input (Usibelli Coal: Ash in Coal = 0.07; Boiler Ash Removal = 0.6; HHV = 7,560)
Aux Power | Q | (%) | 0.25633 | =if Milled Trona M*20/A else M*18/A
Trona Cost | R | ($/ton) | 550 | <-- User Input (based on Stanly DSI quote)
Waste Disposal Cost | S | ($/ton) | 50
Aux Power Cost | T | ($/kWh) | 0.21 | <-- User Input (http://www.gvea.com/rates/rates)
Operating Labor Rate | U | ($/hr) | 63 | <-- User Input (Labor cost including all benefits[AE 2016])
IPM Model - Updates to Cost and Performance for APC Technologies - Dry Sorbent Injection for SO2 Control Cost Development Methodology, March 2013, prepared by Sargent & Lundy LLC for USEPA. https://www.epa.gov/sites/production/files/2015-07/documents/append5_4.pdf
Capital Cost Calculation (2012 dollars) |  |  |  | Comments
Includes - Equipment, installation, building, foundations, electrical, and a retrofit difficulty factor of 1.5
Base Module (BM) ($) |  | = | 14169111 | Base DSI module includes all equipment from unloading to injection
Unmilled Trona = if(M>25 then (682,000*B*M) else 6,833,000*B*(M^0.284)
Milled Trona = if(M>25 then (750,000*B*M) else 7,516,000*B*(M^0.284)
BM ($/kW) |  | = | 515.2404 | Base module cost per kW
Total Project Cost
A1 = 10% of BM |  | = | 1416911.1 | Engineering and construction management costs (CC Manual)
A2 = 10% of BM |  | = | 1416911.1 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc. (CC Manual)
A3 = 10% of BM |  | = | 1416911.1 | Contractor profit and fees (CC Manual)
CECC ($) - Excludes Owner's Costs = BM + A1 + A2 + A3 |  | = | 18419844.3 | Capital, engineering, and construction costs subtotal
CECC ($/kW) - Excludes Owner's Costs |  | = | 669.8125 | Capital, engineering, and construction costst subtotal per kW
B1 = 5% of CECC |  | = | 920992.215 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
TPC ($) - Includes Owners Costs = CECC + B1 |  | = | 19340836.515 | Total project cost without Allowance for Funds Used During Construction (AFUDC)
TPC ($/kW) - Include Owner's Costs |  | = | 703.3031 | Total project cost per kW without AFUDC
B2 = 0% of (CECC + B1) |  | = |  | AFUDC (Zero for less than 1 year engineering and construction cycle)
TPC ($) = CECC + B1 + B2 |  | = | 20604000 | Total project cost
TPC ($/kW) |  | = | 749.2364 | Total project cost per kW
Dry Sorbent Injection System - Chena Power Plant
Direct Annual Costs
Fixed Operating and Maintenance (O&M) Cost
FOMO ($/kW yr) = (1 additional operators)*(2080)*U/(A*1000) |  | = | 4.7651 | Fixed O&M additional operating labor costs
FOMM ($/kW yr) = BM*0.01/(B*A*1000) |  | = | 3.4349 | Fixed O&M additional maintenance material and labor costs
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  | = | 0.18417 | Fixed O&M additional administrative labor costs
FOM ($/kW yr) = FOMO + FOMM + FOMA |  | = | 8.3842 | Total Fixed O&M costs ($/kW yr)
Variable O&M Cost
VOMR ($/MWh) = M*R/A |  | = | 7.0492 | Variable O&M costs for Trona reagent
VOMW ($/MWh) = (N+P)*S/A |  | = | 2.0983 | Variable O&M costs for waste disposal that includes both the sorbent and the fly ash waste not removed prior to the sorbent injection
VOMP ($/MWh) = Q*T*10 |  | = | 0.5383 | Variable O&M costs for additional auxiliary power required (Refer to Aux Power % above)
VOM ($/MWh) = VOMR + VOMW + VOMP |  | = | 9.6858 | Total Variable O&M Costs ($/MW yr)
Indirect Annual Costs
Overhead (60% of total labor and material costs) |  | = | 138339.2813 | CC Manual
Administrative charges (2% of total capital investment) |  | = | 412080 | CC Manual
Property tax (1% of total capital investment) |  | = | 206040 | CC Manual
Insurance (1% of total capital investment) |  | = | 206040 | CC Manual
Capital Recovery Factor (CRF) = [ i (1+i)n ] / [ (1+i)n - 1 ]
i = Interest rate (%) | 5
n = Equipment life (years) | 15
CRF = | 0.096342 | = | 1985036.4939 | CC Manual
TOTAL INDIRECT ANNUAL OPERATING COSTS |  | = | 2947535.7752
TOTAL ANNUALIZED OPERATING COSTS (2012 $) |  | = | 5511406.5855
Composite CE Index for 2012 (cost year of equation) |  | = | 584.6
Composite CE Index for 2016 (cost year of review) |  | = | 536.4
TOTAL ANNUALIZED OPERATING COSTS (2016 $) |  | = | 5056993.658
TOTAL UNCONTROLLED SO2 EMISSIONS, tons |  | = | 652.5981
SO2 REMOVAL EFFICIENCY, % |  | = | 80
TOTAL SO2 REMOVED, tons |  | = | 522.0785
SO2 COST-EFFECTIVENESS, $/ton removed |  | = | 9686.271
Note on D48: Simpson, Aaron: Rsp to IR #2: "Aurora Energy Preliminary Opinion of Probabale Cost.pdf" and "Aurora_DSI_Opinion_of_Probable_Cost_rev0.pdf" and Comment No. 9 by Aurora Energy on draft SIP Public Notice.

## Spray Dry Absorber
Four Boilers Spray Dry Absorber - Chena Power Plant
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 27.5 | <-- User Input (Gross Output based on sum of turbines rated size; 20MW, 5MW, and 2.5 MW)
Retrofit Factor | B |  | 1.5 | <-- User Input (An "average" retrofit has a factor of 1.0. Site-specific considerations provided by Aurora in 12/22/17 BACT Addendum)
Gross Heat Rate | C | (Btu/kWh) | 18000 | <-- User Input (Heat Rate is higher because district heating is not included in unit size, cell D4)
SO2 Rate | D | (lb/MMBtu) | 0.301 | E.F. is average from two most recent SO2 source tests accepted by the Department which occurred on November 19, 2011 and July 12, 2019
Type of Coal | E |  | sub-bituminous | <-- User Input
Coal Factor | F |  | 1.05 | Bituminous = 1, Sub-Bituminous=1.05, Lignite=1.07
Heat Rate Factor | G |  | 1.8 | C/10000
Heat Input | H | (Btu/hr) | 495000000 | A*C*1000
Lime Rate | K | (ton/hr) | 0.10148 | (0.6702*(D^2)+13.42*D)*A*G/2000 (Based on 95% SO2 Removal)
Waste Rate | L | (ton/hr) | 0.23417 | (0.8016*(D^2)+31.1917*D)*A*G/2000
Aux Power | M | (%) | 2.4608 | (0.000547*(D^2)+0.00649*D+1.3)*F*G Should be used for model input
Makeup Water Rate | N | (1000 gph) | 2.8738 | (0.04898*(D^2)+0.5925*D+55.11)*A*F*G/1000
Lime Cost | P | ($/ton) | 240 | <-- User Input (https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Waste Disposal Cost | Q | ($/ton) | 30 | <-- User Input (https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Aux Power Cost | R | ($/kWh) | 0.21 | <-- User Input (http://www.gvea.com/rates/rates)
Makeup Water Cost | S | ($/1000 gal) | 7.17 | <-- User Input (http://www.newsminer.com/water-rates/article_11a2ba10-c211-562e-8da9-87dd16a7b104.html)
Operating Labor Rate | T | ($/hr) | 63 | Labor cost including all benefits
IPM Model - Updates to Cost and Performance for APC Technologies - SDA FGD for SO2 Control Cost Development Methodology, March 2013, prepared by Sargent & Lundy LLC for US EPA. https://www.epa.gov/sites/production/files/2015-07/documents/chapter_5_appendix_5-1b_sda_fgd.pdf
Capital Cost Calculation (2012 dollars) |  |  |  | Comments
Includes - Equipment, installation, building, foundations, electrical, and a retrofit difficulty factor of 1.5
BMR ($) = if(A>600 then (A*92,000) else 566,000*(A^0.716))*B*(F*G)^0.6*(D/4)^0.01 |  | = | 13005050.6086 | Base module absorber island cost
BMF ($) = if(A>600 then (A*48,700) else 300,000*(A^0.716))*B*(D*G)^0.2 |  | = | 4271127.3691 | Base module reagent preparation and waste recycle/handling cost
BMB ($) = if(A>600 then (A*129,900) else 799,000*(A^0.716))*B*(F*G)^0.4 |  | = | 16587654.0357 | Base module balance of plan costs inlcuding: ID or booster fans, piping, ductwork, electrical, etc.
BM ($) = BMR + BMF + BMB |  | = | 33863832.0134 | Total base module cost including retrofit factor
BM ($/kW) |  | = | 1231.4121 | Base module cost per kW
Total Project Cost
A1 = 10% of BM |  | = | 3386383.2013 | Engineering and construction management costs
A2 = 10% of BM |  | = | 3386383.2013 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc.
A3 = 10% of BM |  | = | 3386383.2013 | Contractor profit and fees
CECC ($) - Excludes Owner's Costs = BM + A1 + A2 + A3 |  | = | 44022981.6174 | Capital, engineering, and construction costs subtotal
CECC ($/kW) - Excludes Owner's Costs = |  | = | 1600.8357 | Capital, engineering, and construction costst subtotal per kW
B1 = 5% of CECC |  | = | 2201149.0809 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
TPC ($) - Includes Owners Costs = CECC + B1 |  | = | 46224130.6983 | Total project cost without Allowance for Funds Used During Construction (AFUDC)
TPC ($/kW) - Include Owner's Costs = |  | = | 1680.8775 | Total project cost per kW without AFUDC
B2 = 10% of (CECC + B1) |  | = | 4622413.0698 | AFUDC (based on a 3 year engineering and construction cycle)
TPC ($) - Includes Owner's Costs and AFUDC = CECC + B1 + B2 |  | = | 50846543.7681 | Total project cost
TPC ($/kW) - Includes Owner's Costs and AFUDC = |  | = | 1848.9652 | Total project cost per kW
Spray Dry Absorber - Chena Power Plant
Direct Annual Costs
Fixed Operating and Maintenance (O&M) Cost
FOMO ($/kW yr) = (4 additional operators)*(2080)*T/(A*1000) |  | = | 38.1207 | Fixed O&M additional operating labor costs
FOMM ($/kW yr) = BM*0.015/(B*A*1000) |  | = | 12.3141 | Fixed O&M additional maintenance material and labor costs
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  | = | 1.2914 | Fixed O&M additional administrative labor costs
FOM ($/kW yr) = FOMO + FOMM + FOMA |  | = | 51.7262 | Total Fixed O&M costs
Variable O&M Cost
VOMR ($/MWh) = K*P/A |  | = | 0.88563 | Variable O&M costs for lime reagent
VOMW ($/MWh) = L*Q/A |  | = | 0.25546 | Variable O&M costs for waste disposal
VOMP ($/MWh) = M*R*10 |  | = | 5.1677 | Variable O&M costs for additional auxiliary power required including additional fan power (Refer to Aux Power % above)
VOMM ($/MWh) = N*S/A |  | = | 0.74929 | Variable O&M costs for makeup water
VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM |  | = | 7.058 | Total Variable O&M Costs
Indirect Annual Costs
Overhead (60% of total labor and material costs) |  | = | 853482.948 | CC Manual
Administrative charges (2% of total capital investment) |  | = | 1016930.8754 | CC Manual
Property tax (1% of total capital investment) |  | = | 508465.4377 | CC Manual
Insurance (1% of total capital investment) |  | = | 508465.4377 | CC Manual
Capital Recovery Factor (CRF) = [ i (1+i)n ] / [ (1+i)n - 1 ]
i = Interest rate (%) | 5
n = Equipment life (years) | 15
CRF = | 0.096342 | = | 4898672.3436 | CC Manual
TOTAL INDIRECT ANNUAL OPERATING COSTS |  | = | 7786017.0424
TOTAL ANNUALIZED OPERATING COSTS (2012 $) |  | = | 10908766.9422
Composite CE Index for 2012 (cost year of equation) |  | = | 584.6
Composite CE Index for 2016 (cost year of review) |  | = | 536.4
TOTAL ANNUALIZED OPERATING COSTS (2016 $) |  | = | 10009344.1461
TOTAL UNCONTROLLED SO2 EMISSIONS, tons |  | = | 652.5981
SO2 REMOVAL EFFICIENCY, % |  | = | 90
TOTAL SO2 REMOVED, tons |  | = | 587.3383
SO2 COST-EFFECTIVENESS, $/ton removed |  | = | 17041.8723

## Wet Scrubber
Four Boilers Wet Scrubber - Chena Power Plant
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 27.5 | <-- User Input (Gross Output based on sum of turbines rated size; 20MW, 5MW, and 2.5 MW)
Retrofit Factor | B |  | 1.5 | <-- User Input (An "average" retrofit has a factor of 1.0. Site-specific considerations provided by Aurora in 12/22/17 BACT Addendum)
Gross Heat Rate | C | (Btu/kWh) | 18000 | <-- User Input (Heat Rate is higher than default input because district heating is not included in unit size, cell D4)
SO2 Rate | D | (lb/MMBtu) | 0.301 | E.F. is average from two most recent SO2 source tests accepted by the Department which occurred on November 19, 2011 and July 12, 2019
Type of Coal | E |  | sub-bituminous | <-- User Input
Coal Factor | F |  | 1.05 | Bituminous = 1, Sub-Bituminous = 1.05, Lignite = 1.07
Heat Rate Factor | G |  | 1.8 | C/10000
Heat Input | H | (Btu/hr) | 495000000 | A*C*1000
Limestone Rate | K | (ton/hr) | 0.13052 | 17.52*A*D*G/2000
Waste Rate | L | (ton/hr) | 0.23637 | 1.811*K
Aux Power | M | (%) | 2.0793 | (1.05e^(0.155*D))*F*G
Makeup Water Rate | N | (1000 gph) | 3.9077 | (1.674*D+74.68)*A*F*G/1000
Limestone Cost | P | ($/ton) | 240 | <-- User Input (https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Waste Disposal Cost | Q | ($/ton) | 30 | <-- User Input (https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Aux Power Cost | R | ($/kWh) | 0.21 | <-- User Input (http://www.gvea.com/rates/rates)
Makeup Water Cost | S | ($/1000 gal) | 7.17 | <-- User Input (http://www.newsminer.com/water-rates/article_11a2ba10-c211-562e-8da9-87dd16a7b104.html)
Operating Labor Rate | T | ($/hr) | 63 | Labor cost including all benefits
IPM Model - Updates to Cost and Performance for APC Technologies - Wet FGD for SO2 Control Cost Development Methodology, August 2010, prepared by Sargent & Lundy LLC for US EPA. https://www.epa.gov/sites/production/files/2015-07/documents/chapter_5_appendix_5-1a_wet_fgd.pdf
Capital Cost Calculation (2012 dollars) |  |  |  | Comments
Includes - Equipment, installation, building, foundations, electrical, minor physical/chemical waste water treatment, and a retrofit difficulty factor of 1.5
BMR ($) = 550,000*(B)*((F*G)^0.6)*((D/2)^0.02)*(A^0.716) |  | = | 12486593.3938 | Base absorber island cost
BMF ($) = 190,000*(B)*((D*G)^0.3)*(A^0.716) |  | = | 2544244.0585 | Base reagent preparation cost
BMW ($) = 100,000*(B)*((D*G)^0.45)*(A^0.716) |  | = | 1221464.9747 | Base waste handling cost
BMB ($) = 1,010,000*(B)*((F*G)^0.4)*(A^0.716) |  | = | 20968123.3743 | Base balance of plan cost including: ID or booster fans, new wet chimney, piping, ductwork, minor waste water treatment, etc…
BMWW ($) = |  | = | 0 | Base wastewater treatment facility, beyond minor physical/chemcial treatment
Base Module (BM) ($) = BMR + BMF + BMW + BMB + BMWW |  | = | 37220425.8013 | Total base cost including retrofit factor
BM ($/kW) |  | = | 1353.47 | Base cost per kW
Total Project Cost
A1 = 10% of BM |  | = | 3722042.5801 | Engineering and construction management costs (CC Manual)
A2 = 10% of BM |  | = | 3722042.5801 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc. (CC Manual)
A3 = 10% of BM |  | = | 3722042.5801 | Contractor profit and fees (CC Manual)
CECC ($) - Excludes Owner's Costs = BM + A1 + A2 + A3 |  | = | 48386553.5417 | Capital, engineering, and construction costs subtotal
CECC ($/kW) - Excludes Owner's Costs = |  | = | 1759.511 | Capital, engineering, and construction costst subtotal per kW
B1 = 5% of CECC |  | = | 2419327.6771 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
TPC ($) - Includes Owners Costs = CECC + B1 |  | = | 50805881.2188 | Total project cost without Allowance for Funds Used During Construction (AFUDC)
TPC ($/kW) - Include Owner's Costs = |  | = | 1847.4866 | Total project cost per kW without AFUDC
B2 = 10% of (CECC + B1) |  | = | 5080588.1219 | AFUDC (based on a 3 year engineering and construction cycle)
TPC ($) - Includes Owner's Costs and AFUDC = CECC + B1 + B2 |  | = | 55886469.3407 | Total project cost
TPC ($/kW) - Includes Owner's Costs and AFUDC = |  | = | 2032.2352 | Total project cost per kW
Wet Scrubber - Chena Power Plant
Direct Annual Costs
Fixed O&M Cost
FOMO ($/kW yr) = (6 additional operators)*(2080)*T/(A*1000) |  | = | 28.5905 | Fixed O&M additional operating labor costs
FOMM ($/kW yr) = BM*0.015/(B*A*1000) |  | = | 13.5347 | Fixed O&M additional maintenance material and labor costs
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  | = | 1.0201 | Fixed O&M additional administrative labor costs
FOMWW ($/kW yr) = |  |  | 0 | Fixed O&M costs for wastewater treatment facility
FOM ($/kW yr) = FOMO + FOMM + FOMA + FOMWW |  | = | 43.1454 | Total Fixed O&M costs ($/kW yr)
Variable O&M Cost
VOMR ($/MWh) = K*P/A |  | = | 1.1391 | Variable O&M costs for limestone reagent
VOMW ($/MWh) = L*Q/A |  | = | 0.25786 | Variable O&M costs for waste disposal
VOMP ($/MWh) = M*R*10 |  | = | 4.3665 | Variable O&M costs for additional auxiliary power required including additional fan power (Refer to Aux Power % above)
VOMM ($/MWh) = N*S/A |  | = | 1.0188 | Variable O&M costs for makeup water
VOMWW ($/MWh) = |  | = | 0 | Variable O&M costs for wastewater treatment facility
VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM + VOMWW |  | = | 6.7823 | Total Variable O&M Costs ($/MW yr)
Indirect Annual Costs
Overhead (60% of total labor and material costs) |  | = | 711898.7455 | CC Manual
Administrative charges (2% of total capital investment) |  | = | 1117729.3868 | CC Manual
Property tax (1% of total capital investment) |  | = | 558864.6934 | CC Manual
Insurance (1% of total capital investment) |  | = | 558864.6934 | CC Manual
Capital Recovery Factor (CRF) = [ i (1+i)n ] / [ (1+i)n - 1 ]
i = Interest rate (%) | 5
n = Equipment life (years) | 15
CRF = | 0.096342 | = | 5384230.3027 | CC Manual
TOTAL INDIRECT ANNUAL OPERATING COSTS |  | = | 8331587.8218
TOTAL ANNUALIZED OPERATING COSTS (2012 $) |  | = | 11151934.1468
Composite CE Index for 2012 (cost year of equation) |  | = | 584.6
Composite CE Index for 2016 (cost year of review) |  | = | 536.4
TOTAL ANNUALIZED OPERATING COSTS (2016 $) |  | = | 10232462.327
TOTAL UNCONTROLLED SO2 EMISSIONS, tons |  | = | 652.5981
SO2 REMOVAL EFFICIENCY, % |  | = | 99
TOTAL SO2 REMOVED, tons |  | = | 646.0721
SO2 COST-EFFECTIVENESS, $/ton removed |  | = | 15837.9568 | Does not include costs associated with building and maintaining a wastewater treatment facility

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only