## DSI - 50% Removal
Dry Sorbent Injection with Trona for SO2 Control
CAPITAL COSTS (Excluding Site Preparation and Building Costs)
1) DIRECT PURCHASE EQUIPMENT COSTS (PEC) | 3304000
a) Equipment cost | 2800000 | From Amerair Quote, excludes Owner-Supplied Equipment
b) Instrumentation | 280000 | 0.1 x EC
c) Sales tax | 84000 | 0.03 x EC
d) Freight | 140000 | 0.05 x EC
2) DIRECT INSTALLATION COSTS (DIC) | 1090320
a) Foundation and supports | 330400 | 0.1 x PEC
b) Handling and erection | 660800 | 0.2 x PEC
c) Electrical | 33040 | 0.01 x PEC
d) Ducting | 33040 | 0.01 x PEC
e) Insulation and Painting | 33040 | 0.01 x PEC
3) DIRECT CONTINGENCY | 330400 | 0.1 x PEC
TOTAL DIRECT CAPTIAL COSTS (DC) | 4724720
4) OTHER INDIRECT CAPITAL COSTS (INSTALLATION) (IC) | 1222480
a) Engineering | 330400 | 0.1 x PEC
b) Construction and field expenses | 165200 | 0.05 x PEC
c) Contractor fees | 330400 | 0.1 x PEC
d) Start-up | 66080 | 0.02 x PEC
e) Performance test | 330400 | 0.1 x PEC
5) INDIRECT CONTINGENCY | 244496 | 0.2 x IC
TOTAL INDIRECT CAPITAL COSTS (ICC) | 1466976 | IC + ICC
TOTAL CAPITAL INVESTMENT (TCI) | 6191696 | DC + ICC
ANNUAL COSTS
1) DIRECT ANNUAL COSTS (DAC) | 2589856.48
a) Annual Maintenance | 30958.48 | 0.005*TCI, per SCR Cost Template
b) Electricity of 500 kW blower requirements | 1169898 | $0.2671/kwh per Ashish Agrawal, 4/21/17
b) Annual Reagent Cost | 1389000 | Amerair 6/2/17
2) INDIRECT ANNUAL COSTS (IC) | 2683139.9421
a) Overhead | 1553913.888 | 60% Direct Annual Costs
b) Administrative Charges | 123833.92 | 2% of TCI
c) Property Taxes | 61916.96 | 1% of TCI
d) Insurance | 61916.96 | 1% of TCI
e) Capital Recovery | 881558.2141 | CRF*TCI
TOTAL ANNUAL COST | 5272996.4221
Cost Effectiveness, dollars per ton of NOx removed | 5968.3038 | Amerair Proposal for 50% removal
Capital Recovery Factor:
Parameter | Equation | Calculated Value
Capital Recovery Factor (CRF) = | i (1+ i)n/(1+ i)n - 1 = | 0.14238
Where n = Equipment Life and i= Interest Rate
Equipment Life, n | 10
Interest rate, i | 7
Basecase |  | 1767
Removal | 50% | 883.5

## DSI - 80% Removal
Dry Sorbent Injection with Trona for SO2 Control
CAPITAL COSTS (Excluding Site Preparation and Building Costs)
1) DIRECT PURCHASE EQUIPMENT COSTS (PEC) | 3304000
a) Equipment cost | 2800000 | From Amerair Quote, excludes Owner-Supplied Equipment
b) Instrumentation | 280000 | 0.1 x EC
c) Sales tax | 84000 | 0.03 x EC
d) Freight | 140000 | 0.05 x EC
2) DIRECT INSTALLATION COSTS (DIC) | 1090320
a) Foundation and supports | 330400 | 0.1 x PEC
b) Handling and erection | 660800 | 0.2 x PEC
c) Electrical | 33040 | 0.01 x PEC
d) Ducting | 33040 | 0.01 x PEC
e) Insulation and Painting | 33040 | 0.01 x PEC
3) DIRECT CONTINGENCY | 330400 | 0.1 x PEC
TOTAL DIRECT CAPTIAL COSTS (DC) | 4724720
4) OTHER INDIRECT CAPITAL COSTS (INSTALLATION) (IC) | 1222480
a) Engineering | 330400 | 0.1 x PEC
b) Construction and field expenses | 165200 | 0.05 x PEC
c) Contractor fees | 330400 | 0.1 x PEC
d) Start-up | 66080 | 0.02 x PEC
e) Performance test | 330400 | 0.1 x PEC
5) INDIRECT CONTINGENCY | 244496 | 0.2 x IC
TOTAL INDIRECT CAPITAL COSTS (ICC) | 1466976 | IC + ICC
TOTAL CAPITAL INVESTMENT (TCI) | 6191696 | DC + ICC
ANNUAL COSTS
1) DIRECT ANNUAL COSTS (DAC) | 3284356.48
a) Annual Maintenance | 30958.48 | 0.005*TCI, per SCR Cost Template
b) Electricity of 500 kW blower requirements | 1169898 | $0.2671/kwh per Ashish Agrawal, 4/21/17
b) Annual Reagent Cost | 2083500 | Amerair 6/2/17
2) INDIRECT ANNUAL COSTS (IC) | 3099839.9421
a) Overhead | 1970613.888 | 60% Direct Annual Costs
b) Administrative Charges | 123833.92 | 2% of TCI
c) Property Taxes | 61916.96 | 1% of TCI
d) Insurance | 61916.96 | 1% of TCI
e) Capital Recovery | 881558.2141 | CRF*TCI
TOTAL ANNUAL COST | 6384196.4221
Cost Effectiveness, dollars per ton of NOx removed | 4516.268 | Amerair Proposal for 80% removal
Capital Recovery Factor:
Parameter | Equation | Calculated Value
Capital Recovery Factor (CRF) = | i (1+ i)n/(1+ i)n - 1 = | 0.14238
Where n = Equipment Life and i= Interest Rate
Equipment Life, n | 10
Interest rate, i | 7
Basecase |  | 1767
Removal | 80% | 1413.6