## Dry Sorbent Injection
Dry Sorbent Injection System - Fort Wainwright
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 138 | <-- User Input (Conservative assumption based on a total heat input of 1380 MMBtu/hour)
Retrofit Factor | B |  | 1.5 | <-- User Input (An "average" retrofit has a factor of 1.0)
Gross Heat Rate | C | (Btu/kWh) | 10000 | <-- User Input
SO2 Rate | D | (lb/MMBtu) | 0.46 | <-- User Input
Type of Coal | E |  | sub-bituminous | <-- User Input
Particulate Capture | F |  | Baghouse | <-- User Input
Milled Trona | G |  | TRUE | Based on in-line milling equipment
Removal Target | H | (%) | 80 | Maximum Removal Targets: Unmilled Trona with an ESP = 65% Milled Trona with an ESP = 80% Unmilled Trona with a Baghouse = 80% Milled Trona with Baghouse = 90%
Heat Input | J | (Btu/hr) | 1380000000 | A*C*1000
NSR | K |  | 1.9695 | Unmilled Trona with an ESP = if( H<40,0.0350*H,0.352e^(0.0345*H)) Milled Trona with an ESP = if( H<40,0.0270*H,0.353e^(0.0280*H)) Unmilled Trona with an BGH = if( H<40,0.0215*H,0.295e^(0.0267*H)) Milled Trona with an BGH = if( H<40,0.0160*H,0.208e^(0.0281*H))
Trona Feed Rate | M | (ton/hr) | 1.5017 | (1.2011x10^-06)*K*A*C*D
Sorbent Waste Rate | N | (ton/hr) | 1.0115 | (0.7035-0.00073696*H/K)*M Based on a final reaction product of Na2SO4 and unreacted dry sorbent as Na2CO3.
Fly Ash Waste Rate | P | (ton/hr) | 2.5556 | (A*C)*Ash incoal*(1-Boiler Ash Removal)/(2*HHV) For Bituminous Coal: Ash in Coal = 0.12; Boiler Ash Removal = 0.2, HHV = 11,000 For PRB Coal: Ash in Coal = 0.06; Boiler Ash Removal = 0.2, HHV = 8,400 For Lignite Coal: Ash in Coal = 0.08; Boiler Ash Removal = 0.2, HHV = 7,200 <-- User Input (Usibelli Coal: Ash in Coal = 0.07; Boiler Ash Removal = 0.6; HHV = 7,560)
Aux Power | Q | (%) | 0.21763 | =if Milled Trona M*20/A else M*18/A
Trona Cost | R | ($/ton) | 451 | <-- User Input (based on delivered price paid by Healy)
Waste Disposal Cost | S | ($/ton) | 50
Aux Power Cost | T | ($/kWh) | 0.21 | <-- User Input ( http://www.gvea.com/rates/rates )
Operating Labor Rate | U | ($/hr) | 60 | <-- User Input (Labor cost including all benefits)
IPM Model - Updates to Cost and Performance for APC Technologies - Dry Sorbent Injection for SO2 Control Cost Development Methodology, August 2010, prepared by Sargent & Lundy LLC for USEPA. https://www.epa.gov/sites/production/files/2015-07/documents/append5_4.pdf
Capital Cost Calculation (2012 dollars) |  |  |  | Comments
Includes - Equipment, installation, building, foundations, electrical, and a retrofit difficulty factor of 1.0
Base Module (BM) ($) |  | = | 12653914.0556 | Base DSI module includes all equipment from unloading to injection
Unmilled Trona = if(M>25 then (682,000*B*M) else 6,833,000*B*(M^0.284)
Milled Trona = if(M>25 then (750,000*B*M) else 7,516,000*B*(M^0.284)
BM ($/kW) |  | = | 91.695 | Base module cost per kW
Total Project Cost
A1 = 10% of BM |  | = | 632695.7028 | Engineering and construction management costs (CC Manual)
A2 = 10% of BM |  | = | 632695.7028 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc. (CC Manual)
A3 = 10% of BM |  | = | 632695.7028 | Contractor profit and fees (CC Manual)
CECC ($) - Excludes Owner's Costs = BM + A1 + A2 + A3 |  | = | 14552001.1639 | Capital, engineering, and construction costs subtotal
CECC ($/kW) - Excludes Owner's Costs |  | = | 105.4493 | Capital, engineering, and construction costst subtotal per kW
B1 = 5% of CECC |  | = | 727600.0582 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
TPC ($) - Includes Owners Costs = CECC + B1 |  | = | 15279601.2221 | Total project cost without Allowance for Funds Used During Construction (AFUDC)
TPC ($/kW) - Include Owner's Costs |  | = | 110.7217 | Total project cost per kW without AFUDC
B2 = 0% of (CECC + B1) |  | = | 0 | AFUDC (Zero for less than 1 year engineering and construction cycle)
TPC ($) = CECC + B1 + B2 |  | = | 15279601.2221 | Total project cost
TPC ($/kW) |  | = | 110.7217 | Total project cost per kW
Dry Sorbent Injection System - Fort Wainwright
Direct Annual Costs
Fixed Operating and Maintenance (O&M) Cost
FOMO ($/kW yr) = (1 additional operators)*(2080)*U/(A*1000) |  | = | 0.90435 | Fixed O&M additional operating labor costs
FOMM ($/kW yr) = BM*0.01/(B*A*1000) |  | = | 0.6113 | Fixed O&M additional maintenance material and labor costs
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  | = | 0.034466 | Fixed O&M additional administrative labor costs
FOM ($/kW yr) = FOMO + FOMM + FOMA |  | = | 1.5501 | Total Fixed O&M costs ($/kW yr)
Variable O&M Cost
VOMR ($/MWh) = M*R/A |  | = | 4.9076 | Variable O&M costs for Trona reagent
VOMW ($/MWh) = (N+P)*S/A |  | = | 1.2924 | Variable O&M costs for waste disposal that includes both the sorbent and the fly ash waste not removed prior to the sorbent injection
VOMP ($/MWh) = Q*T*10 |  | = | 0.45703 | Variable O&M costs for additional auxiliary power required (Refer to Aux Power % above)
VOM ($/MWh) = VOMR + VOMW + VOMP |  | = | 6.657 | Total Variable O&M Costs ($/MW yr)
Indirect Annual Costs
Overhead (60% of total labor and material costs) |  | = | 128349.4441 | CC Manual
Administrative charges (2% of total capital investment) |  | = | 305592.0244 | CC Manual
Property tax (1% of total capital investment) |  | = | 152796.0122 | CC Manual
Insurance (1% of total capital investment) |  | = | 152796.0122 | CC Manual
Capital Recovery Factor (CRF) = [ i (1+i)n ] / [ (1+i)n - 1 ]
i = Interest rate (%) | 5.5
n = Equipment life (years) | 15
CRF = | 0.099626 | = | 1522239.4029 | CC Manual
TOTAL INDIRECT ANNUAL OPERATING COSTS |  | = | 2261772.8959
TOTAL ANNUALIZED OPERATING COSTS (2012 $) |  | = | 10523261.8005
Composite CE Index for 2012 (cost year of equation) |  | = | 584.6
Composite CE Index for 2016 (cost year of review) |  | = | 536.4
TOTAL ANNUALIZED OPERATING COSTS (2016 $) |  | = | 9655623.7253
TOTAL UNCONTROLLED SO2 EMISSIONS, tons |  | = | 1168.4736 | 15.12 | MMBtu/ton of coal, http://www.usibelli.com/coal/data-sheet
SO2 REMOVAL EFFICIENCY, % |  | = | 80 | 336000 | tons coal/year (existing permit limit)
TOTAL SO2 REMOVED, tons |  | = | 934.7789
SO2 COST-EFFECTIVENESS, $/ton removed |  | = | 10329.3131

## Spray Dry Absorber
Spray Dry Absorber - Fort Wainwright
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 138 | <-- User Input (Conservative assumption based on a total heat input of 1380 MMBtu/hr)
Retrofit Factor | B |  | 1.5 | <-- User Input (An "average" retrofit has a factor of 1.0)
Gross Heat Rate | C | (Btu/kWh) | 10000 | <-- User Input
SO2 Rate | D | (lb/MMBtu) | 0.46 | <-- User Input (SDA FGD Estimation only valid up to 3lb/MMBtu SO2 Rate)
Type of Coal | E |  | sub-bituminous | <-- User Input
Coal Factor | F |  | 1.05 | Bituminous = 1, Sub-Bituminous = 1.05, Lignite = 1.07
Heat Rate Factor | G |  | 1 | C/10000
Heat Input | H | (Btu/hr) | 1380000000 | A*C*1000
Lime Rate | K | (ton/hr) | 0.43574 | (0.6702*(D^2)+13.42*D)*A*G/2000 (Based on 95% SO2 Removal)
Waste Rate | L | (ton/hr) | 1.0017 | (0.8016*(D^2)+31.1917*D)*A*G/2000
Aux Power | M | (%) | 1.3683 | (0.000547*(D^2)+0.00649*D+1.3)*F*G
Makeup Water Rate | N | (1000 gph) | 8.0264 | (0.04898*(D^2)+0.5925*D+55.11)*A*F*G/1000
Lime Cost | P | ($/ton) | 80 | <-- User Input ( https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf )
Waste Disposal Cost | Q | ($/ton) | 30 | <-- User Input ( https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf )
Aux Power Cost | R | ($/kWh) | 0.21 | <-- User Input ( http://www.gvea.com/rates/rates )
Makeup Water Cost | S | ($/1000 gal) | 7.17 | <-- User Input ( http://www.newsminer.com/water-rates/article_11a2ba10-c211-562e-8da9-87dd16a7b104.html )
Operating Labor Rate | T | ($/hr) | 60 | Labor cost including all benefits
IPM Model - Updates to Cost and Performance for APC Technologies - SDA FGD for SO2 Control Cost Development Methodology, March 2013, prepared by Sargent & Lundy LLC for US EPA. https://www.epa.gov/sites/production/files/2015-07/documents/chapter_5_appendix_5-1b_sda_fgd.pdf
Capital Cost Calculation (2012 dollars) |  |  |  | Comments
Includes - Equipment, installation, building, foundations, electrical, and a retrofit difficulty factor of 1.0
BMR ($) = if(A>600 then (A*92,000) else 566,000*(A^0.716))*B*(F*G)^0.6*(D/4)^0.01 |  | = | 29132762.8763 | Base module absorber island cost
BMF ($) = if(A>600 then (A*48,700) else 300,000*(A^0.716))*B*(D*G)^0.2 |  | = | 13119506.7096 | Base module reagent preparation and waste recycle/handling cost
BMB ($) = if(A>600 then (A*129,900) else 799,000*(A^0.716))*B*(F*G)^0.4 |  | = | 41616656.3072 | Base module balance of plan cost including: ID or booster fans, piping, ductwork, electrical, etc…
Base Module (BM) ($) |  | = | 83868925.8931 | Base DSI module includes all equipment from unloading to injection
BM ($/kW) |  | = | 607.7458 | Base module cost per kW
Total Project Cost
A1 = 10% of BM |  | = | 8386892.5893 | Engineering and construction management costs (CC Manual)
A2 = 10% of BM |  | = | 8386892.5893 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc. (CC Manual)
A3 = 10% of BM |  | = | 8386892.5893 | Contractor profit and fees (CC Manual)
CECC ($) - Excludes Owner's Costs = BM + A1 + A2 + A3 |  | = | 109029603.6611 | Capital, engineering, and construction costs subtotal
CECC ($/kW) - Excludes Owner's Costs |  | = | 790.0696 | Capital, engineering, and construction costst subtotal per kW
B1 = 5% of CECC |  | = | 5451480.1831 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
TPC ($) - Includes Owners Costs = CECC + B1 |  | = | 114481083.8441 | Total project cost without Allowance for Funds Used During Construction (AFUDC)
TPC ($/kW) - Include Owner's Costs |  | = | 829.5731 | Total project cost per kW without AFUDC
B2 = 10% of (CECC + B1) |  | = | 11448108.3844 | AFUDC (Zero for less than 1 year engineering and construction cycle)
TPC ($) = CECC + B1 + B2 |  | = | 125929192.2286 | Total project cost
TPC ($/kW) |  | = | 912.5304 | Total project cost per kW
Spray Dry Absorber - Fort Wainwright
Direct Annual Costs
Fixed O&M Cost
FOMO ($/kW yr) = (4 additional operators)*(2080)*T/(A*1000) |  | = | 3.6174 | Fixed O&M additional operating labor costs
FOMM ($/kW yr) = BM*0.015/(B*A*1000) |  | = | 6.0775 | Fixed O&M additional maintenance material and labor costs
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  | = | 0.18145 | Fixed O&M additional administrative labor costs
FOM ($/kW yr) = FOMO + FOMM + FOMA |  | = | 9.8763 | Total Fixed O&M costs ($/kW yr)
Variable O&M Cost
VOMR ($/MWh) = K*P/A |  | = | 0.2526 | Variable O&M costs for lime reagent
VOMW ($/MWh) = L*Q/A |  | = | 0.21777 | Variable O&M costs for waste disposal
VOMP ($/MWh) = M*R*10 |  | = | 2.8733 | Variable O&M costs for additional auxiliary power required (Refer to Aux Power % above)
VOMM ($/MWh) = N*S/A |  | = | 0.41703 | Variable O&M costs for makeup water
VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM |  | = | 3.7607 | Total Variable O&M Costs ($/MW yr)
Indirect Annual Costs
Overhead (60% of total labor and material costs) |  | = | 817757.718 | CC Manual
Administrative charges (2% of total capital investment) |  | = | 2518583.8446 | CC Manual
Property tax (1% of total capital investment) |  | = | 1259291.9223 | CC Manual
Insurance (1% of total capital investment) |  | = | 1259291.9223 | CC Manual
Capital Recovery Factor (CRF) = [ i (1+i)n ] / [ (1+i)n - 1 ]
i = Interest rate (%) | 5.5
n = Equipment life (years) | 15
CRF = | 0.099626 | = | 12545771.0317 | CC Manual
TOTAL INDIRECT ANNUAL OPERATING COSTS |  | = | 18400696.4388
TOTAL ANNUALIZED OPERATING COSTS (2012 $) |  | = | 24309898.6544
Composite CE Index for 2012 (cost year of equation) |  | = | 584.6
Composite CE Index for 2016 (cost year of review) |  | = | 536.4
TOTAL ANNUALIZED OPERATING COSTS (2016 $) |  | = | 22305558.738
TOTAL UNCONTROLLED SO2 EMISSIONS, tons |  | = | 1168.4736 | 15.12 | MMBtu/ton of coal, http://www.usibelli.com/coal/data-sheet
SO2 REMOVAL EFFICIENCY, % |  | = | 90 | 336000 | tons coal/year (existing permit limit)
TOTAL SO2 REMOVED, tons |  | = | 1051.6262
SO2 COST-EFFECTIVENESS, $/ton removed |  | = | 21210.5384

## Wet Scrubber
Wet Scrubber - Fort Wainwright
Variable | Designation | Units | Value | Calculation
Unit Size (Gross) | A | (MW) | 138 | <-- User Input (Conservative assumption based on a total heat input of 1380 MMBtu/hr)
Retrofit Factor | B |  | 1.5 | <-- User Input (An "average" retrofit has a factor of 1.0) Sargent and Lundy has a drop down menu for selection of an additional waste water treatment plant facility, but no capital or operational cost are implemented so it is not reproduced here.
Gross Heat Rate | C | (Btu/kWh) | 10000 | <-- User Input
SO2 Rate | D | (lb/MMBtu) | 0.46 | <-- User Input
Type of Coal | E |  | sub-bituminous | <-- User Input
Coal Factor | F |  | 1.05 | Bituminous = 1, Sub-Bituminous = 1.05, Lignite = 1.07
Heat Rate Factor | G |  | 1 | C/10000
Heat Input | H | (Btu/hr) | 1380000000 | A*C*1000
Limestone Rate | K | (ton/hr) | 0.55608 | 17.52*A*D*G/2000
Waste Rate | L | (ton/hr) | 1.0071 | 1.811*K
Aux Power | M | (%) | 1.184 | (1.05e^(0.155*D))*F*G
Makeup Water Rate | N | (1000 gph) | 10.9327 | (1.674*D+74.68)*A*F*G/1000
Limestone Cost | P | ($/ton) | 20 | <-- User Input (https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Waste Disposal Cost | Q | ($/ton) | 30 | <-- User Input (https://www3.epa.gov/ttncatc1/dir1/ffdg.pdf)
Aux Power Cost | R | ($/kWh) | 0.21 | <-- User Input (http://www.gvea.com/rates/rates)
Makeup Water Cost | S | ($/1000 gal) | 7.17 | <-- User Input (http://www.newsminer.com/water-rates/article_11a2ba10-c211-562e-8da9-87dd16a7b104.html)
Operating Labor Rate | T | ($/hr) | 60 | Labor cost including all benefits
IPM Model - Updates to Cost and Performance for APC Technologies - Wet FGD for SO2 Control Cost Development Methodology, August 2010, prepared by Sargent & Lundy LLC for US EPA. https://www.epa.gov/sites/production/files/2015-07/documents/chapter_5_appendix_5-1a_wet_fgd.pdf
Capital Cost Calculation (2012 dollars) |  |  |  | Comments
Includes - Equipment, installation, building, foundations, electrical, minor physical/chemical waste water treatment, and a retrofit difficulty factor of 1.0
BMR ($) = 550,000*(B)*((F*G)^0.6)*((D/2)^0.02)*(A^0.716) |  | = | 28090243.9321 | Base absorber island cost
BMF ($) = 190,000*(B)*((D*G)^0.3)*(A^0.716) |  | = | 7688217.0456 | Base reagent preparation cost
BMW ($) = 100,000*(B)*((D*G)^0.45)*(A^0.716) |  | = | 3601518.991 | Base waste handling cost
BMB ($) = 1,010,000*(B)*((F*G)^0.4)*(A^0.716) |  | = | 52606787.0717 | Base balance of plan cost including: ID or booster fans, new wet chimney, piping, ductwork, minor waste water treatment, etc…
BMWW ($) = |  | = | 0 | Base wastewater treatment facility, beyond minor physical/chemcial treatment
Base Module (BM) ($) = BMR + BMF + BMW + BMB + BMWW |  | = | 91986767.0404 | Total base cost including retrofit factor
BM ($/kW) |  | = | 666.5708 | Base cost per kW
Total Project Cost
A1 = 10% of BM |  | = | 9198676.704 | Engineering and construction management costs (CC Manual)
A2 = 10% of BM |  | = | 9198676.704 | Labor adjustment for 6 x 10 hour shift premium, per diem, etc. (CC Manual)
A3 = 10% of BM |  | = | 9198676.704 | Contractor profit and fees (CC Manual)
CECC ($) - Excludes Owner's Costs = BM + A1 + A2 + A3 |  | = | 119582797.1525 | Capital, engineering, and construction costs subtotal
CECC ($/kW) - Excludes Owner's Costs = |  | = | 866.542 | Capital, engineering, and construction costst subtotal per kW
B1 = 5% of CECC |  | = | 5979139.8576 | Owner's costs including all "home office" costs (owner's engineering, management, and procurement activities)
TPC ($) - Includes Owners Costs = CECC + B1 |  | = | 125561937.0102 | Total project cost without Allowance for Funds Used During Construction (AFUDC)
TPC ($/kW) - Include Owner's Costs = |  | = | 909.8691 | Total project cost per kW without AFUDC
B2 = 10% of (CECC + B1) |  | = | 12556193.701 | AFUDC (based on a 3 year engineering and construction cycle)
TPC ($) - Includes Owner's Costs and AFUDC = CECC + B1 + B2 |  | = | 138118130.7112 | Total project cost
TPC ($/kW) - Includes Owner's Costs and AFUDC = |  | = | 1000.856 | Total project cost per kW
Wet Scrubber - Fort Wainwright
Direct Annual Costs
Fixed O&M Cost
FOMO ($/kW yr) = (6 additional operators)*(2080)*T/(A*1000) |  | = | 5.4261 | Fixed O&M additional operating labor costs
FOMM ($/kW yr) = BM*0.015/(B*A*1000) |  | = | 6.6657 | Fixed O&M additional maintenance material and labor costs
FOMA ($/kW yr) = 0.03*(FOMO+0.4*FOMM) |  | = | 0.24277 | Fixed O&M additional administrative labor costs
FOMWW ($/kW yr) = |  |  | 0 | Fixed O&M costs for wastewater treatment facility
FOM ($/kW yr) = FOMO + FOMM + FOMA + FOMWW |  | = | 12.3346 | Total Fixed O&M costs ($/kW yr)
Variable O&M Cost
VOMR ($/MWh) = K*P/A |  | = | 0.080592 | Variable O&M costs for limestone reagent
VOMW ($/MWh) = L*Q/A |  | = | 0.21893 | Variable O&M costs for waste disposal
VOMP ($/MWh) = M*R*10 |  | = | 2.4864 | Variable O&M costs for additional auxiliary power required including additional fan power (Refer to Aux Power % above)
VOMM ($/MWh) = N*S/A |  | = | 0.56803 | Variable O&M costs for makeup water
VOMWW ($/MWh) = |  | = | 0 | Variable O&M costs for wastewater treatment facility
VOM ($/MWh) = VOMR + VOMW + VOMP + VOMM + VOMWW |  | = | 3.3539 | Total Variable O&M Costs ($/MW yr)
Indirect Annual Costs
Overhead (60% of total labor and material costs) |  | = | 1021302.0495 | CC Manual
Administrative charges (2% of total capital investment) |  | = | 2762362.6142 | CC Manual
Property tax (1% of total capital investment) |  | = | 1381181.3071 | CC Manual
Insurance (1% of total capital investment) |  | = | 1381181.3071 | CC Manual
Capital Recovery Factor (CRF) = [ i (1+i)n ] / [ (1+i)n - 1 ]
i = Interest rate (%) | 5.5
n = Equipment life (years) | 15
CRF = | 0.099626 | = | 13760101.3122 | CC Manual
TOTAL INDIRECT ANNUAL OPERATING COSTS |  | = | 20306128.5901
TOTAL ANNUALIZED OPERATING COSTS (2012 $) |  | = | 26062761.9354
Composite CE Index for 2012 (cost year of equation) |  | = | 584.6
Composite CE Index for 2016 (cost year of review) |  | = | 536.4
TOTAL ANNUALIZED OPERATING COSTS (2016 $) |  | = | 23913899.251
TOTAL UNCONTROLLED SO2 EMISSIONS, tons |  | = | 1168.4736 | 15.12 | MMBtu/ton of coal, http://www.usibelli.com/coal/data-sheet
SO2 REMOVAL EFFICIENCY, % |  | = | 99 | 336000 | tons coal/year (existing permit limit)
TOTAL SO2 REMOVED, tons |  | = | 1156.7889
SO2 COST-EFFECTIVENESS, $/ton removed |  | = | 20672.6569 | Does not include costs associated with building and maintaining a wastewater treatment facility

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only