## 4-1 Available-PM
Table 4-1. Summary of Available PM2.5 Emission Control Technologies
Emission Unit |  | Emission Control Technology
ID | Description
1, 2 | Simple Cycle Gas Turbine | Low Sulfur Fuel
Low Ash Fuel
Good Combustion Practices
5, 6 | Combined Cycle Gas Turbine | Low Sulfur Fuel
Good Combustion Practices
7 | Emergency Generator Engine | Limited Operation
DPF
Low Sulfur Fuel
Low Ash Fuel
Positive Crankcase Ventilation
Good Combustion Practices
11, 12 | Propane-Fired Boiler | Low Sulfur Fuel
FGR
Good Combustion Practices
Note:
Data are based on a RBLC review from January 1, 2005 through September 15, 2015.

## 4-2 Feasible-PM
Table 4-2. Summary of Technically Feasible PM2.5 Control Technology
Emission Unit |  | Emission Control Technology
ID | Description
1, 2 | Simple Cycle Gas Turbine | Good Combustion Practices
5, 6 | Combined Cycle Gas Turbine | Good Combustion Practices
7 | Emergency Generator Engine | Limited Operation
DPF
Good Combustion Practices
11, 12 | Propane-Fired Boiler | Low Sulfur Fuel
Good Combustion Practices
Note:
Data are based on a RBLC review from January 1, 2005 through September 15, 2015.

## 4-3 Ranking-PM
Table 4-3. Ranking of Technically Feasible PM2.5 Emission Control Technology
Emission Unit |  | Emission Control Technology | Control Efficiency (pct) | PM2.5 Emissions (tpy) | PM2.5 Emission Reduction (tpy)
ID | Description
7 | Emergency Generator Engine | DPF + Limited Operation + Good Combustion Practices | 85 | 0.0053111 | 0.030096
|  | Limited Operation + Good Combustion Practices (existing) | 0 | 0.035407 | 0
11, 12 | Propane-Fired Boiler | Low Sulfur Fuel (existing) | 0 | 0.2 | 0
Note:
Data are based on a RBLC review from January 1, 2005 through September 15, 2015.

## 4-4 EU 7 DPF TCI
Table 4-4. Capital Costs for DPF
on the Diesel-Fired Engine (EU ID 7)
Shaded cells indicate user inputs.
Total Capital Investment Determination - DPF | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Emergency Generator Engine (EU ID 7) | [5 empty] | Prepared By:
Checked By:
Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | DPF
| (a) | Basic equipment
|  | Total DPF System | 1 | EA | 25954 | 25954
[8 empty] | TOTAL = | 25954
| (b) | Instrumentation
|  | Total Instrumentation |  | EA |  | 0 | Included in above price
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | DPF Freight | 1 | % MATL COST | 10% | 2595.4 | -
[8 empty] | TOTAL = | 2595.4
| (d) | Labor
|  | Labor - offsite fab | 0 | MH |  | None required | 0
|  | Labor - onsite | 16 | MH | 105 |  | 1680
[8 empty] | TOTAL = | 1680
| (e) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 0 | Days |  |  | 0
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 0 | Days |  |  | 0
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 30229.4
Direct Installation Costs (DIC) |  |  | DPF replaces existing silencer, no direct installation costs necessary |  |  |  |  | DIC = | 0
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 30229.4
INDIRECT COSTS
(2) | Engineering, Procurement & Construction Support Services |  |  | % TDC |  |  | 0 |  | Excluded in this estimate.
(3) | Performance tests |  |  | EA |  |  | 0 |  | Excluded in this estimate.
Total Indirect Costs (TIC) | [7 empty] | TIC = | 0
MANAGEMENT AND CONTINGENCY COSTS
(4) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(5) | Contingency |  |  | 30% PEC |  |  | 0 |  | Excluded in this estimate.
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 0
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 30229.4
Note on E23: Author: Vendor indicated 1 to 2 days of install time.

## 4-5 EU 7 DPF CE
Table 4-5. Annualized Costs for DPF
on the Diesel-Fired Engine (EU ID 7)
Shaded cells indicate user inputs
Cost Effectiveness Determination - DPF | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Emergency Generator Engine (EU ID 7) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  |  | MH |  |  | 0 |  | 0
(2) | DPF |  |  | MH |  |  | 0 |  | 0
(3) | Maintenance Labor |  |  | MH |  |  | 0 |  | 0
(4) | Maintenance Materials |  |  | LOT |  | 0 |  |  | 0
Total Direct Annual Costs (TDAC) |  |  |  | Excluded in this estimate |  |  |  | TDAC = | 0
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(6) | Administrative Charges |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(7) | Property tax |  |  |  |  | Excluded in this estimate.
(8) | Insurance |  |  |  |  | Excluded in this estimate.
| Capital Recovery Factor [see inputs below] |  | 0.14238
(9) | Capital Recovery | [6 empty] | CRF * TCI = | 4303.9865
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 4303.9865
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 4303.9865
Cost Effectiveness Summary
TOTAL TONS AVOIDED PER YEAR | [7 empty] | = | 0.030096
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 143008.3402
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | N/A | years
|  | Asset Utilization | N/A | %

## 4-6 Cost Effectiveness
Table 4-6. GVEA North Pole Facility - PM2.5 BACT Cost Effectiveness
Summary1 for Each Emission Unit
Control Technology Option | PM2.5 Emissions (tpy) | Total Installed Capital ($) | Total Annualized Cost ($/year) | Annual O&M Cost ($/year) | Cost Effectiveness ($/ton PM2.5 removed)
Emergency Generator Engine (EU ID 7)
DPF + Limited Operation + Good Combustion Practices | 0.0053111 | 30229.4 | 4303.9865 | ~ | 143008.3402
Limited Operation + Good Combustion Practices2 (existing) | 0.035407 | ~ | ~ | ~ | ~
Notes:
1 All emissions costs are on a per unit basis.
2 This technology is proposed as the baseline case.

## 4-7 Proposed BACT
Table 4-7. GVEA North Pole Facility - Proposed PM2.5 BACT and Associated
Emission Rate for Each Emission Unit
Emission Unit |  | Fuel | PM2.5 BACT
ID | Description |  | Description | Emission Rate1
1 | Simple Cycle Gas Turbine | Fuel Oil | Good Combustion Practices | 0.12 lb/MMBtu
2 | Simple Cycle Gas Turbine | Fuel Oil | Good Combustion Practices | 0.12 lb/MMBtu
5, 6 | Combined Cycle Gas Turbine | LSR | Good Combustion Practices | 0.12 lb/MMBtu
7 | Emergency Generator Engine | Fuel Oil | Limited Operation + Good Combustion Practices | 0.0022 lb/hp-hr
11, 12 | Boiler | Propane | Low Sulfur Fuel | 0.7 lb/103 gal
Note:
1 Emissions are on a per unit basis.
2 Each proposed BACT is an existing control technology.

## DO NOT INCLUDE - Identified-PM
Table D-1a. Summary of Identified PM2.5 Control Technology - Liquid Fuel-Fired Simple Cycle Turbines > 25 MW (RBLC 15.190)
Pollutant | Control Technology Used | Number of RBLC Entries (11 Total)
PM | None | 8
| Good Combustion Practices | 1
| Low Ash Fuel | 1
| Low Sulfur Fuel | 1
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.
Table D-1b. Summary of Identified PM2.5 Control Technology - Liquid Fuel-Fired Combined Cycle Turbines > 25 MW (RBLC 15.290)
Pollutant | Control Technology Used | Number of RBLC Entries (8 Total)
PM | Good Combustion Practices | 4
| None | 3
| Low Sulfur Fuel | 3
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.
Table D-1c. Summary of Identified PM2.5 Control Technology - Large Diesel Engines > 500 hp (RBLC 17.110)
Pollutant | Control Technology Used | Number of RBLC Entries (81 Total)
PM | Good Combustion Practices | 27
| None | 27
| Federal Standards | 13
| Limited Operation | 5
| Low Sulfur Fuel | 5
| Low Ash Fuel | 3
| Positive Crankcase Ventilation | 1
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.
Table D-1d. Summary of Identified PM2.5 Control Technology - Natural Gas-Fired Commercial/Institutional Boilers <100 MMBtu/hr (RBLC 13.310)
Pollutant | Control Technology Used | Number of RBLC Entries (65 Total)
PM | Good Control Practices | 27
| None | 25 | 54
| Low Sulfur Fuel | 19
| Operational Limit | 2
| FGR | 1
| Baghouse | 1
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.