## 1-2 Inventory Details
Table 1-2. Significant Emission Unit Potential Emission Inventory
Emission Unit |  |  | Fuel | Rating |  | Maximum |  | Allowable Annual Operation |  | Maximum Fuel |  | Construction | Life | Potential Emissions (tpy)
ID | Description | Make/Model | Type |  |  | Capacity |  |  |  | Flow Rate |  | Date | Span | NOX 1 | PM2.5 | SO2 2,3 | VOC
1 | Simple Cycle Gas Turbine | GE Frame 7, Series 7001, Model BR | Fuel Oil | 60.5 | MW | 672 | MMBtu/hr | 8760 | hr/yr | 187 | gallon/hr | 1976 | 10 years | 1600 | 35.3203 | 1486.3968 | 1.2068
2 | Simple Cycle Gas Turbine | GE Frame 7, Series 7001, Model BR | Fuel Oil | 60.5 | MW | 672 | MMBtu/hr | 7992 | hr/yr4 | 187 | gallon/hr | 1977 | 10 years | 2363.0746 | 32.2237 | 1356.0826 | 1.101
3 | Fuel Storage Tank | N/A | HAGO/LAGO/ Fuel Oil5 | 50000 | Gallons | 50000 | Gallons | 8760 | hr/yr | 187 | gallon/hr | 1995 | 10 years | 0 | 0 | 0 | 0.04
4 | Fuel Storage Tank | N/A | HAGO/LAGO/ Fuel Oil5 | 50000 | Gallons | 50000 | Gallons | 8760 | hr/yr | 187 | gallon/hr | 1995 | 10 years | 0 | 0 | 0 | 0.06
5 | Combined Cycle Gas Turbine | GE LM6000PC | GVEA LSR Turbine Fuel/GVEA Naphtha6 | 43 | MW | 455 | MMBtu/hr | 8760 | hr/yr | 187 | gallon/hr | 2005 | 10 years | 478.296 | 23.9148 | 6.0385 | 0.81709
6 | Combined Cycle Gas Turbine | GE LM6000PC | GVEA LSR Turbine Fuel/GVEA Naphtha6 | 43 | MW | 455 | MMBtu/hr | 8760 | hr/yr | 11 | gallon/hr | N/A | 10 years | 478.296 | 23.9148 | 6.0385 | 0.81709
7 | Emergency Generator Engine | Generac 5231150100 | Fuel Oil | 400 | kW | 461.6 | kW | 52 | hr/yr7 |  |  | 2005 | 10 years | 0.49892 | 0.035407 | 0.011814 | 0.040462
11 | Boiler | Bryan Steam RV500 | Gas Fuel/Propane | 5 | MMBtu/hr | 5 | MMBtu/hr | 8760 | hr/yr | 11 | gallon/hr | 2005 | 10 years | 3.1115 | 0.16754 | 0.00028721 | 0.19148
12 | Boiler | Bryan Steam RV500 | Gas Fuel/Propane | 5 | MMBtu/hr | 5 | MMBtu/hr | 8760 | hr/yr | 5.4 | gallon/hr | 2005 | 10 years | 3.1115 | 0.16754 | 0.00028721 | 0.19148
Total Potential Emissions | [13 empty] | 3969.7964 | 115.7442 | 2854.5687 | 4.4653
1 Combined emissions from EU IDs 1, 5, and 6 are limited to 1,600 tpy emissions of NOX on a 12-month rolling basis per Permit AQ0110TVP03, Condition 13. Each emission unit can operate individually up to the potential NOX emissions shown above.
2 EU IDs 1 and 2 can combust No. 1 and No. 2 fuel oil, which (by specification) can have a maximum sulfur content of 0.5 wt. pct. The two emission units may emit no more than 24,500 pounds of SO2 per day, combined,
per Permit AQ0110TVP03, Condition 14. The fuel oil sulfur content specification of 0.5 wt. pct. S is more restrictive. Each unit could be operated individually up to the potential SO2 emissions shown above.
3 EU IDs 5 and 6 are limited to a combined 12-month rolling total consumption of 1.5 million gallons of startup fuel per Permit AQ0110TVP03, Condition 16.1. Each unit could be operated individually up to that limit.
4 EU ID 2 is limited to operating no more than 7,992 hours on a 12-month rolling basis per Permit AQ0110TVP03, Condition 12.
5 HAGO and Lago are listed for completeness, but those fuels are no longer available due to the closure of the Flint Hills Refinery in North Pole.
6 GVEA LSR Turbine Fuel (LSR) is currently being combusted in EU ID 5. This fuel is obtained from directly from the Petro Star Inc. (PSI) refinery via pipeline. PSI is supplying this fuel under a long-term contract with GVEA.
7 EU ID 7 is limited to operating no more than 52 hours on a 12-month rolling basis per Permit AQ0110TVP03, Condition 10.

## 1-3 NOX
Table 1-3. Significant Emission Unit Potential NOX Emissions
Significant Emission Units |  | Factor | NOX Emission |  | Maximum |  | Maximum |  | Regulatory Limits | Existing Control Technology |  | Potential NOX
ID | Description | Reference | Factor |  | Capacity |  | Operation |  |  | Description | Efficiency (pct.) | Emissions
1 | Simple Cycle Gas Turbine | AP-42 Table 3.1-1 | 0.88 | lb/MMBtu | 672 | MMBtu/hr | 8760 | hr/yr | NA | Regenerative System | Unknown | 1600 | tpy 1
2 | Simple Cycle Gas Turbine | AP-42 Table 3.1-1 | 0.88 | lb/MMBtu | 672 | MMBtu/hr | 7992 | hr/yr2 | NA | Regenerative System | Unknown6 | 2363.0746 | tpy
3 | Fuel Storage Tank | NA | NA |  | 50000 | Gallons | 8760 | hr/yr | NA | NA |  | 0 | tpy
4 | Fuel Storage Tank | NA | NA |  | 50000 | Gallons | 8760 | hr/yr | NA | NA |  | 0 | tpy
5 | Combined Cycle Gas Turbine | AP-42 Table 3.1-1 | 0.24 | lb/MMBtu | 455 | MMBtu/hr | 8760 | hr/yr | Subpart GG 146 ppmvd at 15 pct. O2 | Water Injection | 73 3 | 478.296 | tpy 1
6 | Combined Cycle Gas Turbine | AP-42 Table 3.1-1 | 0.24 | lb/MMBtu | 455 | MMBtu/hr | 8760 | hr/yr | Subpart KKKK 74 ppm at 15 pct. O2 or 3.6 lb/MWh | Water Injection | 73 3 | 478.296 | tpy 1
7 | Emergency Generator Engine | AP-42 Table 3.3-1 | 0.031 | lb/hp-hr | 461.6 | kW | 52 | hr/yr5 | NA | Turbocharger and Aftercooler + Limited Operation | 99.4064 | 0.49892 | tpy
11 | Boiler | AP-42 Table 1.5-1 | 13 | lb/103gal | 5 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 3.1115 | tpy
12 | Boiler | AP-42 Table 1.5-1 | 13 | lb/103gal | 5 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 3.1115 | tpy
[11 empty] | Total Potential Emissions | 3969.7964 | tpy4
Sample Calculations:
Turbine Emissions, tpy= |  | (Emission factor, lb/MMBtu) * (Capacity, MMBtu/hr) * (Operation, hr/yr) / (2,000 lb/ton)
| Engine Emissions, tpy= | (Emission factor, lb/hp-hr) * (Capacity, kW) * (Conversion, 1.341 hp/kW) * (Operation, hr/yr) / (2,000 lb/ton)
Heater (Boiler) Emissions, tpy= |  | (Emission factor, lb/103gal) * (Conversion, 103gal/91.5 MMBtu) * (Capacity, MMBtu/hr) * (Operation, hr/yr) / (2,000 lb/ton)
- Propane heat content is assumed to equal 91.5 MMBtu/103 gallon per AP-42 Table 1.5-1.
Notes:
1 Combined emissions from EU IDs 1, 5, and 6 are limited to 1,600 tpy NOX emissions on a 12-month rolling basis per Permit AQ0110TVP03, Condition 13. Each unit can operate individually up to the potential emissions shown above.
2 EU ID 2 is limited to operating no more than 7,992 hours on a 12-month rolling basis per Permit AQ0110TVP03, Condition 12.
3 AP-42, Table 3.1-1 infers a control efficiency of 73 pct. for water injection. While 77 pct. was listed in recent Emission Unit Inventory submittals, 73 pct. is used in this analysis. Permit AQ0110TVP03, Condition 13.2 requires water injection for EU IDs 5 and 6.
4 Total potential emissions have been adjusted to reflect ORL restrictions.
5 EU ID 7 is limited to operating no more than 52 hours on a 12-month rolling basis per Permit AQ0110TVP03, Condition 10.
6 The EU ID 2 regenerative system was rebuilt during 2012-2013 and is expected to be more effective than the regenerative system on EU ID 1 but has not been quantified.

## 1-4 PM
Table 1-4. Significant Emission Unit Potential PM2.5 Emissions
Significant Emission Units |  | Factor | PM Emission |  | Maximum |  | Maximum |  | Regulatory Limits | Existing Control Technology |  | Potential PM2.5
ID | Description | Reference | Factor |  | Capacity |  | Operation |  |  | Description | Efficiency (pct.) | Emissions
1 | Simple Cycle Gas Turbine | AP-42 Table 3.1-2a | 0.012 | lb/MMBtu | 672 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 35.3203 | tpy
2 | Simple Cycle Gas Turbine | AP-42 Table 3.1-2a | 0.012 | lb/MMBtu | 672 | MMBtu/hr | 7992 | hr/yr1 | NA | Limited Operation | 8.7671 | 32.2237 | tpy
3 | Fuel Storage Tank | NA | NA |  | 50000 | Gallons | 8760 | hr/yr | NA | NA |  | 0 | tpy
4 | Fuel Storage Tank | NA | NA |  | 50000 | Gallons | 8760 | hr/yr | NA | NA |  | 0 | tpy
5 | Combined Cycle Gas Turbine | AP-42 Table 3.1-2a | 0.012 | lb/MMBtu | 455 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 23.9148 | tpy
6 | Combined Cycle Gas Turbine | AP-42 Table 3.1-2a | 0.012 | lb/MMBtu | 455 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 23.9148 | tpy
7 | Emergency Generator Engine | AP-42 Table 3.3-1 | 0.0022 | lb/hp-hr | 461.6 | kW | 52 | hr/yr2 | NA | Limited Operation + Positive Crankcase Ventilation | 99.4064 | 0.035407 | tpy
11 | Boiler | AP-42 Table 1.5-1 | 0.7 | lb/103gal | 5 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 0.16754 | tpy
12 | Boiler | AP-42 Table 1.5-1 | 0.7 | lb/103gal | 5 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 0.16754 | tpy
[11 empty] | Total Potential Emissions | 115.7442 | tpy
Sample Calculations:
Turbine Emissions, tpy= |  | (Emission factor, lb/MMBtu) * (Capacity, MMBtu/hr) * (Operation, hr/yr) / (2,000 lb/ton)
| Engine Emissions, tpy= | (Emission factor, lb/hp-hr) x (Capacity, kW) * (Conversion, 1.341 hp/kW) * (Operation, hr/yr) / (2,000 lb/ton)
Heater (Boiler) Emissions, tpy= |  | (Emission factor, lb/103gal) * (Conversion, 103gal/91.5 MMBtu) * (Capacity, MMBtu/hr) * (Operation, hr/yr) / (2,000 lb/ton)
- Propane heat content is assumed to equal 91.5 MMBtu/103 gallon per AP-42 Table 1.5-1.
Notes:
1 EU ID 2 is limited to operating no more than 7,992 hours on a 12-month rolling basis per Permit AQ0110TVP03, Condition 12.
2 EU ID 7 is limited to operating no more than 52 hours on a 12-month rolling basis per Permit AQ0110TVP03, Condition 10.

## 1-5 SO2
Table 1-5. Significant Emission Unit Potential SO2 Emissions
Significant Emission Units |  | Factor | Maximum Fuel |  | SO2 Emission |  | Maximum |  | Maximum |  | Regulatory Limits | Existing Control Technology |  | Potential SO2
ID | Description | Reference | Sulfur Content |  | Factor |  | Capacity |  | Operation |  |  | Description | Efficiency (pct.) | Emissions
1 | Simple Cycle Gas Turbine | AP-42 Table 3.1-2a | 0.5 | wt. pct. S1 | 0.505 | lb/MMBtu | 672 | MMBtu/hr | 8760 | hr/yr | Permit AQ0110TVP03 Combined emission limit of 24,500 lb/day1 | NA |  | 1486.3968 | tpy1
2 | Simple Cycle Gas Turbine | AP-42 Table 3.1-2a | 0.5 | wt. pct. S1 | 0.505 | lb/MMBtu | 672 | MMBtu/hr | 7992 | hr/yr2 |  | Limited Operation | 8.7671 | 1356.0826 | tpy1
3 | Fuel Storage Tank | NA | NA |  | NA |  | 50000 | Gallons | 8760 | hr/yr | NA | NA |  | 0 | tpy
4 | Fuel Storage Tank | NA | NA |  | NA |  | 50000 | Gallons | 8760 | hr/yr | NA | NA |  | 0 | tpy
5 | Combined Cycle Gas Turbine | AP-42 Table 3.1-2a (non-startup) | 0.003 | wt. pct. S3 | 0.00303 | lb/MMBtu | 455 | MMBtu/hr | 8760 | hr/yr | Subpart GG 150 ppmvd at 1 5 pct. O2 or 0.8 wt. pct. S | Low Sulfur Fuel (0.05 pct by weight) | N/A | 6.0385 | tpy
|  | Mass Balance (startup) | 0.3 | wt. pct. S4 | 0.0372 | lb/gal |  |  | 1500000 | gal/yr |  | NA |  | N/A4
|  | Total | [11 empty] | 6.0385 | tpy
6 | Combined Cycle Gas Turbine | AP-42 Table 3.1-2a (non-startup) | 0.003 | wt. pct. S3 | 0.00303 | lb/MMBtu | 455 | MMBtu/hr | 8760 | hr/yr | Subpart KKKK 0.9 lb/MWh emissions | Low Sulfur Fuel (0.05 pct by weight) | N/A | 6.0385 | tpy
|  | Mass Balance (startup) | 0.3 | wt. pct. S4 | 0.0372 | lb/gal |  |  | 1500000 | gal/yr | Subpart KKKK 0.06 lbSO2/MMBtu fuel | NA |  | N/A4
|  | Total | [11 empty] | 6.0385 | tpy
7 | Emergency Generator Engine | Mass Balance | 0.1 | wt. pct. S5 | 0.0142 | lb/gal | 32 | gal/hr6 | 52 | hr/yr7 | NA | Limited Operation | 99.4064 | 0.011814 | tpy
11 | Boiler | AP-42 Table 1.5-1 | 0.012 | wt. pct. S8 | 0.0012 | lb/103gal | 5 | MMBtu/hr | 8760 | hr/yr | NA | Low Sulfur Fuel (propane - 120 ppmv) | Unknown | 0.00028721 | tpy
12 | Boiler | AP-42 Table 1.5-1 | 0.012 | wt. pct. S8 | 0.0012 | lb/103gal | 5 | MMBtu/hr | 8760 | hr/yr | NA | Low Sulfur Fuel (propane - 120 ppmv) | Unknown | 0.00028721 | tpy
[13 empty] | Total Potential Emissions | 2854.5687 | tpy9
Sample Calculations:
Molar mass ratio is 32 lb S/mol : 64 lb SO2/mol
Stoichiometry: 1 mol S = 1 mol SO2
Mass Balance Emission Factor, lb/gal = (Molar mass ratio, 2 lb SO2:1 lb S) * (wt. pct. S in fuel) * (density of fuel, lb/gal) / 100%
Turbine Emissions (Normal Operation), tpy= |  | (Emission factor, lb/MMBtu) * (Capacity, MMBtu/hr) x (Operation, hr/yr) / (2,000 lb/ton)
Turbine Emissions (Startup), tpy= |  | (Emission factor, lb/gal) * (Throughput, gal/yr) / (2,000 lb/ton)
Engine Emissions, tpy= |  | (Emission factor, lb/gal) * (Capacity, gal/hr) * (Operation, hr/yr) / (2,000 lb/ton)
Heater (Boiler) Emissions, tpy= |  | (Emission factor, lb/103gal) * (Conversion, 103gal / 91.5 MMBtu) * (Capacity, MMBtu/hr) * (Operation, hr/yr) / (2,000 lb/ton)
wt. pct. S (in diesel) = |  | (Sulfur compound emission limit, ppmv SO2) * (Conversion, 1.66E-7 lb SO2/scf / ppm SO2) x (F-factor, 9,190 scf/MMBtu) * (Conversion, 0.0193 MMBtu/lb) * (Conversion, mole SO2/64 lb SO2) x (Conversion, mole S/mole SO2) * (Conversion, 32 lb S/ mole S)
-Turbine startup fuel is assumed to have an average density of 6.2 lb/gal. Emergency generator fuel is assumed to equal 7.1 lb/gal per note (a) of AP-42 Table 3.4-1.
- Propane heat content is assumed to equal 91.5 MMBtu/103 gallon per AP-42 Table 1.5-1.
Notes:
1 EU IDs 1 and 2 can combust No. 1 and No. 2 fuel oil, which (by specification) can have a maximum sulfur content of 0.5 wt. pct. The two emission units may emit no more than 24,500 pounds of SO2 per day, combined,
per Permit AQ0110TVP03, Condition 14. The fuel oil sulfur content specification of 0.5 wt. pct. S is more restrictive. Each unit could be operated individually up to the potential SO2 emissions shown above.
2 EU ID 2 is limited to operating no more than 7,992 hours on a 12-month rolling basis per Permit AQ0110TVP03, Condition 12.
3 The normal operating fuel for EU IDs 5 and 6 is LSR obtained from PSI under a long-term contract. The sulfur content of the LSR is limited to no more than 30 ppmw by the terms of that contract. That fuel sulfur content is used for calculating SO2 emissions from
EU IDs 5 and 6.
4 EU ID 5 is a "base-load" unit that is operated continuously for extended periods of time. EU ID 6, if constructed, will be operated in the same manner. As a result, startups on No. 1 or No. 2 fuel oil are infrequent, so potential emissions from startups are not included.
5 EU ID 7 is limited to a fuel sulfur content of 0.1 wt. pct per Permit AQ0110TVP03, Condition 9.
6 The engine specification datasheet indicates a maximum fuel throughput of 32 gal/hr.
7 EU ID 7 is limited to operating no more than 52 hours on a 12-month rolling basis per Permit AQ0110TVP03, Condition 10.
8 EU IDs 11 and 12 are limited to a fuel sulfur content of 0.012 wt. pct. per Permit AQ0110TVP03, Condition 11.
9 Total potential emissions have been adjusted to reflect annual operating hour restrictions.

## 1-6 VOC
Table 1-6. Significant Emission Unit Potential VOC Emissions
Significant Emission Units |  | Factor | VOC Emission |  | Maximum |  | Maximum |  | Regulatory Limits | Existing Control Technology |  | Potential VOC
ID | Description | Reference | Factor |  | Capacity |  | Operation |  |  | Description | Efficiency (pct.) | Emissions
1 | Simple Cycle Gas Turbine | AP-42 Table 3.1-2a | 0.00041 | lb/MMBtu | 672 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 1.2068 | tpy
2 | Simple Cycle Gas Turbine | AP-42 Table 3.1-2a | 0.00041 | lb/MMBtu | 672 | MMBtu/hr | 7992 | hr/yr1 | NA | Limited Operation | 9 | 1.101 | tpy
3 | Fuel Storage Tank | TANKS 4.0.9d | - |  | 50000 | Gallons | 8760 | hr/yr | NA | NA |  | 0.04 | tpy
4 | Fuel Storage Tank | TANKS 4.0.9d | - |  | 50000 | Gallons | 8760 | hr/yr | NA | NA |  | 0.06 | tpy
5 | Combined Cycle Gas Turbine | AP-42 Table 3.1-2a | 0.00041 | lb/MMBtu | 455 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 0.81709 | tpy
6 | Combined Cycle Gas Turbine | AP-42 Table 3.1-2a | 0.00041 | lb/MMBtu | 455 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 0.81709 | tpy
7 | Emergency Generator Engine | AP-42 Table 3.3-1 | 0.0025141 | lb/hp-hr | 461.6 | kW | 52 | hr/yr2 | NA | Limited Operation | 99.4064 | 0.040462 | tpy
11 | Boiler | AP-42 Table 1.5-1 | 0.8 | lb/103gal | 5 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 0.19148 | tpy
12 | Boiler | AP-42 Table 1.5-1 | 0.8 | lb/103gal | 5 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 0.19148 | tpy
[11 empty] | Total Potential Emissions | 4.4653 | tpy
Sample Calculations:
Turbine Emissions, tpy= |  | (Emission factor, lb/MMBtu) * (Capacity, MMBtu/hr) * (Operation, hr/yr) / (2,000 lb/ton)
| Engine Emissions, tpy= | (Emission factor, lb/hp-hr) * (Capacity, kW) * (Conversion, 1.341 hp/kW) * (Operation, hr/yr) / (2,000 lb/ton)
Heater (Boiler) Emissions, tpy= |  | (Emission factor, lb/103gal) * (Conversion, 103gal/91.5 MMBtu) * (Capacity, MMBtu/hr) * (Operation, hr/yr) / (2,000 lb/ton)
- Propane heat content is assumed to equal 91.5 MMBtu/103 gallon per AP-42 Table 1.5-1.
Notes:
1 EU ID 2 is limited to operating no more than 7,992 hours on a 12-month rolling basis per Permit AQ0110TVP03, Condition 12.
2 EU ID 7 is limited to operating no more than 52 hours on a 12-month rolling basis per Permit AQ0110TVP03, Condition 10.