## 3-1 Available-NOx
Table 3-1. GVEA North Pole Facility - Summary of Available NOX Emission Control Technologies
Emission Unit |  | Available Control Technologies
ID | Description
1, 2 | Simple Cycle Gas Turbine | SCR
Water Injection
Limited Operation
Good Combustion Practices
5, 6 | Combined Cycle Gas Turbine | SCR
Water Injection
Good Combustion Practices
7 | Emergency Generator Engine | SCR
Turbocharger and Aftercooler
FITR
ITR
Limited Operation
Good Combustion Practices
11, 12 | Propane-Fired Boiler | Low NOX
FGR
Fuel Type
Good Combustion Practices

## 3-2 Feasible-NOx
Table 3-2. GVEA North Pole Facility - Summary of Technically Feasible NOX Emission Control Technologies
Emission Unit |  | Technically Feasible Control Options
ID | Description
1, 2 | Simple Cycle Gas Turbine | SCR + Water Injection
SCR
Water Injection
Limited Operation
5, 6 | Combined Cycle Gas Turbine | SCR + Water Injection
Water Injection
7 | Emergency Generator Engine | SCR
Turbocharger + Aftercooler
Limited Operation
Good Combustion Practices
11, 12 | Propane-Fired Boiler | Low NOX
Good Combustion Practices

## 3-3 Ranking-NOx
Table 3-3. GVEA North Pole Facility - Ranking of Technically Feasible NOX Emission Control Technologies
Emission Unit |  | Control Technology Used | Control Efficiency (pct.) | NOX Emissions Per Unit (tpy) | NOX Emission Reduction (tpy)
ID | Description
1 | Simple Cycle Gas Turbine | SCR + Water Injection | 90 | 259 | 1341
|  | SCR | 85 | 388.5 | 1211.5
|  | Water Injection | 73 | 699.3 | 900.7
|  | Limited Operation (existing)1 | 38.2 | 1600 | 0
|  | Good Combustion Practices2 | 0 | 2590 | N/A
2 | Simple Cycle Gas Turbine | Limited Operation + SCR + Water Injection | 90 | 236.3 | 2126.7
|  | Limited Operation + SCR | 85 | 354.45 | 2008.55
|  | Limited Operation + Water Injection | 73 | 638.01 | 1724.99
|  | Limited Operation (existing)3 | 0 | 2363 | N/A
5, 6 | Combined Cycle Gas Turbine | SCR + Water Injection4 | 90 | 175.3767 | 302.9233
|  | Water Injection (existing)1 | 72.7273 | 478.3 | N/A
|  | Good Combustion Practices4 | 0 | 1753.7667 | N/A
7 | Emergency Generator Engine | Turbocharger and Aftercooler + Limited Operation + SCR | 90 | 0.05 | 0.45
|  | Turbocharger and Aftercooler + Limited Operation5 (existing) | 0 | 0.5 | N/A
11, 12 | Propane-Fired Boiler | Low NOX | 78 | 0.682 | 2.418
|  | Good Combustion Practices (existing) | 0 | 3.1 | N/A
Notes.
1 Combined emissions from EU IDs 1, 5, and 6 are limited to 1,600 tpy on a 12-month rolling period per Permit AQ0110TVP03, Condition 13. EU ID 1 can individually emit up to 1,600 tpy and EU IDs 5 and 6 can each individually emit up to 478.3 tpy. Note that NOX emissions from EU ID 1 are based on the control efficiency and maximum potential emissions from good combustion practices. The NOX emission reduction for all EU 1 control technologies other than good combustion practices are based on the potential NOX of 1,600 tpy.
2 Emissions from good combustion practices are included because the resulting potential emissions after applying the control efficiencies of the various emission control technologies under consideration render the existing ORL unnecessary. As a result, the PTE for the emission control technology options is based on the PTE represented by good combustion practices.
3 EU ID 2 is limited to operating no more than 7,992 hours in a 12-month rolling period by Permit AQ0110TVP03, Condition 12.
4 Emissions from good combustion practices are included to show the uncontrolled PTE. The PTE for SCR and water injection is based on a 90 percent reduction from the uncontrolled emissions, while the emissions reduction due to the addition of SCR is the difference between the PTE for water injection and the PTE for SCR and water injection.
5 EU ID 7 is limited to operating no more than 52 hours in a 12-month rolling period by Permit AQ0110TVP03, Condition 10.

## 3-4 EU 1 SCR_WI TCI
Table 3-4. GVEA North Pole Facility - Capital Costs for SCR and Water Injection on the Diesel-fired Simple Cycle Gas Turbine (EU ID 1)
Shaded cells indicate user inputs.
Total Capital Investment Determination - Water Injection + SCR | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Frame 7E CT (EU ID 1) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Water Injection1 | 1 | EA | 2000000 | 2000000
|  | SCR2,3 | 1 | EA | 5000000 | 5000000
|  | Reagent Prep/Water Treatment/Structure | 1 |  | 4669000 | 4669000 |  | TOTAL = | 11669000
| (b) | Instrumentation
|  | Total Instrumentation4 |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | Injection System Freight |  | % MATL COST |  |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab |  | MH |  |  | 0
|  | Labor - onsite |  | MH |  |  | 0
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR | 0.5% | % |  | 25000
[8 empty] | TOTAL = | 25000
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 10 | Days | 1800 |  | 18000
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 8 | Days | 2500 |  | 20000
[8 empty] | TOTAL = | 38000
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope except SCR spares and SCR vendor rep. fees |  |  |  |  | PEMC = | 11732000
(2) | Direct Installation Costs5,6
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Functional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) | [7 empty] | DIC = | 11000000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 22732000
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 22% | % TDC |  |  | 5001040
(4) | Performance tests |  | 1 | EA | 10000 |  | 10000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 5011040
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs7 |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  | 30% | % PEMC |  |  | 3519600
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 3519600
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 31262640
1 | For the water injection option, costs have been estimated to expand water treatment capacity. Consideration of source water (i.e. wells) would likely be an additional factor.
2 | Source of SCR Capital Costs: ATCO Emissions Management. These were supply-only costs given in a range for the Frame 7s. The high point of the range provided ($3 – $5 million) was used, see discussion in separately submitted CBI package.
3 | ATCO was aware that the preferred reagent was urea, however they did not specify any capital costs for reagent prep. Costs for reagent prep equipment and additional structures are discussed in a separately submitted CBI package.
4 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
5 | Construction costs associated directly with SCR installation were conservatively estimated at double the capital cost. This seems reasonable given the current footprint of the turbine building. Additional structure costs were included under part (1)(a) This should be viewed as an engineering estimate only.
6 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This is based on the assumption that some water treatment system work in addition to SCR treated water needs will be required to add water injection. This should be viewed as an engineering estimate only.
7 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
8 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements. However the reagent solutions will require continual heating to keep them in in liquid form and a notable station load compared to the unit actual operation is expected.
Note on G13: Author: GE quote
Note on G14: Author: Vendor quote
Note on E28: Author: Cost of startup spares indicated as a percentage of equipment cost per similar project.
Note on E31: Author: days based on data from similar project
Note on E32: Author: days based on data from similar project
Note on K48: Author: It has been assumed that some modification of the existing water treatment system will be needed to accommodate mulitple turbines. Assume that SCR installation costs are 2x the SCR equipment costs.
Note on E55: Author: Blended rate based on18% of SCR TDC that was used in similar project and 33% of water injection TDC based on Table 6-4 of EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines (EPA-453/R-93-007)
Note on E56: Author: Performance test for SCR system.
Note on E62: Author: Based on OAQPS Control Cost Manual standard contingency estimate.

## 3-5 EU 1 SCR_WI CE
Table 3-5. GVEA North Pole Facility - Annualized Costs for SCR and Water Injection on
the Diesel-fired Simple Cycle Gas Turbine (EU ID 1)
Shaded cells indicate user inputs
Cost Effectiveness Determination - Water Injection + SCR | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Frame 7E CT (EU ID 1) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 730 | MH | 105 |  | 76650 |  | 76650
(2) | Supervisory Labor |  | 182.5 | MH | 125 |  | 22812.5 |  | 22812.5
(3) | Maintenance Labor (water treatment) |  | 38814.7466 | 1000 GALS | 2.3704 |  | 92008.3563 |  | 92008.3563
(4) | Maintenance Labor (SCR system) |  | 365 | MH | 105 |  | 38325 |  | 38325
(5) | Maintenance Materials |  |  | LOT |  | 0 | Included in water treatment below |  | 0
(6) | Utilities
| a) | Water Use: | 30088.9509 | 1000 GALS | 1.3004 | 39126.4771 |  |  | 39126.4771
| b) | Water Pump Energy: | 91391.328 | kWh | 0.18 | 16450.439 |  |  | 16450.439
| c) | CT Fuel Use: | 42968759.1241 | GALS
| d) | Fuel Penalty: | 1218164.3212 | GALS | 1.7 | 2070879.346 |  |  | 2070879.346
| e) | Water Treatment Capacity: | 50459.1706 | 1000 GALS | 6.6711 | 336619.1434 |  |  | 336619.1434
| f) | Water Waste Disposal: | 14633.1595 | 1000 GALS | 12.9359 | 189292.7346 |  |  | 189292.7346
| g) | Urea/DEF: | 27.456 | TON | 356 | 9774.336 |  |  | 9774.336
| h) | SCR Energy Use8: |  | kWh | 0.18 | Excluded in this estimate. |  |  | 0
(7) | Catalyst Replacement Costs (every 3 years)
| (a) | Replacement of SCR Catalyst: % of total equipment cost | 30% | % total equip | 5000000 | 1500000 |  |  | 466577.4985
| (b) | Replacement labor for SCR Catalyst | 180 | MH | 105 |  | 18900 |  | 5878.8765
| (c) | Transport cost direct to site (SCR catalyst) | 13% | % replacement |  |  | 195000 |  | 60655.0748
| (d) | Transport cost for spent SCR catalyst | 13% | % replacement |  |  | 195000 |  | 60655.0748
Sinking Fund Factor [see inputs below]: |  |  | 0.31105
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 3485704.857
INDIRECT ANNUAL COSTS
(8) | Overhead |  | 30% | % WT Labor |  |  | 27602.5069 |  | 27602.5069
(9) | Administrative Charges, Property Taxes, Insurance |  | 4% | % total capital |  |  | 1250505.6 |  | 1250505.6
| Capital Recovery Factor [see inputs below] |  | 0.14238
(10) | Capital Recovery | [6 empty] | CRF * TCI = | 4451096.6119
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 5729204.7187
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 9214909.5757
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 1341
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 6871.6701
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON ACTUALS, AVOIDING 222 TONS PER YEAR)9 | [7 empty] | (TAC)/(TPY) = | 41508.6017
Data Inputs for Capital Recovery Factor & Sinking Fund Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | 3 | years
|  | Asset Utilization | 100 | %
1 | For the water injection option, costs have been estimated to expand water treatment capacity. Consideration of source water (i.e. wells) would likely be an additional factor.
2 | Source of SCR Capital Costs: ATCO Emissions Management. These were supply-only costs given in a range for the Frame 7s. The high point of the range provided ($3 – $5 million) was used, see discussion in separately submitted CBI package.
3 | ATCO was aware that the preferred reagent was urea, however they did not specify any capital costs for reagent prep. Costs for reagent prep equipment and additional structures are discussed in a separately submitted CBI package.
4 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
5 | Construction costs associated directly with SCR installation were conservatively estimated at double the capital cost. This seems reasonable given the current footprint of the turbine building. Additional structure costs were included under part (1)(a) This should be viewed as an engineering estimate only.
6 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This is based on the assumption that some water treatment system work in addition to SCR treated water needs will be required to add water injection. This should be viewed as an engineering estimate only.
7 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
8 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements. However the reagent solutions will require continual heating to keep them in in liquid form and a notable station load compared to the unit actual operation is expected.
9 | Annual average run hours for EU 1 from 2009-2016 is 833 hours, and the peak in the last four years has been 600 hours.
Note on E10: Author: Have historically used 2 hours per day for operating.
Note on G10: Author: Labor cost from similar project.
Note on E11: Author: Assumed to be half of maintenance labor.
Note on G11: Author: Labor cost from similar project.
Note on E12: Author: Water use x 1.29 to account for waste water labor as well. See table 6-5 of EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.
Note on G12: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 0.7 $/1000gal, Table 6-5, note g.
Note on E13: Author: Have historically used 1 hours per day for maintenance
Note on G13: Author: Labor cost from similar project.
Note on E16: Author: used lb water/lb fuel ratio for similarly sized GE turbine in EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines (Table 6-2)
Note on G16: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 0.384 $/1000gal, Table 6-3
Note on E17: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Use water flow of 64.8 gal/min and formula in Table 6-5.
Note on G17: Author: Current rate GVEA charges to industrial users.
Note on E18: Author: Based on 670 MMBtu/hr and fuel HHV of 137 MMBtu/1000 gals. @ 7992 hours per year.
Note on E19: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Use 3.5% of annual fuel use and water/fuel ratio of 0.81 (Table 6-2).
Note on G19: Author: EIA Monthly energy pricing report (Dec 2015).
Note on E20: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Water use plus 30% design factor and 29% waste factor.
Note on G20: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 1.97 $/1000gal, Table 6-3
Note on E21: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. 29% waste water from treatment capacity.
Note on G21: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 3.82 $/1000gal, Table 6-3
Note on E22: Author: Based on SCR controlling emissions up to 1440 tons/yr NOx after water injection, which controls up to 1232 tons/yr based on a 77% CE. 2.2 moles urea to control 1 ton NOx, 50% urea solution.
Note on G22: Author: December 2015 price according to Farmer's Coop Association.
Note on E26: Author: Miratech indicated that catalyst makes up 30% of the SCR system cost
Note on E27: Author: Replacement labor data from similar project.
Note on G27: Author: Labor cost from similar project.
Note on E28: Author: From similar project.
Note on E29: Author: From similar project.
Note on E36: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Assumes 30% of water treatment labor above.
Note on E37: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.
Note on E55: Author: Common time frame

## 3-6 EU 2 SCR_WI TCI
Table 3-6. GVEA North Pole Facility - Capital Costs for SCR and Water Injection on the
Diesel-fired Simple Cycle Gas Turbine (EU ID 2)
Shaded cells indicate user inputs.
Total Capital Investment Determination - Water Injection + SCR | [7 empty] | Date: | 2017-07-05
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Frame 7E CT (EU ID 2) | [5 empty] | Prepared By: | Lain P.
[8 empty] | Checked By: | J. Rubino
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Water Injection1 | 1 | EA | 2000000 | 2000000
|  | SCR2,3 | 1 | EA | 5000000 | 5000000
|  | Reagent Prep/Water Treatment/Structure | 1 | EA | 4669000 | 4669000 |  | TOTAL = | 11669000
| (b) | Instrumentation
|  | Total Instrumentation4 |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | Injection System Freight |  | % MATL COST |  |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab |  | MH |  |  | 0
|  | Labor - onsite |  | MH |  |  | 0
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR | 0.5% | % |  | 25000
[8 empty] | TOTAL = | 25000
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 10 | Days | 1800 |  | 18000
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 8 | Days | 2500 |  | 20000
[8 empty] | TOTAL = | 38000
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope except SCR spares and SCR vendor rep. fees |  |  |  |  | PEMC = | 11732000
(2) | Direct Installation Costs5,6
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Funtional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) | [7 empty] | DIC = | 11000000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 22732000
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 22% | % TDC |  |  | 5001040
(4) | Performance tests |  | 1 | EA | 10000 |  | 10000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 5011040
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs7 |  |  | % TDC |  |  |  |  | Excluded in this estimate.1
(6) | Contingency |  | 30% | % PEMC |  |  | 3519600
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 3519600
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 31262640
1 | For the water injection option, costs have been estimated to expand water treatment capacity. Consideration of source water (i.e. wells) would likely be an additional factor.
2 | Source of SCR Capital Costs: ATCO Emissions Management. These were supply-only costs given in a range for the Frame 7s. The high point of the range provided ($3 – $5 million) was used, see discussion in separately submitted CBI package.
3 | ATCO was aware that the preferred reagent was urea, however they did not specify any capital costs for reagent prep. Costs for reagent prep equipment and additional structures are discussed in a separately submitted CBI package.
4 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
5 | Construction costs associated directly with SCR installation were conservatively estimated at double the capital cost. This seems reasonable given the current footprint of the turbine building. Additional structure costs were included under part (1)(a) This should be viewed as an engineering estimate only.
6 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This is based on the assumption that some water treatment system work in addition to SCR treated water needs will be required to add water injection. This should be viewed as an engineering estimate only.
7 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
8 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements. However the reagent solutions will require continual heating to keep them in in liquid form and a notable station load compared to the unit actual operation is expected.
Note on G13: Author: GE quote
Note on G14: Author: Vendor quote
Note on E28: Author: Cost of startup spares indicated as a percentage of equipment cost per data from similar project.
Note on E31: Author: days based on data from similar project
Note on E32: Author: days based on data from similar project
Note on K48: Author: It has been assumed that some modiification to the existing water treatment system will be needed to accommodate multiple turbines. Assume that SCR installation costs are 2x the SCR equipment costs.
Note on E55: Author: Blended rate based on18% of SCR TDC that was used in similar project and 33% of water injection TDC based on Table 6-4 of EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines (EPA-453/R-93-007)
Note on E56: Author: Performance test for SCR system.
Note on E62: Author: Based on OAQPS Control Cost Manual standard contingency estimate.

## 3-7 EU 2 SCR_WI CE
Table 3-7. GVEA North Pole Facility - Annualized Costs for SCR and Water Injection on the Diesel-fired Simple Cycle Gas Turbine (EU ID 2)
Shaded cells indicate user inputs
Cost Effectiveness Determination - Water Injection + SCR | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Frame 7E CT (EU ID 2) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 730 | MH | 105 |  | 76650 |  | 76650
(2) | Supervisory Labor |  | 182.5 | MH | 125 |  | 22812.5 |  | 22812.5
(3) | Maintenance Labor (water treatment) |  | 35411.8099 | 1000 GALS | 2.3704 |  | 83941.8702 |  | 83941.8702
(4) | Maintenance Labor (SCR system) |  | 365 | MH | 105 |  | 38325 |  | 38325
(5) | Maintenance Materials |  |  | LOT |  | 0 | Included in water treatment below |  | 0
(6) | Utilities
| a) | Water Use: | 27451.0154 | 1000 GALS | 1.3004 | 35696.2106 |  |  | 35696.2106
| b) | Water Pump Energy: | 83378.9376 | kWh | 0.18 | 15008.2088 |  |  | 15008.2088
| c) | CT Fuel Use: | 39201635.0365 | GALS
| d) | Fuel Penalty: | 1111366.3533 | GALS | 1.7 | 1889322.8006 |  |  | 1889322.8006
| e) | Water Treatment Capacity: | 46035.3529 | 1000 GALS | 6.6711 | 307107.3281 |  |  | 307107.3281
| f) | Water Waste Disposal: | 13350.2523 | 1000 GALS | 12.9359 | 172697.2072 |  |  | 172697.2072
| g) | Urea/DEF: | 40.5504 | TON | 356 | 14435.9424 |  |  | 14435.9424
| h) | SCR Energy Use8: |  | kWh | 0.18 | Excluded in this estimate. |  |  | 0
(7) | Catalyst Replacement Costs (every 3 years)
| (a) | Replacement of SCR Catalyst: % of total equipment cost | 30% | % total equip | 5000000 | 1500000 |  |  | 466577.4985
| (b) | Replacement labor for SCR Catalyst | 180 | MH | 105 |  | 18900 |  | 5878.8765
| (c) | Transport cost direct to site (SCR catalyst) | 13% | % replacement |  |  | 195000 |  | 60655.0748
| (d) | Transport cost for spent SCR catalyst | 13% | % replacement |  |  | 195000 |  | 60655.0748
Sinking Fund Factor [see inputs below]: |  |  | 0.31105
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 3249763.5925
INDIRECT ANNUAL COSTS
(8) | Overhead |  | 30% | % WT Labor |  |  | 25182.5611 |  | 25182.5611
(9) | Administrative Charges, Property Taxes, Insurance |  | 4% | % total capital |  |  | 1250505.6 |  | 1250505.6
| Capital Recovery Factor [see inputs below] |  | 0.14238
(10) | Capital Recovery | [6 empty] | CRF * TCI = | 4451096.6119
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 5726784.7729
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 8976548.3654
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 2126.7
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 4220.8813
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON ACTUALS, AVOIDING 658 TONS PER YEAR)9 | [7 empty] | (TAC)/(TPY) = | 13642.1708
Data Inputs for Capital Recovery Factor & Sinking Fund Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | 3 | years
|  | Asset Utilization | 100 | %
1 | For the water injection option, costs have been estimated to expand water treatment capacity. Consideration of source water (i.e. wells) would likely be an additional factor.
2 | Source of SCR Capital Costs: ATCO Emissions Management. These were supply-only costs given in a range for the Frame 7s. The high point of the range provided ($3 – $5 million) was used, see discussion in separately submitted CBI package.
3 | ATCO was aware that the preferred reagent was urea, however they did not specify any capital costs for reagent prep. Costs for reagent prep equipment and additional structures are discussed in a separately submitted CBI package.
4 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
5 | Construction costs associated directly with SCR installation were conservatively estimated at double the capital cost. This seems reasonable given the current footprint of the turbine building. Additional structure costs were included under part (1)(a) This should be viewed as an engineering estimate only.
6 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This is based on the assumption that some water treatment system work in addition to SCR treated water needs will be required to add water injection. This should be viewed as an engineering estimate only.
7 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
8 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements. However the reagent solutions will require continual heating to keep them in in liquid form and a notable station load compared to the unit actual operation is expected.
9 | Annual average run hours for EU 2 from 2009-2016 is 2472 hours, and the peak in the last four years has been 2873 hours.
Note on E10: Author: Have historically used 2 hours per day for operating.
Note on G10: Author: Labor cost from similar project.
Note on E11: Author: Assumed to be half of maintenance labor.
Note on G11: Author: Labor cost from similar project
Note on E12: Author: Water use x 1.29 to account for waste water labor as well. See table 6-5 of EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.
Note on G12: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 0.7 $/1000gal, Table 6-5, note g.
Note on E13: Author: Have historically used 1 hours per day for maintenance
Note on G13: Author: Labor cost from similar project
Note on E16: Author: used fuel/water ratio for similarly sized GE turbine in EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines (Table 6-2)
Note on G16: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 0.384 $/1000gal, Table 6-3
Note on E17: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Use water flow of 64.8 gal/min and formula in Table 6-5.
Note on G17: Author: Current rate GVEA charges to industrial users.
Note on E18: Author: Based on 670 MMBtu/hr and fuel HHV of 137 MMBtu/1000 gals. @ 7992 hours per year.
Note on E19: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Use 3.5% of annual fuel use and water/fuel ratio of 0.81 (Table 6-2).
Note on G19: Author: EIA Monthly energy pricing report (Dec 2015).
Note on E20: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Water use plus 30% design factor and 29% waste factor.
Note on G20: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 1.97 $/1000gal, Table 6-3
Note on E21: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. 29% waste water from treatment capacity.
Note on G21: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 3.82 $/1000gal, Table 6-3
Note on E22: Author: Based on SCR controlling emissions up to 2126.8 tons/yr NOx after water injection, which controls up to 1819.6 tons/yr based on a 77% CE. 2.2 moles urea to control 1 ton NOx, 50% urea solution.
Note on G22: Author: December 2015 price according to Farmer's Coop Association.
Note on E26: Author: Miratech indicated that catalyst makes up 30% of the SCR system cost
Note on E27: Author: Replacement labor from similar project.
Note on G27: Author: Labor cost from similar project.
Note on E28: Author: From similar project.
Note on E29: Author: From similar project.
Note on E36: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Assumes 30% of water treatment labor above.
Note on E37: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.
Note on E55: Author: Common time frame

## 3-8 EU1 SCR TCI
Table 3-8. GVEA North Pole Facility - Capital Costs for SCR on the Diesel-fired Simple Cycle Gas Turbine (EU ID 1)
Shaded cells indicate user inputs.
Total Capital Investment Determination - SCR | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Frame 7E CTs (EU ID 1) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | SCR1,2 | 1 | EA | 5000000 | 5000000
|  | Reagent Prep/Water Treatment/Structure | 1 | EA | 4669000 | 4669000 |  | TOTAL = | 9669000
| (b) | Instrumentation
|  | Total Instrumentation3 |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (c) | Freight
|  |  |  | % MATL COST |  |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab |  | MH |  |  | 0
|  | Labor - onsite |  | MH |  |  | 0
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR | 0.5% | % |  | 25000
[8 empty] | TOTAL = | 25000
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 10 | Days | 1800 |  | 18000
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 8 | Days | 2500 |  | 20000
[8 empty] | TOTAL = | 38000
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope except SCR spares and SCR vendor rep. fees |  |  |  |  | PEMC = | 9732000
(2) | Direct Installation Costs4
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Funtional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) | [7 empty] | DIC = | 10000000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 19732000
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 18% | % TDC |  |  | 3551760
(4) | Performance tests |  | 1 | EA | 10000 |  | 10000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 3561760
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs5 |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  | 30% | % PEMC |  |  | 2919600
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 2919600
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 26213360
1 | Source of SCR Capital Costs: ATCO Emissions Management. These were supply-only costs given in a range for the Frame 7s. The high point of the range provided ($3 – $5 million) was used, see discussion in separately submitted CBI package.
2 | ATCO was aware that the preferred reagent was urea, however they did not specify any capital costs for reagent prep. Costs for reagent prep equipment and additional structures are discussed in a separately submitted CBI package.
3 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
4 | Construction costs associated directly with SCR installation were conservatively estimated at double the capital cost. This seems reasonable given the current footprint of the turbine building. Additional structure costs were included under part (1)(a) This should be viewed as an engineering estimate only.
5 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
6 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements. However the reagent solutions will require continual heating to keep them in in liquid form and a notable station load compared to the unit actual operation is expected.
7 | Indirect annual costs for operational overhead were excluded as vendor quotes did not specify overhead costs.
Note on G13: Author: Vendor quote
Note on E27: Author: Cost of startup spares indicated as a percentage of equipment cost per data from similar project.
Note on E30: Author: days based on similar project.
Note on E31: Author: days based on similar project.
Note on K47: Author: Assume that SCR installation costs are 2 x the SCR equipment costs.
Note on E53: Author: 18% was used in similar project for SCR only.
Note on E60: Author: Based on OAQPS Control Cost Manual standard contingency estimate.

## 3-9 EU1 SCR CE
Table 3-9. GVEA North Pole Facility - Annualized Costs for SCR on the Diesel-fired Simple Cycle Gas Turbine (EU ID 1)
Shaded cells indicate user inputs
Cost Effectiveness Determination - SCR | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Frame 7E CT (EU ID 1) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 730 | MH | 105 |  | 76650 |  | 76650
(2) | Supervisory Labor |  | 182.5 | MH | 125 |  | 22812.5 |  | 22812.5
(3) | Maintenance Labor (SCR system) |  | 365 | MH | 105 |  | 38325 |  | 38325
(4) | Maintenance Materials |  |  | LOT |  | 0 | Excluded in this estimate.1 |  | 0
(5) | Utilities
| a) | Urea/DEF: | 159.918 | TON | 356 | 56930.808 |  |  | 56930.808
| b) | SCR Energy Use6: |  | kWh | 0.18 | Excluded in this estimate. |  |  | 0
(6) | Catalyst Replacement Costs (every 3 years)
| (a) | Replacement of SCR Catalyst: % of total equipment cost | 30% | % total equip | 5000000 | 1500000 |  |  | 466577.4985
| (b) | Replacement labor for SCR Catalyst | 180 | MH | 105 |  | 18900 |  | 5878.8765
| (c) | Transport cost direct to site (SCR catalyst) | 13% | % replacement |  |  | 195000 |  | 60655.0748
| (d) | Transport cost for spent SCR catalyst | 13% | % replacement |  |  | 195000 |  | 60655.0748
Sinking Fund Factor [see inputs below]: |  |  | 0.31105
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 788484.8326
INDIRECT ANNUAL COSTS
(7) | Overhead7 |  |  |  |  | Excluded in this estimate. | 0 |  | 0
(8) | Administrative Charges, Property Taxes, Insurance |  | 4% | % total capital |  |  | 1048534.4 |  | 1048534.4
| Capital Recovery Factor [see inputs below] |  | 0.14238
(9) | Capital Recovery | [6 empty] | CRF * TCI = | 3732192.7349
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 4780727.1349
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 5569211.9675
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 1211.5
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 4596.9558
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON ACTUALS, AVOIDING 209 TONS PER YEAR)8 | [7 empty] | (TAC)/(TPY) = | 26646.9472
Data Inputs for Capital Recovery Factor & Sinking Fund Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | 3 | years
|  | Asset Utilization | 100 | %
1 | Source of SCR Capital Costs: ATCO Emissions Management. These were supply-only costs given in a range for the Frame 7s. The high point of the range provided ($3 – $5 million) was used, see discussion in separately submitted CBI package.
2 | ATCO was aware that the preferred reagent was urea, however they did not specify any capital costs for reagent prep. Costs for reagent prep equipment and additional structures are discussed in a separately submitted CBI package.
3 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
4 | Construction costs associated directly with SCR installation were conservatively estimated at double the capital cost. This seems reasonable given the current footprint of the turbine building. Additional structure costs were included under part (1)(a) This should be viewed as an engineering estimate only.
5 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
6 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements. However the reagent solutions will require continual heating to keep them in in liquid form and a notable station load compared to the unit actual operation is expected.
7 | Indirect annual costs for operational overhead were excluded as vendor quotes did not specify overhead costs.
8 | Annual average run hours for EU 1 from 2009-2016 is 833 hours, and the peak in the last four years has been 600 hours.
Note on E10: Author: Have historically used 2 hours per day for operating.
Note on G10: Author: Labor cost from similar project.
Note on E11: Author: Assumed to be half of maintenance labor.
Note on G11: Author: Labor cost from similar project.
Note on E12: Author: Have historically used 1 hours per day for maintenance
Note on G12: Author: Labor cost from similar project.
Note on E15: Author: Based on SCR control only. 2.2 moles urea to control 1 ton NOx, 50% urea solution.
Note on G15: Author: December 2015 price according to Farmer's Coop Association.
Note on E18: Author: Miratech indicated that catalyst makes up 30% of the SCR system cost
Note on E19: Author: Replacement labor from similar project.
Note on G19: Author: Labor cost from similar project.
Note on E20: Author: From similar project.
Note on E21: Author: From similar project.
Note on E29: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.
Note on E48: Author: Common time frame

## 3-10 EU 2 SCR TCI
Table 3-10. GVEA North Pole Facility - Capital Costs for SCR on the Diesel-fired Simple Cycle Gas Turbine (EU ID 2)
Shaded cells indicate user inputs.
Total Capital Investment Determination - SCR | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Frame 7E CT (EU ID 2) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | SCR1,2 | 1 | EA | 5000000 | 5000000
|  | Reagent Prep/Water Treatment/Structure | 1 | EA | 4669000 | 4669000 |  | TOTAL = | 9669000
| (b) | Instrumentation
|  | Total Instrumentation3 |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (c) | Freight
|  |  |  | % MATL COST |  |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab |  | MH |  |  | 0
|  | Labor - onsite |  | MH |  |  | 0
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR | 0.5% | % |  | 25000
[8 empty] | TOTAL = | 25000
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 10 | Days | 1800 |  | 18000
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 8 | Days | 2500 |  | 20000
[8 empty] | TOTAL = | 38000
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope except SCR spares and SCR vendor rep. fees |  |  |  |  | PEMC = | 9732000
(2) | Direct Installation Costs4
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Funtional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) | [7 empty] | DIC = | 10000000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 19732000
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 18% | % TDC |  |  | 3551760
(4) | Performance tests |  | 1 | EA | 10000 |  | 10000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 3561760
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs5 |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  | 30% | % PEMC |  |  | 2919600
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 2919600
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 26213360
1 | Source of SCR Capital Costs: ATCO Emissions Management. These were supply-only costs given in a range for the Frame 7s. The high point of the range provided ($3 – $5 million) was used, see discussion in separately submitted CBI package.
2 | ATCO was aware that the preferred reagent was urea, however they did not specify any capital costs for reagent prep. Costs for reagent prep equipment and additional structures are discussed in a separately submitted CBI package.
3 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
4 | Construction costs associated directly with SCR installation were conservatively estimated at double the capital cost. This seems reasonable given the current footprint of the turbine building. Additional structure costs were included under part (1)(a) This should be viewed as an engineering estimate only.
5 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
6 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements. However the reagent solutions will require continual heating to keep them in in liquid form and a notable station load compared to the unit actual operation is expected.
7 | Indirect annual costs for operational overhead were excluded as vendor quotes did not specify overhead costs.
Note on G13: Author: Vendor quote
Note on E26: Author: Cost of startup spares indicated as a percentage of equipment cost per data from similar project.
Note on E29: Author: days based on similar project
Note on E30: Author: days based on similar project
Note on K46: Author: Assume that SCR installation costs are 2 x the SCR equipment costs.
Note on E53: Author: 18% was used in similar project for SCR only.
Note on E60: Author: Based on OAQPS Control Cost Manual standard contingency estimate.

## 3-11 EU2 SCR CE
Table 3-11. GVEA North Pole Facility - Annualized Costs for SCR on the Diesel-fired Simple Cycle Gas Turbine (EU ID 2)
Shaded cells indicate user inputs
Cost Effectiveness Determination - SCR | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Frame 7E CT (EU ID 2) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 730 | MH | 105 |  | 76650 |  | 76650
(2) | Supervisory Labor |  | 182.5 | MH | 125 |  | 22812.5 |  | 22812.5
(3) | Maintenance Labor (SCR system) |  | 365 | MH | 105 |  | 38325 |  | 38325
(4) | Maintenance Materials |  |  | LOT |  | 0 | Excluded in this estimate.1 |  | 0
(5) | Utilities
| a) | Urea/DEF: | 265.1286 | TON | 356 | 94385.7816 |  |  | 94385.7816
| b) | SCR Energy Use6: |  | kWh | 0.18 | Excluded in this estimate. |  |  | 0
(6) | Catalyst Replacement Costs (every 3 years)
| (a) | Replacement of SCR Catalyst: % of total equipment cost | 30% | % total equip | 5000000 | 1500000 |  |  | 466577.4985
| (b) | Replacement labor for SCR Catalyst | 180 | MH | 105 |  | 18900 |  | 5878.8765
| (c) | Transport cost direct to site (SCR catalyst) | 13% | % replacement |  |  | 195000 |  | 60655.0748
| (d) | Transport cost for spent SCR catalyst | 13% | % replacement |  |  | 195000 |  | 60655.0748
Sinking Fund Factor [see inputs below]: |  |  | 0.31105
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 825939.8062
INDIRECT ANNUAL COSTS
(7) | Overhead7 |  | 0% |  | Excluded in this estimate. |  | 0 |  | 0
(8) | Administrative Charges, Property Taxes, Insurance |  | 4% | % total capital |  |  | 1048534.4 |  | 1048534.4
| Capital Recovery Factor [see inputs below] |  | 0.14238
(9) | Capital Recovery | [6 empty] | CRF * TCI = | 3732192.7349
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 4780727.1349
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 5606666.9411
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 2008.55
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 2791.4002
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON ACTUALS, AVOIDING 621 TONS PER YEAR)8 | [7 empty] | (TAC)/(TPY) = | 9028.4492
Data Inputs for Capital Recovery Factor & Sinking Fund Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | 3 | years
|  | Asset Utilization | 100 | %
1 | Source of SCR Capital Costs: ATCO Emissions Management. These were supply-only costs given in a range for the Frame 7s. The high point of the range provided ($3 – $5 million) was used, see discussion in separately submitted CBI package.
2 | ATCO was aware that the preferred reagent was urea, however they did not specify any capital costs for reagent prep. Costs for reagent prep equipment and additional structures are discussed in a separately submitted CBI package.
3 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
4 | Construction costs associated directly with SCR installation were conservatively estimated at double the capital cost. This seems reasonable given the current footprint of the turbine building. Additional structure costs were included under part (1)(a) This should be viewed as an engineering estimate only.
5 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
6 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements. However the reagent solutions will require continual heating to keep them in in liquid form and a notable station load compared to the unit actual operation is expected.
7 | Indirect annual costs for operational overhead were excluded as vendor quotes did not specify overhead costs.
8 | Annual average run hours for EU 2 from 2009-2016 is 2472 hours, and the peak in the last four years has been 2873 hours.
Note on E10: Author: Have historically used 2 hours per day for operating.
Note on G10: Author: Labor cost from similar project
Note on E11: Author: Assumed to be half of maintenance labor.
Note on G11: Author: Labor cost from similar project
Note on E12: Author: Have historically used 1 hours per day for maintenance
Note on G12: Author: Labor cost from similar project
Note on E15: Author: Based on SCR control only. 2.2 moles urea to control 1 ton NOx, 50% urea solution.
Note on G15: Author: December 2015 price according to Farmer's Coop Association.
Note on E18: Author: Miratech indicated that catalyst makes up 30% of the SCR system cost
Note on E19: Author: Replacement labor from similar project.
Note on G19: Author: Labor cost from similar project.
Note on E20: Author: From similar project
Note on E21: Author: From similar project
Note on E29: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.
Note on E47: Author: Common time frame

## 3-12 EU1 WI TCI
Table 3-12. GVEA North Pole Facility - Capital Costs for Water Injection on the Diesel-fired Simple Cycle Gas Turbine (EU ID 1)
Shaded cells indicate user inputs.
Total Capital Investment Determination - Water Injection | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Frame 7E CT (EU ID 1) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Water Injection1 | 1 | EA | 2000000 | 2000000
|  |  |  | EA |  | 0 |  | TOTAL = | 2000000
| (b) | Instrumentation
|  | Total Instrumentation2 |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | Injection System Freight |  | % MATL COST |  |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab |  | MH |  |  | 0
|  | Labor - onsite |  | MH |  |  | 0
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR |  | % |  | 0
[8 empty] | TOTAL = | 0
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | 0
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | 0
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor (GE) scope |  |  |  |  | PEMC = | 2000000
(2) | Direct Installation Costs3
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Functional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) | [7 empty] | DIC = | 1000000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 3000000
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 33% | % TDC |  |  | 990000
(4) | Performance tests |  | 1 | EA | 10000 |  | 10000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 1000000
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs4 |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  | 30% | % PEMC |  |  | 600000
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 600000
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 4600000
1 | For the water injection option, costs have been estimated to expand water treatment capacity. Consideration of source water (i.e. wells) would likely be an additional factor.
2 | Continuous emissions monitoring system upgrade is included in capital costs under Reagent Prep/Water Treatment/Structure.
3 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This estimate is low based on the assumption that a complete water treatment system will be required to add water injection. This should be viewed as an engineering estimate only.
4 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
5 | Operator and supervisory labor costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
Note on G13: Author: GE quote
Note on K45: Author: It has been assumed that some modification to the existing water treatment system will be needed to provide capacity for multiple turbines.
Note on E52: Author: Based on Table 6-4 of EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines (EPA-453/R-93-007), where it indicates 33% of TDC.
Note on K54: Author: It has been assumed that some modification to the existing water treatment system will be needed to provide capacity for multiple turbines
Note on E59: Author: Based on OAQPS Control Cost Manual standard contingency estimate.

## 3-13 EU1 WI CE
Table 3-13. GVEA North Pole Facility - Annualized Costs for Water Injection on the Diesel-fired Simple Cycle Gas Turbine (EU ID 1)
Shaded cells indicate user inputs
Cost Effectiveness Determination - Water Injection | [7 empty] | Date: | 2017-07-05
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Frame 7E CT (EU ID 1) | [5 empty] | Prepared By: | Lain P.
[8 empty] | Checked By: | J. Rubino
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor5 |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(2) | Supervisory Labor5 |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(3) | Maintenance Labor (water treatment) |  | 38814.7466 | 1000 GALS | 2.3704 |  | 92008.3563 |  | 92008.3563
(4) | Maintenance Materials |  |  | LOT |  | 0 | Included in water treatment below |  | 0
(5) | Utilities
| a) | Water Use: | 30088.9509 | 1000 GALS | 1.3004 | 39126.4771 |  |  | 39126.4771
| b) | Water Pump Energy: | 91391.328 | kWh | 0.18 | 16450.439 |  |  | 16450.439
| c) | CT Fuel Use: | 42968759.1241 | GALS
| d) | Fuel Penalty: | 1218164.3212 | GALS | 1.7 | 2070879.346 |  |  | 2070879.346
| e) | Water Treatment Capacity: | 50459.1706 | 1000 GALS | 6.6711 | 336619.1434 |  |  | 336619.1434
| f) | Water Waste Disposal: | 14633.1595 | 1000 GALS | 12.9359 | 189292.7346 |  |  | 189292.7346
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 2744376.4964
INDIRECT ANNUAL COSTS
(6) | Overhead |  | 30% | % WT Labor |  |  | 27602.5069 |  | 27602.5069
(7) | Administrative Charges, Property Taxes, Insurance |  | 4% | % total capital |  |  | 184000 |  | 184000
| Capital Recovery Factor [see inputs below] |  | 0.14238
(8) | Capital Recovery | [6 empty] | CRF * TCI = | 654936.5125
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 866539.0194
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 3610915.5158
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 900.7
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 4009.0102
Data Inputs for Capital Recovery Factor & Sinking Fund Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | N/A | years
|  | Asset Utilization | 100 | %
1 | For the water injection option, costs have been estimated to expand water treatment capacity. Consideration of source water (i.e. wells) would likely be an additional factor.
2 | Continuous emissions monitoring system upgrade is included in capital costs under Reagent Prep/Water Treatment/Structure.
3 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This estimate is low based on the assumption that a complete water treatment system will be required to add water injection. This should be viewed as an engineering estimate only.
4 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
5 | Operator and supervisory labor costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
Note on E12: Author: Water use x 1.29 to account for waste water labor as well. See table 6-5 of EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.
Note on G12: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 0.7 $/1000gal, Table 6-5, note g.
Note on E15: Author: used lb water/lb fuel ratio for similarly sized GE turbine in EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines (Table 6-2)
Note on G15: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 0.384 $/1000gal, Table 6-3
Note on E16: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Use water flow of 64.8 gal/min and formula in Table 6-5.
Note on G16: Author: Current rate GVEA charges to industrial users.
Note on E17: Author: Based on 670 MMBtu/hr and fuel HHV of 137 MMBtu/1000 gals. @ 8760 hours per year.
Note on E18: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Use 3.5% of annual fuel use and water/fuel ratio of 0.81 (Table 6-2).
Note on G18: Author: EIA Monthly energy pricing report (Dec 2015).
Note on E19: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Water use plus 30% design factor and 29% waste factor.
Note on G19: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 1.97 $/1000gal, Table 6-3
Note on E20: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. 29% waste water from treatment capacity.
Note on G20: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 3.82 $/1000gal, Table 6-3
Note on E25: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Assumes 30% of water treatment labor above.
Note on E26: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.

## 3-14 EU2 WI TCI
Table 3-13. GVEA North Pole Facility - Annualized Costs for Water Injection on the Diesel-fired Simple Cycle Gas Turbine (EU ID 1)
Shaded cells indicate user inputs.
Total Capital Investment Determination - Water Injection | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Frame 7E CT (EU ID 2) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Water Injection1 | 1 | EA | 2000000 | 2000000
|  |  |  | EA |  | 0 |  | TOTAL = | 2000000
| (b) | Instrumentation
|  | Total Instrumentation2 |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | Injection System Freight |  | % MATL COST |  |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab |  | MH |  |  | 0
|  | Labor - onsite |  | MH |  |  | 0
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR |  | % |  | 0
[8 empty] | TOTAL = | 0
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | 0
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | 0
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor (GE) scope |  |  |  |  | PEMC = | 2000000
(2) | Direct Installation Costs3
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Funtional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) | [7 empty] | DIC = | 1000000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 3000000
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 33% | % TDC |  |  | 990000
(4) | Performance tests |  | 1 | EA | 10000 |  | 10000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 1000000
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs4 |  |  | % TDC |  |  | Excluded in this estimate
(6) | Contingency |  | 30% | % PEMC |  |  | 600000
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 600000
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 4600000
1 | For the water injection option, costs have been estimated to expand water treatment capacity. Consideration of source water (i.e. wells) would likely be an additional factor.
2 | Continuous emissions monitoring system upgrade is included in capital costs under Reagent Prep/Water Treatment/Structure.
3 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This estimate is low based on the assumption that a complete water treatment system will be required to add water injection. This should be viewed as an engineering estimate only.
4 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
5 | Operator and supervisory labor costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
Note on G13: Author: GE quote
Note on K45: Author: It has been assumed that some modification to existing water treatment system will be needed to accommodate capacity for multiple turbines.
Note on E52: Author: Based on Table 6-4 of EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines (EPA-453/R-93-007), where it indicates 33% of TDC.
Note on K54: Author: It has been assumed that some modification to existing water treatment system will be needed to accommodate capacity for multiple turbines.
Note on E59: Author: Based on OAQPS Control Cost Manual standard contingency estimate.

## 3-15 EU2 WI CE
Table 3-15. GVEA North Pole Facility - Annualized Costs for Water Injection on the Diesel-fired Simple Cycle Gas Turbine (EU ID 2)
Shaded cells indicate user inputs
Cost Effectiveness Determination - Water Injection | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Frame 7E CT (EU ID 2) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor5 |  |  | MH |  | Excluded in this estimate | 0 |  | 0
(2) | Supervisory Labor5 |  |  | MH |  | Excluded in this estimate | 0 |  | 0
(3) | Maintenance Labor (water treatment) |  | 35411.8099 | 1000 GALS | 2.3704 |  | 83941.8702 |  | 83941.8702
(4) | Maintenance Materials |  |  | LOT |  | 0 | Included in water treatment below |  | 0
(5) | Utilities
| a) | Water Use: | 27451.0154 | 1000 GALS | 1.3004 | 35696.2106 |  |  | 35696.2106
| b) | Water Pump Energy: | 83378.9376 | kWh | 0.18 | 15008.2088 |  |  | 15008.2088
| c) | CT Fuel Use: | 39201635.0365 | GALS
| d) | Fuel Penalty: | 1111366.3533 | GALS | 1.7 | 1889322.8006 |  |  | 1889322.8006
| e) | Water Treatment Capacity: | 46035.3529 | 1000 GALS | 6.6711 | 307107.3281 |  |  | 307107.3281
| f) | Water Waste Disposal: | 13350.2523 | 1000 GALS | 12.9359 | 172697.2072 |  |  | 172697.2072
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 2503773.6255
INDIRECT ANNUAL COSTS
(6) | Overhead |  | 30% | % WT Labor |  |  | 25182.5611 |  | 25182.5611
(7) | Administrative Charges, Property Taxes, Insurance |  | 4% | % total capital |  |  | 184000 |  | 184000
| Capital Recovery Factor [see inputs below] |  | 0.14238
(8) | Capital Recovery | [6 empty] | CRF * TCI = | 654936.5125
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 864119.0736
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 3367892.6991
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 1724.99
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 1952.4129
Data Inputs for Capital Recovery Factor & Sinking Fund Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | N/A | years
|  | Asset Utilization | 100 | %
1 | For the water injection option, costs have been estimated to expand water treatment capacity. Consideration of source water (i.e. wells) would likely be an additional factor.
2 | Continuous emissions monitoring system upgrade is included in capital costs under Reagent Prep/Water Treatment/Structure.
3 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This estimate is low based on the assumption that a complete water treatment system will be required to add water injection. This should be viewed as an engineering estimate only.
4 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
5 | Operator and supervisory labor costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
Note on E12: Author: Water use x 1.29 to account for waste water labor as well. See table 6-5 of EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.
Note on G12: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 0.7 $/1000gal, Table 6-5, note g.
Note on E15: Author: used fuel/water ratio for similarly sized GE turbine in EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines (Table 6-2)
Note on G15: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 0.384 $/1000gal, Table 6-3
Note on E16: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Use water flow of 64.8 gal/min and formula in Table 6-5.
Note on G16: Author: Current rate GVEA charges to industrial users.
Note on E17: Author: Based on 670 MMBtu/hr and fuel HHV of 137 MMBtu/1000 gals. @ 7992 hours per year.
Note on E18: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Use 3.5% of annual fuel use and water/fuel ratio of 0.81 (Table 6-2).
Note on G18: Author: EIA Monthly energy pricing report (Dec 2015).
Note on E19: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Water use plus 30% design factor and 29% waste factor.
Note on G19: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 1.97 $/1000gal, Table 6-3
Note on E20: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. 29% waste water from treatment capacity.
Note on G20: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 3.82 $/1000gal, Table 6-3
Note on E25: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Assumes 30% of water treatment labor above.
Note on E26: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.

## 3-16 EU5-6 SCR_WI TCI
Table 3-16. GVEA North Pole Facility - Capital Costs for SCR on the Combined Cycle Gas Turbines (EU IDs 5 and 6)
Shaded cells indicate user inputs.
Total Capital Investment Determination - SCR | [7 empty] | Date:
Project: |  | GVEA NP - PM2.5 BACT Analysis (EU ID 5 & 6 - LM6000) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | SCR1,2,3,4,5 | 1 | EA | 1197900 | 1197900 | -
|  | Water treatment upgrades, reagent prep structure upgrades | 1 | EA | 1706000 | 1706000
[8 empty] | TOTAL = | 2903900
| (b) | Instrumentation
|  | Total Instrumentation6 |  | EA |  | Included above | -
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | SCR Freight7 | 10% | % MATL COST | 119790 | 119790 | -
[8 empty] | TOTAL = | 119790
| (d) | Labor
|  | Labor - shop fab | 2075 | MH | 68 |  | 141100
|  | Labor - onsite | 4340 | MH | 105 |  | 455700
[8 empty] | TOTAL = | 596800
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR | 0.5% | % MATL COST | 5989.5 | 5989.5 | -
[8 empty] | TOTAL = | 5989.5
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 10 | Days | 1800 |  | 18000
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 8 | Days | 2500 |  | 20000
[8 empty] | TOTAL = | 38000
Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 3664479.5
(2) | Direct Installation Costs8,9
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Funtional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) - 1 x SCR Equipment Capital | [7 empty] | DIC = | 2903900
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 6568379.5
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 18% | % TDC |  |  | 1182308.31
(4) | Performance tests |  | 1 | EA | 10000 |  | 10000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 1192308.31
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs10 |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  | 30% | % PEMC |  |  | 1099343.85
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 1099343.85
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 8860031.66
1 | Source of SCR Capital Costs: Innovative Steam Technologies (IST).
2 | The following items are included in cost of $1,197,900: SCR Catalyst Blocks, SCR Catalyst Loading Cart, SCR Catalyst Frame, Jib Crane, Complete Urea System (Dry Urea Silo, Urea Mixing Tank with the immersion heater and mixing agitator, Urea Transfer Pump unit, urea storage tank, urea feeding pump unit), Valves & Instruments required for Urea system operation, AFCU Skid including dilution air blower, Ammonia Injection Grid & Ammonia Manifold Distribution Header, Stack Cap is also included to protect the SCR catalyst from water ingress.
3 | IST also gave a quote for an aqueous ammonia-based system $ 838,200. This amount was inclusive of same equipment as above with the addition of electric heater & vaporizer chamber to the AFCU and removal of the urea system.
4 | Excluded Items: Interconnecting piping between AFCU Skid and the Ammonia Manifold Distribution Header; Interconnecting piping between the Manifold Distribution Header up to the Ammonia Injection Grid at the module injection points; Interconnecting piping between each major equipment of the Urea System.
5 | Other modifications that need to be done to the current OTSG which have not been included in the price above, is to make sure the sampling test ports upstream and downstream of the CO & SCR catalysts are existent. CEM port at the stack would be required as well and possibly some pressure test ports upstream and downstream of the SCR catalyst. The ammonia injection grid connections on the CO module casing, just above the CO catalyst would need to be made as well (there would need to be about 12, 2”NPS Sch40 BW connections that would go through the casing for the AIG lances).
6 | Continuous emissions monitoring system was not included in capital costs, though upgrades to the existing system may be needed.
7 | Based on BACT analysis costs for similar SCR installation on CTs in Alaska.
8 | For construction costs, installation was estimated at one times the capital cost. This seems reasonable given the OTSG (Turbine No. 5) has been built with enough empty duct cavity for a future SCR provision. This should be viewed as an engineering estimate only.
9 | Although we have assumed the same costs for Turbine No. 6, the footprint where the turbine and potential add-on control equipment would go is limited. There would have to be additional interaction with IST to determine how that translates into additional construction costs. There would have to be additional interaction with IST to determine how that translates into additional construction costs.
10 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
11 | Annual direct cost for maintenance matrerials were excluded as vendor quotes did not specify quantities and/or type of materials needed.
12 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements.
13 | Indirect annual costs for operational overhead were excluded as vendor quotes did not specify overhead costs.
Note on G13: Author: Vendor quote
Note on E20: Author: Based on similar BACT analysis for SCR installation on CTs
Note on E23: Author: Hours based on similar project
Note on E24: Author: Hours based on similar project
Note on E27: Author: Cost of startup spares indicated as a percentage of equipment cost per data from other project.
Note on E30: Author: days based on similar project
Note on E31: Author: days based on similar project
Note on K47: Author: Assume installation of SCR requires 1 x the SCR equipment capital because SCR duct work already exists.
Note on E54: Author: 18% was used in similar project for smaller CTs.
Note on E61: Author: Based on OAQPS Control Cost Manual standard contingency estimate.

## 3-17 EU5-6 SCR_WI CE
Table 3-17. GVEA North Pole Facility - Annualized Costs for SCR on the Combined Cycle Gas Turbines (EU IDs 5 and 6)
Shaded cells indicate user inputs
Cost Effectiveness Determination - SCR | [7 empty] | Date:
Project: |  | GVEA NP - PM2.5 BACT Analysis (EU ID 5 & 6 - LM6000) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 730 | MH | 105 |  | 76650 |  | 76650
(2) | Supervisory Labor |  | 182.5 | MH | 125 |  | 22812.5 |  | 22812.5
(3) | Maintenance Labor |  | 365 | MH | 105 |  | 38325 |  | 38325
(4) | Maintenance Materials11 |  |  | LOT |  | Excluded in this estimate.
(5) | Utilities
| (a) | Urea/DEF: | 39.9859 | TON | 356 | 14234.9733 |  |  | 14234.9733
| (b) | Energy12: |  | kWh | 0.18 | Excluded in this estimate.
(6) | Catalyst Replacement Costs (every 3 years)
| (a) | Replacement of SCR Catalyst: % of total equipment cost | 30% | % total equip | 3664479.5 | 1099343.85 |  |  | 341952.7357
| (b) | Replacement labor for SCR Catalyst | 180 | MH | 105 |  | 18900 |  | 5878.8765
| (c) | Transport cost direct to site (SCR catalyst) | 13% | % replacement |  |  | 142914.7005 |  | 44453.8556
| (d) | Transport cost for spent SCR catalyst | 13% | % replacement |  |  | 142914.7005 |  | 44453.8556
Sinking Fund Factor [see inputs below]: |  |  | 0.31105
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 588761.7967
INDIRECT ANNUAL COSTS
(7) | Overhead13 |  |  | % |  | Excluded in this estimate. | 0 |  | 0
(8) | Administrative Charges, Property Taxes, Insurance |  | 4% | % total capital |  |  | 354401.2664 |  | 354401.2664
| Capital Recovery Factor [see inputs below] |  | 0.14238
(9) | Capital Recovery | [6 empty] | CRF * TCI = | 1261469.1818
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 1615870.4482
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 2204632.245
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 302.9233
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 7277.8555
Data Inputs for Capital Recovery Factor and Sinking Fund Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | 3 | years
|  | Asset Utilization | 100 | %
1 | Source of SCR Capital Costs: Innovative Steam Technologies (IST).
2 | The following items are included in cost of $1,197,900: SCR Catalyst Blocks, SCR Catalyst Loading Cart, SCR Catalyst Frame, Jib Crane, Complete Urea System (Dry Urea Silo, Urea Mixing Tank with the immersion heater and mixing agitator, Urea Transfer Pump unit, urea storage tank, urea feeding pump unit), Valves & Instruments required for Urea system operation, AFCU Skid including dilution air blower, Ammonia Injection Grid & Ammonia Manifold Distribution Header, Stack Cap is also included to protect the SCR catalyst from water ingress.
3 | IST also gave a quote for an aqueous ammonia-based system $ 838,200. This amount was inclusive of same equipment as above with the addition of electric heater & vaporizer chamber to the AFCU and removal of the urea system.
4 | Excluded Items: Interconnecting piping between AFCU Skid and the Ammonia Manifold Distribution Header; Interconnecting piping between the Manifold Distribution Header up to the Ammonia Injection Grid at the module injection points; Interconnecting piping between each major equipment of the Urea System.
5 | Other modifications that need to be done to the current OTSG which have not been included in the price above, is to make sure the sampling test ports upstream and downstream of the CO & SCR catalysts are existent. CEM port at the stack would be required as well and possibly some pressure test ports upstream and downstream of the SCR catalyst. The ammonia injection grid connections on the CO module casing, just above the CO catalyst would need to be made as well (there would need to be about 12, 2”NPS Sch40 BW connections that would go through the casing for the AIG lances).
6 | Continuous emissions monitoring system was not included in capital costs, though upgrades to the existing system may be needed.
7 | Based on BACT analysis costs for similar SCR installation on CTs in Alaska.
8 | For construction costs, installation was estimated at one times the capital cost. This seems reasonable given the OTSG (Turbine No. 5) has been built with enough empty duct cavity for a future SCR provision. This should be viewed as an engineering estimate only.
9 | Although we have assumed the same costs for Turbine No. 6, the footprint where the turbine and potential add-on control equipment would go is limited. There would have to be additional interaction with IST to determine how that translates into additional construction costs. There would have to be additional interaction with IST to determine how that translates into additional construction costs.
10 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
11 | Annual direct cost for maintenance matrerials were excluded as vendor quotes did not specify quantities and/or type of materials needed.
12 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements.
13 | Indirect annual costs for operational overhead were excluded as vendor quotes did not specify overhead costs.
Note on E10: Author: Have historically used 2 hours per day for operating.
Note on G10: Author: Labor cost from similar project
Note on E11: Author: Assumed to be half of maintenance labor.
Note on G11: Author: Labor cost from similar project
Note on E12: Author: Have historically used 1 hours per day for maintenance
Note on G12: Author: Labor cost from similar project
Note on E15: Author: 50% urea solution and 2.2 moles needed per ton NOx controlled.
Note on G15: Author: December 2015 price according to Farmer's Coop Association.
Note on E18: Author: Miratech indicated that catalyst makes up 30% of the SCR system cost
Note on E19: Author: Replacement labor from similar project
Note on E29: Author: Percentage of total capital investment
Note on E47: Author: Common time frame

## 3-18 EU ID 7 SCR TCI
Table 3-18. GVEA North Pole Facility - Capital Costs for SCR on
the Emergency Generator Engine (EU ID 7)
Shaded cells indicate user inputs.
Total Capital Investment Determination - SCR | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Emergency Generator Engine (EU-7) | [5 empty] | Prepared By:
Checked By:
Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Total SCR System |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (b) | Instrumentation
|  | Total Instrumentation |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | SCR Freight |  | % MATL COST |  |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab |  | MH |  |  | 0
|  | Labor - onsite |  | MH |  |  | 0
[8 empty] | TOTAL = | 0
| (e ) | Startup Spares
|  | Startup Spare for SCR |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | 0
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | 0
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) |  |  | Included in vendor installed estimate |  |  |  |  | PEMC = | 0
(2) | Direct Installation Costs
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Funtional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) |  |  | Included in vendor installed estimate |  |  |  |  | DIC = | 0
Total Direct Costs (TDC) |  |  | Included in vendor installed estimate |  |  |  |  | TDC = (PEMC) + (DIC) = | 100000
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  |  | % TDC |  |  | 0 |  | Excluded in this estimate.
(4) | Performance tests |  |  | EA |  |  | 0 |  | Excluded in this estimate.
Total Indirect Costs (TIC) | [7 empty] | TIC = | 0
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  |  | 30% PEC |  |  | 0 |  | Excluded in this estimate.
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 0
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 100000
Note on K49: Author: Miratech (vendor) quote

## 3-19 EU ID 7 SCR CE
Table 3-19. GVEA North Pole Facility - Annualized Costs for SCR on
the Emergency Generator Engine (EU ID 7)
Shaded cells indicate user inputs
Cost Effectiveness Determination - SCR | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Emergency Generator Engine (EU-7) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  |  | MH |  |  | 0 |  | 0
(2) | Supervisory Labor |  |  | MH |  |  | 0 |  | 0
(3) | Maintenance Labor |  |  | MH |  |  | 0 |  | 0
(4) | Maintenance Materials |  |  | LOT |  | 0 |  |  | 0
Total Direct Annual Costs (TDAC) |  |  |  | Excluded in this estimate. |  |  |  | TDAC = | 0
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(6) | Administrative Charges |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(7) | Property tax |  |  |  |  | Excluded in this estimate.
(8) | Insurance |  |  |  |  | Excluded in this estimate.
| Capital Recovery Factor [see inputs below] |  | 0.14238
(9) | Capital Recovery | [6 empty] | CRF * TCI = | 14237.7503
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 14237.7503
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 14237.7503
Cost Effectiveness Summary
TOTAL TONS AVOIDED PER YEAR | [7 empty] | = | 0.45
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 31639.4451
Data Inputs for Capital Recovery Factor and Sinking Fund Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life (Excluded) |  | years
|  | Asset Utilization (Excluded) |  | %

## 3-20 EU ID 11 & 12 LNB CE
Table 3-20 GVEA North Pole Facility - Capital Costs for Low NOX Burner on
the Propane-fired Boilers (EU IDs 11 and 12)
Shaded cells indicate user inputs.
Total Capital Investment Determination - Low NOX Burners | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Bryan Steam Boiler (EUs ID 11 and 12, cost per boiler) | [5 empty] | Prepared By:
Checked By:
Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Low NOx Burner Retrofit for Bryan RV500 Boiler, Unit 11 | 1 | EA | 21500 | 21500
[8 empty] | TOTAL = | 21500
| (b) | Instrumentation
|  | Total Instrumentation |  | EA |  | Included in above price
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | Freight for burners included in installation costs |  | % MATL COST |  | Included in above price | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab | 0 | MH |  | None required | 0
|  | Labor - onsite | 0 | MH | 0 | Included in installation cost | 0
[8 empty] | TOTAL = | 0
| (e) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 0 | Days |  | None required | 0
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 0 | Days |  | None required | 0
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 21500
Direct Installation Costs (DIC) | [7 empty] | DIC = | 15000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 36500
INDIRECT COSTS
(2) | Engineering, Procurement & Construction Support Services |  |  | % TDC |  |  | 0 |  | Excluded in this estimate.
(3) | Performance tests |  |  | EA |  |  | 0 |  | Excluded in this estimate.
Total Indirect Costs (TIC) | [7 empty] | TIC = | 0
MANAGEMENT AND CONTINGENCY COSTS
(4) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(5) | Contingency |  | 10% | % PEC |  |  | 2150
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 2150
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 38650
Note on G13: Author: Supplier (Proctor Sales) email dated 2/1/16: cost for RS Low NOx burner = $21,500, capable of 30 ppm NOx
Note on K31: Author: Supplier (Proctor Sales) email dated 11/5/2015: cost for install is $15K.
Note on E45: Author: Even though EPA allows for 30%, 10% is considered a conservative estimate based on lower risk for a LNB installation.

## 3-21 EU ID 11 & 12 LNB CE
Table 3-21. GVEA North Pole Facility - Annualized Costs for Low NOX Burner on
the Propane-fired Boilers (EU IDs 11 and 12)
Shaded cells indicate user inputs
Cost Effectiveness Determination - Low NOX Burners | [7 empty] | Date:
Project: |  | GVEA North Pole PM2.5 BACT Analysis - Bryan Steam Boiler (EU IDs 11 and 12, cost per boiler) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  |  | MH |  |  | 0 |  | 0
(2) | Supervisory Labor |  |  | MH |  |  | 0 |  | 0
(3) | Maintenance Labor |  |  | MH |  |  | 0 |  | 0
(4) | Maintenance Materials |  |  | LOT |  | 0 |  |  | 0
Total Direct Annual Costs (TDAC) |  |  |  | Excluded in this estimate |  |  |  | TDAC = | 0
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(6) | Administrative Charges |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(7) | Property tax |  |  |  |  | Excluded in this estimate.
(8) | Insurance |  |  |  |  | Excluded in this estimate.
| Capital Recovery Factor [see inputs below] |  | 0.14238
(9) | Capital Recovery | [6 empty] | CRF * TCI = | 5502.8905
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 5502.8905
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 5502.8905
Cost Effectiveness Summary
TOTAL TONS AVOIDED PER YEAR | [7 empty] | = | 2.418
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 2275.8025
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | N/A | years
|  | Asset Utilization | N/A | %

## Table 3-22
Table 3-22. GVEA North Pole Facility - NOX BACT Cost Effectiveness
Summary1 for Each Emission Unit
Control Technology | NOX Emissions (tpy) | Total Installed Capital ($) | Total Annualized Cost ($/year) | Total Direct Annual Cost ($/year) | Cost Effectiveness ($/ton NOX removed based on PTE) | Incremental Cost Effectiveness2 ($/incremental ton removed)
Simple Cycle Gas Turbine (EU ID 1)
SCR + Water Injection3 | 259 | 31262640 | 9214909.5757 | 3485704.857 | 6871.6701 | 28152.1051
SCR3 | 388.5 | 26213360 | 5569211.9675 | 788484.8326 | 4596.9558 | 6300.8251
Water Injection3 | 699.3 | 4600000 | 3610915.5158 | 2744376.4964 | 4009.0102 | ~
Limited Operation (existing)4 | 1600 | ~ | ~ | ~ | ~ | ~
Simple Cycle Gas Turbine (EU ID 2)
SCR + Water Injection3 | 236.3 | 31262640 | 8976548.3654 | 3249763.5925 | 4220.8813 | 28522.0603
SCR3 | 354.45 | 26213360 | 5606666.9411 | 825939.8062 | 2791.4002 | 7895.24
Water Injection3 | 638.01 | 4600000 | 3367892.6991 | 2503773.6255 | 1952.4129 | ~
Limited Operation (existing)4 | 2363 | ~ | ~ | ~ | ~ | ~
Combined Cycle Gas Turbines (EU IDs 5 and 6, cost per combustion turbine)
SCR + Water Injection3 | 175.3767 | 8860031.66 | 2204632.245 | 588761.7967 | 7277.8555 | ~
Water Injection (existing)4 | 478.3 | ~ | ~ | ~ | ~ | ~
Emergency Generator Engine (EU ID 7)
Turbocharger and Aftercooler + Limited Operation + SCR | 0.05 | 100000 | 14237.7503 | ~ | 31639.4451 | 31639.4451
Turbocharger and Aftercooler + Limited Operation (existing)4 | 0.5 | ~ | ~ | ~ | ~ | ~
Propane-fired Boilers (EU IDs 11 and 12, cost per boiler)
Low NOX | 0.682 | 38650 | 5502.8905 | ~ | $2,276 (>$78,000 based on actual emissions from 2014 and 2015)
Good Combustion Practices (existing)4 | 3.1 | ~ | ~ | ~ | ~ | ~
Notes:
1 All emissions costs are on a per unit basis.
2 Incremental Cost Effectiveness is calculated as follows: [(Annualized Cost of Control Option)-(Annualized Cost of Next Control Option)]/[(Emissions of Next Control Option)-(Emissions of Control Option)]
3 The cost for this technology is underestimated because cost estimates for certain essential equipment and operating needs are not available or included. Site space constraints may make these technologies not feasible.
4 This technology is proposed as the baseline case.

## Table - 3-23
Table 3-23. GVEA North Pole Facility - Proposed NOX BACT and Associated
Emission Rate for Each Emission Unit
Emission Unit |  | Fuel | NOX BACT
ID | Description |  | Description | Emission Rate1
1 | Simple Cycle Gas Turbine | Fuel Oil | Limited Operation (existing) | 0.88 lb/MMBtu
2 | Simple Cycle Gas Turbine | Fuel Oil | Limited Operation (existing) | 0.88 lb/MMBtu
5, 6 | Combined Cycle Gas Turbine | LSR | Water Injection (existing) | 0.24 lb/MMBtu
7 | Emergency Generator Engine | Fuel Oil | Turbocharger and Aftercooler + Limited Operation (existing) | 0.0022 lb/hp-hr
11, 12 | Boiler | Propane | Good Combustion Practices (existing) | 13 lb/kgal
Notes:
1 Emissions are on a per unit basis.

## DO NOT INCLUDE - Identified-NOx
Table A-1a. Summary of Identified NOX Control Technology - Liquid Fuel-Fired Simple Cycle Turbines > 25 MW (RBLC 15.190)
Pollutant | Control Technology Used | Number of RBLC Entries (13 Total)
NOX | Water Injection | 6
| None | 4
| SCR | 2
| Low NOX | 2
| Good Combustion Practices | 2
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.
Table A-1b. Summary of Identified NOX Control Technology - Liquid Fuel-Fired Combined Cycle Turbines > 25 MW (RBLC 15.290)
Pollutant | Control Technology Used | Number of RBLC Entries (10 Total)
NOX | SCR | 6
| Water Injection | 5
| None | 2
| Operational Limit | 1
| Dry Low NOX | 1
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.
Table A-1c. Summary of Identified NOX Control Technology - Large Diesel Engines > 500 hp (RBLC 17.110)
Pollutant | Control Technology Used | Number of RBLC Entries (67 Total)
NOX | Federal Standards | 17
| None | 15
| Good Combustion Practices | 10
| Limited Operation | 8
| Turbocharger and Aftercooler | 6
| Ignition Timing Retard | 5
| Fuel Injection Timing Retard | 3
| SCR | 2
| Turbocharger | 2
| Reduce NOX by 90 Percent | 1
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.
Table A-1d. Summary of Identified NOX Control Technology - Natural Gas-Fired Commercial/Institutional Boilers <100 MMBtu/hr (RBLC 13.310)
Pollutant | Control Technology Used | Number of RBLC Entries (99 Total)
NOX | Low NOX | 51
| FGR | 22
| Ultra Low NOX | 18
| None | 16
| Good Combustion Practices | 8
| SCR | 6
| Limited Operation | 4
| Fuel Type | 3
| Scrubber | 1
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.