## 1-2 - Inventory Details
Table 1-2. Significant Emission Unit Potential Emission Inventory
Emission Unit |  |  | Fuel | Rating |  | Maximum |  | Maximum |  | Maximum Fuel |  | Construction | Life Span | Potential Emissions (tpy)
ID | Description | Make/Model | Type |  |  | Capacity |  | Operation |  | Flow Rate |  | Date |  | NOX | PM2.5 | SO2 1
1 | Simple Cycle Combustion Gas Turbine | General Electric Frame 5 MS 5001-M | Fuel Oil | 18.4 | MW | 268 | MMBtu/hr | 8760 | hr/yr | 187 | gallon/hr | 1971 | 10 years | 1032.9792 | 14.0861 | 580
2 | Simple Cycle Combustion Gas Turbine | General Electric Frame 5 MS 5001-M | Fuel Oil | 18.4 | MW | 268 | MMBtu/hr | 8760 | hr/yr | 187 | gallon/hr | 1972 | 10 years | 1032.9792 | 14.0861 | 580
3 | Diesel Generator Engine | General Motors Electro-Motive Diesel 20-645E4 | Diesel | 2.75 | MW | 28 | MMBtu/hr | 500 | hr/yr3 | 187 | gallon/hr | 1970 | 10 years | 22.4 | 0.7 | 3.7097
4 | Diesel Generator Engine | General Motors Electro-Motive Diesel 20-645E4 | Diesel | 2.75 | MW | 28 | MMBtu/hr | 500 | hr/yr3 | 187 | gallon/hr | 1970 | 10 years | 22.4 | 0.7 | 3.7097
10 | Boiler | Weil McLain H-688 | Diesel | 1.7 | MMBtu/hr | 1.7 | MMBtu/hr | 8760 | hr/yr | 11 | gallon/hr | 2012-01-22 | 10 years | 1.0868 | 0.11574 | 3.858
11 | Boiler | Weil McLain H-688 | Diesel | 1.7 | MMBtu/hr | 1.7 | MMBtu/hr | 8760 | hr/yr | 5.4 | gallon/hr | 2012-01-22 | 10 years | 1.0868 | 0.11574 | 3.858
Total Potential Emissions | [13 empty] | 2112.9319 | 29.8036 | 580
1 Combined emissions from EU IDs 1 through 4, 10, and 11 are limited to 580 tpy SO2 on a 12-month rolling basis per Permit AQ0109TVP03 Condition 9. Each emission unit can operate individually up to the potential emissions shown above. The total potential emissions reflect the operating limit.
2 EU IDs 1 through 4 are limited to a fuel sulfur content of 1 wt. pct. per Permit AQ0109TVP03 Condition 10. EU IDs 1 through 4, 10, and 11 combust No. 1 and No. 2 fuel oil,which (by specification) can have a maximum sulfur content of 0.5 wt. pct.
3 EU IDs 3 and 4 are emergency engines. Potential emissions are based on 500 hours of annual operation per EPA guidance.

## 1-3 - NOX
Table 1-3. Significant Emission Unit Potential NOX Emissions
Emission Unit |  | Factor | NOX Emission |  | Maximum |  | Maximum |  | Regulatory Limits | Existing Control Technology |  | Potential NOX
ID | Description | Reference | Factor |  | Capacity |  | Operation |  |  | Description | Efficiency | Emissions
1 | Simple Cycle Combustion Gas Turbine | AP-42 Table 3.1-1 | 0.88 | lb/MMBtu | 268 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 1032.9792 | tpy
2 | Simple Cycle Combustion Gas Turbine | AP-42 Table 3.1-1 | 0.88 | lb/MMBtu | 268 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 1032.9792 | tpy
3 | Diesel Generator Engine | AP-42 Table 3.4-1 | 3.2 | lb/MMBtu | 28 | MMBtu/hr | 500 | hr/yr1 | NA | Turbocharger and Aftercooler | Unknown | 22.4 | tpy
4 | Diesel Generator Engine | AP-42 Table 3.4-1 | 3.2 | lb/MMBtu | 28 | MMBtu/hr | 500 | hr/yr1 | NA | Turbocharger and Aftercooler | Unknown | 22.4 | tpy
10 | Boiler | AP-42 Table 1.3-1 | 20 | lb/103gal | 1.7 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 1.0868 | tpy
11 | Boiler | AP-42 Table 1.3-1 | 20 | lb/103gal | 1.7 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 1.0868 | tpy
[11 empty] | Total Potential Emissions | 2112.9319 | tpy
Sample Calculations:
Turbine and Engine Emissions, tpy= |  | (Emission factor, lb/MMBtu) * (Capacity, MMBtu/hr) * (Operation, hr/yr) / (2,000 lb/ton)
Boiler Emissions, tpy= |  | (Emission factor, lb/103gal) / (Conversion 1,000 gal/103gal) * (Capacity, MMBtu/hr) x (Conversion, 1,000,000 Btu/MMBtu) / (Conversion, 19,300 Btu/lb) / (Conversion 7.1 lb/gal) * (Operation, hr/yr) / (2,000 lb/ton)
Notes:
1 EU IDs 3 and 4 are emergency engines. Potential emissions are based on 500 hours of annual operation per EPA guidance.
2 Diesel fuel heat content is assumed to equal 19,300 Btu/lb and diesel fuel density is assumed to equal 7.1 lb/gal per note (a) of AP-42 Table 3.4-1.

## 1-4 - PM
Table 1-4. Significant Emission Unit Potential PM2.5 Emissions
Emission Unit |  | Factor | PM Emission |  | Maximum |  | Maximum |  | Regulatory Limits | Existing Control Technology |  | Potential PM
ID | Description | Reference | Factor |  | Capacity |  | Operation |  |  | Description | Efficiency | Emissions
1 | Simple Cycle Combustion Gas Turbine | AP-42 Table 3.1-2a | 0.012 | lb/MMBtu | 268 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 14.0861 | tpy
2 | Simple Cycle Combustion Gas Turbine | AP-42 Table 3.1-2a | 0.012 | lb/MMBtu | 268 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 14.0861 | tpy
3 | Diesel Generator Engine | AP-42 Table 3.4-1 | 0.1 | lb/MMBtu | 28 | MMBtu/hr | 500 | hr/yr1 | NA | NA |  | 0.7 | tpy
4 | Diesel Generator Engine | AP-42 Table 3.4-1 | 0.1 | lb/MMBtu | 28 | MMBtu/hr | 500 | hr/yr1 | NA | NA |  | 0.7 | tpy
10 | Boiler | AP-42 Tables 1.3-2 & 1.3-7 | 2.13 | lb/103gal | 1.7 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 0.11574 | tpy2
11 | Boiler | AP-42 Tables 1.3-2 & 1.3-7 | 2.13 | lb/103gal | 1.7 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 0.11574 | tpy2
[11 empty] | Total Potential Emissions | 29.8036 | tpy
Sample Calculations:
Turbine and Engine Emissions, tpy= |  | (Emission factor, lb/MMBtu) * (Capacity, MMBtu/hr) * (Operation, hr/yr) / (2,000 lb/ton)
Boiler Emissions, tpy= |  | (Emission factor, lb/103gal) / (Conversion 1,000 gal/103gal) * (Capacity, MMBtu/hr) x (Conversion, 1,000,000 Btu/MMBtu) / (Conversion, 19,300 Btu/lb) / (Conversion 7.1 lb/gal) * (Operation, hr/yr) / (2,000 lb/ton)
Notes:
1 EU IDs 3 and 4 are emergency engines. Potential emissions are based on 500 hours of annual operation per EPA guidance.
2 Includes both filterable and condensable particulate matter emissions.
3 Diesel fuel heat content is assumed to equal 19,300 Btu/lb and diesel fuel density is assumed to equal 7.1 lb/gal per note (a) of AP-42 Table 3.4-1.

## 1-5 - SO2
Table 1-5. Significant Emission Unit Potential SO2 Emissions
Emission Unit |  | Factor | Maximum Fuel |  | SO2 Emission |  | Maximum |  | Maximum |  | Regulatory Limits | Existing Control Technology |  | Potential SO2
ID | Description | Reference | Sulfur Content |  | Factor |  | Capacity |  | Operation |  |  | Description | Efficiency | Emissions
1 | Simple Cycle Combustion Gas Turbine | AP-42 Table 3.1-2a | 0.5 | wt. pct. S1 | 0.505 | lb/MMBtu | 268 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 580 | tpy2
2 | Simple Cycle Combustion Gas Turbine | AP-42 Table 3.1-2a | 0.5 | wt. pct. S1 | 0.505 | lb/MMBtu | 268 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 580 | tpy2
3 | Diesel Generator Engine | Mass Balance | 0.5 | wt. pct. S1 | 0.071 | lb/gal | 209 | gal/hr3 | 500 | hr/yr4 | NA | NA |  | 3.7097 | tpy2
4 | Diesel Generator Engine | Mass Balance | 0.5 | wt. pct. S1 | 0.071 | lb/gal | 209 | gal/hr3 | 500 | hr/yr4 | NA | NA |  | 3.7097 | tpy2
10 | Boiler | AP-42 Table 1.3-1 | 0.5 | wt. pct. S5 | 71 | lb/103gal | 1.7 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 3.858 | tpy
11 | Boiler | AP-42 Table 1.3-1 | 0.5 | wt. pct. S5 | 71 | lb/103gal | 1.7 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 3.858 | tpy
[13 empty] | Total Potential Emissions | 580 | tpy6
Sample Calculations:
Molar mass ratio is 32 lb S/mol : 64 lb SO2/mol
Stoichiometry: 1 mol S = 1 mol SO2
Mass Balance Emission Factor, lb/gal = (Molar mass ratio, 2 lb SO2:1 lb S) * (wt. pct. S in fuel) x (density of fuel, lb/gal) / 100%
Turbine Emissions, tpy= |  | (Emission factor, lb/MMBtu) * (Capacity, MMBtu/hr) x (Operation, hr/yr) / (2,000 lb/ton)
Engine Emissions, tpy= |  | (Emission factor, lb/gal) * (Capacity, gal/hr) x (Operation, hr/yr) / (2,000 lb/ton)
Boiler Emissions, tpy= |  | (Emission factor, lb/103gal) / (Conversion 1,000 gal/103gal) * (Capacity, MMBtu/hr) x (Conversion, 1,000,000 Btu/MMBtu) / (Conversion, 19,300 Btu/lb) / (Conversion 7.1 lb/gal) * (Operation, hr/yr) / (2,000 lb/ton)
wt. pct. S= |  | (Sulfur compound emission limit, ppmv SO2) * (Conversion, 1.66E-7 lb SO2/scf / ppm SO2) * (F-factor, 9,190 scf/MMBtu) x (Conversion, 0.0193 MMBtu/lb) * (Conversion, mole SO2/64 lb SO2) x (Conversion, mole S/mole SO2) * (Conversion, 32 lb S/ mole S)
Notes:
1 EU IDs 1 through 4 are limited to a fuel sulfur content of 1 wt. pct. per Permit AQ0109TVP03 Condition 10. EU IDs 1 through 4, 10, and 11 combust No. 1 and No. 2 fuel oil,which (by specification) can have a maximum sulfur content of 0.5 wt. pct.
(The fuel oil sulfur content specification of 0.5 wt. pct. S is more restrictive for EU IDs 1 through 4.)
2 Combined emissions from EU IDs 1 through 4 and 10 through 11 are limited to 580 tpy on a 12-month rolling basis per Permit AQ0109TVP03 Condition 9. Each unit can operate individually up to the potential emissions shown above.
3 The renewal application for Permit AQ0109TVP02 states a maximum fuel throughput of 209 gal/hr.
4 EU IDs 3 and 4 are emergency engines. Potential emissions are based on 500 hours of annual operation per EPA guidance.
5 A fuel sulfur content of 0.5 wt. pct. is assumed for EU IDs 10 and 11 because the use of ULSD is not required by a permit condition.
6 Total potential emissions reflect the operating limit.
7 Diesel fuel heat content is assumed to equal 19,300 Btu/lb and diesel fuel density is assumed to equal 7.1 lb/gal per note (a) of AP-42 Table 3.4-1.

## 1-6 - VOC
Table 1-6. Significant Emission Unit Potential VOC Emissions
Emission Unit |  | Factor | VOC Emission |  | Maximum |  | Maximum |  | Regulatory Limits | Existing Control Technology |  | Potential VOC
ID | Description | Reference | Factor |  | Capacity |  | Operation |  |  | Description | Efficiency | Emissions
1 | Simple Cycle Combustion Gas Turbine | AP-42 Table 3.1-1 | 0.00041 | lb/MMBtu | 268 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 0.48127 | tpy
2 | Simple Cycle Combustion Gas Turbine | AP-42 Table 3.1-1 | 0.00041 | lb/MMBtu | 268 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 0.48127 | tpy
3 | Diesel Generator Engine | AP-42 Table 3.4-1 | 0.09 | lb/MMBtu | 28 | MMBtu/hr | 500 | hr/yr1 | NA | Turbocharger and Aftercooler | Unknown | 0.63 | tpy
4 | Diesel Generator Engine | AP-42 Table 3.4-1 | 0.09 | lb/MMBtu | 28 | MMBtu/hr | 500 | hr/yr1 | NA | Turbocharger and Aftercooler | Unknown | 0.63 | tpy
10 | Boiler | AP-42 Table 1.3-3 | 0.34 | lb/103gal | 1.7 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 0.018475 | tpy
11 | Boiler | AP-42 Table 1.3-3 | 0.34 | lb/103gal | 1.7 | MMBtu/hr | 8760 | hr/yr | NA | NA |  | 0.018475 | tpy
[11 empty] | Total Potential Emissions | 2.2595 | tpy
Sample Calculations:
Turbine and Engine Emissions, tpy= |  | (Emission factor, lb/MMBtu) * (Capacity, MMBtu/hr) * (Operation, hr/yr) / (2,000 lb/ton)
Boiler Emissions, tpy= |  | (Emission factor, lb/103gal) / (Conversion 1,000 gal/103gal) * (Capacity, MMBtu/hr) * (Conversion, 1,000,000 Btu/MMBtu) / (Conversion, 19,300 Btu/lb) / (Conversion 7.1 lb/gal) * (Operation, hr/yr) / (2,000 lb/ton)
Notes:
1 EU IDs 3 and 4 are emergency engines. Potential emissions are based on 500 hours of annual operation per EPA guidance.
2 Diesel fuel heat content is assumed to equal 19,300 Btu/lb and diesel fuel density is assumed to equal 7.1 lb/gal per note (a) of AP-42 Table 3.4-1.