## 3-1 NOx Available
Table 3-1. GVEA - Zehnder Facility - Summary of Available NOX Emission Control Technologies
Emission Unit |  | Available Emission Control Technologies
ID | Description
1, 2 | Simple Cycle Gas Turbine | SCR
Water Injection
Good Combustion Practices
3, 4 | Diesel-fired Generator Engine | SCR
Turbocharger and Aftercooler
FITR
ITR
Limited Operation
Good Combustion Practices
11, 12 | Diesel-fired Boiler | LNB
FGR
Good Combustion Practices

## 3-2 NOx Feasible
Table 3-2. GVEA - Zehnder Facility - Summary of Technically Feasible NOX Emission Control Technology
Emission Unit |  | Techncially Feasible Emission Control Technologies
ID | Description
1,2 | Simple Cycle Gas Turbine | SCR + Water Injection
SCR
Water Injection
Good Combustion Practices
3, 4 | Diesel-fired Generator Engine | SCR
Turbocharger and Aftercooler
Limited Operation
Good Combustion Practices
11, 12 | Diesel-fired Boiler | LNB
Good Combustion Practices

## 3-3 NOx Ranking
Table 3-3. GVEA - Zehnder Facility - Ranking of Technically Feasible NOX Emission Control Technology
Emission Unit |  | Emission Control Technology | Control Efficiency (pct) | NOX Emissions Per Unit (tpy) | NOX Emission Reduction (tpy)
ID | Description
1, 2 | Simple Cycle Gas Turbine | SCR + Water Injection | 90 | 103.3 | 929.7
|  | SCR | 85 | 154.95 | 878.05
|  | Water Injection | 73 | 278.91 | 754.09
|  | Good Combustion Practices (existing) | 0 | 1033 | 0
3, 4 | Diesel-fired Generator Engine | Turbocharger and Aftercooler + Limited Operation + SCR | 80 | 4.48 | 17.92
|  | Turbocharger and Aftercooler + Limited Operation (existing) | 0 | 22.4 | 0
11, 12 | Diesel-fired Boiler | LNB | 33.6364 | 0.73 | 0.37
|  | Good Combustion Practices (existing) | 0 | 1.1 | 0

## 3-4 EU 1&2 SCR_WI TCI
Table 3-4. GVEA - Zehnder Facility - Capital Costs for SCR and Water Injection on the Simple Cycle Gas Turbines (EU IDs 1 and 2)
Shaded cells indicate user inputs.
Total Capital Investment Determination - Water Injection + SCR | [7 empty] | Date:
Project: |  | GVEA Zehnder PM2.5 BACT Analysis - Frame 5 CTs (EU ID 1 and 2, cost per turbine) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Water Injection1 | 1 | EA | 1250000 | 1250000
|  | SCR2,3 | 1 | EA | 3000000 | 3000000
|  | Reagent Prep/Water Treatment/Structure | 1 | EA | 2193500 | 2193500 |  | TOTAL = | 6443500
| (b) | Instrumentation
|  | Total Instrumentation4 |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | Injection System Freight |  | % MATL COST |  |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab |  | MH |  |  | 0
|  | Labor - onsite |  | MH |  |  | 0
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR | 0.5% | % |  | 15000
[8 empty] | TOTAL = | 15000
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 10 | Days | 1800 |  | 18000
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 8 | Days | 2500 |  | 20000
[8 empty] | TOTAL = | 38000
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope except SCR spares and SCR vendor rep. fees |  |  |  |  | PEMC = | 6496500
(2) | Direct Installation Costs5,6
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Functional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) | [7 empty] | DIC = | 7250000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 13746500
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 22% | % TDC |  |  | 3024230
(4) | Performance tests |  | 1 | EA | 10000 |  | 10000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 3034230
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs7 |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  | 30% | % PEMC |  |  | 1948950
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 1948950
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 18729680
Footnotes:
1 | For the water injection option, costs have been included for a water treatment system. Zehnder does not have any water treatment system, thus would need reverse osmosis, electro de-ionization, storage tanks, small pumps, and interconnecting piping. It is unlikely this equipment and reagent preparation equipment would fit inside the existing turbine building as it is all essential for normal maintenance and operation.
2 | Source of SCR Capital Costs: ATCO Emissions Management. These were supply-only costs given in a range for the Frame 5s. The highpoint of the range provided ($2 – $3 million) was used.
3 | Costs for reagent prep equipment and additional structures are discussed in a separately submitted CBI package.
4 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
5 | Construction costs associated directly with SCR installation were conservatively estimated at double the capital cost. This seems reasonable given the current footprint of the turbine building. Additional structure costs were included under part (1)(a) This should be viewed as an engineering estimate only.
6 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This is based on the assumption that some water treatment system work in addition to SCR treated water needs will be required to add water injection. This should be viewed as an engineering estimate only.
7 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
8 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements. However the reagent solutions will require continual heating to keep them in liquid form and a notable station load compared to the unit actual operation is expected.
Note on E28: Author: Cost of startup spares indicated as a percentage of equipment cost per data from similar project.
Note on E31: Author: days based on similar project
Note on E32: Author: days based on similar project
Note on K48: Author: The water injection installation costs would double the capital required due to new water treatment system. Assume that SCR installation costs are 2x the SCR equipment costs.
Note on E55: Author: Blended rate based on18% of SCR TDC that was used in similar project and 33% of water injection TDC based on Table 6-4 of EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines (EPA-453/R-93-007)
Note on E62: Author: Based on OAQPS Control Cost Manual standard contingency estimate.

## 3-5 EU 1&2 SCR_WI CE
Table 3-5. GVEA - Zehnder Facility - Annualized Costs for SCR and Water Injection on the Simple Cycle Gas Turbines (EU IDs 1 and 2)
Shaded cells indicate user inputs
Cost Effectiveness Determination - Water Injection + SCR | [7 empty] | Date:
Project: |  | GVEA Zehnder PM2.5 BACT Analysis - Frame 5 CTs (EU ID 1 and 2, cost per turbine) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 730 | MH | 105 |  | 76650 |  | 76650
(2) | Supervisory Labor |  | 183 | MH | 125 |  | 22875 |  | 22875
(3) | Maintenance Labor (water treatment) |  | 13950.8323 | 1000 GALS | 2.3704 |  | 33069.7289 |  | 33069.7289
(4) | Maintenance Labor (SCR system) |  | 365 | MH | 105 |  | 38325 |  | 38325
(5) | Maintenance Materials |  |  | LOT |  | 0 | Included in water treatment below |  | 0
(6) | Utilities
| a) | Water Use: | 10814.5987 | 1000 GALS | 1.3004 | 14062.8747 |  |  | 14062.8747
| b) | Water Pump Energy: | 33566.568 | kWh | 0.18 | 6041.9822 |  |  | 6041.9822
| c) | CT Fuel Use: | 17136350.365 | GALS
| d) | Fuel Penalty: | 437833.7518 | GALS | 1.7 | 744317.3781 |  |  | 744317.3781
| e) | Water Treatment Capacity: | 18136.082 | 1000 GALS | 6.6711 | 120987.9652 |  |  | 120987.9652
| f) | Water Waste Disposal: | 5259.4638 | 1000 GALS | 12.9359 | 68035.7705 |  |  | 68035.7705
| g) | Urea/DEF: | 17.7276 | TON | 356 | 6311.0256 |  |  | 6311.0256
| h) | SCR Energy Use8: |  | kWh | 0.18 | Excluded in this estimate. |  |  | 0
(7) | Catalyst Replacement Costs (every 3 years)
| (a) | Replacement of SCR Catalyst: % of total equipment cost | 30% | % total equip | 3000000 | 900000 |  |  | 279946.4991
| (b) | Replacement labor for SCR Catalyst | 180 | MH | 105 |  | 18900 |  | 5878.8765
| (c) | Transport cost direct to site (SCR catalyst) | 13% | % replacement |  |  | 117000 |  | 36393.0449
| (d) | Transport cost for spent SCR catalyst | 13% | % replacement |  |  | 117000 |  | 36393.0449
Sinking Fund Factor [see inputs below]: |  |  | 0.31105
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 1489288.1906
INDIRECT ANNUAL COSTS
(8) | Overhead |  | 30% | % WT Labor |  |  | 9920.9187 |  | 9920.9187
(9) | Administrative Charges, Property Taxes, Insurance |  | 4% | % total capital |  |  | 749187.2 |  | 749187.2
| Capital Recovery Factor [see inputs below] |  | 0.14238
(10) | Capital Recovery | [6 empty] | CRF * TCI = | 2666685.0653
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 3425793.1839
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 4915081.3746
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 929.7
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 5286.7391
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | 3 | years
|  | Asset Utilization | 100 | %
Footnotes:
1 | For the water injection option, costs have been included for a water treatment system. Zehnder does not have any water treatment system, thus would need reverse osmosis, electro de-ionization, storage tanks, small pumps, and interconnecting piping. It is unlikely this equipment and reagent preparation equipment would fit inside the existing turbine building as it is all essential for normal maintenance and operation.
2 | Source of SCR Capital Costs: ATCO Emissions Management. These were supply-only costs given in a range for the Frame 5s. The highpoint of the range provided ($2 – $3 million) was used.
3 | Costs for reagent prep equipment and additional structures are discussed in a separately submitted CBI package.
4 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
5 | Construction costs associated directly with SCR installation were conservatively estimated at double the capital cost. This seems reasonable given the current footprint of the turbine building. Additional structure costs were included under part (1)(a) This should be viewed as an engineering estimate only.
6 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This is based on the assumption that some water treatment system work in addition to SCR treated water needs will be required to add water injection. This should be viewed as an engineering estimate only.
7 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
8 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements. However the reagent solutions will require continual heating to keep them in liquid form and a notable station load compared to the unit actual operation is expected.
Note on E10: Author: Have historically used 2 hours per day for operating.
Note on G10: Author: Labor cost from similar project
Note on G11: Author: Labor cost from similar project
Note on E12: Author: Water use x 1.29 to account for waste water labor as well. See table 6-5 of EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.
Note on G12: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 0.7 $/1000gal, Table 6-5, note g.
Note on E13: Author: Have historically used 1 hours per day for maintenance
Note on G13: Author: Labor cost from similar project
Note on E16: Author: used fuel/water ratio for similarly sized GE turbine in EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines (Table 6-2)
Note on G16: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 0.384 $/1000gal, Table 6-3
Note on E17: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Use water flow of 23.8 gal/min and formula in Table 6-5.
Note on G17: Author: Current rate GVEA charges to industrial users.
Note on E18: Author: Based on 268 MMBtu/hr and fuel HHV of 137 MMBtu/1000 gals. @ 8760 hours per year.
Note on E19: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Use 3.5% of annual fuel use and water/fuel ratio of 0.73 (Table 6-2).
Note on G19: Author: EIA Monthly energy pricing report (Dec 2015).
Note on E20: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Water use plus 30% design factor and 29% waste factor.
Note on G20: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 1.97 $/1000gal, Table 6-3
Note on E21: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. 29% waste water from treatment capacity.
Note on G21: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 3.82 $/1000gal, Table 6-3
Note on E22: Author: Based on SCR controlling emissions up to 929.7 tons/yr NOx after water injection, which controls up to 795.4 tons/yr based on a 77% CE alone. 2.2 moles urea to control 1 ton NOx, 50% urea solution.
Note on G22: Author: December 2015 price according to Farmer's Coop Association.
Note on E25: Author: Miratech indicated that catalyst makes up 30% of the SCR system cost
Note on E26: Author: Replacement labor from similar project
Note on G26: Author: Labor cost from similar project
Note on E27: Author: From similar project
Note on E28: Author: From similar project
Note on E35: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Assumes 30% of water treatment labor above.
Note on E36: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.
Note on E54: Author: Common replacement timeframe

## 3-6 EU 1&2 SCR TCI
Table 3-6. GVEA - Zehnder Facility - Capital Costs for SCR on the Simple Cycle Gas Turbines (EU IDs 1 and 2)
Shaded cells indicate user inputs.
Total Capital Investment Determination - SCR | [7 empty] | Date:
Project: |  | GVEA Zehnder PM2.5 BACT Analysis - Frame 5 CTs (EU ID 1 and 2, cost per turbine) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | SCR1,2 | 1 | EA | 2500000 | 2500000
|  | Reagent Prep/Water Treatment/Structure | 1 | EA | 2193500 | 2193500 |  | TOTAL = | 4693500
| (b) | Instrumentation
|  | Total Instrumentation3 |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (c) | Freight
|  |  |  | % MATL COST |  |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab |  | MH |  |  | 0
|  | Labor - onsite |  | MH |  |  | 0
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR | 0.5% | % |  | 12500
[8 empty] | TOTAL = | 12500
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 10 | Days | 1800 |  | 18000
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 8 | Days | 2500 |  | 20000
[8 empty] | TOTAL = | 38000
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope except SCR spares and SCR vendor rep. fees |  |  |  |  | PEMC = | 4744000
(2) | Direct Installation Costs4
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Functional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) | [7 empty] | DIC = | 5000000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 9744000
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 18% | % TDC |  |  | 1753920
(4) | Performance tests |  | 1 | EA | 10000 |  | 10000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 1763920
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs5 |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  | 30% | % PEMC |  |  | 1423200
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 1423200
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 12931120
Footnotes:
1 | For the SCR option, costs have been included for a water treatment system to be used for reagent preparation. Zehnder does not have any water treatment system, thus would need reverse osmosis, electro de-ionization, storage tanks, small pumps, and interconnecting piping. It is unlikely this equipment and reagent preparation equipment would fit inside the existing turbine building as it is all essential for normal maintenance and operation.
2 | Source of SCR Capital Costs: ATCO Emissions Management. These were supply-only costs given in a range for the Frame 5s. The highpoint of the range provided ($2 – $3 million) was used.
3 | Costs for reagent prep equipment and additional structures are discussed in a separately submitted CBI package.
4 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
5 | Construction costs associated directly with SCR installation were conservatively estimated at double the capital cost. This seems reasonable given the current footprint of the turbine building. Additional structure costs were included under part (1)(a) This should be viewed as an engineering estimate only.
6 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This is based on the assumption that some water treatment system work in addition to SCR treated water needs will be required to add water injection. This should be viewed as an engineering estimate only.
7 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
8 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements. However the reagent solutions will require continual heating to keep them in in liquid form and a notable station load compared to the unit actual operation is expected.
Note on G13: Author: Based on vendor cost.
Note on E27: Author: Cost of startup spares indicated as a percentage of equipment cost per data from similar project.
Note on E30: Author: days based on similar project
Note on E31: Author: days based on similar project
Note on K47: Author: Assume that SCR installation costs are 2 x the SCR equipment costs.
Note on E54: Author: 18% was used in similar project for SCR only.
Note on E61: Author: Based on OAQPS Control Cost Manual standard contingency estimate.

## 3-7 EU 1&2 SCR CE
Table 3-7. GVEA - Zehnder Facility - Annualized Costs for SCR on the Simple Cycle Gas Turbines (EU IDs 1 and 2)
Shaded cells indicate user inputs
Cost Effectiveness Determination - SCR | [7 empty] | Date:
Project: |  | GVEA Zehnder PM2.5 BACT Analysis - Frame 5 CTs (EU ID 1 and 2, cost per turbine) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 730 | MH | 105 |  | 76650 |  | 76650
(2) | Supervisory Labor |  | 183 | MH | 125 |  | 22875 |  | 22875
(3) | Maintenance Labor (SCR system) |  | 365 | MH | 105 |  | 38325 |  | 38325
(4) | Maintenance Materials |  |  | LOT |  | 0 | Excluded in this estimate. |  | 0
(5) | Utilities
| a) | Urea/DEF: | 115.9026 | TON | 356 | 41261.3256 |  |  | 41261.3256
| b) | SCR Energy Use6: |  | kWh | 0.18 | Excluded in this estimate. |  |  | 0
(6) | Catalyst Replacement Costs (every 3 years)
| (a) | Replacement of SCR Catalyst: % of total equipment cost | 30% | % total equip | 2500000 | 750000 |  |  | 233288.7493
| (b) | Replacement labor for SCR Catalyst | 180 | MH | 105 |  | 18900 |  | 5878.8765
| (c) | Transport cost direct to site (SCR catalyst) | 13% | % replacement |  |  | 97500 |  | 30327.5374
| (d) | Transport cost for spent SCR catalyst | 13% | % replacement |  |  | 97500 |  | 30327.5374
Sinking Fund Factor [see inputs below]: |  |  | 0.31105
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 478934.0262
INDIRECT ANNUAL COSTS
(7) | Overhead7 |  |  | % |  |  | Excluded in this estimate. |  | -
(8) | Administrative Charges, Property Taxes, Insurance |  | 4% | % total capital |  |  | 517244.8 |  | 517244.8
| Capital Recovery Factor [see inputs below] |  | 0.14238
(9) | Capital Recovery | [6 empty] | CRF * TCI = | 1841100.5731
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 2358345.3731
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 2837279.3992
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 878.05
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 3231.3415
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | 3 | years
|  | Asset Utilization | 100 | %
Footnotes:
1 | For the SCR option, costs have been included for a water treatment system to be used for reagent preparation. Zehnder does not have any water treatment system, thus would need reverse osmosis, electro de-ionization, storage tanks, small pumps, and interconnecting piping. It is unlikely this equipment and reagent preparation equipment would fit inside the existing turbine building as it is all essential for normal maintenance and operation.
2 | Source of SCR Capital Costs: ATCO Emissions Management. These were supply-only costs given in a range for the Frame 5s. The highpoint of the range provided ($2 – $3 million) was used.
3 | Costs for reagent prep equipment and additional structures are discussed in a separately submitted CBI package.
4 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
5 | Construction costs associated directly with SCR installation were conservatively estimated at double the capital cost. This seems reasonable given the current footprint of the turbine building. Additional structure costs were included under part (1)(a) This should be viewed as an engineering estimate only.
6 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This is based on the assumption that some water treatment system work in addition to SCR treated water needs will be required to add water injection. This should be viewed as an engineering estimate only.
7 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
8 | Annual direct cost for SCR power consumption were excluded as vendor quotes did not specify system power requirements. However the reagent solutions will require continual heating to keep them in in liquid form and a notable station load compared to the unit actual operation is expected.
Note on E10: Author: Have historically used 2 hours per day for operating.
Note on G10: Author: Labor cost from similar project
Note on G11: Author: Labor cost from similar project
Note on E12: Author: Have historically used 1 hours per day for maintenance
Note on G12: Author: Labor cost from similar project
Note on E15: Author: Based on amount of NOx controlled by SCR control alone. 2.2 moles urea to control 1 ton NOx, 50% urea solution.
Note on G15: Author: December 2015 price according to Farmer's Coop Association.
Note on E18: Author: Miratech indicated that catalyst makes up 30% of the SCR system cost
Note on E19: Author: Replacement labor from similar project
Note on G19: Author: Labor cost from similar project
Note on E20: Author: From similar project
Note on E21: Author: From similar project
Note on E29: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.
Note on E47: Author: Common replacement timeframe

## 3-8 EU 1&2 WI TCI
Table 3-8. GVEA - Zehnder Facility - Capital Costs for Water Injection on the Simple Cycle Gas Turbines (EU IDs 1 and 2)
Shaded cells indicate user inputs.
Total Capital Investment Determination - Water Injection | [7 empty] | Date:
Project: |  | GVEA Zehnder PM2.5 BACT Analysis - Frame 5 CTs (EU ID 1 and 2, cost per turbine) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Water Injection1 | 1 | EA | 1250000 | 1250000
|  |  |  | EA |  | 0 |  | TOTAL = | 1250000
| (b) | Instrumentation
|  | Total Instrumentation2 |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | Injection System Freight |  | % MATL COST |  |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab |  | MH |  |  | 0
|  | Labor - onsite |  | MH |  |  | 0
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR |  | % |  | 0
[8 empty] | TOTAL = | 0
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | 0
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | 0
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope. |  |  |  |  | PEMC = | 1250000
(2) | Direct Installation Costs3
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Functional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) | [7 empty] | DIC = | 1250000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 2500000
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 33% | % TDC |  |  | 825000
(4) | Performance tests |  | 1 | EA | 10000 |  | 10000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 835000
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs4 |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  | 30% | % PEMC |  |  | 375000
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 375000
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 3710000
Footnotes:
1 | For the water injection only option, costs have not been included for a water treatment system. Zehnder does not have any water treatment system, thus would need reverse osmosis, electro de-ionization, storage tanks, small pumps, and interconnecting piping. It is unlikely this equipment would fit inside the existing turbine building as it is all essential for normal maintenance and operation.
2 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
3 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This is based on the assumption that some water treatment system work in addition to SCR treated water needs will be required to add water injection. This should be viewed as an engineering estimate only.
4 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
5 | Operator and supervisory labor costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
Note on G13: Author: Based on vendor cost.
Note on K47: Author: The water injection installation costs would double the capital required since a water treatment system would be needed.
Note on E54: Author: Based on Table 6-4 of EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines (EPA-453/R-93-007), where it indicates 33% of TDC.
Note on E61: Author: Based on OAQPS Control Cost Manual standard contingency estimate.

## 3-9 EU 1&2 WI CE
Table 3-9. GVEA - Zehnder Facility - Annualized Costs for Water Injection on the Simple Cycle Gas Turbines (EU IDs 1 and 2)
Shaded cells indicate user inputs
Cost Effectiveness Determination - Water Injection | [7 empty] | Date:
Project: |  | GVEA Zehnder PM2.5 BACT Analysis - Frame 5 CTs (EU ID 1 and 2, cost per turbine) | [5 empty] | Prepared By:
Checked By:
*Notes regarding pertinent cost information and cost exclusion reasoning is included on the separate footnote reference page. | [7 empty] | Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor5 |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(2) | Supervisory Labor5 |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(3) | Maintenance Labor (water treatment) |  | 13950.8323 | 1000 GALS | 2.3704 |  | 33069.7289 |  | 33069.7289
(4) | Maintenance Materials |  |  | LOT |  | 0 | Included in water treatment below |  | 0
(5) | Utilities
| a) | Water Use: | 10814.5987 | 1000 GALS | 1.3004 | 14062.8747 |  |  | 14062.8747
| b) | Water Pump Energy: | 33566.568 | kWh | 0.18 | 6041.9822 |  |  | 6041.9822
| c) | CT Fuel Use: | 17136350.365 | GALS
| d) | Fuel Penalty: | 437833.7518 | GALS | 1.7 | 744317.3781 |  |  | 744317.3781
| e) | Water Treatment Capacity: | 18136.082 | 1000 GALS | 6.6711 | 120987.9652 |  |  | 120987.9652
| f) | Water Waste Disposal: | 5259.4638 | 1000 GALS | 12.9359 | 68035.7705 |  |  | 68035.7705
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 986515.6996
INDIRECT ANNUAL COSTS
(6) | Overhead |  | 30% | % WT Labor |  |  | 9920.9187 |  | 9920.9187
(7) | Administrative Charges, Property Taxes, Insurance |  | 4% | % total capital |  |  | 148400 |  | 148400
| Capital Recovery Factor [see inputs below] |  | 0.14238
(8) | Capital Recovery | [6 empty] | CRF * TCI = | 528220.5351
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 686541.4538
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 1673057.1534
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 754.09
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 2218.6439
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | N/A | years
|  | Asset Utilization | 100 | %
Footnotes:
1 | For the water injection only option, costs have not been included for a water treatment system. Zehnder does not have any water treatment system, thus would need reverse osmosis, electro de-ionization, storage tanks, small pumps, and interconnecting piping. It is unlikely this equipment would fit inside the existing turbine building as it is all essential for normal maintenance and operation.
2 | Continuous emissions monitoring system is included in capital costs under Reagent Prep/Water Treatment/Structure.
3 | Construction costs associated directly with water injection installation was conservatively estimated at half the capital cost. This is based on the assumption that some water treatment system work in addition to SCR treated water needs will be required to add water injection. This should be viewed as an engineering estimate only.
4 | Unit operator costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
5 | Operator and supervisory labor costs were excluded as these costs were not specified in vendor quotes and/or appropriate literature.
Note on E12: Author: Water use x 1.29 to account for waste water labor as well. See table 6-5 of EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.
Note on G12: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 0.7 $/1000gal, Table 6-5, note g.
Note on E15: Author: used fuel/water ratio for similarly sized GE turbine in EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines (Table 6-2)
Note on G15: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 0.384 $/1000gal, Table 6-3
Note on E16: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Use water flow of 23.8 gal/min and formula in Table 6-5.
Note on G16: Author: Current rate GVEA charges to industrial users.
Note on E17: Author: Based on 268 MMBtu/hr and fuel HHV of 137 MMBtu/1000 gals. @ 8760 hours per year.
Note on E18: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Use 3.5% of annual fuel use and water/fuel ratio of 0.73 (Table 6-2).
Note on G18: Author: EIA Monthly energy pricing report (Dec 2015).
Note on E19: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Water use plus 30% design factor and 29% waste factor.
Note on G19: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 1.97 $/1000gal, Table 6-3
Note on E20: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. 29% waste water from treatment capacity.
Note on G20: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Escalated cost by 5% a year for inflation. 1990 cost = 3.82 $/1000gal, Table 6-3
Note on E25: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines. Assumes 30% of water treatment labor above.
Note on E26: Author: Based on EPA literature: Alternative Control Techniques Document - NOx emissions from stationary gas turbines.

## 3-10 EU 3&4 SCR TCI
Table 3-10. GVEA - Zehnder Facility - Capital Costs for SCR on
the Diesel-fired Generator Engines (EU IDs 3 and 4)
Shaded cells indicate user inputs.
Total Capital Investment Determination - SCR and Engine Upgrades | [7 empty] | Date:
Project: |  | GVEA Zhender - PM2.5 BACT Analysis (EU ID 3 and 4 - General Motors Gen Set Engines, cost per engine) | [5 empty] | Prepared By:
Checked By:
Rev:
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Total SCR System | 1 | EA | 285000 | 285000
|  | CBOI Injector | 1 | EA | 30000 | 30000
|  | Upper Rod Bearing | 1 | EA | 4723 | 4723
|  | Lower Rod Bearing | 1 | EA | 2655 | 2655
|  | Cylinder Head Seat Ring | 1 | EA | 1245 | 1245
|  | Cylinder Test Valve | 1 | EA | 3447 | 3447
|  | Utex Valve Bridge | 1 | EA | 2496 | 2496
|  | Utex Rocker Shaft Kit | 1 | EA | 10833 | 10833
|  | Seal, TDC | 1 | EA | 140 | 140
|  | Gasket, Handhole Cover | 1 | EA | 116 | 116
|  | Misc Hardware | 1 | EA | 500 | 500
[8 empty] | TOTAL = | 341155
| (b) | Instrumentation
|  | Total Instrumentation |  | EA |  | 0 | Included above
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | SCR System | 10% | % MATL COST |  |  | 28500
|  | Shipping Engine Overhaul Equipment Seattle to Fairbanks |  | EA |  |  | 8050
|  | Shipping engine cores Fairbanks to Seattle |  | EA |  |  | 6025
[8 empty] | TOTAL = | 42575
| (d) | Labor
|  | Labor - Engine Overhaul |  | Days |  |  | 35714
[8 empty] | TOTAL = | 35714
| (e ) | Startup Spares
|  | Startup Spare for SCR | 0.5% | % SCR Capital |  | 1425
[8 empty] | TOTAL = | 1425
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  | Excluded in this estimate | 0
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  | Excluded in this estimate | 0
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 420869
(2) | Direct Installation Costs
| (a) | Concrete |  | CY |  | 0 | Excluded in this estimate |  | 0
| (b) | Piling |  | TON |  | 0 | Excluded in this estimate |  | 0
| (c) | Structural steel |  | TON |  | 0 | Included above |  | 0
| (d) | Electrical |  | LOT |  | 0 | Excluded in this estimate |  | 0
| (e ) | Painting |  | SF |  | 0 | Excluded in this estimate |  | 0
| (f) | Insulation |  | LOT |  | 0 | Excluded in this estimate |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 | Excluded in this estimate |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  | Excluded in this estimate | 0 |  | 0
|  | Funtional Checkout - onsite, enter % |  | % onsite fab labor |  | Excluded in this estimate | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  | Excluded in this estimate | 0 |  | 0
Direct Installation Costs (DIC) | [7 empty] | DIC = | 0
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 420869
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 18% | % TDC |  |  | 75756.42
(4) | Performance tests |  | 1 | EA | 10000 |  | 10000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 85756.42
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  | 30% | % PEMC |  |  | 126260.7
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 126260.7
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 632886.12
Note on D14: Author: Includes oxidation catalyst, urea solutionizing and storage, support steel, and other misc equipment.
Note on G14: Author: Miratech quote
Note on G16: Author: Cost from vendor (Valley Power Systems Northwest)
Note on G17: Author: Cost from vendor (CAT)
Note on G18: Author: Cost from vendor (Valley Power Systems Northwest)
Note on G19: Author: Cost from vendor (CAT)
Note on G20: Author: Cost from vendor (CAT)
Note on G21: Author: Cost from vendor (CAT)
Note on G22: Author: Cost from vendor (CAT)
Note on G23: Author: Cost from vendor (CAT)
Note on G24: Author: Cost from vendor (CAT)
Note on E30: Author: Assume freight is 10% of SCR system capital.
Note on I31: Author: Total given in Valley quote.
Note on I32: Author: Ttoal given in Valley quote.
Note on I35: Author: Direct quote from Valley for labor.
Note on E38: Author: Cost of startup spares indicated as a percentage of equipment cost per data from similar project
Note on K61: Author: Miratech (vendor) quote
Note on E65: Author: 18% was used in similar project for SCR.
Note on E72: Author: Based on OAQPS Control Cost Manual standard contingency estimate.

## 3-11 EU 3&4 SCR CE
Table 3-11. GVEA - Zehnder Facility - Annualized Costs for SCR on
the Diesel-fired Generator Engines (EU IDs 3 and 4)
Shaded cells indicate user inputs
| Total Capital Investment Determination - SCR & Engine Upgrades | [7 empty] | Date:
| Project: |  | GVEA Zhender - PM2.5 BACT Analysis (EU ID 3 and 4 - General Motors Gen Set Engines, cost per engine) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
| DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
| (1) | Operating Labor |  | 365 | MH | 105 |  | 38325 |  | 38325
| (2) | Supervisory Labor |  | 91.25 | MH | 125 |  | 11406.25 |  | 11406.25
Diesel-fired Generator Engines (EU IDs 3 and 4, per engine) | (3) | Maintenance Labor (SCR system) |  | 182.5 | MH | 105 |  | 19162.5 |  | 19162.5
| (4) | Maintenance Materials |  |  | LOT |  | 0 | Excluded |  | 0
| (5) | Utilities
|  | a) | DEF: | 7900 | GAL | 2.8 | 22120 |  |  | 22120
| (6) | Catalyst Replacement Costs (every 3 years)
|  | (a) | Replacement of SCR Catalyst: % of total equipment cost | 30% | % total equip | 285000 | 85500 |  |  | 11952.5409
|  | (b) | Replacement labor for SCR Catalyst | 180 | MH | 105 |  | 18900 |  | 2642.1406
|  | (c) | Transport cost direct to site (SCR catalyst) | 13% | % replacement |  |  | 11115 |  | 1553.8303
|  | (d) | Transport cost for spent SCR catalyst | 13% | % replacement |  |  | 11115 |  | 1553.8303
| Sinking Fund Factor [see inputs below]: |  |  | 0.1398
| Total Direct Annual Costs (TDAC) |  |  |  | Excluded in this estimate. |  |  |  | TDAC = | 108716.0921
INDIRECT ANNUAL COSTS
| (6) | Overhead |  |  | % |  | Excluded in this estimate. | 0 |  | 0
| (7) | Administrative Charges, property taxes, insurance |  | 4% | % total capital |  |  | 25315.4448 |  | 25315.4448
|  | Capital Recovery Factor [see inputs below] |  | 0.14238
| (8) | Capital Recovery | [6 empty] | CRF * TCI = | 90108.7453
| Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 115424.1901
| TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 224140.2822
Cost Effectiveness Summary
| TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 17.92
| COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 12507.8282
Data Inputs for Capital Recovery Factor and Sinking Fund Factor:
|  |  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  |  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  |  | Catalyst Life | 3 | years
|  |  | Asset Utilization | 50 | %
Note on E11: Author: Have historically used 2 hours per day for operating. Conservatively assumed 1 hr/day.
Note on G11: Author: Labor cost from similar project
Note on E12: Author: Assumed to be half of maintenance labor.
Note on G12: Author: Labor cost from similar project
Note on E13: Author: Have historically used 1 hours per day for maintenance. Conservatively assumed 0.5 hr/day.
Note on G13: Author: Labor cost from similar project
Note on E16: Author: Based on amount Miratech quote that indicates 32.5% urea solution consumption at 15.8 gals/hr and 500 hrs/yr of operation.
Note on G16: Author: Current DEF price at pump.
Note on E19: Author: Miratech indicated that catalyst makes up 30% of the SCR system cost
Note on E20: Author: Replacement labor from similar project
Note on G20: Author: Labor cost from similar project
Note on E21: Author: From similar project
Note on E22: Author: From similar project
Note on E30: Author: Percentage of total capital investment

## 3-12 EU 10 & 11 LNB TCI
Table 3-12. GVEA - Zehnder Facility - Capital Costs for LNB on
the Diesel-fired Boilers (EU IDs 10 and 11)
Shaded cells indicate user inputs.
| Total Capital Investment Determination - Low NOX Burners | [7 empty] | Date:
| Project: |  | GVEA Zehnder PM2.5 BACT Analysis - Weil McLain Boilers (EU 10 and 11, cost per boiler) | [5 empty] | Prepared By:
Checked By:
Rev:
Capital Costs
| DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
| (1) | Purchased equipment and material costs
Diesel-fired Generator Engines (EU IDs 3 and 4, per engine) |  | (a) | Basic equipment
|  |  | Low NOx Burner Retrofit for Unit 10 | 1 | EA | 6200 | 6200
[9 empty] | TOTAL = | 6200
|  | (b) | Instrumentation
|  |  | Total Instrumentation |  | EA |  | Included in above price
[9 empty] | TOTAL = | 0
|  | (c) | Freight
|  |  | Freight for burners included in installation costs |  | % MATL COST |  |  | 0
[9 empty] | TOTAL = | 0
|  | (d) | Labor
|  |  | Labor - offsite fab |  | MH |  | None required | 0
|  |  | Labor - onsite |  | MH | 0 | Included in installation | 0
[9 empty] | TOTAL = | 0
|  | (e) | Vendor representatives fees
|  |  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  | None required | 0
|  |  | Onsite Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  | None required | 0
[9 empty] | TOTAL = | 0
| Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 6200
| Direct Installation Costs (DIC) | [7 empty] | DIC = | 15000
| Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 21200
INDIRECT COSTS
| (2) | Engineering, Procurement & Construction Support Services |  |  | % TDC |  |  | 0
| (3) | Performance tests |  |  | EA |  |  | 0
| Total Indirect Costs (TIC) |  |  |  | Not applicable |  |  |  | TIC = | 0
MANAGEMENT AND CONTINGENCY COSTS
| (4) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
| (5) | Contingency |  | 10% | % PEMC |  |  | 620
| Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 620
| TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 21820
Note on G14: Author: Supplier email (Proctor Sales) dated 11/4/2015: WM H688 burners: $6,200 each
Note on K32: Author: Supplier (Proctor Sales) email dated 11/5/2015: cost for install is $15K.
Note on E46: Author: Even though EPA allows for 30%, 10% is considered a conservative estimate.

## 3-13 EU 10 & 11 LNB CE
Table 3-13. GVEA - Zehnder Facility - Annualized Costs for LNB on
the Diesel-fired Boilers (EU IDs 10 and 11)
Shaded cells indicate user inputs
Cost Effectiveness Determination - Low NOX Burners | [7 empty] | Date:
Project: |  | GVEA Zehnder PM2.5 BACT Analysis - Weil McLain Boiler (EU 10 and 11, cost per boiler) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  |  | MH |  |  | 0 |  | 0
(2) | Supervisory Labor |  |  | MH |  |  | 0 |  | 0
(3) | Maintenance Labor |  |  | MH |  |  | 0 |  | 0
(4) | Maintenance Materials |  |  | LOT |  | 0 |  |  | 0
Total Direct Annual Costs (TDAC) |  |  |  | Not applicable |  |  |  | TDAC = | 0
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(6) | Administrative Charges |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(7) | Property tax |  |  |  |  | Excluded in this estimate.
(8) | Insurance |  |  |  |  | Excluded in this estimate.
| Capital Recovery Factor [see inputs below] |  | 0.14238
(9) | Capital Recovery | [6 empty] | CRF * TCI = | 3106.6771
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 3106.6771
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 3106.6771
Cost Effectiveness Summary
TOTAL TONS AVOIDED PER YEAR | [7 empty] | = | 0.37
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 8396.4246
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | N/A | years
|  | Asset Utilization | N/A | %

## Table 3-14
Table 3-14. GVEA - Zehnder Facility - NOX BACT Cost Effectiveness
Summary for Each Emission Unit
Emission Control Technology | NOX Emissions (tpy) | Total Installed Capital ($) | Total Annualized Cost ($/year) | Annual O&M Cost ($/year) | Cost Effectiveness ($/ton NOX removed) | Incremental Cost Effectiveness1 ($/incremental ton removed)
Diesel-fired Simple Cycle Gas Turbines (EU IDs 1 and 2, per turbine)
SCR + Water Injection | 103.3 | 18729680 | 4915081.3746 | 1489288.1906 | 5286.7391 | 40228.499
SCR | 154.95 | 12931120 | 2837279.3992 | 478934.0262 | 3231.3415 | 9391.9187
Water Injection | 278.91 | 3710000 | 1673057.1534 | 986515.6996 | 2218.6439 | 2218.6439
Good Combustion Practices (existing) | 1033 | ~ | ~ | ~ | ~ | ~
Diesel-fired Generator Engines (EU IDs 3 and 4, per engine)
Turbocharger and Aftercooler + Limited Operation + SCR | 4.48 | 632886.12 | 224140.2822 | 108716.0921 | 12507.8282 | 12507.8282
Turbocharger and Aftercooler + Limited Operation (existing) | 22.4 | ~ | ~ | ~ | ~ | ~
Diesel-fired Boilers (EU IDs 10 and 11, per boiler)
LNB | 0.73 | 21820 | 3106.6771 | ~ | $6,888 ($166,000 based on 2014 and 2015 levels of operation)
Good Combustion Practices (existing) | 1.1 | ~ | ~ | ~ | ~
Note:
1Incremental Cost Effectiveness is calculated as follows: [(Annualized Cost of Control Option) - (Annualized Cost of Next Control Option)]/[(Emissions of Next Control Option) - (Emissions of Control Option)]

## Table - 3-15
Table 3-15. GVEA - Zehnder Facility - Proposed NOX BACT and Associated
Emission Rate for Each Emission Unit
Emission Unit |  | Fuel | NOX BACT
ID | Description |  | Description | Emission Rate1
1, 2 | Simple Cycle Gas Turbines | Fuel Oil | Good Combustion Practices (existing) (See Table 3-16) | 0.88 lb/MMBtu
3,4 | Generator Engines | Diesel | Turbocharger and Aftercooler + Limited Operation (existing) | 0.0022 lb/hp-hr
10, 11 | Boilers | Diesel | Good Combustion Practices (existing) | 20 lb/kgal
Notes:
1Emissions are on a per unit basis.

## Table 3-16
Table 3-16. GVEA - Zehnder Facility - NOX BACT Analysis for EU IDs 1 and 2
Based on Actual Operations
| NOX BACT Analysis Based on Potential Emissions |  | NOX BACT Analysis Based on Actual (Historical) Operations
Operating Basis | 8760 | hr/yr | 769.5 | hr/yr
Emissions (EU 1 or EU 2) | 1032.9792 | tpy | 90.7394 | tpy
Good Combustion Practices (existing)
PTE | 1032.9792 | tpy | 90.7394 | tpy
PTE reduction | 0 | tpy | 0 | tpy
Cost effectiveness | N/A |  | N/A
Incremental cost effectiveness | N/A |  | N/A
Water Injection
PTE | 278.9044 | tpy | 24.4996 | tpy
PTE reduction | 754.0748 | tpy | 66.2398 | tpy
Cost effectiveness | 2218.6885 | $/ton | 25257.585 | $/ton
Incremental cost effectiveness | 2218.6885 | $/ton | 25257.585 | $/ton
SCR
PTE | 154.9469 | tpy | 13.6109 | tpy
PTE reduction | 878.0323 | tpy | 77.1285 | tpy
Cost effectiveness | 3231.4066 | $/ton | 36786.3827 | $/ton
Incremental cost effectiveness | 9392.1078 | $/ton | 106919.9022 | $/ton
SCR and water injection
PTE | 103.2979 | tpy | 9.0739 | tpy
PTE reduction | 929.6813 | tpy | 81.6655 | tpy
Cost effectiveness | 5286.8456 | $/ton | 60185.5326 | $/ton
Incremental cost effectiveness | 40229.3091 | $/ton | 457971.0819 | $/ton
Notes:
1. Historical Operating Hours (email from Naomi 6/23/2017)
Year | EU 1 | EU 2 | Total
2007 | 267 | 529 | 797
2008 | 745 | 57 | 802
2009 | 833 | 408 | 1241
2010 | 527 | 1012 | 1539
2011 | 756 | 509 | 1265
2012 | 440 | 635 | 1075
2013 | 226 | 936 | 1162
2014 | 139 | 1068 | 1207
2015 | 339 | 991 | 1330
2016 | 93 | 1137 | 1230
*2016 is not representative of typical use because EU 1 has been down waiting for a rebuild.
*Maximum annual operating hours for each turbine and total are shown in bold.
*The basis for this analysis is half of the total hours from 2010 for each turbine (770 hr/yr).
2. Basis for Emissions Calculations
NOX Emission Factor for EUs 1 and 2 | 0.88 | lb/MMBtu (AP-42 Table 3.1-1)
Heat input capacity for EUs 1 and 2 | 268 | MMBtu/hr
3. Emission Controls Efficiencies and Total Annual Costs
Emission Control Technology | Control Efficiency (pct) from Table 3-3 |  | Total Annualized Costs ($) from Table 3-14
SCR + Water Injection | 90 |  | 4915081.3746
SCR | 85 |  | 2837279.3992
Water Injection | 73 |  | 1673057.1534
Good Combustion Practices (existing) | 0 |  | 0

## NOx Identified - DONT INCLUDE
Table C-1a. Summary of Identified NOX Control Technology - Liquid Fuel-Fired Simple Cycle Turbines > 25 MW (RBLC 15.190)
Pollutant | Control Technology Used | Number of RBLC Entries (13 Total)
NOX | None | 4
| Water Injection | 4
| Good Combustion Practices | 2
| Low NOX+SCR | 1
| SCR + Water Injection | 1
| Low NOX + Water Injection | 1
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.
Table C-1b. Summary of Identified NOX Control Technology - Large Diesel Engines > 500 hp (RBLC 17.110)
Pollutant | Control Technology Used | Number of RBLC Entries (67 Total)
NOX | NSPS Standards | 17
| None | 15
| Good Combustion Practices | 10
| Limited Operation | 8
| Injection Timing Retard | 7
| Turbocharger + Aftercooler | 4
| SCR | 2
| Turbocharger | 2
| Injection Timing + Turbocharger + Aftercooler | 1
| Turbocharger + Aftercooler + Low NOx | 1
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.
Table C-1c. Summary of Identified NOX Control Technology - Diesel-Fired Commercial/Institutional Boilers <100 MMBtu/hr (RBLC 13.220)
Pollutant | Control Technology Used | Number of RBLC Entries (7 Total)
NOX | None | 2
| Low NOX + Flue Gas Recirculation | 2
| Low NOX + Good Combustion Practices | 2
| Low NOX | 1
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.