## 5-1 SO2 Available
Table 5-1. GVEA - Zehnder Facility - Summary of Available SO2 Emission Control Technologies
Emission Unit |  | Available Emission Control Technology
ID | Description
1, 2 | Simple Cycle Gas Turbine | ULSD
Low Sulfur Fuel
Good Combustion Practices
3, 4 | Diesel-fired Emergency Generator Engine | ULSD
Low Sulfur Fuel
Limited Operations
Good Combustion Practices
10, 11 | Diesel-fired Boiler | ULSD
Low Sulfur Fuel
Good Combustion Practices

## 5-2 SO2 Feasible
Table 5-2. GVEA - Zehnder Facility - Summary of Technically Feasible SO2 Emission Control Technologies
Emission Unit |  | Emission Control Technology
ID | Description
1,2 | Simple Cycle Combustion Gas Turbine | ULSD
Low Sulfur Fuel
Good Combustion Practices
3, 4 | Diesel-fired Emergency Generator Engine | ULSD
Low Sulfur Fuel
Limited Operation
Good Combustion Practices
10, 11 | Diesel-fired Boiler | ULSD
Low Sulfur Fuel
Good Combustion Practices

## 5-3 SO2 Ranking
Table 5-3. GVEA - Zehnder Facility - Ranking of Technically Feasible SO2 Emission Control Technology
Emission Unit |  | Control Technology Used | Control Efficiency (pct)2 | SO2 Emissions Per Unit (tpy) | SO2 Emissions Reduction (tpy)
ID | Description
1, 21 | Simple Cycle Combustion Gas Turbines | ULSD Fuel (0.0015 wt. pct. S) | 99.6934 | 1.7784 | 578.2216
|  | Low-Sulfur Fuel (0.05 wt. pct. S) | 89.7795 | 59.2789 | 520.7211
|  | Good Combustion Practices (0.5 wt. pct. S) (existing) | 0 | 580 | 0
3, 41 | Diesel-fired Emergency Generator Engines | ULSD Fuel (0.0015 wt. pct. S) | 99.7 | 0.011129 | 3.6986
|  | Low-Sulfur Fuel (0.05 wt. pct. S) | 90 | 0.37097 | 3.3388
|  | Limited Operation and Good Combustion Practices (0.5 wt. pct. S) (existing) | 0 | 3.7097 | 0
10, 111 | Diesel-fired Boilers | ULSD Fuel (0.0015 wt. pct. S) | 99.7 | 0.011574 | 3.8465
|  | Low-Sulfur Fuel (0.05 wt. pct. S) | 90 | 0.3858 | 3.4722
|  | Good Combustion Practices (0.5 wt. pct. S) (existing) | 0 | 3.858 | 0
Note:
1 Combined SO2 emissions from EU IDs 1 through 4, 10, and 11 are limited to 580 tpy on a 12-month rolling basis per Permit AQ0109TVP03 Condition 9. Each emission unit can operate individually up to the potential emissions listed in this table. The fuel sulfur content is limited to 1.0 wt. pct. for EU IDs 1 through 4, per Permit AQ0109TVP03, Condition 10. However, No. 1 and No. 2 fuel oil (by specification) can have a maximum sulfur content of 0.5 wt. pct., so 0.5 percent fuel sulfur content is used as the baseline for each emission unit.
2 The use of low-sulfur fuel and ULSD both result in the 580 tpy SO2 limit being unncessary. For each emission unit, the control efficiencies are based on the emission reduction between the existing PTE and the PTE that would result due to the use of lower sulfur fuel.

## 5-4 EU ID 1&2 ULSD CE
Table 5-4. Annualized Costs for ULSD Combustion in
the Diesel-fired Simple Cycle Gas Turbines (EU ID 1 and 2)
Shaded cells indicate user inputs
Cost Effectiveness Determination - ULSD Fuel Switch - No Additional Tank Storage | [7 empty] | Date:
Project: |  | GVEA Zhender - SO2 BACT Analysis (EU ID 1 and 2 - Frame 5 CTs, cost per turbine) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT
(4) | Utilities
| (a) | ULSD Costs: | 18059076.92 | GAL | 0.2668 | 4818161.7223 |  |  | 4818161.7223
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 4818161.7223
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  |  | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.14238
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) (refer to Table 5-10) | [7 empty] | TIAC = | 791004.2125
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 5609165.9347
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 578.2216
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 9700.7196
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON ACTUAL HISTORIC RUN TIMES, AVOIDING 51.9 TONS PER YEAR)1 | [7 empty] | (TAC)/(TPY) = | 18700.3964
COST EFFECTIVENESS ($ PER TON PM AVOIDED BASED ON 6 TONS SO2 AVOIDED = 1 TON PM AVOIDED)2 | [7 empty] | (TAC)/(TPY) = | 112202.3784
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
1 | Annual average run hours of 770 for EU IDs 1 and 2, see Table 5-9. 700 hours equates to 1,587,385 gallons of fuel, a TDAC of $423,514 and a TAC of $970,728. The capital cost of bulk fuel storage would be less and the TIAC for actuals is shown in Table 5-9 at $547,268.
2 | Alaska Department of Environmental Conservation, Amendments to State Air Quality Control Plan Vol. III: Appendix III.D.5.7, page 52. In reference to fuel oil emissions, "Ambient sampling and modeling in FNSB indicates that reduction of six tons of SOX emissions result in the same reduction in ambient PM2.5 concentration as the reduction of one ton of directly emitted PM2.5".
Note on E15: Author: Based on unlimited operation. 268 MMBtu/hr @ 8760 hrs/yr and HHV of 0.13 MMBtu/gal.
Note on G15: Author: Difference in cost for delivery of ULSD compared to #2 fuel oil based on data provided by GVEA.

## 5-5 EU ID 3&4 ULSD CE
Table 5-5. Annualized Costs for ULSD Combustion in
the Diesel-fired Engines (EU ID 3 and 4)
Shaded cells indicate user inputs
Cost Effectiveness Determination - ULSD Fuel Switch - No Additional Tank Storage | [7 empty] | Date:
Project: |  | GVEA Zhender - SO2 BACT Analysis (EU ID 3 and 4 - General Motors Gen Set Engines, cost per engine) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT
(4) | Utilities
| (a) | ULSD Costs: | 107692.31 | GAL | 0.2668 | 28732.3083 |  |  | 28732.3083
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 28732.3083
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  |  | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.14238
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) |  |  |  | Not applicable |  |  |  | TIAC = | 0
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 28732.3083
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 3.6986
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 7768.3846
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
Note on E14: Author: Based on limited operation. 28 MMBtu/hr @ 500 hrs/yr and HHV of 0.13 MMBtu/gal.
Note on G14: Author: Difference in cost for delivery of ULSD compared to #2 fuel oil based on data provided by GVEA.

## 5-6 EU ID 10&11 ULSD CE
Table 5-6 Annualized Costs for ULSD Combustion in
the Diesel-fired Boilers (EU ID 10 and 11)
Shaded cells indicate user inputs
Cost Effectiveness Determination - ULSD Fuel Switch - No Additional Tank Storage | [7 empty] | Date:
Project: |  | GVEA Zhender - SO2 BACT Analysis (EU ID 10 and 11 - Weil McLain Boilers, cost per boiler) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT
(4) | Utilities
| (a) | ULSD Costs: | 114553.85 | GAL | 0.2668 | 30562.9672 |  |  | 30562.9672
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 30562.9672
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  |  | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.14238
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) |  |  |  | Not applicable |  |  |  | TIAC = | 0
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 30562.9672
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 3.8465
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 7945.7452
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
Note on E14: Author: Based on unlimited operation. 1.7 MMBtu/hr @ 8760 hrs/yr and HHV of 0.13 MMBtu/gal.
Note on G14: Author: Difference in cost for delivery of ULSD compared to #2 fuel oil based on data provided by GVEA.

## 5-7 Cost Effectiveness
Table 5-7. GVEA - Zehnder Facility - SO2 BACT Cost Effectiveness
Summary for Each Emission Unit
Emission Control Technology | SO2 Emissions (tpy) | Total Installed Capital ($) | Total Annualized Cost ($/year) | Annual O&M Cost ($/year) | Cost Effectiveness ($/ton SO2 removed)
Diesel-fired Simple Cycle Gas Turbines (EU IDs 1 and 2, per turbine)
ULSD Fuel (0.0015 wt. pct. S) | 1.7784 | 4337180.8511 | 5609165.9347 | 4818161.7223 | 9700.7196
Good Combustion Practices (0.5 wt. pct. S) (existing) | 580 | ~ | ~ | ~ | ~
Emergency Generator Engines (EU IDs 3 and 4, per engine)
ULSD Fuel (0.0015 wt. pct. S) | 0.011129 | ~ | 28732.3083 | 28732.3083 | 7768.3846
Limited Operation and Good Combustion Practices (0.5 wt. pct. S) (existing) | 3.7097 | ~ | ~ | ~ | ~
Diesel-fired Boilers (EU IDs 10 and 11, per boiler)
ULSD Fuel (0.0015 wt. pct. S) | 0.011574 | ~ | 30562.9672 | 30562.9672 | 7945.7452
Good Combustion Practices (0.5 wt. pct. S) (existing) | 3.858 | ~ | ~ | ~ | ~
Note:
All costs are on a per unit basis.

## 5-8 Summary
Table 5-8. GVEA - Zehnder Facility - Proposed SO2 BACT and Associated
Emission Rate for Each Emission Unit
Emission Unit |  | Fuel | SO2 BACT
ID | Description |  | Description | Sulfur Content of Fuel
1, 2 | Simple Cycle Gas Turbines | Fuel Oil | Fuel Oil and Good Combustion Practices (existing) - Refer to Table 5-9 | 0.5 wt. pct. S
3, 4 | Emergency Generator Engines | Diesel | Fuel Oil and Good Combustion Practices (existing) | 0.5 wt. pct. S
10, 11 | Boilers | Diesel | ULSD | 0.0015 wt. pct. S
Note:
1 Emissions are on a per unit basis.

## 5-9 Actuals
Table 5-9. GVEA - Zehnder Facility - SO2 BACT Analysis for EU IDs 1 and 2
Based on Actual Operations
| SO2 BACT Analysis Based on Potential Emissions |  | SO2 BACT Analysis Based on Actual (Historical) Operations
Operating Basis | 8760 | hr/yr | 769.5 | hr/yr
Emissions (EU 1 or EU 2) | 580 | tpy | 52.0721 | tpy
Good combustion practices, 0.5 wt. pct. S (existing)
PTE | 580 | tpy | 52.0721 | tpy
PTE reduction | 0 | tpy | 0 | tpy
Cost effectiveness | N/A |  | N/A
ULSD Fuel (0.0015 wt. pct. S)
PTE | 1.7784 | tpy | 0.15966 | tpy
PTE reduction | 578.2216 | tpy | 51.9124 | tpy
Total Direct annual Costs (TDAC) | 4818161.7223 | (Table 5-4) | 423514.2154 | 1
Total Indirect Annual Costs (TIAC) | 791004.2125 | (Table 5-10) | 547268.3212 | (Table 5-10)
Total annualized Costs (TAC = TDAC + TIAC) | 5609165.9347 |  | 970782.5366
Cost effectiveness | 9700.7196 | $/ton | 18700.3964 | $/ton
1 Assuming 770 hours, 268 MMBtu/Hr, and .13 MMBtu/gal, for 1,587,385 gallons, and the fuel costs shown in Table 5-4)
Notes:
1. Historical Operating Hours (email from Naomi 6/23/2017)
Year | EU 1 | EU 2 | Total
2007 | 267 | 529 | 797
2008 | 745 | 57 | 802
2009 | 833 | 408 | 1241
2010 | 527 | 1012 | 1539
2011 | 756 | 509 | 1265
2012 | 440 | 635 | 1075
2013 | 226 | 936 | 1162
2014 | 139 | 1068 | 1207
2015 | 339 | 991 | 1330
2016 | 93 | 1137 | 1230
*2016 is not representative of typical use because EU 1 has been down waiting for a rebuild.
*Maximum annual operating hours for each turbine and total are shown in bold.
*The basis for this analysis is half of the total hours from 2010 for each turbine (770 hr/yr).
2. Basis for Emissions Calculations
SO2 Emission Factor for EUs 1 and 2
Fuel with 0.5 wt. pct. S content | 0.505 | lb/MMBtu (AP-42 Table 3.1-2a)
Fuel with 0.05 wt. pct. S content | 0.0505 | lb/MMBtu (AP-42 Table 3.1-2a)
Fuel with 0.015 wt. pct. S content | 0.01515 | lb/MMBtu (AP-42 Table 3.1-2a)
Heat input capacity for EUs 1 and 2 | 268 | MMBtu/hr
3. Emission Controls Efficiencies and Total Annual Costs
Emission Control Technology | Control Efficiency (pct) from Table 5-3
ULSD Fuel (0.0015 wt. pct. S) | 99.6934
Good Combustion Practices (existing) | 0

## 5-10 NP & Zehnder
Table 5-10. Capital Cost for New ULSD Storage Based on
PTE Maximum Fuel Use and Historic Actual Use
| North Pole EUs 1 and 2 Maximum Fuel Use | Zehnder EUs 1 and 2 Maximum Fuel Use | North Pole EUs 1 and 2 Actual Fuel Use | Zehnder EUs 1 and 2 Actual Fuel Use
Capital Cost Estimate | 30425000 |  | 21050000
Heat Input, MMBtu/day (combined for each set of combustion turbines) | 32256 | 12864 | 32256 | 12864
Percentage of Heat Input | 71.49% | 28.51% | 71.49% | 28.51%
Capital Cost (apportioned based on heat input ratio) | 21750638.2979 | 8674361.7021 | 15048510.6383 | 6001489.3617
Capital Cost (apportioned per combustion turbine) | 10875319.1489 | 4337180.8511 | 7524255.3191 | 3000744.6809
Capital Recovery (per combustion turbine) | 1548400.7818 | 617516.9785 | 1071284.6822 | 427238.534
Administrative Charges, Property Taxes, Insurance (per combustion turbine) | 435012.766 | 173487.234 | 300970.2128 | 120029.7872
Total Annual Indirect Cost (per combustion turbine) | 1983413.5477 | 791004.2125 | 1372254.895 | 547268.3212
Capital recovery factor | 0.14238
Data Inputs for Capital Recovery Factor:
Annual Interest Rate (EPA OAQPS Control |  | 7 | pct.
Cost Manual)
Project Life (EPA OAQPS Control Cost |  | 10 | years
Manual)
Administrative Charges, Property Taxes |  | 4%
Insurance (percentage of total capital
cost)

## SO2 Identified - DONT INCLUDE
Table E-1a. Summary of Identified SO2 Control Technology - Liquid Fuel-Fired Simple Cycle Turbines > 25 MW (RBLC 15.190)
Pollutant | Control Technology Used | Number of RBLC Entries (11 Total)
SO2 | Low Sulfur Fuel | 7
| None | 4
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.
Table E-1b. Summary of Identified SO2 Control Technology - Large Diesel Engines > 500 hp (RBLC 17.110)
Pollutant | Control Technology Used | Number of RBLC Entries (30 Total)
SO2 | Low-Sulfur Fuel | 13
| ULSD Fuel | 7
| None | 3
| Good Combustion Practices | 5
| NSPS Standards | 2
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.
Table E-1c. Summary of Identified SO2 Control Technology - Diesel-Fired Commercial/Institutional Boilers <100 MMBtu/hr (RBLC 13.220)
Pollutant | Control Technology Used | Number of RBLC Entries (6 Total)
SO2 | Low Sulfur Fuel | 2
| Low Sulfur Fuel + Good Combustion Practices | 2
| Wet or Dry Scrubber + Good Combustion Practices | 1
| None | 1
Note: Data is based on a RBLC review from January 1, 2005 through September 15, 2015.