## 3-1
Table 3-1. UAF - Available NOX Control Options
Emission Unit |  | Available Control
ID | Description | Options
113 | Large Coal-fired Boiler | SCR
SNCR
CFB with Staged Combustion
Good Combustion Practices
3 and 4 | Mid-sized Diesel-fired Boilers | SCR
SNCR
LNB/FGR
Limited Operation
Good Combustion Practices
19 through 21 | Small Diesel-fired Boilers | LNB
Limited Operation
Good Combustion Practices
8 | Large Diesel-fired Engine | SCR
Turbocharger and Aftercooler
Limited Operation
Good Combustion Practices
27 | Small Diesel-fired Engines | SCR
Turbocharger and Aftercooler
Federal Standard
Limited Operation
Good Combustion Practices
9A | Medical/Pathological Waste Incinerator | SCR
SNCR
LNB
Limited Operation
Good Combustion Practices

## 3-2
Table 3-2. UAF - Technically Feasible NOX Control Options
Emission Unit |  | Technically Feasible
ID | Description | Control Options
113 | Large Coal-fired Boiler | SCR
SNCR
CFB with Staged Combustion
Good Combustion Practices
3 | Mid-sized Diesel-fired Boilers | SCR
LNB/FGR
Good Combustion Practices
4 | Mid-sized Diesel-fired Boilers | LNB/FGR
Limited Operation
Good Combustion Practices
19 through 21 | Small Diesel-fired Boilers | LNB
Limited Operation
8 | Large Diesel-fired Engine | SCR
Turbocharger and Aftercooler + Limited Operation
27 | Small Diesel-fired Engine | SCR
Turbocharger and Aftercooler + Federal Standard + Limited Operation
9A | Medical/Pathological Waste Incinerator | Good Combustion Practices
Limited Operation

## 3-3
Table 3-3. UAF - Ranking of Technically Feasible NOX Control Options
Emission Unit |  | Control | Control | NOX Emissions | Emissions
ID | Description | Technology | Efficiency (pct.) | (tpy) | Reduction (tpy)
113 | Large Coal and Biomass-fired Boiler | SCR + (CFB with staged combustion) | 80 | 51.8 | 207.2
|  | SNCR + (CFB with staged combustion) | 20 | 207.2 | 51.8
|  | CFB with staged combustion | 0 | 259 | 0
3 | Mid-Sized Diesel-fired Boiler | SCR | 85 | 20.82 | 117.98
|  | LNB/FGR | 42.9148 | 79.2342 | 59.5658
|  | Good Combustion Practices | 0 | 138.8 | 0
4 | Mid-Sized Diesel and Natural Gas-fired Boiler | LNB/FGR | 8.7952 | 12.6775 | 1.2225
|  | Limited Operation1 | 0 | 13.9 | 0
19 through 21 | Small Diesel-fired Boilers | Limited Operation2 | N/A | 8.8 | NA
|  | LNB + Limited Operation | N/A | 13.87 | 0
8 | Large Diesel-fired Engine | SCR + (Turbocharger + Aftercooler + Limited Operation) | 90 | 4 | 36
|  | Turbocharger + Aftercooler + Limited Operation | 0 | 40 | 0
27 | Small Diesel-fired Engine | SCR + (Turbocharger + Aftercooler + Federal Limit + Limited Operation) | 90 | 0.77 | 6.93
|  | Turbocharger + Aftercooler + Federal Limit + Limited Operation | 0 | 7.7 | 0
Notes:
1EU 4 NOx emissions are limited to 13.9 tpy by the 10 percent capacity factor in Condition 17 of Permit AQ0316TVP02 and are less than the 40 tpy shared NOX limit with EU 8 from Condition 16 of that permit.
2Vendor emission estimates for retrofitting LNB on the boilers was for a higher NOX emission rate than the AP-42 emission rate used to estimate the emissions of the boilers with limited operation.

## 3-4 - EU 113 - SCR TCI
Table 3-4. UAF - Capital Costs for SCR on
the Large CFB Coal-fired Boiler (EU ID 113)
Shaded cells indicate user inputs.
Total Capital Investment Determination - SCR | [7 empty] | Date: | 2016-02-02
Project: |  | UAF - PM2.5 BACT Analysis (EU ID 113 - CFB Boiler) | [5 empty] | Prepared By: | L. Pacini
[8 empty] | Checked By: | C. Stevenson
[8 empty] | Rev: | A
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Total SCR System | 1 | EA | 6000000 | 6000000
[8 empty] | TOTAL = | 6000000
| (b) | Instrumentation
|  | Total Instrumentation |  | EA |  | 0 | Included above
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | SCR Freight |  | % | 0 |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - shop fab |  | MH |  |  | 0
|  | Labor - onsite |  | MH |  |  | 0
[8 empty] | TOTAL = | 0
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR | 0.5% | % |  | 30000
[8 empty] | TOTAL = | 30000
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 10 | Days | 1800 |  | 18000
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 8 | Days | 2500 |  | 20000
[8 empty] | TOTAL = | 38000
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope except SCR spares and SCR vendor rep. fees |  |  |  |  | PEMC = | 6068000
(2) | Direct Installation Costs
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Functional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) - 2 x SCR Equipment Capital | [7 empty] | DIC = | 12000000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 18068000
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 18% | % TDC |  |  | 3252240
(4) | Performance tests |  | 0 | EA |  |  | 0 |  | Excluded in this estimate.
Total Indirect Costs (TIC) | [7 empty] | TIC = | 3252240
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  | 30% | % TDC |  |  | 5420400
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 5420400
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 26740640
Note on G13: Pacini, Lain: Babcock proposal figure
Note on E26: Courtney Kimball: Cost of startup spares indicated as a percentage of equipment cost per similar project.
Note on E29: Courtney Kimball: days based on similar project
Note on E30: Courtney Kimball: days based on similar project
Note on K46: Pacini, Lain: Assume installation of SCR requires 2 x the SCR equipment capital based on FTEK proposal for Zurn unit
Note on E53: Courtney Kimball: 18% was used in similar SCR BACT analysis for smaller CTs.
Note on E60: Pacini, Lain: +/- 30% based on FTEK quote for SCR on another unit.

## 3-5 - EU 113 - SCR CE
Table 3-5. UAF - Annualized Costs for SCR on
the Large CFB Coal-fired Boiler (EU ID 113)
Shaded cells indicate user inputs
Cost Effectiveness Determination - SCR | [7 empty] | Date: | 2016-02-02
Project: |  | UAF - PM2.5 BACT Analysis (EU ID 113 - CFB Boiler) | [5 empty] | Prepared By: | L. Pacini
[8 empty] | Checked By: | C. Stevenson
[8 empty] | Rev: | A
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  |  | MH |  | excluded in this estimate | 0 |  | 0
(2) | Supervisory Labor |  |  | MH |  | excluded in this estimate | 0 |  | 0
(3) | Maintenance Labor |  |  | MH |  | excluded in this estimate | 0 |  | 0
(4) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(5) | Utilities
| (a) | Aqueous Ammonia: | 262.8 | TON | 200.08 | 52581.0324 |  |  | 52581.0324
| (b) | Energy: | 613200 | kWh | 0.18 | 110376 |  |  | 110376
(6) | Catalyst Replacement Costs (every 2 years)
| (a) | Replacement of SCR Catalyst: % of total equipment cost | 30% | % total equip | 6068000 | 1820400 |  |  | 879420.2899
| (b) | Replacement labor for SCR Catalyst | 180 | MH | 105 |  | 18900 |  | 9130.4348
| (c) | Transport cost direct to site (SCR catalyst) | 13% | % replacement |  |  | 236652 |  | 114324.6377
| (d) | Transport cost for spent SCR catalyst | 13% | % replacement |  |  | 236652 |  | 114324.6377
Sinking Fund Factor [see inputs below]: |  |  | 0.48309
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 1280157.0324
INDIRECT ANNUAL COSTS
(7) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(8) | Administrative Charges and Insurance |  | 3% | % total capital |  |  | 802219.2 |  | 802219.2
| Capital Recovery Factor [see inputs below] |  | 0.14238
(9) | Capital Recovery | [6 empty] | CRF * TCI = | 3807265.5445
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 4609484.7445
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 5889641.7769
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 207.2
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 28424.9121
Data Inputs for Capital Recovery Factor and Sinking Fund Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | 2 | years
|  | Asset Utilization | 100 | %
Note on E15: Pacini, Lain: Based on Babcock proposal indicating consumption rate of 60 lbs/hr.
Note on G15: Courtney Kimball: Based on ammonia solution cost from similar BACT analysis - $0.75/gal and specific gravity of 0.9.
Note on E16: Pacini, Lain: 70 kW energy requirement from vendor and assume 8760 hours/yr.
Note on G16: Pacini, Lain: Current Per kW price based on GVEA data.
Note on E19: Courtney Kimball: Replacement labor based on similar project.
Note on G19: Courtney Kimball: Labor cost based on similar project.
Note on E29: Pacini, Lain: Percentage of total capital investment
Note on K39: Pacini, Lain: based on 80% control as indicated by vendor.
Note on E47: Pacini, Lain: Based on FTEK SCR life expectations on other unit

## 3-6 - EU 113 - SNCR TCI
Table 3-6. UAF - Capital Costs for SNCR on
the Large CFB Coal-fired Boiler (EU ID 113)
Shaded cells indicate user inputs.
Total Capital Investment Determination - SNCR | [7 empty] | Date: | 2016-02-03
Project: |  | UAF - PM2.5 BACT Analysis (EU ID 113 - CFB Boiler) | [5 empty] | Prepared By: | L. Pacini
[8 empty] | Checked By: | C. Stevenson
[8 empty] | Rev: | A
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Total DSI System | 1 | EA | 1000000 | 1000000
|  | (per Babcock & Wilcox) | [5 empty] | TOTAL = | 1000000
| (b) | Instrumentation
|  | Total Instrumentation |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | SNCR Freight |  | % MATL COST | 0% |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab |  | MH |  |  | 0
|  | Labor - onsite |  | MH |  |  | 0
[8 empty] | TOTAL = | 0
| (e) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | 0
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | 0
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope. |  |  |  |  | PEMC = | 1000000
(2) | Direct Installation Costs
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Functional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) - 1 x SNCR Equipment Capital | [7 empty] | DIC = | 1000000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 2000000
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 18% | % TDC |  |  | 360000
(4) | Performance tests |  |  | EA |  |  | 0
Total Indirect Costs (TIC) | [7 empty] | TIC = | 360000
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  | 30% | % TDC |  |  | 600000
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 600000
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 2960000
Note on G13: Pacini, Lain: Based on Babcock proposal.
Note on K43: Pacini, Lain: Assume SNCR installation cost are 1 x the capital required for equipment purchases. Assumption is based on the FTEK proposal indicating an SCR is 2 x capital costs for installation and that SNCR will involve less equipment (only need reagent injection system).
Note on E50: Courtney Kimball: 18% was used in similar SCR BACT analysis. Assume same amount for SNCR.
Note on E57: Pacini, Lain: +/- 30% for SCR, assume same for SNCR based on FTEK proposal.

## 3-7 - EU 113 - SNCR CE
Table 3-7. UAF - Annualized Costs for SNCR on
the Large CFB Coal-fired Boiler (EU ID 113)
Shaded cells indicate user inputs
Total Capital Investment Determination - SNCR | [7 empty] | Date: | 2016-02-03
Project: |  | UAF - PM2.5 BACT Analysis (EU ID 113 - CFB Boiler) | [5 empty] | Prepared By: | L. Pacini
[8 empty] | Checked By: | C. Stevenson
[8 empty] | Rev: | A
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  |  | MH |  | - | Excluded |  | Excluded
(2) | Supervisory Labor |  |  | MH |  | - | Excluded |  | Excluded
(3) | Maintenance Labor |  |  | MH |  | - | Excluded |  | Excluded
(4) | Maintenance Materials |  |  | LOT |  | Excluded | - |  | Excluded
(5) | Utilities
| (a) | Aqueous Ammonia: | 87.6 | TON | 200.08 | 17527.0108 |  |  | 17527.0108
| (b) | Electricity: |  | KWH | 0.18 | 0 |  |  | 0
(per Babcock & Wilcox)
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 17527.0108
INDIRECT ANNUAL COSTS
(6) | Overhead |  |  | % |  | Excluded | 0 |  | 0
(7) | Administrative Charges and Insurance |  | 3% | % total capital |  |  | 88800 |  | 88800
| Capital Recovery Factor [see inputs below] |  | 0.14238
(8) | Capital Recovery | [6 empty] | CRF * TCI = | 421437.4081
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 510237.4081
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 527764.4189
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 51.78
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 10192.4376
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
Note on E15: Pacini, Lain: Based on Babcock proposal indicating consumption rate of 20 lbs/hr.
Note on G15: Courtney Kimball: Based on ammonia solution cost from similar BACT analysis - $0.75/gal and specific gravity of 0.9
Note on E16: Pacini, Lain: Babcock characterized this energy use as minimal in their proposal, so a firm estimate was not included.
Note on G16: Pacini, Lain: Current Per kW price based on GVEA data.
Note on E23: Pacini, Lain: Percentage of total capital investment
Note on K33: Pacini, Lain: Babcock proposal indicates SNCR NOX control in the range of 10%-20%. 20% was used here as a worst-case estimate.

## 3-8 - EU 3 - SCR TCI
Table 3-8. UAF - Capital Costs for SCR on
the Mid-sized Diesel Boiler (EU ID 3)
Shaded cells indicate user inputs.
Total Capital Investment Determination - SCR | [7 empty] | Date: | 2016-02-17
Project: |  | UAF - PM2.5 BACT Analysis (EU ID 3 - Zurn Boiler) | [5 empty] | Prepared By: | L. Pacini
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | C
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Total SCR System | 1 | EA | 850000 | 850000
|  | (per Fuel Tech) | [5 empty] | TOTAL = | 850000
| (b) | Instrumentation
|  | NOx CEMs System | 1 | EA | 50000 | 50000
|  | NOx CEMS Certification Testing | 1 | EA | 10000 | 10000
[8 empty] | TOTAL = | 60000
| (c) | Freight
|  | SCR Freight | 1 |  | 20000
[8 empty] | TOTAL = | 20000
| (d) | Labor
|  | Labor - shop fab |  | MH |  |  | Included above
|  | Labor - onsite |  | MH |  |  | Included above
[8 empty] | TOTAL = | 0
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR | 0.5% | % |  | 4250
[8 empty] | TOTAL = | 4250
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | Included above
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | Included above
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope. |  |  |  |  | PEMC = | 934250
(2) | Direct Installation Costs
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  |  |  | 0
|  | Functional Checkout - onsite, enter % |  | % onsite fab labor |  |  |  |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) - 2 x SCR Equipment Capital | [7 empty] | DIC = | 1700000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 2634250
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  |  | % TDC |  |  | 0 |  | Included in PEMC above.
(4) | Performance tests |  | 1 | EA | 10000 |  | 10000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 10000
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  | 30% | % TDC |  |  | 790275
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 790275
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 3434525
Note on G13: Pacini, Lain: Fuel Tech (FTEK) proposal
Note on G16: Pacini, Lain: Based on engineering estimates/experience.
Note on G17: Pacini, Lain: Based on engineering estimates/experience.
Note on K47: Pacini, Lain: Assume installation of SCR requires 2 x the SCR equipment capital.
Note on E61: Pacini, Lain: Based on +/- 30% contingency included in FTEK proposal.

## 3-9 - EU 3 - SCR CE
Table 3-9. UAF - Annualized Costs for SCR on
the Mid-sized Diesel Boiler (EU ID 3)
Shaded cells indicate user inputs
Cost Effectiveness Determination - SCR | [7 empty] | Date: | 2016-02-17
Project: |  | UAF - PM2.5 BACT Analysis (EU ID 3 - Zurn Boiler) | [5 empty] | Prepared By: | L. Pacini
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | C
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 730 | MH | 105 |  | 76650 |  | 76650
(2) | Supervisory Labor |  | 182.5 | MH | 125 |  | 22812.5 |  | 22812.5
(3) | Maintenance Labor |  | 365 | MH | 105 |  | 38325 |  | 38325
(4) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(5) | Utilities
| (a) | Urea Solution: | 15.5734 | TON | 356 | 5544.1162 |  |  | 5544.1162
(50% Urea solution and 2.2 moles needed per ton of NOX removed.)
| (b) | Energy: | 376680 | kWh | 0.18 | 67802.4 |  |  | 67802.4
(6) | Annual RATA Testing |  | 1 | EA | 10000 | 10000 |  |  | 10000
(7) | Catalyst Replacement Costs (every 2 years)
(per FuelTech)
| (a) | Replacement of SCR Catalyst: % of total equipment cost | 30% | % total equip | 934250 | 280275 |  |  | 135398.5507
(per MiraTech)
| (b) | Replacement labor for SCR Catalyst | 180 | MH | 105 |  | 18900 |  | 9130.4348
| (c) | Transport cost direct to site (SCR catalyst) | 13% | % replacement |  |  | 36435.75 |  | 17601.8116
| (d) | Transport cost for spent SCR catalyst | 13% | % replacement |  |  | 36435.75 |  | 17601.8116
Sinking Fund Factor [see inputs below]: |  |  | 0.48309
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 400866.6249
INDIRECT ANNUAL COSTS
(8) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(9) | Administrative Charges and Insurance |  | 3% | % total capital |  |  | 103035.75 |  | 103035.75
| Capital Recovery Factor [see inputs below] |  | 0.14238
(10) | Capital Recovery | [6 empty] | CRF * TCI = | 488999.0926
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 592034.8426
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 992901.4674
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 117.98
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 8415.8456
Data Inputs for Capital Recovery Factor and Sinking Fund Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life (from vendor) | 2 | years
|  | Asset Utilization | 100 | %
Note on E10: Pacini, Lain: Have historically used 2 hours per day for operating.
Note on G10: Courtney Kimball: Based on similar project.
Note on E11: Pacini, Lain: Assumed to be half of maintenance labor.
Note on G11: Courtney Kimball: Based on similar project.
Note on E12: Pacini, Lain: Have historically used 1 hours per day for maintenance
Note on G12: Courtney Kimball: Based on similar project.
Note on E15: Pacini, Lain: 50% urea solution and 2.2 moles needed per ton NOx controlled.
Note on G15: Pacini, Lain: December 2015 price according to Farmer's Coop Association.
Note on E17: Pacini, Lain: 43 kW energy consumption based on 70 kW required for the 295.6 MMBtu/hr CFB boiler. Assuming that the ratio of the 180.9 MMBtu/hr to the 295.6 MMBtu/hr boiler would proportionally decrease the power consumption required by the SCR. Assume 8760 hours/yr.
Note on G17: Pacini, Lain: Current Per kW price based on GVEA data.
Note on C21: Pacini, Lain: Based on FTEK proposal
Note on E23: Pacini, Lain: Miratech indicated that catalyst makes up 30% of the SCR system cost
Note on E25: Courtney Kimball: Replacement labor based on similar project.
Note on G25: Courtney Kimball: Based on similar project.
Note on E26: Courtney Kimball: Based on similar project.
Note on E27: Courtney Kimball: Based on similar project.
Note on E35: Pacini, Lain: Percentage of total capital investment
Note on K45: Pacini, Lain: Based on 85% control in FTEK proposal.

## 3-10 - EU ID 3 LNB-FGR TCI
Table 3-10. UAF - Capital Costs for LNB/FGR on
the Mid-sized Diesel Boiler (EU ID 3)
Total Capital Investment Determination - Low NOX Burners & FGR | [7 empty] | Date: | 2016-04-12
Project: |  | UAF PM2.5 BACT Analysis - Zurn Boiler #3 (EU ID 3) | [5 empty] | Prepared By: | L. Pacini
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | C
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Low NOx Burner | 1 | EA | 419484 | 419484
|  | FGR FD Fans | 1 | EA | 198872 | 198872 |  | TOTAL = | 618356
(from Indeck)
| (b) | Instrumentation
|  | Total Instrumentation |  | EA |  | 0 | Included in above price
[8 empty] | TOTAL = | 0
| (c) | Freight
|  |  |  | % MATL COST | 10% |  | 61835.6
[8 empty] | TOTAL = | 61835.6
| (d) | Labor
|  | Labor - offsite fab | 0 | MH |  | None required | 0
|  | Labor - onsite | 30 | MH | 105 |  | 3150
|  | (from Indeck) | [5 empty] | TOTAL = | 3150
| (e) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees | 0 | MH |  | None required | 0
|  | Onsite Vendor Representatives fees | 46 | MH | 223.7 |  | 10290.2
|  | Onsite Vendor Representatives Travel & Expenses | 1 | EA | 3500 | 3500
|  | (from Indeck) | [5 empty] | TOTAL = | 13790.2
Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 697131.8
Direct Installation Costs (DIC) | [7 empty] | DIC = | 340947.5
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 1038079.3
INDIRECT COSTS
(2) | Engineering, Procurement & Construction Support Services |  | 10% | % TDC |  |  | 103807.93
(3) | Performance tests for NOX emissions |  | 1 | EA | 10000 |  | 10000 |  | Excluded in this estimate.
Total Indirect Costs (TIC) | [7 empty] | TIC = | 113807.93
MANAGEMENT AND CONTINGENCY COSTS
(4) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(5) | Contingency |  | 10% | % TDC |  |  | 103807.93
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 103807.93
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 1255695.16
Note on G13: Pacini, Lain: Supplier (INDeck) proposal dated 2/5/2016
Note on G14: Pacini, Lain: Supplier (INDeck) proposal dated 2/5/2016
Note on G20: Pacini, Lain: Based on vendor estimate for DPF on CAT emergency engine.
Note on E24: Pacini, Lain: Indeck service quote indicates 30 hours of boiler inspection work. Assume UAF staff would participate.
Note on G24: Courtney Kimball: Based on similar project.
Note on E28: Pacini, Lain: Indeck quote includes 40 hours of standard staff labor and 6 hours of overtime.
Note on G28: Pacini, Lain: Combined wieghted cost from Indeck considering standard tims and overtime rates.
Note on G29: Pacini, Lain: Indeck service quote
Note on K33: Pacini, Lain: Based on labor, materials and subcontractor quote from Haskell Corp. Quote includes an accuracy note of +/- 25%. 25% was added here to cost.

## 3-11 - EU ID 3 LNB-FGR CE
Table 3-11. UAF - Annualized Costs for LNB/FGR on
the Mid-sized Diesel Boiler (EU ID 3)
Shaded cells indicate user inputs
Cost Effectiveness Determination - Low NOX Burners & FGR | [7 empty] | Date: | 2016-04-12
Project: |  | UAF PM2.5 BACT Analysis - Zurn Boiler #3 (EU ID 3) | [5 empty] | Prepared By: | L. Pacini
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | C
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor - Not required |  |  | MH |  |  | 0 |  | 0
(2) | Supervisory Labor - Not required |  |  | MH |  |  | 0 |  | 0
(3) | Maintenance Labor - Not required |  |  | MH |  |  | 0 |  | 0
(4) | Maintenance Materials - Not required |  |  | LOT |  | 0 | 0 |  | 0
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 0
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(6) | Administrative Charges and Insurance |  | 3% | % total capital |  |  | 37670.8548 |  | 37670.8548
| Capital Recovery Factor [see inputs below] |  | 0.14238
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 178782.7411
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 216453.5959
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 216453.5959
Cost Effectiveness Summary
TOTAL TONS AVOIDED PER YEAR | [7 empty] | = | 59.5658
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 3633.8569
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | N/A | years
|  | Asset Utilization | N/A | %
Note on E19: Pacini, Lain: Percentage of total capital investment
Note on K29: Pacini, Lain: Indeck quote indicates LNB + FGR can redcue emissions to 0.1 lbs/MMBtu. Uncontrolled PTE is 138.8 TPY.

## 3-12 - EU ID 4 - LNB-FGR TCI
Table 3-12. UAF - Capital Costs for LNB/FGR on
the Mid-sized Diesel Boiler (EU ID 4)
Shaded cells indicate user inputs.
Total Capital Investment Determination - Low NOX Burners & FGR | [7 empty] | Date: | 2016-03-18
Project: |  | UAF PM2.5 BACT Analysis - Zurn Boiler (EU ID 4) | [5 empty] | Prepared By: | L. Pacini
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | A
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Low NOx Burner | 1 | EA | 444039 | 444039
|  | FGR FD Fans | 1 | EA | 187755 | 187755 |  | TOTAL = | 631794
| (b) | Instrumentation
|  | Total Instrumentation |  | EA |  | 0 | Included in above price
[8 empty] | TOTAL = | 0
| (c) | Freight
|  |  |  | % MATL COST | 10% |  | 44403.9
[8 empty] | TOTAL = | 44403.9
| (d) | Labor
|  | Labor - offsite fab | 0 | MH |  | None required | 0
|  | Labor - onsite | 0 | MH | 0 |  | 0
[8 empty] | TOTAL = | 0
| (e) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 0 | Days |  |  | 0
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 0 | Days |  |  | 0
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 676197.9
Direct Installation Costs (DIC) | [7 empty] | DIC = | 442659.0538
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 1118856.9538
INDIRECT COSTS
(2) | Engineering, Procurement & Construction Support Services |  | 10% | % TDC |  |  | 111885.6954
(3) | Performance tests |  |  | EA |  |  | 0 |  | Excluded in this estimate.
Total Indirect Costs (TIC) | [7 empty] | TIC = | 111885.6954
MANAGEMENT AND CONTINGENCY COSTS
(4) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(5) | Contingency |  | 10% | % TDC |  |  | 111885.6954
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 111885.6954
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 1342628.3446
Note on G13: Pacini, Lain: Supplier (INDeck) proposal dated 2/5/2016
Note on G14: Pacini, Lain: Supplier (INDeck) proposal dated 2/5/2016
Note on G20: Pacini, Lain: Based on vendor estimate for DPF on CAT emergency engine.
Note on K32: Pacini, Lain: Supplier (Proctor Sales) email dated 11/5/2015: cost for install is $15K for 6.13 MMBtu/hr Boiler. Scaled cost up to 180.9 MMBtu/hr for Zurn boiler.

## 3-13 EU ID 4 - LNB-FGR CE
Table 3-13. UAF - Annualized Costs for LNB/FGR on
the Mid-sized Diesel Boiler (EU ID 4)
Shaded cells indicate user inputs
Cost Effectiveness Determination - Low NOX Burners & FGR | [7 empty] | Date: | 2016-03-18
Project: |  | UAF PM2.5 BACT Analysis - Zurn Boiler (EU ID 4) | [5 empty] | Prepared By: | L. Pacini
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | A
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  |  | MH |  |  | 0 |  | 0
(2) | Supervisory Labor |  |  | MH |  |  | 0 |  | 0
(3) | Maintenance Labor |  |  | MH |  |  | 0 |  | 0
(4) | Maintenance Materials |  |  | LOT |  | 0 | 0 |  | 0
Total Direct Annual Costs (TDAC) |  |  |  | Excluded in this estimate |  |  |  | TDAC = | 0
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(6) | Administrative Charges and Insurance |  | 3% | % total capital |  |  | 40278.8503 |  | 40278.8503
| Capital Recovery Factor [see inputs below] |  | 0.14238
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 191160.0708
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 231438.9211
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 231438.9211
Cost Effectiveness Summary
TOTAL TONS AVOIDED PER YEAR | [7 empty] | = | 1.2225
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 189311.7549
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | N/A | years
|  | Asset Utilization | N/A | %
Note on E19: Pacini, Lain: Percentage of total capital investment
Note on K29: Pacini, Lain: Indeck quote indicates LNB + FGR can reduce emissions to 0.16 lbs/MMBtu and 12.7 TPY based on 10% capacity factor. Uncontrolled PTE is based on 10% capacity factor limit is 13.9 TPY.

## 3-14 EU8 SCR TCI
Table 3-14. UAF - Capital Costs for SCR on
the Large Diesel-Fired Engine (EU ID 8)
Shaded cells indicate user inputs
Total Capital Investment Determination - SCR | [7 empty] | Date: | 2016-10-13
Project: |  | UAF - PM2.5 BACT Analysis (EU ID 8 - Peaking/Backup Generator Engine) | [5 empty] | Prepared By: | J. Rubino
[8 empty] | Checked By: | L. Pacini
[8 empty] | Rev: | A
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Total SCR System | 1 | EA | 2842107.84 | 2842107.84
[8 empty] | TOTAL = | 2842107.84
| (b) | Instrumentation
|  | NOx CEMs System |  | EA |  | 0
|  | NOx CEMS Certification Testing |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (c) | Freight
SCR Freight
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - shop fab |  | MH
|  | Labor - onsite |  | MH
[8 empty] | TOTAL = | 0
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR |  | % |  | 0
[8 empty] | TOTAL = | 0
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) |  | Days
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) |  | Days
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) |  |  | Note: Although existing SCR to be used, capital costs needed for catalyst replacement costs. |  |  |  |  | PEMC = | 2842107.84
(2) | Direct Installation Costs
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  |  |  | 0
|  | Functional Checkout - onsite, enter % |  | % onsite fab labor |  |  |  |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) |  |  | Note: Although existing SCR to be used, capital costs needed for catalyst replacement costs. |  |  |  |  | DIC = | 5684215.68
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 8526323.52
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  |  | % TDC |  | N/A | 0
(4) | Performance tests |  |  | EA |  | N/A | 0
Total Indirect Costs (TIC) | [7 empty] | TIC = | 0
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  |  | % TDC |  | N/A | 0
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 0
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 8526323.52
Note on G13: Pacini, Lain: Used the capital cost for SCR on the 500 HP ACEP engine and ratioed up the cost based on the 13,266 HP DEG (EU ID8).

## 3-15 EU8 SCR CE
Table 3-15. UAF - Annualized Costs for SCR on
the Large Diesel-Fired Engine (EU ID 8)
Shaded cells indicate user inputs
Cost Effectiveness Determination - SCR | [7 empty] | Date: | 2016-10-13
Project: |  | UAF - PM2.5 BACT Analysis (EU ID 8 - Peaking/Backup Generator Engine) | [5 empty] | Prepared By: | J. Rubino
[8 empty] | Checked By: | L. Pacini
[8 empty] | Rev: | A
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 730 | MH | 105 |  | 76650 |  | 76650
(2) | Supervisory Labor |  | 182.5 | MH | 125 |  | 22812.5 |  | 22812.5
(3) | Maintenance Labor |  | 365 | MH | 105 |  | 38325 |  | 38325
(4) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(5) | Utilities
| (a) | Aqueous Ammonia | 29.9592 | TON | 200.08 | 5994.2377 |  |  | 5994.2377
| (b) | Energy: | 69904.8 | kWh | 0.18 | 12582.864 |  |  | 12582.864
(6) | Annual RATA Testing |  | 0 | EA | 10000 | 0 |  |  | 0
(7) | Catalyst Replacement Costs (every 2 years)
| (a) | Replacement of SCR Catalyst: % of total equipment cost | 30% | % total equip | 2842107.84 | 852632.352 |  |  | 411899.687
| (b) | Replacement labor for SCR Catalyst | 180 | MH | 105 |  | 18900 |  | 9130.4348
| (c) | Transport cost direct to site (SCR catalyst) | 13% | % replacement |  |  | 110842.2058 |  | 53546.9593
| (d) | Transport cost for spent SCR catalyst | 13% | % replacement |  |  | 110842.2058 |  | 53546.9593
Sinking Fund Factor [see inputs below]: |  |  | 0.48309
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 684488.642
INDIRECT ANNUAL COSTS
(8) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(9) | Administrative Charges, Property Taxes, Insurance |  | 3% | % total capital |  |  | 255789.7056 |  | 255789.7056
| Capital Recovery Factor [see inputs below] |  | 0.14238
(10) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 255789.7056
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 940278.3476
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 36
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 26118.843
Data Inputs for Capital Recovery Factor and Sinking Fund Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life (from vendor) | 2 | years
|  | Asset Utilization | 100 | %
Note on E10: Pacini, Lain: Have historically used 2 hours per day for operating.
Note on G10: Courtney Kimball: Based on similar project.
Note on E11: Pacini, Lain: Assumed to be half of maintenance labor.
Note on G11: Courtney Kimball: Based on similar project.
Note on E12: Pacini, Lain: Have historically used 1 hours per day for maintenance
Note on G12: Courtney Kimball: Based on similar project.
Note on E15: Pacini, Lain: 6.84 lbs/hr reagent consumption based on 60 lbs/hr required for the 295.6 MMBtu/hr CFB boiler. Assuming that the ratio of the 33.75 MMBtu/hr generator to the 295.6 MMBtu/hr boiler would proportionally decrease the reagent consumption required by the SCR. Assume 8760 hours/yr.
Note on G15: Courtney Kimball: Based on ammonia solution cost from similar BACT analysis - $0.75/gal and specific gravity of 0.9.
Note on E16: Pacini, Lain: 7.98 kW energy consumption based on 70 kW required for the 295.6 MMBtu/hr CFB boiler. Assuming that the ratio of the 33.75 MMBtu/hr generator to the 295.6 MMBtu/hr boiler would proportionally decrease the power consumption required by the SCR. Assume 8760 hours/yr.
Note on G16: Pacini, Lain: Current Per kW price based on GVEA data.
Note on E21: Pacini, Lain: Miratech indicated that catalyst makes up 30% of the SCR system cost
Note on E22: Courtney Kimball: Based on similar project.
Note on G22: Courtney Kimball: Based on similar project.
Note on E23: Courtney Kimball: Based on similar project.
Note on E24: Courtney Kimball: Based on similar project.
Note on E32: Pacini, Lain: Percentage of total capital investment
Note on K42: Pacini, Lain: Based on 90% control.

## 3-16 - EU 27 - SCR TCI
Table 3-16. UAF - Capital Costs for SCR on
the Small Diesel-Fired Engine (EU ID 27)
Shaded cells indicate user inputs.
Total Capital Investment Determination - SCR | [7 empty] | Date: | 2015-12-18
Project: |  | UAF PM2.5 BACT Analysis - ACEP Engine (EU ID 27) | [5 empty] | Prepared By: | L. Pacini
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | D
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Total SCR System | 1 | EA | 107120 | 107120
|  | (per NC Power Systems) | [5 empty] | TOTAL = | 107120
| (b) | Instrumentation
|  | Total Instrumentation |  | EA |  | 0
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | SCR Freight |  |  | 10500 |  | 10500
|  | (per NC Power Systems) | [5 empty] | TOTAL = | 10500
| (d) | Labor
|  | Labor - offsite fab |  | MH |  | Not included | 0
|  | Labor - onsite | 16 | MH | 105 |  | 1680
[8 empty] | TOTAL = | 1680
| (e ) | Startup Spares
|  | Startup Spare Parts for SCR | 0.5% | % |  | 535.6
[8 empty] | TOTAL = | 535.6
| (f) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | 0
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) |  | Days |  |  | 0
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 119835.6
(2) | Direct Installation Costs
| (a) | Concrete |  | CY |  | 0 |  |  | 0
| (b) | Piling |  | TON |  | 0 |  |  | 0
| (c) | Structural steel |  | TON |  | 0 |  |  | 0
| (d) | Electrical |  | LOT |  | 0 |  |  | 0
| (e ) | Painting |  | SF |  | 0 |  |  | 0
| (f) | Insulation |  | LOT |  | 0 |  |  | 0
| (g) | Abovegrade piping |  | LF |  | 0 |  |  | 0
| (h) | Functional Checkouts
|  | Functional Checkout - fab site, enter %: |  | % offsite fab labor |  |  | 0 |  | 0
|  | Functional Checkout - onsite, enter % |  | % onsite fab labor |  |  | 0 |  | 0
|  | Contractor Commissioning, enter %: |  | % of equipment total cost |  |  | 0 |  | 0
Direct Installation Costs (DIC) - estimated at 10% Purchased Equipment Cost | [7 empty] | DIC = | 11983.56
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 131819.16
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 15% | % TDC |  |  | 19772.874
(4) | Performance tests |  | 0 | EA |  |  | 0 |  | Excluded in this estimate.
Total Indirect Costs (TIC) | [7 empty] | TIC = | 19772.874
MANAGEMENT AND CONTINGENCY COSTS
(5) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(6) | Contingency |  |  | % TDC |  |  | 0 |  | Excluded in this estimate.
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 0
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 151592.034
Note on E26: Courtney Kimball: Cost of startup spares indicated as a percentage of equipment cost per similar BACT analysis.

## 3-17 - EU 27 - SCR CE
Table 3-17. UAF - Annualized Costs for SCR on
the Small Diesel-Fired Engine (EU ID 27)
Shaded cells indicate user inputs
Cost Effectiveness Determination - SCR | [7 empty] | Date: | 2015-12-18
Project: |  | UAF PM2.5 BACT Analysis - ACEP Engine (EU ID 27) | [5 empty] | Prepared By: | L Pacini
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | D
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 60.8333 | MH | 105 |  | 6387.5 |  | 6387.5
(2) | Supervisory Labor |  | 91.25 | MH | 125 |  | 11406.25 |  | 11406.25
(3) | Maintenance Labor |  | 182.5 | MH | 105 |  | 19162.5 |  | 19162.5
(4) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(5) | Utilities
| (a) | Urea/DEF: | 39.7635 | TON | 587 | 23341.1919 |  |  | 23341.1919
| (b) | Energy: |  | kW |  | excluded in this estimate
(6) | Catalyst Replacement Costs (every 5 years)
| (a) | Replacement of SCR Catalyst: % of total equipment cost | 30% | % total equip | 119835.6 | 35950.68 |  |  | 2858.2435
(per Miratech)
| (b) | Replacement labor for SCR Catalyst | 8 | MH | 105 |  | 840 |  | 66.7838
| (c) | Transport cost direct to site (Urea, SCR catalyst) |  | % |  | excluded in this estimate | 0 |  | 0
| (d) | Transport cost for spent SCR catalyst |  | % |  | excluded in this estimate | 0 |  | 0
Sinking Fund Factor [see inputs below]: |  |  | 0.079505
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 63222.4693
INDIRECT ANNUAL COSTS
(7) | Overhead |  |  | MH |  | excluded in this estimate | 0 |  | 0
(8) | Administrative Charges |  |  | MH |  | excluded in this estimate | 0 |  | 0
(9) | Property tax |  |  |  |  | excluded in this estimate
(10) | Insurance |  |  |  |  | excluded in this estimate
| Capital Recovery Factor [see inputs below] |  | 0.080243
(11) | Capital Recovery | [6 empty] | CRF * TCI = | 12164.137
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 12164.137
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 75386.6063
Cost Effectiveness Summary
TOTAL TONS NOx AVOIDED PER YEAR | [7 empty] | = | 6.93
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 10878.2982
Data Inputs for Capital Recovery Factor and Sinking Fund Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 20 | years
|  | Catalyst Life | 5 | years
|  | Asset Utilization | 50 | %
Note on G15: Pacini, Lain: Current DEF price at pump $2.79/gal and density of 9.50 lbs/gal; 50% urea solution

## 3-18
Table 3-18. UAF - NOX BACT Cost Effectiveness
Summary for Each Emission Unit Type
Control Technology Option | Total Installed Capital ($) | Annualized Capital Cost ($/year) | Annual O&M Cost ($/year) | Cost Effectiveness ($/ton NOX removed)
Large Coal-fired Boiler (Emission Unit 113)
SCR + (CFB with staged combustion) | 26740640 | 5889641.7769 | 1280157.0324 | 28424.9121
SNCR + (CFB with staged combustion) | 2960000 | 527764.4189 | 17527.0108 | 10192.4376
CFB with staged combustion | ~ | ~ | ~ | ~
Mid-sized Boiler (EU ID 3)
SCR | 3434525 | 992901.4674 | 400866.6249 | 8415.8456
LNB/FGR1 | 1255695.16 | 216453.5959 | ~ | 3633.8569
Good Combustion Practices | ~ | ~ | ~ | ~
Mid-sized Boiler (EU ID 4)
LNB/FGR | 1342628.3446 | 231438.9211 | ~ | 189311.7549
Good Combustion Practices | ~ | ~ | ~ | ~
Large Diesel-fired Engine (EU ID 8)
SCR + (Turbocharger and Aftercooler + Limited Operation) | 8526323.52 | 940278.3476 | 684488.642 | 26118.843
Turbocharger and Aftercooler + Limited Operation | ~ | ~ | ~ | ~
Small Diesel-fired Engine (EU ID 27)
SCR + (Turbocharger and Aftercooler + Federal Limit + Limited Operation) | 151592.034 | 75386.6063 | 63222.4693 | 10878.2982
Turbocharger and Aftercooler + Federal Limit + Limited Operation | ~ | ~ | ~ | ~
Notes:
1 If the cost effectiveness of a LNB/FGR system were based on the actual operation of EU ID 3 during the last five years, the cost effectiveness of LNB/FGR would be approximately $35,500 per ton of NOX removed.

## 3-19
Table 3-19. UAF - Proposed NOX BACT and Associated
Emission Rate for Each Emission Unit Type
Emission Unit |  | Fuel | NOX BACT
ID | Description |  | Description | Emission Rate1
113 | Large Boiler | Coal and Biomass | CFB with staged combustion | 0.2 lb/MMBtu
3 | Mid-sized Boiler | Diesel | Good Combustion Practices | 0.2 lb/MMBtu
4 | Mid-sized Boiler | Diesel | Limited Operation + Good Combustion Practices | 0.2 lb/MMBtu
|  | Natural Gas | Limited Operation + Good Combustion Practices | 140 lb/MMscf
19 through 21 | Small Boilers | ULSD | Limited Operation | 1.24 g/MMBtu
8 | Large Engine | Diesel | Turbocharger and Aftercooler + Limited Operation | 0.0195 g/hp-hr
27 | Small Engine | ULSD | Turbocharger and Aftercooler + Federal Limit + Limited Operation | 3.20 g/hp-hr
9A | Medical/Pathological Waste Incinerator | Waste | Good Combustion Practices + Limited Operation | 3.56 lb/ton
Notes:
1 Emissions are on a per unit basis.

## 5-22 (hidden)
Table 5-22. Point Thomson Project - Proposed VOC BACT and Associated
Emission Rate for Each Emission Unit Type
Emission Unit |  | Fuel | CO BACT
ID | Description |  | Description | Emission Rate
101 and 102 | Solar Taurus Turbine | Fuel Gas | Catalytic Oxidation | 25 ppm at ≥10 degrees F (in SoLoNOX mode)
103 and 104 | Solar Taurus Turbine | Dual Fuel-fired | Catalytic Oxidation | 100 ppm at ≥10 degrees F (in SoLoNOX mode)
105 | Waste Incinerator | ULSD | Good Combustion Practices | 1.0 g/hp-hr
106 through 109, 115, and 116 | Distillate-fired Engines | ULSD | Good Combustion Practices | 0.19 g/KW-hr
110 through 112 | Fine Water Mist Supply and Firewater Pumps | ULSD | Good Combustion Practices | 0.00247 lb/hp-hr
113 and 114 | Flares | Fuel Gas | None | 4.0 g/KW-hr (NOX and HC, combined)
Notes:
1 Emissions are on a per unit basis.
2 ULSD fired engines have NSPS Subpart IIII VOC emission limits.