## 4-1
Table 4-1. UAF - Available PM2.5 Control Options
Emission Unit |  | Available Control
ID | Description | Options
113 | Large Coal and Biomass-fired Boiler | Fabric Filters
ESP
Scrubber
Cyclone
Good Combustion Practices
3 and 4 | Mid-sized Diesel-fired Boilers | Fabric Filters
ESP
Scrubber
Cyclone
Limited Operation
Good Combustion Practices
19 through 21 | Small Diesel-fired Boilers | Scrubber
Limited Operation
Good Combustion Practices
8 | Large Diesel-fired Engine | DPF
Positive Crankcase Ventilation
Low Ash Diesel
Limited Operation
Good Combustion Practices
27 | Small Diesel-fired Engines | DPF
Federal Standard
Limited Operation
Good Combustion Practices
9A | Medical/Pathological Waste Incinerator | Fabric Filters
ESP
Limited Operation
Good Combustion Practices
Multiple Chambers
105, 107, 109, 110, 114, and 128 through 130 | Material Handling Sources with Fabric Filtration | Fabric Filters
Scrubber
Suppressant
Enclosure
Closed System Vent
111 | Material Handling Sources without Fabric Filtration | Suppressant
Enclosure

## 4-2
Table 4-2. UAF - Technically Feasible PM2.5 Control Options
Emission Unit |  | Technically Feasible
ID | Description | Control Options
113 | Large Coal and Biomass-fired Boiler | Fabric Filters
ESP
Scrubber
Cyclone
Good Combustion Practices
3 | Mid-sized Diesel Fired Boiler | Good Combustion Practices
4 | Mid-sized Diesel Fired Boiler | Limited Operation
19 through 21 | Small Diesel-fired Boilers | Scrubber
Limited Operation
8 | Large Diesel-fired Engine | Positive Crankcase Ventilation
Low Ash Diesel
Limited Operation
27 | Small Diesel-fired Engine | DPF
Federal Standard
Limited Operation
9A | Medical/Pathological Waste Incinerator | Fabric Filters
Limited Operation
Good Combustion Practices
Multiple Chambers
105, 107, 109, 110, 114, and 128 through 130 | Material Handling Emission Units with Fabric Filtration | Fabric Filters
Enclosure
Closed System Venting
111 | Material Handling Emission Unit without Fabric Filtration | Enclosure

## 4-3
Table 4-3. UAF - Ranking of Technically Feasible PM2.5 Control Options
Emission Unit |  | Control | Control | PM2.5 Emissions | Emissions
ID | Description | Technology | Efficiency (pct.) | (tpy) | Reduction (tpy)
113 | Large Coal and Biomass-fired Boiler | Fabric filter | 95 | 15.5 | 294.5
|  | ESP | 90 | 31 | 279
|  | Scrubber | 70 | 93 | 217
|  | Cyclone | 20 | 248 | 62
|  | Good Combustion Practices | 0 | 310 | 0
19 through 21 | Small Diesel-fired Boilers1 | Scrubber + Limited Operation | 99 | 0.0094 | 0.9306
|  | Limited Operation | 0 | 0.94 | 0
27 | Small Diesel-fired Engine | DPF + (Federal Limit + Limited Operation) | 85 | 0.03945 | 0.22355
|  | Federal Limit + Limited Operation | 0 | 0.263 | 0
9A | Medical/Pathological Waste Incinerator | Fabric Filters + Multiple Chambers | 95 | 0.012725 | 0.24178
|  | Multiple Chambers + (Limited Operation) | 0 | 0.2545 | 0
105, 107, 109, 110, 114, and 128 through 130 | Material Handling Emission Units with Fabric Filtration | Closed System Venting | 100 | 0 | Varies2
|  | Fabric Filter + Enclosure | 0 | Varies2 | 0
1EU ID 19 through 21 PM2.5 emissions of 0.94 tpy are the joint emissions from all three boilers.
2The total PM2.5 emissions for EU IDs 105, 107, 109, 110, 114, and 128 through 130 is 1.2 tpy. Emissions reduction due to any control
technology for any one of these emission units will be less than or equal to 0.2 tpy.

## 4-4 - 19-21 - TCI
Table 4-4. UAF - Capital Costs for Scrubber on
the Small Diesel-Fired Boilers (EU IDs 19 through 21)
Shaded cells indicate user inputs.
Total Capital Investment Determination - Scrubber | [7 empty] | Date: | 2015-12-18
Project: |  | UAF PM2.5 BACT Analysis - BiRD Boilers 1 through 3 (EU19 through 21; WM 2094W) | [5 empty] | Prepared By: | C. Stevenson
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | B
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Scrubber for 3 Boilers, Units 19, 20, & 21 (includes freight & install) | 1 | EA | 300000 | 300000
|  | (per Proctor Sales Inc.) | [5 empty] | TOTAL = | 300000
| (b) | Instrumentation
|  | Total Instrumentation |  | EA |  | 0 | Included in above price
[8 empty] | TOTAL = | 0
| (c) | Freight
|  |  |  | % MATL COST |  |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab | 0 | MH |  | None required | 0
|  | Labor - onsite | 0 | MH | 0 |  | 0
[8 empty] | TOTAL = | 0
| (e) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 0 | Days |  |  | 0
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 0 | Days |  |  | 0
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 300000
Direct Installation Costs (DIC) | [7 empty] | DIC =
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 300000
INDIRECT COSTS
(2) | Engineering, Procurement & Construction Support Services |  |  | % TDC |  |  | 0 |  | Excluded in this estimate.
(3) | Performance tests |  |  | EA |  |  | 0 |  | Excluded in this estimate.
Total Indirect Costs (TIC) | [7 empty] | TIC = | 0
MANAGEMENT AND CONTINGENCY COSTS
(4) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(5) | Contingency |  |  | % TDC |  |  | 0 |  | Excluded in this estimate.
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 0
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 300000

## 4-5 - 19-21 - CE
Table 4-5. UAF - Annualized Costs for Scrubber on
the Small Diesel-Fired Boilers (EU IDs 19 through 21)
Shaded cells indicate user inputs
Cost Effectiveness Determination - Scrubber | [7 empty] | Date: | 2015-12-18
Project: |  | UAF PM2.5 BACT Analysis - BiRD Boilers 1 through 3 (EU19 through 21; WM 2094W) | [5 empty] | Prepared By: | C. Stevenson
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | B
Annualized Costs
DIRECT ANNUAL COSTS - EXCLUDED IN THIS ESTIMATE |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  |  | MH |  |  | 0 |  | 0
(2) | Supervisory Labor |  |  | MH |  |  | 0 |  | 0
(3) | Maintenance Labor |  |  | MH |  |  | 0 |  | 0
(4) | Maintenance Materials |  |  | LOT |  | 0 |  |  | 0
Total Direct Annual Costs (TDAC) |  |  |  | Excluded in this estimate |  |  |  | TDAC = | 0
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(6) | Administrative Charges |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(7) | Property tax |  |  |  |  | Not Applicable
(8) | Insurance |  |  |  |  | Excluded in this estimate.
| Capital Recovery Factor [see inputs below] |  | 0.14238
(9) | Capital Recovery | [6 empty] | CRF * TCI = | 42713.2508
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 42713.2508
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 42713.2508
Cost Effectiveness Summary
TOTAL TONS AVOIDED PER YEAR | [7 empty] | = | 0.891
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 47938.5531
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | N/A | years
|  | Asset Utilization | N/A | %
Note on K31: Stevenson, Cindy: PM2.5 PTE = 0.9 tpy for all three boilers combined from UAF NAA BACT PTE.xlsx, assume 99% reduction in emissions from a scrubber.

## 4-6 - 27 - TCI
Table 4-6. UAF - Capital Costs for DPF on
the Small Diesel-Fired Engine (EU ID 27)
Shaded cells indicate user inputs.
Total Capital Investment Determination - DPF | [7 empty] | Date: | 2015-12-18
Project: |  | UAF PM2.5 BACT Analysis - ACEP Engine (EU 27) | [5 empty] | Prepared By: | C. Stevenson
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | C
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Total DPF System | 1 | EA | 26428 | 26428
|  | (per NC Power Systems) | [5 empty] | TOTAL = | 26428
| (b) | Instrumentation
|  | Total Instrumentation |  | EA |  | 0 | Included in above price
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | DPF Freight |  | % MATL COST | 10% |  | 2642.8
[8 empty] | TOTAL = | 2642.8
| (d) | Labor
|  | Labor - offsite fab | 0 | MH |  | None required | 0
|  | Labor - onsite | 16 | MH | 105 |  | 1680
|  | (per SCI) | [5 empty] | TOTAL = | 1680
| (e) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 0 | Days |  |  | 0
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 0 | Days |  |  | 0
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 30750.8
Direct Installation Costs (DIC) |  |  | DPF replaces existing silencer, no direct installation costs necessary |  |  |  |  | DIC = | 0
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 30750.8
INDIRECT COSTS
(2) | Engineering, Procurement & Construction Support Services |  |  | % TDC |  |  | 0 |  | Excluded in this estimate.
(3) | Performance tests |  |  | EA |  |  | 0 |  | Excluded in this estimate.
Total Indirect Costs (TIC) | [7 empty] | TIC = | 0
MANAGEMENT AND CONTINGENCY COSTS
(4) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(5) | Contingency |  |  | % TDC |  |  | 0 |  | Excluded in this estimate.
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 0
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 30750.8
Note on E23: Pacini, Lain: Vendor indicated 1 to 2 days of install time.

## 4-7 - 27 - CE
Table 4-7. UAF - Annualized Costs for DPF on
the Small Diesel-Fired Engine (EU ID 27)
Shaded cells indicate user inputs
Cost Effectiveness Determination - DPF | [7 empty] | Date: | 2015-12-18
Project: |  | UAF PM2.5 BACT Analysis - ACEP Engine (EU 27) | [5 empty] | Prepared By: | C. Stevenson
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | C
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  |  | MH |  |  | 0 |  | 0
(2) | Supervisory Labor |  |  | MH |  |  | 0 |  | 0
(3) | Maintenance Labor |  |  | MH |  |  | 0 |  | 0
(4) | Maintenance Materials |  |  | LOT |  | 0 |  |  | 0
Total Direct Annual Costs (TDAC) |  |  |  | Excluded in this estimate |  |  |  | TDAC = | 0
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(6) | Administrative Charges |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(7) | Property tax |  |  |  |  | Not Applicable
(8) | Insurance |  |  |  |  | Excluded in this estimate.
| Capital Recovery Factor [see inputs below] |  | 0.14238
(9) | Capital Recovery | [6 empty] | CRF * TCI = | 4378.2221
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 4378.2221
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 4378.2221
Cost Effectiveness Summary
TOTAL TONS AVOIDED PER YEAR | [7 empty] | = | 0.221
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 19810.9598
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | N/A | years
|  | Asset Utilization | N/A | %

## 4-8 - 9A - TCI
Table 4-8. UAF - Capital Costs for a Fabric Filter on
the Medical/Pathological Waste Incinerator (EU ID 9A)
Shaded cells indicate user inputs.
Total Capital Investment Determination - Fabric Filter | [7 empty] | Date: | 2015-12-18
Project: |  | UAF PM2.5 BACT Analysis - BiRD INCINERATOR (EU 9A) | [5 empty] | Prepared By: | C. Stevenson
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | B
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | FABRIC FILTRATION - INSTALLED | 1 | EA | 1300000 | 1300000
|  | (per Thermtec) | [5 empty] | TOTAL = | 1300000
| (b) | Instrumentation
|  | Total Instrumentation |  | EA |  | 0 | Included in above price
[8 empty] | TOTAL = | 0
| (c) | Freight
|  | Freight included in basic equipment cost |  | % MATL COST |  |  | 0
[8 empty] | TOTAL = | 0
| (d) | Labor
|  | Labor - offsite fab | 0 | MH |  |  | 0
|  | Labor - onsite | 0 | MH | 0 |  | 0
[8 empty] | TOTAL = | 0
| (e) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees (enter no. of days and daily rate) | 0 | Days |  |  | 0
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 0 | Days |  |  | 0
[8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 1300000
Direct Installation Costs (DIC) | [7 empty] | DIC =
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 1300000
INDIRECT COSTS
(2) | Engineering, Procurement & Construction Support Services |  |  | % TDC |  |  | 0 |  | Excluded in this estimate.
(3) | Performance tests |  |  | EA |  |  | 0 |  | Excluded in this estimate.
Total Indirect Costs (TIC) | [7 empty] | TIC = | 0
MANAGEMENT AND CONTINGENCY COSTS
(4) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(5) | Contingency |  |  | % TDC |  |  | 0 |  | Excluded in this estimate.
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 0
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 1300000

## 4-9 - 9A - CE
Table 4-9. UAF - Annualized Costs for a Fabric Filter on
the Medical/Pathological Waste Incinerator (EU ID 9A)
Shaded cells indicate user inputs
Cost Effectiveness Determination - Fabric Filter | [7 empty] | Date: | 2015-12-18
Project: |  | UAF PM2.5 BACT Analysis - BiRD INCINERATOR (EU 9A) | [5 empty] | Prepared By: | C. Stevenson
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | B
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  |  | MH |  |  | 0 |  | 0
(2) | Supervisory Labor |  |  | MH |  |  | 0 |  | 0
(3) | Maintenance Labor (clean boiler/heat exchanger) |  | 104 | MH | 105 |  | 10920 |  | 10920
(4) | Maintenance Materials (Bag replacement) |  | 70 | LOT | 300 | 21000 |  |  | 21000
(per Thermtec)
Total Direct Annual Costs (TDAC) |  |  |  | Excluded in this estimate |  |  |  | TDAC = | 31920
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(6) | Administrative Charges |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(7) | Property tax |  |  |  |  | Not Applicable
(8) | Insurance |  |  |  |  | Excluded in this estimate.
| Capital Recovery Factor [see inputs below] |  | 0.14238
(9) | Capital Recovery | [6 empty] | CRF * TCI = | 185090.7535
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 185090.7535
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 217010.7535
Cost Effectiveness Summary
TOTAL TONS AVOIDED PER YEAR | [7 empty] | = | 0.285
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 761441.2405
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 10 | years
|  | Catalyst Life | N/A | years
|  | Asset Utilization | N/A | %
Note on G12: Stevenson, Cindy: Estimate $105/hr
Note on K31: Stevenson, Cindy: PM2.5 PTE = 0.3 tpy from UAF NAA BACT PTE.xlsx, assume 95% reduction in emissions.

## 4-10 - PM Cost Effectiveness
Table 4-10. UAF - PM2.5 BACT Cost Effectiveness
Summary for Each Emission Unit Type
Control Technology Option | Total Installed Capital ($) | Annualized Capital Cost ($/year) | Annual O&M Cost ($MM/year) | Cost Effectiveness ($/ton PM2.5 removed)
Small Diesel-fired Boilers (EU ID 19 through 21)
Scrubber + Limited Operation | 300000 | 42713.2508 | NA | 47938.5531
Limited Operation1 | ~ | ~ | ~ | ~
Small Diesel-fired Engine (EU ID 27)
DPF + Federal Limits + Limited Operation | 30750.8 | 4378.2221 | NA | 19810.9598
Federal Limits1 + Limited Operation1 | ~ | ~ | ~ | ~
Medical/Pathological Waste Incinerator (EU ID 9A)
Fabric Filters + Multiple Chambers | 1300000 | 217010.7535 | 31920 | 761441.2405
Multiple Chambers + Limited Operation1 | ~ | ~ | ~ | ~
Notes:
1 This technology is proposed as the baseline case.

## 4-11 BACT Summary
Table 4-11. UAF - Proposed PM2.5 BACT and Associated
Emission Rate for Each Emission Unit Type
Emission Unit |  | Fuel | PM2.5 BACT
ID | Description |  | Description | Emission Rate1
113 | Large Boiler | Coal and Biomass | Fabric Filter | 0.012 lb/MMBtu
3 | Mid-sized Boiler | Diesel | Good Combustion Practices | 0.016 lb/MMBtu
4 | Mid-sized Boiler | Diesel | Limited Operation | 0.016 lb/MMBtu
|  | Natural Gas |  | 7.6 lb/MMscf
19 through 21 | Small Boilers | ULSD | Limited Operation | 7.06 g/MMBtu
8 | Large Engine | Diesel | Positive Crankcase Ventilation + Low Ash Fuel + Limited Operation | 0.32 g/hp-hr
27 | Small Engine | ULSD | Federal Limit (NSPS Subpart IIII, Tier 3) + Limited Operation | 0.11 g/hp-hr
9A | Medical/Pathological Waste Incinerator | Waste | Multiple Chambers + Limited Operation | 4.67 lb/ton
105, 107, 109, 110, and 128 through 130 | Material Handling Emission Units with Fabric Filtration | N/A | Fabric Filter + Enclosure | 0.003 gr/dscf
114 | Material Handling Emission Units with Fabric Filtration | N/A | Fabric Filter + Enclosure | 0.05 gr/dscf
111 | Material Handling Emission Unit without Fabric Filtration | N/A | Enclosure | 5.5e-5 lb/ton
Notes:
1 Emissions are on a per unit basis.

## 5-22 (hidden)
Table 5-22. Point Thomson Project - Proposed VOC BACT and Associated
Emission Rate for Each Emission Unit Type
Emission Unit |  | Fuel | CO BACT
ID | Description |  | Description | Emission Rate
101 and 102 | Solar Taurus Turbine | Fuel Gas | Catalytic Oxidation | 25 ppm at ≥10 degrees F (in SoLoNOX mode)
103 and 104 | Solar Taurus Turbine | Dual Fuel-fired | Catalytic Oxidation | 100 ppm at ≥10 degrees F (in SoLoNOX mode)
105 | Waste Incinerator | ULSD | Good Combustion Practices | 1.0 g/hp-hr
106 through 109, 115, and 116 | Distillate-fired Engines | ULSD | Good Combustion Practices | 0.19 g/KW-hr
110 through 112 | Fine Water Mist Supply and Firewater Pumps | ULSD | Good Combustion Practices | 0.00247 lb/hp-hr
113 and 114 | Flares | Fuel Gas | None | 4.0 g/KW-hr (NOX and HC, combined)
Notes:
1 Emissions are on a per unit basis.
2 ULSD fired engines have NSPS Subpart IIII VOC emission limits.