## Executive Summary Table
Table ES-1. Summary of Proposed BACT Determinations for Equipment at the
University of Alaska Fairbanks Campus
Emission Unit |  | Proposed BACT Determination1
ID | Description | NOX | PM2.5 | SO2
3 | Mid-sized Boiler | Good Combustion Practices | Good Combustion Practices | ULSD
4 | Mid-sized Boiler | Limited Operation | Limited Operation | ULSD + Limited Operation
8 | Large Engine | Turbocharger and Aftercooler + Limited Operation | Positive Crankcase Ventilation + Low Ash Fuel + Limited Operation | ULSD + Limited Operation
9A | Medical/Pathological Waste Incinerator | Good Combustion Practices + Limited Operation | Multiple Chambers + Limited Operation | ULSD + Limited Operation
19 | Small Boiler | Limited Operation | Limited Operation | ULSD
20 | Small Boiler
21 | Small Boiler
27 | Small Engine | Turbocharger and Aftercooler + Federal Limit + Limited Operating | Federal Limit (NSPS Subpart IIII, Tier 3) + Limited Operation | ULSD
105 | Limestone Handling System | N/A | Fabric Filter + Enclosure | N/A
107 | Sand Handling System | N/A | Fabric Filter + Enclosure | N/A
109 | Ash Handling System | N/A | Fabric Filter + Enclosure | N/A
110 | Ash Handling System Vacuum | N/A | Fabric Filter + Enclosure | N/A
111 | Ash Loadout to Truck | N/A | Enclosure | N/A
113 | Large Boiler | CFB with staged combustion | Fabric Filter | Limestone Injection + Low Sulfur Fuel
114 | Dry Sorbent Handling Vent Filter Exhaust | N/A | Fabric Filter + Enclosure | N/A
128 | Coal Silo No. 1 with bin vent | N/A | Fabric Filter + Enclosure | N/A
129 | Coal Silo No. 2 with bin vent | N/A | Fabric Filter + Enclosure | N/A
130 | Coal Silo No. 3 with bin vent | N/A | Fabric Filter + Enclosure | N/A
Notes:
1 Determinations in bold are changes to the required controls in the applicable operating permit or minor permit.

## Table 1-2. Sig EUI PTE
Table 1-2. Potential to Emit Inventory for BACT Basis of Worst-Case Emissions - Significant Emission Units
University of Alaska Fairbanks Campus
Emission Unit |  |  |  | Installation | Fuel Type | Maximum Rating/Capacity |  | Maximum Operation |  | Potential Emissions (tpy)
ID | Description | Make/Model | Bldg. No. | Date | [5 empty] | NOX | PM2.5 | SO2
3 | Dual-Fired Boiler | Zurn | FS802 | 1970 | Diesel1 | 180.9 | MMBtu/hr | 8760 | hr/yr | 138.8044 | 12.3189 | 410.6298
4 | Dual-Fired Boiler | Zurn | FS802 | 1987 | Duel - Diesel and NG | 180.9 | MMBtu/hr2 | 158468.4 | MMBtu/yr2 | 13.8804 | 1.2319 | 40
[8 empty] | 8760 | hr/yr2 | 11.0928 | 0.60218 | 0.047541
8 | Peaking/Backup Generator (DEG) Engine | Fairbanks Morse Colt-Pielstick PC2.6 | FS817 | 1999 | Diesel3 | 13266 | hp | 8760 | hr/yr | 40 | 0.95972 | 40
9A | BiRD - Medical/Pathological Waste Incinerator | Therm-Tec/G-30P-1H | FS919 | 2006 | Medical/Pathological Waste4 | 83.3333 | lb/hr5 | 109 | tpy6 | 0.19402 | 0.25451 | 0.11826
19 | BiRD RM 100U3 Boiler No. 1 | Weil McLain/2094W | FS919 | 2004 | ULSD7 | 6.1333 | MMBtu/hr8 | 19650 | hr/yr9 | 8.7971 | 0.93689 | 0.093689
20 | BiRD RM 100U3 Boiler No. 2 | Weil McLain/2094W | FS919 | 2004 | ULSD7 | 6.1333 | MMBtu/hr8
21 | BiRD RM 100U3 Boiler No. 3 | Weil McLain/2094W | FS919 | 2004 | ULSD7 | 6.1333 | MMBtu/hr8
27 | Alaska Center for Energy and Power Generator Engine | Caterpillar C-15 (Tier 3) | FS814 | June 2012 | ULSD | 500 | hp | 4380 | hr/yr10 | 7.7088 | 0.2628 | 0.011917
105 | Limestone Handling System | TBD | TBD | TBD | N/A | 1200 | acfm | 8760 | hr/yr | N/A | 0.13515 | N/A
107 | Sand Handling System | TBD | TBD | TBD | N/A | 1600 | acfm | 8760 | hr/yr | N/A | 0.18021 | N/A
109 | Ash Handling System | TBD | TBD | TBD | N/A | 1000 | acfm | 8760 | hr/yr | N/A | 0.11263 | N/A
110 | Ash Handling System Vacuum | TBD | TBD | TBD | N/A | 2000 | acfm | 8760 | hr/yr | N/A | 0.22526 | N/A
111 | Ash Loadout to Truck | TBD | TBD | TBD | N/A | N/A |  | 26280 | tpy | N/A | 0.00072306 | N/A
113 | Replacement Dual-fired CFB Boiler | Babcock & Wilcox | TBD | TBD | Coal/Woody Biomass | 295.6 | MMBtu/hr | 8760 | hr/yr | 258.9456 | 15.5367 | 258.9456
114 | Dry Sorbent Handling Vent Filter Exhaust | TBD | TBD | TBD | N/A | 5 | acfm | 8760 | hr/yr | N/A | 0.0093857 | N/A
128 | Coal Silo No. 1 with bin vent | TBD | TBD | TBD | N/A | 1650 | acfm | 8760 | hr/yr | N/A | 0.18584 | N/A
129 | Coal Silo No. 2 with bin vent | TBD | TBD | TBD | N/A | 1650 | acfm | 8760 | hr/yr | N/A | 0.18584 | N/A
130 | Coal Silo No. 3 with bin vent | TBD | TBD | TBD | N/A | 1650 | acfm | 8760 | hr/yr | N/A | 0.18584 | N/A
[9 empty] | Total11 | 454.4499 | 33.3245 | 709.7993
Notes:
1 Although this boiler is permitted as a dual fuel-fired boiler, the unit is configured to fire only diesel. A BACT analysis will only be completed for diesel firing for this unit.
2 EU ID 4 has a 10 percent capacity factor limit and a 158,468 MMBtu/yr limit per Condition 17 of Permit No. AQ0316TVP02, Rev 1.
3 EU ID 8 is also authorized to combust coal slurry fuel. The unit has not operated on this fuel and will not do so in the future. Emission estimates for this unit are based on diesel fuel combustion.
4 EU ID 9A fuel is piped with EU IDs 19 through 21. Because EU IDs 19 through 21 are required to use ULSD, EU ID 9A is also firing ULSD.
5 The rating of EU ID 9A is listed incorrectly in the existing Title V permit. The correct rating provided here is from the Title V permit renewal application.
6 EU ID 9A is limited by Condition 8 of Permit No. AQ0316MSS04 to 109 tons of waste combustion per rolling 12-month period.
7 EU IDs 19 through 21 are limited to operating on ULSD per Condition 9 of Permit No. AQ316MSS04.
8 The nameplates for EU IDs 19 through 21 list the ratings in gross output or do not specify whether the rating is output or input. A 75 percent efficiency has been assumed for these units to conservatively calculate the heat input rating per the Title V permit renewal application.
9 EU IDs 19 through 21 are limited to operating no more than 19,650 hr/yr, combined, per Condition 10 of Permit No. AQ0316MSS04.
10 EU ID 27 is limited to operating no more than 4,380 hr/yr per Condition 4 of Permit No. AQ0316MSS03.
11 The total emissions for NOX and SO2 are restricted for EU IDs 4 and 8 to 40 tpy for each pollutant because the units share these limits for both pollutants. Emission for PM2.5 is the sum of all emissions from all units.

## Table 1-3. NOx
Table 1-3. Potential to Emit Calculations for BACT Basis of Worst-Case Emissions - NOX Emissions
University of Alaska Fairbanks Campus
Emission Unit |  | Fuel Type | NOX Emission Factor |  |  | Maximum Rating/Capacity |  | Allowable Annual Operation1 |  | Control | Technology | Short Term |  | Potential NOX Emissions2
ID | Description |  | Reference | Factor | [5 empty] | Technology | Efficiency | NOX Emissions
Significant Emission Units
3 | Dual-Fired Boiler | Diesel | AP-42 Table 1.3-1 | 24 | lb/kgal | 180.9 | MMBtu/hr | 8760 | hr/yr | Standard Combustor when firing Diesel |  | 0.17518 | lb/MMBtu | 138.8044 | tpy3
4 | Dual-Fired Boiler | Diesel | AP-42 Table 1.3-1 | 24 | lb/kgal | 180.9 | MMBtu/hr | 158468.4 | MMBtu/yr | Standard Combustor when firing Diesel + 10 Percent Capacity Factor | 90% | 0.17518 | lb/MMBtu | 13.8804 | tpy4
4 | Dual-Fired Boiler | Natural Gas | AP-42 Table 1.4-1 low NOX | 140 | lb/MMscf | 180.9 | MMBtu/hr | 8760 | hr/yr | Low NOx Burners + 10 Percent Capacity Factor | 90% | 140 | lb/MMscf | 11.0928 | tpy4
8 | Peaking/Backup Generator (DEG) Engine | Diesel | AQ0316MSS02, Cond.12.3b | 0.571 | lb/gal | 13266 | hp | 140105.0788 | gal/yr5 | Turbocharging and Intercooler |  | 0.019541 | g/hp-hr | 40 | tpy5
9A | BiRD - Medical/Pathological Waste Incinerator | Medical/Pathological Waste | AP-42 Table 2.3-1 | 3.56 | lb/ton | 83.3333 | lb/hr | 109 | ton/yr6 | Multi-chamber (4 primary burners and 2 flue duct burners) |  | 3.56 | lb/ton | 0.19402 | tpy
19 | BiRD RM 100U3 Boiler No. 1 | ULSD7 | AP-42 Table 1.3-1 | 20 | lb/kgal | 6.1333 | MMBtu/hr | 19650 | hr/yr8 | N/A |  | 1.244 | g/MMBtu | 8.7971 | tpy
20 | BiRD RM 100U3 Boiler No. 2 | ULSD7 | AP-42 Table 1.3-1 | 20 | lb/kgal | 6.1333 | MMBtu/hr |  |  | N/A |  | 1.244 | g/MMBtu
21 | BiRD RM 100U3 Boiler No. 3 | ULSD7 | AP-42 Table 1.3-1 | 20 | lb/kgal | 6.1333 | MMBtu/hr |  |  | N/A |  | 1.244 | g/MMBtu
27 | Alaska Center for Energy and Power Generator Engine | ULSD | Vendor Data | 3.52 | lb/hr | 500 | hp | 4380 | hr/yr9 | Tier 3, Turbocharger and aftercooler |  | 3.1962 | g/hp-hr | 7.7088 | tpy
105 | Limestone Handling System | N/A |  | N/A |  | 1200 | acfm | 8760 | hr/yr | N/A |  |  |  | N/A
107 | Sand Handling System | N/A |  | N/A |  | 1600 | acfm | 8760 | hr/yr | N/A |  |  |  | N/A
109 | Ash Handling System | N/A |  | N/A |  | 1000 | acfm | 8760 | hr/yr | N/A |  |  |  | N/A
110 | Ash Handling System Vacuum | N/A |  | N/A |  | 2000 | acfm | 8760 | hr/yr | N/A |  |  |  | N/A
111 | Ash Loadout to Truck | N/A |  | N/A |  | N/A |  | 26280 | tpy | N/A |  |  |  | N/A
113 | Replacement Dual-fired CFB Boiler | Coal/Woody Biomass | 40 CFR 60.44b(l)(1) | 0.2 | lb/MMBtu heat input | 295.6 | MMBtu/hr | 8760 | hr/yr | N/A |  | 0.2 | lb/MMBtu heat input | 258.9456 | tpy
114 | Dry Sorbent Handling Vent Filter Exhaust | N/A |  | N/A |  | 5 | acfm | 8760 | hr/yr | N/A |  |  |  | N/A
128 | Coal Silo No. 1 with bin vent | N/A |  | N/A |  | 1650 | acfm | 8760 | hr/yr | N/A |  |  |  | N/A
129 | Coal Silo No. 2 with bin vent | N/A |  | N/A |  | 1650 | acfm | 8760 | hr/yr | N/A |  |  |  | N/A
130 | Coal Silo No. 3 with bin vent | N/A |  | N/A |  | 1650 | acfm | 8760 | hr/yr | N/A |  |  |  | N/A
Notes:
1 Maximum annual operation for all units based on full-time operation, or permitted operating limits, where applicable.
2 Conversion factors: |  |  | Mass Conversion | 454 | g/lb
|  |  | Diesel Heating Value | 0.137 | MMBtu/gal
|  |  | Natural Gas Heat Content | 1000 | Btu/scf
3 Although this boiler is permitted as a dual fuel-fired boiler, the unit is configured to fire only diesel. The potential NOX emissions for EU ID 3 are based on diesel fuel combustion.
4 Maximum annual operation of EU ID 4 while firing diesel or gas is restricted by a 10 percent capacity factor limit on the annual the heat input, and by a limit that restrict emissions to less the 40 tpy for EU ID and EU ID 8, combined per Condition 16 of Operating Permit AQ0316TVP02.
5 Maximum annual operation of EU ID 8 is restricted by the 40 tpy of NOX emission limit that is shared with EU ID 4. EU ID 8 can consume no more than 140,105 gal/year of fuel and be in compliance this limit. (40 ton/yr * 2,000 lb/ton/0.571 lb/gal = 140,105 gal/yr)
6 EU ID 9A is limited by Condition 8 of Permit No. AQ0316MSS04 to 109 tons of waste combustion per rolling 12-month.
7 EU IDs 19 through 21 are limited to operating on ULSD per Condition 9 of Permit No. AQ316MSS04.
8 EU IDs 19 through 21 are limited to operate no more than 19,650 hr/yr, combined, per Condition 10 of Permit No. AQ0316MSS04.
9 EU ID 27 limited to operating no more than 4,380 hr/yr per Condition 4 of Permit No. AQ0316MSS03.

## Table 1-4. PM2.5
Table 1-4. Potential to Emit Calculations for BACT Basis of Worst-Case Emissions - PM2.5 Emissions
University of Alaska Fairbanks Campus
Emission Unit |  | Fuel Type | PM2.5 Emission Factor |  |  | Maximum Rating/Capacity |  | Allowable Annual Operation1 |  | Control | Technology | Short Term |  | Potential PM2.5 Emissions2
ID | Description |  | Reference | Factor | [5 empty] | Technology | Efficiency | PM2.5 Emissions
Significant Emission Units
3 | Dual-Fired Boiler | Diesel | AP-42 Tables 1.3-2, 1.3-7 | 2.13 | lb/kgal | 180.9 | MMBtu/hr | 8760 | hr/yr | N/A |  | 0.015547 | lb/MMBtu | 12.3189 | tpy3
4 | Dual-Fired Boiler | Diesel | AP-42 Tables 1.3-2, 1.3-7 | 2.13 | lb/kgal | 180.9 | MMBtu/hr | 158468.4 | MMBtu/yr | Standard Combustor when firing Diesel + 10 Percent Capacity Factor | 90% | 0.015547 | lb/MMBtu | 1.2319 | tpy4
4 | Dual-Fired Boiler | Natural Gas | AP-42 Table 1.4-2 | 7.6 | lb/MMscf | 180.9 | MMBtu/hr | 8760 | hr/yr | Low NOx Burners + 10 Percent Capacity Factor | 90% | 7.6 | lb/MMscf | 0.60218 | tpy4
8 | Peaking/Backup Generator (DEG) Engine | Diesel | AP-42 Table 3.4-1 | 0.1 | lb/MMBtu | 13266 | hp | 140105.0788 | gal/yr | Positive Crankcase Ventilation |  | 0.1 | lb/MMBtu | 0.95972 | tpy5
9A | BiRD - Medical/Pathological Waste Incinerator | Medical/Pathological Waste | AP-42 Table 2.3-2 | 4.67 | lb/ton | 83.3333 | lb/hr | 109 | ton/yr6 | Multi-chamber (4 primary burners and 2 flue duct burners) |  | 4.67 | lb/ton | 0.25451 | tpy
19 | BiRD RM 100U3 Boiler No. 1 | ULSD7 | AP-42 Tables 1.3-2, 1.3-7 | 2.13 | lb/kgal | 6.1333 | MMBtu/hr | 19650 | hr/yr8 | N/A |  | 7.0585 | g/MMBtu | 0.93689 | tpy
20 | BiRD RM 100U3 Boiler No. 2 | ULSD7 | AP-42 Tables 1.3-2, 1.3-7 | 2.13 | lb/kgal | 6.1333 | MMBtu/hr |  |  | N/A |  | 7.0585 | g/MMBtu
21 | BiRD RM 100U3 Boiler No. 3 | ULSD7 | AP-42 Tables 1.3-2, 1.3-7 | 2.13 | lb/kgal | 6.1333 | MMBtu/hr |  |  | N/A |  | 7.0585 | g/MMBtu
27 | Alaska Center for Energy and Power Generator Engine | ULSD | Vendor Data | 0.12 | lb/hr | 500 | hp | 4380 | hr/yr9 | Tier 3 |  | 0.10896 | g/hp-hr | 0.2628 | tpy
105 | Limestone Handling System | N/A | Design Specifications | 0.003 | gr/dcf | 1200 | acfm | 8760 | hr/yr | Dust Collector |  | 0.003 | gr/dcf | 0.13515 | tpy
107 | Sand Handling System | N/A | Design Specifications | 0.003 | gr/dcf | 1600 | acfm | 8760 | hr/yr | Dust Collector |  | 0.003 | gr/dcf | 0.18021 | tpy
109 | Ash Handling System | N/A | Design Specifications | 0.003 | gr/dcf | 1000 | acfm | 8760 | hr/yr | Dust Collector |  | 0.003 | gr/dcf | 0.11263 | tpy
110 | Ash Handling System Vacuum | N/A | Design Specifications | 0.003 | gr/dcf | 2000 | acfm | 8760 | hr/yr | Dust Collector |  | 0.003 | gr/dcf | 0.22526 | tpy
111 | Ash Loadout to Truck | N/A | AP-42 Table 13.2.4 | 5.5028e-05 | lb/ton10 | N/A |  | 26280 | tpy | Enclosure |  | 5.5028e-05 | lb/ton | 0.00072306 | tpy
113 | Replacement Dual-fired CFB Boiler | Coal/Woody Biomass | Vendor Data | 0.012 | lb/MMBtu | 295.6 | MMBtu/hr | 8760 | hr/yr | Baghouse |  | 0.012 | lb/MMBtu | 15.5367 | tpy
114 | Dry Sorbent Handling Vent Filter Exhaust | N/A | AK state SIP PM emission std. | 0.05 | gr/dcf | 5 | acfm | 8760 | hr/yr | Dust Collector |  | 0.05 | gr/dcf | 0.0093857 | tpy
128 | Coal Silo No. 1 with bin vent | N/A | Design Specifications | 0.003 | gr/dcf | 1650 | acfm | 8760 | hr/yr | Dust Collector |  | 0.003 | gr/dcf | 0.18584 | tpy
129 | Coal Silo No. 2 with bin vent | N/A | Design Specifications | 0.003 | gr/dcf | 1650 | acfm | 8760 | hr/yr | Dust Collector |  | 0.003 | gr/dcf | 0.18584 | tpy
130 | Coal Silo No. 3 with bin vent | N/A | Design Specifications | 0.003 | gr/dcf | 1650 | acfm | 8760 | hr/yr | Dust Collector |  | 0.003 | gr/dcf | 0.18584 | tpy
Notes:
1 Maximum annual operation for all units based on full-time operation, or permitted operating limits, where applicable.
2 Conversion factors:
|  |  | Mass Conversion | 454 | g/lb
|  |  | Diesel Heating Value | 0.137 | MMBtu/gal
|  |  | Mass Conversion | 7000 | gr/lb
|  |  | Natural Gas Heat Content | 1000 | Btu/scf
|  |  | Engine Heat Rate | 7000 | Btu/hp-hr
3 Although this boiler is permitted as a dual fuel-fired boiler, the unit is configured to fire only diesel. The potential PM2.5 emissions for EU ID 3 are based on diesel fuel combustion.
4 Maximum annual operation of EU ID 4 while firing diesel or gas is limited by the 10 percent annual capacity factor which restricts the heat input.
5 The highest potential PM2.5 emissions for EU ID 8 is shown using the NOX-driven fuel restriction.
6 EU ID 9A is limited by Condition 8 of Permit No. AQ0316MSS04 to 109 tons of waste combustion per rolling 12-month.
7 EU IDs 19 through 21 are limited to operating on ULSD per Condition 9 of Permit No. AQ316MSS04.
8 EU IDs 19 through 21 are limited to operating no more than 19,650 hr/yr, combined, per Condition 10 of Permit No. AQ0316MSS04.
9 EU ID 27 limited to operating no more than 4,380 hr/yr per Condition 4 of Permit No. AQ0316MSS03.
10 Ash loadout emission calculations:
Emission factor from AP-42, Section 13.2.4 based on empirical equation E = k x 0.0032 x (U/5)1.3/(M/2)1.4 lb/ton transferred where:
| k for PM2.5 = | 0.053
U = mean wind speed = 5.4 mph in Fairbanks, per National Climactic Data Center (http://lwf.ncdc.noaa.gov/oa/climate/online/ccd/avgwind.html)
M = ash moisture content = 4.8 percent (AP-42, page 13.2.4-4)
| Ash loadout emissions based on maximum boiler total coal consumption capacity |  |  | 26280 | tpy
Ash content of coal = 8.5% per Usibelli Coal Mine website
Operations, ash tons/hr = (Σ coal capacity, ton/hr) x (0.085 ash content) + (captured sulfur, captured oxygen, and limestone inerts) = 3 ton/hr per design engineers
Operations, ash tons/yr = (3 ton/hr) * (8,760 hr/yr)
Ash loadout emissions, tons/yr = (emission factor, lb/ton) x (ash loading, ton/yr) / (2,000 lb/ton)

## Table 1-5. SO2
Table 1-5. Potential to Emit Calculations for BACT Basis of Worst-Case Emissions - SO2 Emissions
University of Alaska Fairbanks Campus
Emission Unit |  | Fuel Type | Fuel Sulfur Content |  | SO2 Emission Factor |  |  | Maximum Rating/Capacity |  | Allowable Annual Operation1 |  | Control | Technology | Short Term |  | Potential SO2 Emissions2
ID | Description |  |  |  | Reference | Factor | [5 empty] | Technology | Efficiency | SO2 Emissions
Significant Emission Units
3 | Dual-Fired Boiler | Diesel | 0.5 | weight % | AP-42 Table 1.3-1 | 142 | *S lb/kgal | 180.9 | MMBtu/hr | 8760 | hr/yr | N/A |  | 0.51825 | lb/MMBtu | 410.6298 | tpy3
4 | Dual-Fired Boiler | Diesel | 0.5 | weight % | AP-42 Table 1.3-1 | 142 | *S lb/kgal | 180.9 | MMBtu/hr | 154366.1972 | MMBtu/yr4 | Standard Combustor when firing Diesel + 10 Percent Capacity Factor | 90% | 0.51825 | lb/MMBtu | 40 | tpy4
4 | Dual-Fired Boiler | Natural Gas | N/A |  | AP-42 Table 1.4-2 | 0.6 | lb/MMscf | 180.9 | MMBtu/hr | 8760 | hr/yr | Low NOx Burners + 10 Percent Capacity Factor | 90% | 0.6 | lb/MMscf | 0.047541 | tpy4
8 | Peaking/Backup Generator (DEG) Engine | Diesel | 0.5 | weight % | AP-42 Table 3.4-1 | 0.00809 | *S lb/hp-hr | 13266 | hp | 1010529.355 | galyr5 | N/A |  | 1.8364 | g/hp-hr | 40 | tpy
9A | BiRD - Medical/Pathological Waste Incinerator | Medical/Pathological Waste | N/A |  | AP-42 Table 2.3-1 | 2.17 | lb/ton | 83.3333 | lb/hr | 109 | tpy6 | N/A |  | 2.17 | lb/ton | 0.11826 | tpy
19 | BiRD RM 100U3 Boiler No. 1 | ULSD | 0.0015 | weight %7 | AP-42 Table 1.3-1 | 142 | *S lb/kgal | 6.1333 | MMBtu/hr | 19650 | hr/yr8 | ULSD |  | 0.013248 | g/MMBtu | 0.093689 | tpy
20 | BiRD RM 100U3 Boiler No. 2 | ULSD | 0.0015 | weight %7 | AP-42 Table 1.3-1 | 142 | *S lb/kgal | 6.1333 | MMBtu/hr |  |  | ULSD |  | 0.013248 | g/MMBtu
21 | BiRD RM 100U3 Boiler No. 3 | ULSD | 0.0015 | weight %7 | AP-42 Table 1.3-1 | 142 | *S lb/kgal | 6.1333 | MMBtu/hr |  |  | ULSD |  | 0.013248 | g/MMBtu
27 | Alaska Center for Energy and Power Generator Engine | ULSD | 0.0015 | weight % | Mass Balance | 1.0883e-05 | lb/hp-hr | 500 | hp | 4380 | hr/yr9 | ULSD |  | 0.004941 | g/hp-hr | 0.011917 | tpy
105 | Limestone Handling System | N/A | N/A |  | N/A | N/A |  | 1200 | acfm | 8760 | hr/yr | N/A |  | N/A |  | N/A
107 | Sand Handling System | N/A | N/A |  | N/A | N/A |  | 1600 | acfm | 8760 | hr/yr | N/A |  | N/A |  | N/A
109 | Ash Handling System | N/A | N/A |  | N/A | N/A |  | 1000 | acfm | 8760 | hr/yr | N/A |  | N/A |  | N/A
110 | Ash Handling System Vacuum | N/A | N/A |  | N/A | N/A |  | 2000 | acfm | 8760 | hr/yr | N/A |  | N/A |  | N/A
111 | Ash Loadout to Truck | N/A | N/A |  | N/A | N/A |  | N/A |  | 26280 | tpy | N/A |  | N/A |  | N/A
113 | Replacement Dual-fired CFB Boiler | Coal/Woody Biomass | N/A |  | 40 CFR 60.42b(k)(1) | 0.2 | lb/MMBtu heat input | 295.6 | MMBtu/hr | 8760 | hr/yr | Limestone Injection, Low sulfur coal |  | 0.2 | lb/MMBtu | 258.9456 | tpy
114 | Dry Sorbent Handling Vent Filter Exhaust | N/A | N/A |  | N/A | N/A |  | 5 | acfm | 8760 | hr/yr | N/A |  | N/A |  | N/A
128 | Coal Silo No. 1 with bin vent | N/A | N/A |  | N/A | N/A |  | 1650 | acfm | 8760 | tpy | N/A |  | N/A |  | N/A
129 | Coal Silo No. 2 with bin vent | N/A | N/A |  | N/A | N/A |  | 1650 | acfm | 8760 | hr/yr | N/A |  | N/A |  | N/A
130 | Coal Silo No. 3 with bin vent | N/A | N/A |  | N/A | N/A |  | 1650 | acfm | 8760 | hr/yr | N/A |  | N/A |  | N/A
Notes:
1 Maximum annual operation for all units based on full-time operation, or permitted operating limits, where applicable.
2 Conversion factors:
|  |  | Mass Conversion | 454 | g/lb
|  |  | Diesel Heating Value | 0.137 | MMBtu/gal
|  |  | Natural Gas Heat Content | 1000 | Btu/scf
|  |  | Density of Diesel | 7.1 | lb/gal
|  |  | Engine Heat Rate | 7000 | Btu/hp-hr
3 Although this boiler is permitted as a dual fuel-fired boiler, the unit is configured to fire only diesel. The potential SO2 emissions for EU ID 3 are based on diesel fuel combustion.
4 Maximum annual operation of EU ID 4 while firing diesel is limited to 40 tpy of SO2, a shared limit with EU ID 8. EU ID 4 can consume no more than 154,366 MMBtu/year and be in compliance with the 40 tpy limit. (40 ton/yr * 2,000 lb/ton /(0.52 lb/MMBtu) = 154,366 MMBtu/yr. Firing on natural gas is restricted by a 10 percent annual capacity factor.
5 Maximum annual operation of EU ID 8 is limited to 40 tpy of SO2, a limit shared with EU ID 4. EU ID 8 can consume no more than 1,010,529 gal/year and be in compliance with the 40 tpy limit. (40 ton/yr * 2,000 lb/ton /(8.09e-3 lb/hp-hr * 0.5%S) * 7,000 Btu/hp-hr * 1 MMBtu/106 Btu / 0.137 MMBtu/gal = 1,010,529 gal/yr)
6 EU ID 9A is limited by Condition 8 of Permit No. AQ0316MSS04 to 109 tons of waste combustion per rolling 12-month period.
7 EU IDs 19 through 21 are limited to operating on ULSD per Condition 9 of Permit No. AQ316MSS04.
8 EU IDs 19 through 21 are limited to operating no more than 19,650 hr/yr, combined, per Condition 10 of Permit No. AQ0316MSS04.
9 EU ID 27 limited to operating no more than 4,380 hr/yr per Condition 4 of Permit No. AQ0316MSS03.