## LNB-FGR TCI
Table 3-10. UAF - Capital Costs for LNB/FGR on
the Mid-sized Diesel Boiler (EU ID 3)
Total Capital Investment Determination - Low NOX Burners & FGR | [7 empty] | Date: | 2016-04-12
Project: |  | UAF PM2.5 BACT Analysis - Zurn Boiler #3 (EU ID 3) | [5 empty] | Prepared By: | L. Pacini
[8 empty] | Checked By: | J. Rubino
[8 empty] | Rev: | C
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | Low NOx Burner | 1 | EA | 419484 | 419484
|  | FGR FD Fans | 1 | EA | 198872 | 198872 |  | TOTAL = | 618356
(from Indeck)
| (b) | Instrumentation
|  | Total Instrumentation |  | EA |  | 0 | Included in above price
[8 empty] | TOTAL = | 0
| (c) | Freight
|  |  |  | % MATL COST | 10% |  | 61835.6
[8 empty] | TOTAL = | 61835.6
| (d) | Labor
|  | Labor - offsite fab | 0 | MH |  | None required | 0
|  | Labor - onsite | 30 | MH | 105 |  | 3150
|  | (from Indeck) | [5 empty] | TOTAL = | 3150
| (e) | Vendor representatives fees
|  | Fab Site Vendor Representatives fees | 0 | MH |  | None required | 0
|  | Onsite Vendor Representatives fees | 46 | MH | 223.7 |  | 10290.2
|  | Onsite Vendor Representatives Travel & Expenses | 1 | EA | 3500 | 3500
|  | (from Indeck) | [5 empty] | TOTAL = | 13790.2
Purchased Equipment and Material Cost (PEMC) | [7 empty] | PEMC = | 697131.8
Direct Installation Costs (DIC) | [7 empty] | DIC = | 340947.5
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 1038079.3
INDIRECT COSTS
(2) | Engineering, Procurement & Construction Support Services |  | 10% | % TDC |  |  | 103807.93
(3) | Performance tests for NOX emissions |  | 1 | EA | 10000 |  | 10000 |  | Excluded in this estimate.
Total Indirect Costs (TIC) | [7 empty] | TIC = | 113807.93
MANAGEMENT AND CONTINGENCY COSTS
(4) | Unit Operator Costs |  |  | % TDC |  |  |  |  | Excluded in this estimate.
(5) | Contingency |  | 10% | % TDC |  |  | 103807.93
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 103807.93
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 1255695.16
Note on G13: Pacini, Lain: Supplier (INDeck) proposal dated 2/5/2016
Note on G14: Pacini, Lain: Supplier (INDeck) proposal dated 2/5/2016
Note on G20: Pacini, Lain: Based on vendor estimate for DPF on CAT emergency engine.
Note on E24: Pacini, Lain: Indeck service quote indicates 30 hours of boiler inspection work. Assume UAF staff would participate.
Note on G24: Courtney Kimball: Based on similar project.
Note on E28: Pacini, Lain: Indeck quote includes 40 hours of standard staff labor and 6 hours of overtime.
Note on G28: Pacini, Lain: Combined wieghted cost from Indeck considering standard tims and overtime rates.
Note on G29: Pacini, Lain: Indeck service quote
Note on K33: Pacini, Lain: Based on labor, materials and subcontractor quote from Haskell Corp. Quote includes an accuracy note of +/- 25%. 25% was added here to cost.

## LNB-FGR CE
Table 3-11. UAF - Annualized Costs for LNB/FGR on
the Mid-sized Diesel Boiler (EU ID 3)
Shaded cells indicate user inputs
Cost Effectiveness Determination - Low NOX Burners & FGR
UAF PM2.5 BACT Analysis - Zurn Boiler #3 (EU ID 3)
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor - Not required |  |  | MH |  |  | 0 |  | 0
(2) | Supervisory Labor - Not required |  |  | MH |  |  | 0 |  | 0
(3) | Maintenance Labor - Not required |  |  | MH |  |  | 0 |  | 0
(4) | Maintenance Materials - Not required |  |  | LOT |  | 0 | 0 |  | 0
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 0
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | MH |  | Excluded in this estimate. | 0 |  | 0
(6) | Administrative Charges and Insurance |  | 3% | % total capital |  |  | 37670.8548 |  | 37670.8548
| Capital Recovery Factor [see inputs below] |  | 0.080243
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 100760.2284
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 138431.0832
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 138431.0832
Cost Effectiveness Summary
TOTAL TONS AVOIDED PER YEAR | [7 empty] | = | 76.34
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 1813.3493
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 20 | years
|  | Catalyst Life | N/A | years
|  | Asset Utilization | N/A | %
Note on E19: Pacini, Lain: Percentage of total capital investment

## 5-22 (hidden)
Table 5-22. Point Thomson Project - Proposed VOC BACT and Associated
Emission Rate for Each Emission Unit Type
Emission Unit |  | Fuel | CO BACT
ID | Description |  | Description | Emission Rate
101 and 102 | Solar Taurus Turbine | Fuel Gas | Catalytic Oxidation | 25 ppm at ≥10 degrees F (in SoLoNOX mode)
103 and 104 | Solar Taurus Turbine | Dual Fuel-fired | Catalytic Oxidation | 100 ppm at ≥10 degrees F (in SoLoNOX mode)
105 | Waste Incinerator | ULSD | Good Combustion Practices | 1.0 g/hp-hr
106 through 109, 115, and 116 | Distillate-fired Engines | ULSD | Good Combustion Practices | 0.19 g/KW-hr
110 through 112 | Fine Water Mist Supply and Firewater Pumps | ULSD | Good Combustion Practices | 0.00247 lb/hp-hr
113 and 114 | Flares | Fuel Gas | None | 4.0 g/KW-hr (NOX and HC, combined)
Notes:
1 Emissions are on a per unit basis.
2 ULSD fired engines have NSPS Subpart IIII VOC emission limits.

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only