## Stack Flow Calcs
Rev 12/5/19, G. Allen |  |  |  | NOTE: | If Col. E Stack P is not in " Hg, the last term in H3 must be edited. | [6 empty] | These columns are static for a series of runs.
|  |  | Anemometer |  | Velocity |  | Velocity | Velocity
2020-01-03 | Stack T | Stack delta-p | Velocity | Stack P | m/s, cal. | Stack T | m/s | m/min | stack flow | stack flow |  | stack dia: | 6 | inches
Time (hh:mm) | deg F | "H20 absolute | m/sec raw | " Hg | corrected | deg C | at STP | STP | m3/min STP | CFM@STP |  | stack area: | 28.2744 | sq. inches |  |  |  |  | For Hontzsch ZS25/25 350GE/500/p10/ZG4 vane anemometer
9:24 |  |  | 0 | 29.5 | 0.16099 | -17.7778 | 0.18533 | 11.1198 | 0.18713 | 6.6084 |  | probe blockage area: | 2.63 | sq. inches | % block: | 9.3017 | Fc = | 8.3971 | This is the corrected blockage factor from EPA Nomograph 2, table VI. (October 1978) using a curve fit for actual blockage of 7.9 to 10.8% of area
9:34 | 90 | 0.0048107 | 1.45 | 29.4996 | 1.4364 | 32.2222 | 1.3828 | 82.9653 | 1.3962 | 49.3055 | [8 empty] | Raw blockage factor of 2.63 sq in. from O5 is based on sensor at the stack centerline and 1" circular probe diameter
9:44 | 191.6 | 0.0038403 | 1.41 | 29.4997 | 1.3947 | 88.6667 | 1.133 | 67.983 | 1.144 | 40.4016 |  | effective area: | 26.0841 | sq. in. -- using corrected blockage factor from U5
9:54 | 267.6 | 0.0032 | 1.36 | 29.4998 | 1.3431 | 130.8889 | 0.97703 | 58.622 | 0.98651 | 34.8385 |  | effective area: | 0.016828 | m2
10:04 | 291.2 | 0.003009 | 1.34 | 29.4998 | 1.3226 | 144 | 0.93187 | 55.9124 | 0.94092 | 33.2282
10:14 | 300 | 0.0027138 | 1.28 | 29.4998 | 1.2616 | 148.8889 | 0.87864 | 52.7185 | 0.88717 | 31.3301 |  |  |  | Anemometer model number: | ZS25/25-350GE/500/P10/ZG4
10:24 | 304 | 0.0028277 | 1.31 | 29.4998 | 1.292 | 151.1111 | 0.89507 | 53.7042 | 0.90376 | 31.9159 |  |  |  | Anemometer serial number: | mn20-13393
10:34 | 306 | 0.0026926 | 1.28 | 29.4998 | 1.2616 | 152.2222 | 0.87175 | 52.3052 | 0.88021 | 31.0845 |  | Anemometer cal equation factors:
10:44 | 308 | 0.0026856 | 1.28 | 29.4998 | 1.2616 | 153.3333 | 0.86948 | 52.1689 | 0.87792 | 31.0035 |  | B0 | B1 | B2 | Cal Date: | 2019-11-14
10:54 | 310 | 0.0025956 | 1.26 | 29.4998 | 1.2415 | 154.4444 | 0.85339 | 51.2033 | 0.86167 | 30.4297 |  | 0.16099 | 0.71124 | 0.11613
11:04 | 308 | 0.0026856 | 1.28 | 29.4998 | 1.2616 | 153.3333 | 0.86948 | 52.1689 | 0.87792 | 31.0035 |  | actual = 0.161 + (0.7112 * observed) + (0.11613 * observed^2)
11:14 | 305 | 0.0026541 | 1.27 | 29.4998 | 1.2516 | 151.6667 | 0.86592 | 51.9555 | 0.87433 | 30.8766
11:24 | 306 | 0.0026507 | 1.27 | 29.4998 | 1.2516 | 152.2222 | 0.86479 | 51.8876 | 0.87319 | 30.8363 |  |  | Room BP at start of test: | 29.5 | " Hg
11:34 | 253 | 0.0032654 | 1.36 | 29.4998 | 1.3431 | 122.7778 | 0.99706 | 59.8234 | 1.0067 | 35.5525 |  |  | Room BP at end of test: | 29.5 | " Hg
11:44 | 254 | 0.0032131 | 1.35 | 29.4998 | 1.3328 | 123.3333 | 0.98805 | 59.2832 | 0.99764 | 35.2314 |  |  | Avg BP: | 29.5 | " Hg
11:54 | 253 | 0.0032176 | 1.35 | 29.4998 | 1.3328 | 122.7778 | 0.98944 | 59.3664 | 0.99904 | 35.2809
12:04 | 253 | 0.0032654 | 1.36 | 29.4998 | 1.3431 | 122.7778 | 0.99706 | 59.8234 | 1.0067 | 35.5525 |  | 1 " H20 = | 0.07348 | " Hg
12:14 | 250 | 0.0033276 | 1.37 | 29.4998 | 1.3534 | 121.1111 | 1.0089 | 60.5363 | 1.0187 | 35.9761 |  | 1 mb = | 0.02953 | " Hg
12:24 | 258 | 0.0030548 | 1.32 | 29.4998 | 1.3022 | 125.5556 | 0.95996 | 57.5974 | 0.96927 | 34.2296
12:34 | 260 | 0.0031393 | 1.34 | 29.4998 | 1.3226 | 126.6667 | 0.97229 | 58.3372 | 0.98172 | 34.6693
12:44 | 249 | 0.003188 | 1.34 | 29.4998 | 1.3226 | 120.5556 | 0.98738 | 59.2431 | 0.99697 | 35.2076
12:54 | 252 | 0.0032221 | 1.35 | 29.4998 | 1.3328 | 122.2222 | 0.99083 | 59.4498 | 1.0004 | 35.3305
13:04 | 258 | 0.0030087 | 1.31 | 29.4998 | 1.292 | 125.5556 | 0.95246 | 57.1477 | 0.96171 | 33.9624 |  |  | 85.49 | Kp pitot tube constant
13:14 | 248 | 0.0032403 | 1.35 | 29.4998 | 1.3328 | 120 | 0.99643 | 59.786 | 1.0061 | 35.5302 |  |  | 29 | lb/lb mol | dry gas molecular weight
13:24 | 256 | 0.0032041 | 1.35 | 29.4998 | 1.3328 | 124.4444 | 0.98529 | 59.1174 | 0.99485 | 35.1329 |  | 1 m/s = | 3.2808 | ft/sec
13:34 | 247 | 0.0031022 | 1.32 | 29.4998 | 1.3022 | 119.4444 | 0.97491 | 58.4943 | 0.98437 | 34.7626
13:44 | 215 | 0.0033484 | 1.34 | 29.4998 | 1.3226 | 101.6667 | 1.0372 | 62.2298 | 1.0472 | 36.9826
13:54 | 214 | 0.003254 | 1.32 | 29.4998 | 1.3022 | 101.1111 | 1.0227 | 61.3608 | 1.0326 | 36.4661
14:04 | 217 | 0.0031907 | 1.31 | 29.4998 | 1.292 | 102.7778 | 1.0102 | 60.6117 | 1.02 | 36.021
14:14 | 214 | 0.003254 | 1.32 | 29.4998 | 1.3022 | 101.1111 | 1.0227 | 61.3608 | 1.0326 | 36.4661
14:24 | 213 | 0.0032588 | 1.32 | 29.4998 | 1.3022 | 100.5556 | 1.0242 | 61.4521 | 1.0341 | 36.5204
14:34 | 211 | 0.0033683 | 1.34 | 29.4998 | 1.3226 | 99.4444 | 1.0434 | 62.6011 | 1.0535 | 37.2032
14:44 | 208 | 0.0032336 | 1.31 | 29.4998 | 1.292 | 97.7778 | 1.0238 | 61.4291 | 1.0338 | 36.5067
14:54 | 212 | 0.0032144 | 1.31 | 29.4998 | 1.292 | 100 | 1.0177 | 61.0631 | 1.0276 | 36.2892
15:04 | 215 | 0.0033484 | 1.34 | 29.4998 | 1.3226 | 101.6667 | 1.0372 | 62.2298 | 1.0472 | 36.9826
15:14 | 209 | 0.0033784 | 1.34 | 29.4998 | 1.3226 | 98.3333 | 1.0465 | 62.7884 | 1.0566 | 37.3146
15:24 | 215 | 0.0032001 | 1.31 | 29.4998 | 1.292 | 101.6667 | 1.0132 | 60.7915 | 1.023 | 36.1278
15:34 | 212 | 0.0032637 | 1.32 | 29.4998 | 1.3022 | 100 | 1.0257 | 61.5436 | 1.0357 | 36.5748
15:44 | 218 | 0.003186 | 1.31 | 29.4998 | 1.292 | 103.3333 | 1.0087 | 60.5222 | 1.0185 | 35.9678
15:54 | 207 | 0.0032881 | 1.32 | 29.4998 | 1.3022 | 97.2222 | 1.0334 | 62.0054 | 1.0435 | 36.8492
16:04 | 220 | 0.0033238 | 1.34 | 29.4998 | 1.3226 | 104.4444 | 1.0295 | 61.7718 | 1.0395 | 36.7104
16:14 | 215 | 0.0032492 | 1.32 | 29.4998 | 1.3022 | 101.6667 | 1.0212 | 61.2698 | 1.0311 | 36.4121
16:24 | 217 | 0.0034389 | 1.36 | 29.4997 | 1.3431 | 102.7778 | 1.0501 | 63.0073 | 1.0603 | 37.4446
[10 empty] | 34.7005 | Average
Note on O5: this is from physical dims of the probe

## Sheet1
ISS 2
| SCFH | SCFM
1 | 4.99 | 0.083167
2 | 19.98 | 0.333
3 | 34.99 | 0.58317
4 | 50.01 | 0.8335
5 | 65.02 | 1.0837
6 | 79.94 | 1.3323
7 | 95.05 | 1.5842
8 | 110.01 | 1.8335

## Instructions
For Hontzsch ZS25/25 350GE/500/p10/ZG4 vane anemometer
Enter or verify all values in cells with this highlight:
Blockage correction factor is constant for a given probe insertion distance. See anemometer SOP for more information.
Stack P is based on room BP minus the measured delta-P in the stack.
C3 is absolute Delta-P -- always a postive #.
"Stack velocity, m/s raw" is the flow read from the anemometer software.
If the Hontzsch anemometer is not in the centerline of a 6" stack, the blockage factor in O5 must be changed. | 11/14/19 TransCat calibration results:
| actual | observed | (m/s) | corrected reading
| 0.44 | 0.37 |  | 0.44004
| 0.59 | 0.56 |  | 0.5957
Revision history: | 0.79 | 0.77 |  | 0.7775
11/13/19 First release | 1 | 1.02 |  | 1.0073
11/14/19 improved documentation; no data changes | 1.99 | 1.95 |  | 1.9895
11/14/19 Fixed bad formula in K5 [Kelli] | 5 | 4.9 |  | 6.4343
11/14/19 Entered actual cal factors from 11/14/19 calibration and corrected the example info for that equation.
11/14/19 Fixed bad formula in F5 [Nick] | Without 5 lpm point:
11/15/19 Put check for 'out of curve range' in U5 | y = 0.160985 + 0.711244*x + 0.116128*x^2
11/29/19 Added more sig figures to cal equation | r2 = 1.000