## Stack Flow Calcs
Rev 12/5/19, G. Allen |  |  |  | NOTE: | If Col. E Stack P is not in " Hg, the last term in H3 must be edited. | [5 empty] | These columns are static for a series of runs.
|  |  | Anemometer |  | Velocity |  | Velocity | Velocity
2020-01-29 | Stack T | Stack delta-p | Velocity | Stack P | m/s, cal. | Stack T | m/s | m/min | stack flow | stack flow | stack dia: | 6 | inches
Time (hh:mm) | deg F | "H20 absolute | m/sec raw | " Hg | corrected | deg C | at STP | STP | m3/min STP | CFM@STP | stack area: | 28.2744 | sq. inches |  |  |  |  | For Hontzsch ZS25/25 350GE/500/p10/ZG4 vane anemometer
8:45 | 60.2 |  | 0 | 29.675 | 0.16099 | 15.6667 | 0.16483 | 9.8898 | 0.16643 | 5.8774 | probe blockage area: | 2.63 | sq. inches | % block: | 9.3017 | Fc = | 8.3971 | This is the corrected blockage factor from EPA Nomograph 2, table VI. (October 1978) using a curve fit for actual blockage of 7.9 to 10.8% of area
8:55 | 62.5 |  | 1.28 | 29.675 | 1.2616 | 16.9444 | 1.2861 | 77.1646 | 1.2986 | 45.8582 | [7 empty] | Raw blockage factor of 2.63 sq in. from O5 is based on sensor at the stack centerline and 1" circular probe diameter
9:05 | 107 |  | 1.3 | 29.675 | 1.2819 | 41.6667 | 1.204 | 72.2414 | 1.2157 | 42.9324 | effective area: | 26.0841 | sq. in. -- using corrected blockage factor from U5
9:15 | 198.1 |  | 1.12 | 29.675 | 1.1032 | 92.2778 | 0.89268 | 53.5608 | 0.90134 | 31.8307 | effective area: | 0.016828 | m2
9:25 | 243.2 |  | 1.09 | 29.675 | 1.0742 | 117.3333 | 0.81339 | 48.8035 | 0.82129 | 29.0035
9:35 | 259.5 |  | 1.04 | 29.675 | 1.0263 | 126.3889 | 0.75948 | 45.5688 | 0.76685 | 27.0811 |  |  | Anemometer model number: | ZS25/25-350GE/500/P10/ZG4
9:45 | 265.1 |  | 1.05 | 29.675 | 1.0358 | 129.5 | 0.76061 | 45.6369 | 0.768 | 27.1216 |  |  | Anemometer serial number: | mn20-13393
9:55 | 266.6 |  | 1.06 | 29.675 | 1.0454 | 130.3333 | 0.76605 | 45.9631 | 0.77349 | 27.3154 | Anemometer cal equation factors:
10:05 | 266.2 |  | 1.06 | 29.675 | 1.0454 | 130.1111 | 0.76647 | 45.9884 | 0.77391 | 27.3305 | B0 | B1 | B2 | Cal Date: | 2019-11-14
10:15 | 268.3 |  | 1.06 | 29.675 | 1.0454 | 131.2778 | 0.76426 | 45.8557 | 0.77168 | 27.2516 | 0.16099 | 0.71124 | 0.11613
10:25 | 275.4 |  | 0.98 | 29.675 | 0.96953 | 135.2222 | 0.70196 | 42.1175 | 0.70877 | 25.03 | actual = 0.161 + (0.7112 * observed) + (0.11613 * observed^2)
10:35 | 278.1 |  | 0.98 | 29.675 | 0.96953 | 136.7222 | 0.69939 | 41.9633 | 0.70618 | 24.9384
10:45 | 279.4 |  | 0.99 | 29.675 | 0.97893 | 137.4444 | 0.70493 | 42.2956 | 0.71177 | 25.1359 |  | Room BP at start of test: | 29.65 | " Hg
10:55 | 258.3 |  | 1.01 | 29.675 | 0.9978 | 125.7222 | 0.73964 | 44.3784 | 0.74682 | 26.3736 |  | Room BP at end of test: | 29.7 | " Hg
11:05 | 226.9 |  | 1.09 | 29.675 | 1.0742 | 108.2778 | 0.83271 | 49.9627 | 0.84079 | 29.6923 |  | Avg BP: | 29.675 | " Hg
11:15 | 225.1 |  | 1.1 | 29.675 | 1.0839 | 107.2778 | 0.84241 | 50.5443 | 0.85058 | 30.038
11:25 | 224.9 |  | 1.08 | 29.675 | 1.0646 | 107.1667 | 0.82766 | 49.6594 | 0.83569 | 29.5121 | 1 " H20 = | 0.07348 | " Hg
11:35 | 228.7 |  | 1.09 | 29.675 | 1.0742 | 109.2778 | 0.83053 | 49.832 | 0.83859 | 29.6147 | 1 mb = | 0.02953 | " Hg
11:45 | 227.8 |  | 1.09 | 29.675 | 1.0742 | 108.7778 | 0.83162 | 49.8972 | 0.83969 | 29.6534
11:55 | 229.8 |  | 1.08 | 29.675 | 1.0646 | 109.8889 | 0.82177 | 49.3063 | 0.82975 | 29.3023 | Sample Calculation @ 9:45 Start Time (Line 7)
12:05 | 233.5 |  | 1.08 | 29.675 | 1.0646 | 111.9444 | 0.81738 | 49.043 | 0.82532 | 29.1458
12:15 | 227.2 |  | 1.08 | 29.675 | 1.0646 | 108.4444 | 0.82488 | 49.493 | 0.83289 | 29.4132 | Velocity @ STP = 0.165 = 0.16 m/sec x (298 K / (16˚C +273) ) x (29.675 in Hg/29.92 in Hg)
12:25 | 229.9 |  | 1.06 | 29.675 | 1.0454 | 109.9444 | 0.80684 | 48.4102 | 0.81467 | 28.7697
12:35 | 231.8 |  | 1.1 | 29.675 | 1.0839 | 111 | 0.83424 | 50.0544 | 0.84234 | 29.7468 | Stack Flow = 5.9 cfm = 0.165 m/sec x (60 sec/min) x EFFECTIVE STACK AREA of 0.01683 m2 x (35.3147 cf / m2)
12:45 | 236.4 |  | 1.1 | 29.675 | 1.0839 | 113.5556 | 0.82872 | 49.7235 | 0.83677 | 29.5502
12:55 | 220.5 |  | 1.1 | 29.675 | 1.0839 | 104.7222 | 0.8481 | 50.8863 | 0.85634 | 30.2412
13:05 | 196.2 |  | 1.12 | 29.675 | 1.1032 | 91.2222 | 0.89527 | 53.716 | 0.90396 | 31.9229
13:15 | 199.3 |  | 1.11 | 29.675 | 1.0935 | 92.9444 | 0.88322 | 52.9931 | 0.89179 | 31.4933
13:25 | 198.6 |  | 1.09 | 29.675 | 1.0742 | 92.5556 | 0.86853 | 52.1115 | 0.87695 | 30.9694
13:35 | 199.3 |  | 1.04 | 29.675 | 1.0263 | 92.9444 | 0.82889 | 49.7335 | 0.83694 | 29.5561
13:45 | 195.7 |  | 1.09 | 29.675 | 1.0742 | 90.9444 | 0.87237 | 52.3422 | 0.88084 | 31.1065
13:55 | 194.9 |  | 1.1 | 29.675 | 1.0839 | 90.5 | 0.88129 | 52.8772 | 0.88984 | 31.4244
14:05 | 196.7 |  | 1.08 | 29.675 | 1.0646 | 91.5 | 0.86323 | 51.7938 | 0.87161 | 30.7805
14:15 | 194.5 |  | 1.1 | 29.675 | 1.0839 | 90.2778 | 0.88183 | 52.9096 | 0.89038 | 31.4437
14:25 | 195.3 |  | 1.09 | 29.675 | 1.0742 | 90.7222 | 0.8729 | 52.3742 | 0.88137 | 31.1255
14:35 | 194.4 |  | 1.09 | 29.675 | 1.0742 | 90.2222 | 0.8741 | 52.4463 | 0.88259 | 31.1683
14:45 | 196.2 |  | 1.08 | 29.675 | 1.0646 | 91.2222 | 0.86389 | 51.8333 | 0.87227 | 30.804
14:55 | 195 |  | 1.1 | 29.675 | 1.0839 | 90.5556 | 0.88115 | 52.8692 | 0.8897 | 31.4196
15:05 | 192.8 |  | 1.11 | 29.675 | 1.0935 | 89.3333 | 0.89202 | 53.5212 | 0.90068 | 31.8071
15:15 | 196.1 |  | 1.1 | 29.675 | 1.0839 | 91.1667 | 0.87967 | 52.7804 | 0.88821 | 31.3669
15:25 | 195.4 |  | 1.09 | 29.675 | 1.0742 | 90.7778 | 0.87277 | 52.3662 | 0.88124 | 31.1207
15:35 | 197.7 |  | 1.07 | 29.675 | 1.055 | 92.0556 | 0.85414 | 51.2482 | 0.86243 | 30.4563
15:45 | 195 |  | 1.06 | 29.675 | 1.0454 | 90.5556 | 0.84987 | 50.992 | 0.85811 | 30.3041
Note on O5: this is from physical dims of the probe

## Sheet1
ISS 2
| SCFH | SCFM
1 | 4.99 | 0.083167
2 | 19.98 | 0.333
3 | 34.99 | 0.58317
4 | 50.01 | 0.8335
5 | 65.02 | 1.0837
6 | 79.94 | 1.3323
7 | 95.05 | 1.5842
8 | 110.01 | 1.8335

## Instructions
For Hontzsch ZS25/25 350GE/500/p10/ZG4 vane anemometer
Enter or verify all values in cells with this highlight:
Blockage correction factor is constant for a given probe insertion distance. See anemometer SOP for more information.
Stack P is based on room BP minus the measured delta-P in the stack.
C3 is absolute Delta-P -- always a postive #.
"Stack velocity, m/s raw" is the flow read from the anemometer software.
If the Hontzsch anemometer is not in the centerline of a 6" stack, the blockage factor in O5 must be changed. | 11/14/19 TransCat calibration results:
| actual | observed | (m/s) | corrected reading
| 0.44 | 0.37 |  | 0.44004
| 0.59 | 0.56 |  | 0.5957
Revision history: | 0.79 | 0.77 |  | 0.7775
11/13/19 First release | 1 | 1.02 |  | 1.0073
11/14/19 improved documentation; no data changes | 1.99 | 1.95 |  | 1.9895
11/14/19 Fixed bad formula in K5 [Kelli] | 5 | 4.9 |  | 6.4343
11/14/19 Entered actual cal factors from 11/14/19 calibration and corrected the example info for that equation.
11/14/19 Fixed bad formula in F5 [Nick] | Without 5 lpm point:
11/15/19 Put check for 'out of curve range' in U5 | y = 0.160985 + 0.711244*x + 0.116128*x^2
11/29/19 Added more sig figures to cal equation | r2 = 1.000