## Diesel Eng-SCR_Ox_DPF(4060hp)
Alaska LNG Project
Diesel Driven Equipment - Black Start Generator
SCR/DPF Cost Effectiveness Analysis
Cost Quantification:
Cost Category | Project Cost | Default Estimate | Default % Applied | EPA Equation / Estimate Basis | Reference | Default | Final | Final Units | Cond Format | Notes
Direct Capital Costs
Purchased Equipment:
Purchased Equipment Costs | 80000 |  | - | A | Vendor Estimate (includes all add-on control equipment) |  | 80000 | $ | FALSE | Need input
Ammonia System |  |  | - | B | Included in A |  | 0 | $ | Req'd | Need input
Instrumentation & Controls |  | 8000 | 10% | C = 0.10 x A |  |  | 8000 | $
Freight |  | 4000 | 5% | D = 0.05 x (A+B) |  |  | 4000 | $
Taxes (Enter sales tax rate in "% Applied") |  | 0 | 0% | TaxRate x (A+B+C) | No sales tax in Alaska |  | 0 | $
Total Purchased Equipment Cost (PE) | 92000 |  | - | PE |  |  | 92000 | $
Direct Installation Costs:
Foundation & Supports | 0 | 9200 | 10% | 0.10 x PE | Not needed, equipment is skid mounted |  | 0 | $
Erection and Handling |  | 32200 | 35% | 0.35 x PE |  |  | 32200 | $
Electrical |  | 5520 | 6% | 0.06 x PE |  |  | 5520 | $
Piping |  | 7360 | 8% | 0.08 x PE |  |  | 7360 | $
Insulation |  | 1840 | 2% | 0.02 x PE |  |  | 1840 | $
Painting | 0 | 3680 | 4% | 0.04 x PE | Not needed, included in equipment purchase price |  | 0 | $
Site Preparation | 5600 |  | 7% | 0.07 x (A+B) | engineering judgement |  | 5600 | $ | FALSE
Total Direct Installation Cost (DI) | 52520 |  | - | DI |  |  | 52520 | $
Total Direct Capital Costs (DC) | 144520 |  | - | DC = PE + DI |  |  | 144520 | $
Indirect Capital Costs
Indirect Costs:
Engineering & Supervision |  | 13800 | 15% | 0.15 x PE |  |  | 13800 | $ | FALSE
Construction and Field Expenses |  | 9200 | 10% | 0.10 x PE |  |  | 9200 | $ | FALSE
Contractor Fees |  | 4600 | 5% | 0.05 x PE |  |  | 4600 | $ | FALSE
Startup-up |  | 920 | 1% | 0.01 x PE |  |  | 920 | $ | FALSE
Performance Testing |  | 920 | 1% | 0.01 x PE |  |  | 920 | $ | FALSE
Total Indirect Costs (TIC) | 29440 |  | - | IC |  |  | 29440 | $
Capital Investment:
Project Contingency |  | 26094 | 15% | E = 0.15 x (DC+IC) | OAQPS (15% of DC & TIC) |  | 26094 | $
Preproduction Cost |  | 4001.08 | 2% | F = 0.02 x (DC+IC+Cont) | OAQPS (2% of DC & TIC & Proj Contingency) |  | 4001.08 | $
Inventory Capital (initial reagent fill) |  | 0 | - | G = [Storage Gal] x [Reagent $/gal] | See parameters below |  | 0 | $ |  | Eqn. 2.44 (Section 4.2, Ch. 2)
Total Capital Investment | 204055.08 |  | - | TCI = DC + IC + E + F + G |  |  | 204055.08 | $
Direct Annual Costs
Direct Annual Costs:
Operating Labor |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Supervisory Labor |  | 0 | 15% | 15% of Op. Labor | OAQPS (15% of Op Labor) |  | 0 |  |  | Need input
Maintenance Labor |  | 3060.8262 | 1.5% | 0.015 x TCI | OAQPS (1.5% of TCI) |  | 3060.8262
Maintenance Materials |  | 3060.8262 | - | 100% of Maint. Labor | OAQPS (15% of Maint. Labor) |  | 3060.8262
Annual Reagent Cost |  | 12738.3418 | - | q*Cost*[op hr/yr] | See parameters below |  | 12738.3418 |  |  | Eqn 2.47 (Section 4.2, Ch. 2)
Annual Electricity Cost |  | 237964.8012 | - | See parameters below | See parameters below |  | 237964.8012 |  |  | Eqn 2.49 (Section 4.2, Ch. 2)
Catalyst Replacement |  | 1888.7057 | - | See parameters below | See parameters below |  | 1888.7057
Catalyst Disposal Cost |  | 188.8706 | 10% | 0.100 x Cat Repl | Engineering Estimate |  | 188.8706
Fuel Penalty Costs (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Other Maintenance Cost (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Total Direct Annual Costs | 258902.3717 |  | - | DAC |  |  | 258902.3717
Indirect Annual Costs
Indirect Annual Costs:
Overhead |  | 3672.9914 | 60% | 0.600 x Op/Super/Maint Labor & Mtls | OAQPS (60% of Op/Super/Maint. Labor & Mtls) |  | 3672.9914
Property Tax |  | 3060.8262 | 1.5% | 0.0150 x TCI | OAQPS (1%) |  | 3060.8262
Insurance |  | 2040.5508 | 1% | 0.010 x TCI | OAQPS (1%) |  | 2040.5508
General Administrative |  | 4081.1016 | 2% | 0.020 x TCI | OAQPS (2%) |  | 4081.1016
Total Indirect Annual Costs | 12855.47 |  | - | DAC |  |  | 12855.47
Capital Recovery Cost
Equipment Life (years) |  | 20 | - | n | Vendor Supplied |  | 20 | years | FALSE
Interest Rate | 7% | 7% | - | i | 7% per Agrium US Inc, Kenai Nitrogen Operations Facility Air Quality Control Construction Permit AQ0083CPT06 |  | 0.07 | % | FALSE
Capital Recovery Factor | 0.094393 |  | - | CRF = i/(1-(1+i)^-n) | -
Capital Recovery Cost (CRC) | 19261.356 |  | - |  | OAQPS Eqn 2.54 (Section 4.2, Ch. 2) |  | 19261.356 |  |  | Eqn 2.54 (Section 4.2, Ch. 2)
Total Annual Costs | 291019.1978 |  | - | TAC = DA + IDAC + CRC | OAQPS Eqn 2.56 (Section 4.2, Ch. 2) |  | 291019.1978 | $/yr |  | Eqn 2.56 (Section 4.2, Ch. 2)
Cost Effectiveness Analysis:
| NOx |  |  |  | Reference
Uncontrolled Emissions (tpy) | 5.8403 |  |  |  | PTE Calculations before add on emissions controls
Controlled NOx Emissions (tpy) | 0.40882 |  |  |  | Vendor Emissions Reduction Percentage
NOx Reduction (tpy) | 5.4315 |  |  |  | Calculated below
Total Annual Costs | 291019.1978 |  |  |  | Calculated above
Cost Effectiveness ($/ton/yr) | 53580.3057 |  |  |  | OAQPS Eqn 2.58 (Section 4.2, Ch. 2)
Cost Effectiveness Threshold ($/ton/yr) | [8 empty] | Req'd
Conclusion:
Project costs exceed BACT cost effectiveness threshold and may not be considered cost effective.
Design Parameters:
Enter values in boxes below. Where default value is available, entered value will override default.
Required data is highlighted yellow.
Combustion Unit Sizing | [5 empty] | Default | Final | Final Units | Cond Format | Notes
Reference
Turbine heat capacity: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | Req'd
Duct burner heat capacity, if applicable: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | FALSE
NOx Emission Rates
Reference
Turbine uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | FALSE
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | FALSE
or |  | ppmv @ 15% O2 |  |  | Assumption for baseline/uncontrolled emissions | 0 |  |  | FALSE
or (default) |  | ppmv @ 15% O2 |  |  |  | 0 |  |  | FALSE
Duct burner uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | N/A
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | N/A
or |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
or (default) |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
Controlled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | Req'd
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | Req'd
or |  | ppmv @ 15% O2 |  |  | Most stringent limit identified as BACT | 0 |  |  | Req'd
Natural Gas Properties
Reference
HHV [Default: 1050 Btu/scf] |  | Btu/scf |  |  |  | 1050 | 1050 | Btu/scf | FALSE
F-factor (dry) [Default: 8710 dscf/MMBtu] |  | dscf/MMBtu |  |  | EPA 40 CFR Part 60 Appendix A, Method 19, Table 19-2 | 8710 | 8710 | dscf/MMBtu | FALSE
Operational Parameters
Reference
Max annual op hours [Default: 8760 hr/yr] | 500 | hr/yr |  |  |  | 8760 | 500 | hours | FALSE
Annual Electricity Costs: Enter values below. Where default value is available, entered number overrides default.
Reference
Power demand: | 3027.542 | kW |  |  | Calculated below | #DIV/0! | 3027.542 | kW |  | Eqn 2.48 (Section 4.2, Ch. 2)
If power demand is not known, estimate on the basis of the parameters below:
delta P duct [Default: 3 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 3 | 3 | in H2O | N/A
delta P catalyst (per layer) [Default: 1 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 1 | 1 | in H2O | N/A
number of layers of catalyst | [6 empty] | 0 | # layers | N/A
Calculated Power demand: | 3027.542 | kW |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) |  |  |  | N/A
Electricity Cost [Default: 0.1572 $/kWh] | 0.1572 | $/kWh |  |  |  | 0.1572 | 0.1572 | $/kWh | FALSE
Aqueous Ammonia Costs: Enter values below or parameters to estimate.
Reference
Aqueous ammonia cost: | 5.67 | $/gallon |  |  |  |  | 5.67 | $/gallon | FALSE
Aqueous ammonia storage volume: |  | gallons |  |  | Calculated below |  | 0 | gallons | Req'd
or |  | days' worth |  |  | Engineering Estimate |  | 0 | gallons | Req'd
Aqueous ammonia consumption rate: |  | gal/hr |  |  | Calculated below | 4.4932 | 4.4932 | gal/hr
If aqueous ammonia consumption rate not known, estimate on the basis of the parameters below:
Stored NH3 concentration [Default: 19.4%] | 32.5% | wt% |  |  |  | 19.4% | 32.5% | wt% | FALSE | Eqn 2.34 (Section 4.2, Ch. 2)
NH3 solution mass flow rate (msol) | 33 | lb/hr |  |  | Calculated below | 0 | 33 | lb/hr | FALSE | Eqn 2.32, 2.33 (Section 4.2, Ch. 2)
NH3 solution density [Default: 7.344 lb/gal] |  | lb/gal |  |  | Engineeering Data | 7.3444 | 7.3444 | lb/gal | FALSE
Calculated Aqueous ammonia consumption rate: | 4.4932 | gal/hr |  |  | OAQPS Eqn 2.32-2.34 (Section 4.2, Ch. 2) |  |  |  | FALSE
Catalyst Costs:
Reference
Initial catalyst cost: | 6072 |  |  |  | Vendor Data |  | 6072 | $ | FALSE
Catalyst replacement frequency: | 3 | years |  |  |  |  | 3 | years | FALSE
Interest Rate | 7% | % |  |  | ADEC Default |  | 7% | % | FALSE
Annual Catalyst Replacement Cost | 1888.7057 |  |  |  | OAQPS Eqn 2.51 (Section 4.2, Ch. 2) | 1888.7057 | 1888.7057 | $ | FALSE | Eqn 2.51 (Section 4.2, Ch. 2)
* OAQPS refers to the EPA Air Pollution Control Cost Manual, Sixt Edition and subsequent revisions.
Note on A130: Note: Default cost from EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a
Note on I130: Note: From EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a

## Diesel Eng-SCR_Ox_DPF(250hp)
Alaska LNG Project
Diesel Driven Equipment - Firewater Pump
SCR/DPF Cost Effectiveness Analysis
Cost Quantification:
Cost Category | Project Cost | Default Estimate | Default % Applied | EPA Equation / Estimate Basis | Reference | Default | Final | Final Units | Cond Format | Notes
Direct Capital Costs
Purchased Equipment:
Purchased Equipment Costs | 26453.3333 |  | - | A | Vendor Supplied (includes all add-on control equipment) |  | 26453.3333 | $ | FALSE | Need input
Ammonia System |  |  | - | B | Included in A |  | 0 | $ | Req'd | Need input
Instrumentation & Controls |  | 2645.3333 | 10% | C = 0.10 x A |  |  | 2645.3333 | $
Freight |  | 1322.6667 | 5% | D = 0.05 x (A+B) |  |  | 1322.6667 | $
Taxes (Enter sales tax rate in "% Applied") |  | 0 | 0% | TaxRate x (A+B+C) | No sales tax in Alaska |  | 0 | $
Total Purchased Equipment Cost (PE) | 30421.3333 |  | - | PE |  |  | 30421.3333 | $
Direct Installation Costs:
Foundation & Supports | 0 | 3042.1333 | 10% | 0.10 x PE | Not needed, equipment is skid mounted |  | 0 | $
Erection and Handling |  | 10647.4667 | 35% | 0.35 x PE |  |  | 10647.4667 | $
Electrical |  | 1825.28 | 6% | 0.06 x PE |  |  | 1825.28 | $
Piping |  | 2433.7067 | 8% | 0.08 x PE |  |  | 2433.7067 | $
Insulation |  | 608.4267 | 2% | 0.02 x PE |  |  | 608.4267 | $
Painting | 0 | 1216.8533 | 4% | 0.04 x PE | Not needed, included in equipment purchase price |  | 0 | $
Site Preparation | 1851.7333 |  | 7% | 0.07 x (A+B) | engineering judgement |  | 1851.7333 | $ | FALSE
Total Direct Installation Cost (DI) | 17366.6133 |  | - | DI |  |  | 17366.6133 | $
Total Direct Capital Costs (DC) | 47787.9467 |  | - | DC = PE + DI |  |  | 47787.9467 | $
Indirect Capital Costs
Indirect Costs:
Engineering & Supervision |  | 4563.2 | 15% | 0.15 x PE |  |  | 4563.2 | $ | FALSE
Construction and Field Expenses |  | 3042.1333 | 10% | 0.10 x PE |  |  | 3042.1333 | $ | FALSE
Contractor Fees |  | 1521.0667 | 5% | 0.05 x PE |  |  | 1521.0667 | $ | FALSE
Startup-up |  | 304.2133 | 1% | 0.01 x PE |  |  | 304.2133 | $ | FALSE
Performance Testing |  | 304.2133 | 1% | 0.01 x PE |  |  | 304.2133 | $ | FALSE
Total Indirect Costs (TIC) | 9734.8267 |  | - | IC |  |  | 9734.8267 | $
Capital Investment:
Project Contingency |  | 8628.416 | 15% | E = 0.15 x (DC+IC) | OAQPS (15% of DC & TIC) |  | 8628.416 | $
Preproduction Cost |  | 1323.0238 | 2% | F = 0.02 x (DC+IC+Cont) | OAQPS (2% of DC & TIC & Proj Contingency) |  | 1323.0238 | $
Inventory Capital (initial reagent fill) |  | 0 | - | G = [Storage Gal] x [Reagent $/gal] | See parameters below |  | 0 | $ |  | Eqn. 2.44 (Section 4.2, Ch. 2)
Total Capital Investment | 67474.2131 |  | - | TCI = DC + IC + E + F + G |  |  | 67474.2131 | $
Direct Annual Costs
Direct Annual Costs:
Operating Labor |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Supervisory Labor |  | 0 | 15% | 15% of Op. Labor | OAQPS (15% of Op Labor) |  | 0 |  |  | Need input
Maintenance Labor |  | 1012.1132 | 1.5% | 0.015 x TCI | OAQPS (1.5% of TCI) |  | 1012.1132
Maintenance Materials |  | 1012.1132 | - | 100% of Maint. Labor | OAQPS (15% of Maint. Labor) |  | 1012.1132
Annual Reagent Cost |  | 12738.3418 | - | q*Cost*[op hr/yr] | See parameters below |  | 12738.3418 |  |  | Eqn 2.47 (Section 4.2, Ch. 2)
Annual Electricity Cost |  | 14653.9875 | - | See parameters below | See parameters below |  | 14653.9875 |  |  | Eqn 2.49 (Section 4.2, Ch. 2)
Catalyst Replacement |  | 1888.7057 | - | See parameters below | See parameters below |  | 1888.7057
Catalyst Disposal Cost |  | 188.8706 | 10% | 0.100 x Cat Repl | Engineering Estimate |  | 188.8706
Fuel Penalty Costs (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Other Maintenance Cost (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Total Direct Annual Costs | 31494.132 |  | - | DAC |  |  | 31494.132
Indirect Annual Costs
Indirect Annual Costs:
Overhead |  | 1214.5358 | 60% | 0.600 x Op/Super/Maint Labor & Mtls | OAQPS (60% of Op/Super/Maint. Labor & Mtls) |  | 1214.5358
Property Tax |  | 1012.1132 | 1.5% | 0.0150 x TCI | OAQPS (1%) |  | 1012.1132
Insurance |  | 674.7421 | 1% | 0.010 x TCI | OAQPS (1%) |  | 674.7421
General Administrative |  | 1349.4843 | 2% | 0.020 x TCI | OAQPS (2%) |  | 1349.4843
Total Indirect Annual Costs | 4250.8754 |  | - | DAC |  |  | 4250.8754
Capital Recovery Cost
Equipment Life (years) |  | 20 | - | n | Vendor Supplied |  | 20 | years | FALSE
Interest Rate | 7% | 7% | - | i | 7% per Agrium US Inc, Kenai Nitrogen Operations Facility Air Quality Control Construction Permit AQ0083CPT06 |  | 0.07 | % | FALSE
Capital Recovery Factor | 0.094393 |  | - | CRF = i/(1-(1+i)^-n) | -
Capital Recovery Cost (CRC) | 6369.0884 |  | - |  | OAQPS Eqn 2.54 (Section 4.2, Ch. 2) |  | 6369.0884 |  |  | Eqn 2.54 (Section 4.2, Ch. 2)
Total Annual Costs | 42114.0958 |  | - | TAC = DA + IDAC + CRC | OAQPS Eqn 2.56 (Section 4.2, Ch. 2) |  | 42114.0958 | $/yr |  | Eqn 2.56 (Section 4.2, Ch. 2)
Cost Effectiveness Analysis:
| NOx |  |  |  | Reference
Uncontrolled Emissions (tpy) | 0.39272 |  |  |  | PTE Calculations before add on emissions controls
Controlled NOx Emissions (tpy) | 0.02749 |  |  |  | Vendor Emissions Reduction Percentage
NOx Reduction (tpy) | 0.36523 |  |  |  | Calculated below
Total Annual Costs | 42114.0958 |  |  |  | Calculated above
Cost Effectiveness ($/ton/yr) | 115309.0999 |  |  |  | OAQPS Eqn 2.58 (Section 4.2, Ch. 2)
Cost Effectiveness Threshold ($/ton/yr) | [8 empty] | Req'd
Conclusion:
Project costs exceed BACT cost effectiveness threshold and may not be considered cost effective.
Design Parameters:
Enter values in boxes below. Where default value is available, entered value will override default.
Required data is highlighted yellow.
Combustion Unit Sizing | [5 empty] | Default | Final | Final Units | Cond Format | Notes
Reference
Turbine heat capacity: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | Req'd
Duct burner heat capacity, if applicable: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | FALSE
NOx Emission Rates
Reference
Turbine uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | FALSE
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | FALSE
or |  | ppmv @ 15% O2 |  |  | Assumption for baseline/uncontrolled emissions | 0 |  |  | FALSE
or (default) |  | ppmv @ 15% O2 |  |  |  | 0 |  |  | FALSE
Duct burner uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | N/A
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | N/A
or |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
or (default) |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
Controlled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | Req'd
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | Req'd
or |  | ppmv @ 15% O2 |  |  | Most stringent limit identified as BACT | 0 |  |  | Req'd
Natural Gas Properties
Reference
HHV [Default: 1050 Btu/scf] |  | Btu/scf |  |  |  | 1050 | 1050 | Btu/scf | FALSE
F-factor (dry) [Default: 8710 dscf/MMBtu] |  | dscf/MMBtu |  |  | EPA 40 CFR Part 60 Appendix A, Method 19, Table 19-2 | 8710 | 8710 | dscf/MMBtu | FALSE
Operational Parameters
Reference
Max annual op hours [Default: 8760 hr/yr] | 500 | hr/yr |  |  |  | 8760 | 500 | hours | FALSE
Annual Electricity Costs: Enter values below. Where default value is available, entered number overrides default.
Reference
Power demand: | 186.4375 | kW |  |  | Calculated below | #DIV/0! | 186.4375 | kW |  | Eqn 2.48 (Section 4.2, Ch. 2)
If power demand is not known, estimate on the basis of the parameters below:
delta P duct [Default: 3 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 3 | 3 | in H2O | N/A
delta P catalyst (per layer) [Default: 1 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 1 | 1 | in H2O | N/A
number of layers of catalyst | [6 empty] | 0 | # layers | N/A
Calculated Power demand: | 186.4375 | kW |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) |  |  |  | N/A
Electricity Cost [Default: 0.1572 $/kWh] | 0.1572 | $/kWh |  |  |  | 0.1572 | 0.1572 | $/kWh | FALSE
Aqueous Ammonia Costs: Enter values below or parameters to estimate.
Reference
Aqueous ammonia cost: | 5.67 | $/gallon |  |  |  |  | 5.67 | $/gallon | FALSE
Aqueous ammonia storage volume: |  | gallons |  |  | Calculated below |  | 0 | gallons | Req'd
or |  | days' worth |  |  | Engineering Estimate |  | 0 | gallons | Req'd
Aqueous ammonia consumption rate: |  | gal/hr |  |  | Calculated below | 4.4932 | 4.4932 | gal/hr
If aqueous ammonia consumption rate not known, estimate on the basis of the parameters below:
Stored NH3 concentration [Default: 19.4%] | 32.5% | wt% |  |  |  | 19.4% | 32.5% | wt% | FALSE | Eqn 2.34 (Section 4.2, Ch. 2)
NH3 solution mass flow rate (msol) | 33 | lb/hr |  |  | Calculated below | 0 | 33 | lb/hr | FALSE | Eqn 2.32, 2.33 (Section 4.2, Ch. 2)
NH3 solution density [Default: 7.344 lb/gal] |  | lb/gal |  |  | Engineeering Data | 7.3444 | 7.3444 | lb/gal | FALSE
Calculated Aqueous ammonia consumption rate: | 4.4932 | gal/hr |  |  | OAQPS Eqn 2.32-2.34 (Section 4.2, Ch. 2) |  |  |  | FALSE
Catalyst Costs:
Reference
Initial catalyst cost: | 6072 |  |  |  | Vendor Data |  | 6072 | $ | FALSE
Catalyst replacement frequency: | 3 | years |  |  |  |  | 3 | years | FALSE
Interest Rate | 7% | % |  |  | ADEC Default |  | 7% | % | FALSE
Annual Catalyst Replacement Cost | 1888.7057 |  |  |  | OAQPS Eqn 2.51 (Section 4.2, Ch. 2) | 1888.7057 | 1888.7057 | $ | FALSE | Eqn 2.51 (Section 4.2, Ch. 2)
* OAQPS refers to the EPA Air Pollution Control Cost Manual, Sixt Edition and subsequent revisions.
Note on A130: Note: Default cost from EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a
Note on I130: Note: From EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a

## Diesel Eng-SCR_Ox_DPF(335hp)
Alaska LNG Project
Diesel Driven Equipment - Dormitory Emergency Generator
SCR/DPF Cost Effectiveness Analysis
Cost Quantification:
Cost Category | Project Cost | Default Estimate | Default % Applied | EPA Equation / Estimate Basis | Reference | Default | Final | Final Units | Cond Format | Notes
Direct Capital Costs
Purchased Equipment:
Purchased Equipment Costs | 26453.3333 |  | - | A | Vendor Supplied (includes all add-on control equipment) |  | 26453.3333 | $ | FALSE | Need input
Ammonia System |  |  | - | B | Included in A |  | 0 | $ | Req'd | Need input
Instrumentation & Controls |  | 2645.3333 | 10% | C = 0.10 x A |  |  | 2645.3333 | $
Freight |  | 1322.6667 | 5% | D = 0.05 x (A+B) |  |  | 1322.6667 | $
Taxes (Enter sales tax rate in "% Applied") |  | 0 | 0% | TaxRate x (A+B+C) | No sales tax in Alaska |  | 0 | $
Total Purchased Equipment Cost (PE) | 30421.3333 |  | - | PE |  |  | 30421.3333 | $
Direct Installation Costs:
Foundation & Supports | 0 | 3042.1333 | 10% | 0.10 x PE | Not needed, equipment is skid mounted |  | 0 | $
Erection and Handling |  | 10647.4667 | 35% | 0.35 x PE |  |  | 10647.4667 | $
Electrical |  | 1825.28 | 6% | 0.06 x PE |  |  | 1825.28 | $
Piping |  | 2433.7067 | 8% | 0.08 x PE |  |  | 2433.7067 | $
Insulation |  | 608.4267 | 2% | 0.02 x PE |  |  | 608.4267 | $
Painting | 0 | 1216.8533 | 4% | 0.04 x PE | Not needed, included in equipment purchase price |  | 0 | $
Site Preparation | 1851.7333 |  | 7% | 0.07 x (A+B) | engineering judgement |  | 1851.7333 | $ | FALSE
Total Direct Installation Cost (DI) | 17366.6133 |  | - | DI |  |  | 17366.6133 | $
Total Direct Capital Costs (DC) | 47787.9467 |  | - | DC = PE + DI |  |  | 47787.9467 | $
Indirect Capital Costs
Indirect Costs:
Engineering & Supervision |  | 4563.2 | 15% | 0.15 x PE |  |  | 4563.2 | $ | FALSE
Construction and Field Expenses |  | 3042.1333 | 10% | 0.10 x PE |  |  | 3042.1333 | $ | FALSE
Contractor Fees |  | 1521.0667 | 5% | 0.05 x PE |  |  | 1521.0667 | $ | FALSE
Startup-up |  | 304.2133 | 1% | 0.01 x PE |  |  | 304.2133 | $ | FALSE
Performance Testing |  | 304.2133 | 1% | 0.01 x PE |  |  | 304.2133 | $ | FALSE
Total Indirect Costs (TIC) | 9734.8267 |  | - | IC |  |  | 9734.8267 | $
Capital Investment:
Project Contingency |  | 8628.416 | 15% | E = 0.15 x (DC+IC) | OAQPS (15% of DC & TIC) |  | 8628.416 | $
Preproduction Cost |  | 1323.0238 | 2% | F = 0.02 x (DC+IC+Cont) | OAQPS (2% of DC & TIC & Proj Contingency) |  | 1323.0238 | $
Inventory Capital (initial reagent fill) |  | 0 | - | G = [Storage Gal] x [Reagent $/gal] | See parameters below |  | 0 | $ |  | Eqn. 2.44 (Section 4.2, Ch. 2)
Total Capital Investment | 67474.2131 |  | - | TCI = DC + IC + E + F + G |  |  | 67474.2131 | $
Direct Annual Costs
Direct Annual Costs:
Operating Labor |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Supervisory Labor |  | 0 | 15% | 15% of Op. Labor | OAQPS (15% of Op Labor) |  | 0 |  |  | Need input
Maintenance Labor |  | 1012.1132 | 1.5% | 0.015 x TCI | OAQPS (1.5% of TCI) |  | 1012.1132
Maintenance Materials |  | 1012.1132 | - | 100% of Maint. Labor | OAQPS (15% of Maint. Labor) |  | 1012.1132
Annual Reagent Cost |  | 12738.3418 | - | q*Cost*[op hr/yr] | See parameters below |  | 12738.3418 |  |  | Eqn 2.47 (Section 4.2, Ch. 2)
Annual Electricity Cost |  | 19636.3433 | - | See parameters below | See parameters below |  | 19636.3433 |  |  | Eqn 2.49 (Section 4.2, Ch. 2)
Catalyst Replacement |  | 1888.7057 | - | See parameters below | See parameters below |  | 1888.7057
Catalyst Disposal Cost |  | 188.8706 | 10% | 0.100 x Cat Repl | Engineering Estimate |  | 188.8706
Fuel Penalty Costs (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Other Maintenance Cost (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Total Direct Annual Costs | 36476.4878 |  | - | DAC |  |  | 36476.4878
Indirect Annual Costs
Indirect Annual Costs:
Overhead |  | 1214.5358 | 60% | 0.600 x Op/Super/Maint Labor & Mtls | OAQPS (60% of Op/Super/Maint. Labor & Mtls) |  | 1214.5358
Property Tax |  | 1012.1132 | 1.5% | 0.0150 x TCI | OAQPS (1%) |  | 1012.1132
Insurance |  | 674.7421 | 1% | 0.010 x TCI | OAQPS (1%) |  | 674.7421
General Administrative |  | 1349.4843 | 2% | 0.020 x TCI | OAQPS (2%) |  | 1349.4843
Total Indirect Annual Costs | 4250.8754 |  | - | DAC |  |  | 4250.8754
Capital Recovery Cost
Equipment Life (years) |  | 20 | - | n | Vendor Supplied |  | 20 | years | FALSE
Interest Rate | 7% | 7% | - | i | 7% per Agrium US Inc, Kenai Nitrogen Operations Facility Air Quality Control Construction Permit AQ0083CPT06 |  | 0.07 | % | FALSE
Capital Recovery Factor | 0.094393 |  | - | CRF = i/(1-(1+i)^-n) | -
Capital Recovery Cost (CRC) | 6369.0884 |  | - |  | OAQPS Eqn 2.54 (Section 4.2, Ch. 2) |  | 6369.0884 |  |  | Eqn 2.54 (Section 4.2, Ch. 2)
Total Annual Costs | 47096.4516 |  | - | TAC = DA + IDAC + CRC | OAQPS Eqn 2.56 (Section 4.2, Ch. 2) |  | 47096.4516 | $/yr |  | Eqn 2.56 (Section 4.2, Ch. 2)
Cost Effectiveness Analysis:
| NOx |  |  |  | Reference
Uncontrolled Emissions (tpy) | 0.52329 |  |  |  | PTE Calculations before add on emissions controls
Controlled NOx Emissions (tpy) | 0.03663 |  |  |  | Vendor Emissions Reduction Percentage
NOx Reduction (tpy) | 0.48666 |  |  |  | Calculated below
Total Annual Costs | 47096.4516 |  |  |  | Calculated above
Cost Effectiveness ($/ton/yr) | 96775.295 |  |  |  | OAQPS Eqn 2.58 (Section 4.2, Ch. 2)
Cost Effectiveness Threshold ($/ton/yr) | [8 empty] | Req'd
Conclusion:
Project costs exceed BACT cost effectiveness threshold and may not be considered cost effective.
Design Parameters:
Enter values in boxes below. Where default value is available, entered value will override default.
Required data is highlighted yellow.
Combustion Unit Sizing | [5 empty] | Default | Final | Final Units | Cond Format | Notes
Reference
Turbine heat capacity: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | Req'd
Duct burner heat capacity, if applicable: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | FALSE
NOx Emission Rates
Reference
Turbine uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | FALSE
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | FALSE
or |  | ppmv @ 15% O2 |  |  | Assumption for baseline/uncontrolled emissions | 0 |  |  | FALSE
or (default) |  | ppmv @ 15% O2 |  |  |  | 0 |  |  | FALSE
Duct burner uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | N/A
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | N/A
or |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
or (default) |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
Controlled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | Req'd
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | Req'd
or |  | ppmv @ 15% O2 |  |  | Most stringent limit identified as BACT | 0 |  |  | Req'd
Natural Gas Properties
Reference
HHV [Default: 1050 Btu/scf] |  | Btu/scf |  |  |  | 1050 | 1050 | Btu/scf | FALSE
F-factor (dry) [Default: 8710 dscf/MMBtu] |  | dscf/MMBtu |  |  | EPA 40 CFR Part 60 Appendix A, Method 19, Table 19-2 | 8710 | 8710 | dscf/MMBtu | FALSE
Operational Parameters
Reference
Max annual op hours [Default: 8760 hr/yr] | 500 | hr/yr |  |  |  | 8760 | 500 | hours | FALSE
Annual Electricity Costs: Enter values below. Where default value is available, entered number overrides default.
Reference
Power demand: | 249.8263 | kW |  |  | Calculated below | #DIV/0! | 249.8263 | kW |  | Eqn 2.48 (Section 4.2, Ch. 2)
If power demand is not known, estimate on the basis of the parameters below:
delta P duct [Default: 3 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 3 | 3 | in H2O | N/A
delta P catalyst (per layer) [Default: 1 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 1 | 1 | in H2O | N/A
number of layers of catalyst | [6 empty] | 0 | # layers | N/A
Calculated Power demand: | 249.8263 | kW |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) |  |  |  | N/A
Electricity Cost [Default: 0.1572 $/kWh] | 0.1572 | $/kWh |  |  |  | 0.1572 | 0.1572 | $/kWh | FALSE
Aqueous Ammonia Costs: Enter values below or parameters to estimate.
Reference
Aqueous ammonia cost: | 5.67 | $/gallon |  |  |  |  | 5.67 | $/gallon | FALSE
Aqueous ammonia storage volume: |  | gallons |  |  | Calculated below |  | 0 | gallons | Req'd
or |  | days' worth |  |  | Engineering Estimate |  | 0 | gallons | Req'd
Aqueous ammonia consumption rate: |  | gal/hr |  |  | Calculated below | 4.4932 | 4.4932 | gal/hr
If aqueous ammonia consumption rate not known, estimate on the basis of the parameters below:
Stored NH3 concentration [Default: 19.4%] | 32.5% | wt% |  |  |  | 19.4% | 32.5% | wt% | FALSE | Eqn 2.34 (Section 4.2, Ch. 2)
NH3 solution mass flow rate (msol) | 33 | lb/hr |  |  | Calculated below | 0 | 33 | lb/hr | FALSE | Eqn 2.32, 2.33 (Section 4.2, Ch. 2)
NH3 solution density [Default: 7.344 lb/gal] |  | lb/gal |  |  | Engineeering Data | 7.3444 | 7.3444 | lb/gal | FALSE
Calculated Aqueous ammonia consumption rate: | 4.4932 | gal/hr |  |  | OAQPS Eqn 2.32-2.34 (Section 4.2, Ch. 2) |  |  |  | FALSE
Catalyst Costs:
Reference
Initial catalyst cost: | 6072 |  |  |  | Vendor Data |  | 6072 | $ | FALSE
Catalyst replacement frequency: | 3 | years |  |  |  |  | 3 | years | FALSE
Interest Rate | 7% | % |  |  | ADEC Default |  | 7% | % | FALSE
Annual Catalyst Replacement Cost | 1888.7057 |  |  |  | OAQPS Eqn 2.51 (Section 4.2, Ch. 2) | 1888.7057 | 1888.7057 | $ | FALSE | Eqn 2.51 (Section 4.2, Ch. 2)
* OAQPS refers to the EPA Air Pollution Control Cost Manual, Sixt Edition and subsequent revisions.
Note on A130: Note: Default cost from EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a
Note on I130: Note: From EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a

## Diesel Eng-SCR_Ox_DPF(201hp)
Alaska LNG Project
Diesel Driven Equipment - Communications Tower Generator
SCR/DPF Cost Effectiveness Analysis
Cost Quantification:
Cost Category | Project Cost | Default Estimate | Default % Applied | EPA Equation / Estimate Basis | Reference | Default | Final | Final Units | Cond Format | Notes
Direct Capital Costs
Purchased Equipment:
Purchased Equipment Costs | 26453.3333 |  | - | A | Vendor Supplied (includes all add-on control equipment) |  | 26453.3333 | $ | FALSE | Need input
Ammonia System |  |  | - | B | Included in A |  | 0 | $ | Req'd | Need input
Instrumentation & Controls |  | 2645.3333 | 10% | C = 0.10 x A |  |  | 2645.3333 | $
Freight |  | 1322.6667 | 5% | D = 0.05 x (A+B) |  |  | 1322.6667 | $
Taxes (Enter sales tax rate in "% Applied") |  | 0 | 0% | TaxRate x (A+B+C) | No sales tax in Alaska |  | 0 | $
Total Purchased Equipment Cost (PE) | 30421.3333 |  | - | PE |  |  | 30421.3333 | $
Direct Installation Costs:
Foundation & Supports | 0 | 3042.1333 | 10% | 0.10 x PE | Not needed, equipment is skid mounted |  | 0 | $
Erection and Handling |  | 10647.4667 | 35% | 0.35 x PE |  |  | 10647.4667 | $
Electrical |  | 1825.28 | 6% | 0.06 x PE |  |  | 1825.28 | $
Piping |  | 2433.7067 | 8% | 0.08 x PE |  |  | 2433.7067 | $
Insulation |  | 608.4267 | 2% | 0.02 x PE |  |  | 608.4267 | $
Painting | 0 | 1216.8533 | 4% | 0.04 x PE | Not needed, included in equipment purchase price |  | 0 | $
Site Preparation | 1851.7333 |  | 7% | 0.07 x (A+B) | engineering judgement |  | 1851.7333 | $ | FALSE
Total Direct Installation Cost (DI) | 17366.6133 |  | - | DI |  |  | 17366.6133 | $
Total Direct Capital Costs (DC) | 47787.9467 |  | - | DC = PE + DI |  |  | 47787.9467 | $
Indirect Capital Costs
Indirect Costs:
Engineering & Supervision |  | 4563.2 | 15% | 0.15 x PE |  |  | 4563.2 | $ | FALSE
Construction and Field Expenses |  | 3042.1333 | 10% | 0.10 x PE |  |  | 3042.1333 | $ | FALSE
Contractor Fees |  | 1521.0667 | 5% | 0.05 x PE |  |  | 1521.0667 | $ | FALSE
Startup-up |  | 304.2133 | 1% | 0.01 x PE |  |  | 304.2133 | $ | FALSE
Performance Testing |  | 304.2133 | 1% | 0.01 x PE |  |  | 304.2133 | $ | FALSE
Total Indirect Costs (TIC) | 9734.8267 |  | - | IC |  |  | 9734.8267 | $
Capital Investment:
Project Contingency |  | 8628.416 | 15% | E = 0.15 x (DC+IC) | OAQPS (15% of DC & TIC) |  | 8628.416 | $
Preproduction Cost |  | 1323.0238 | 2% | F = 0.02 x (DC+IC+Cont) | OAQPS (2% of DC & TIC & Proj Contingency) |  | 1323.0238 | $
Inventory Capital (initial reagent fill) |  | 0 | - | G = [Storage Gal] x [Reagent $/gal] | See parameters below |  | 0 | $ |  | Eqn. 2.44 (Section 4.2, Ch. 2)
Total Capital Investment | 67474.2131 |  | - | TCI = DC + IC + E + F + G |  |  | 67474.2131 | $
Direct Annual Costs
Direct Annual Costs:
Operating Labor |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Supervisory Labor |  | 0 | 15% | 15% of Op. Labor | OAQPS (15% of Op Labor) |  | 0 |  |  | Need input
Maintenance Labor |  | 1012.1132 | 1.5% | 0.015 x TCI | OAQPS (1.5% of TCI) |  | 1012.1132
Maintenance Materials |  | 1012.1132 | - | 100% of Maint. Labor | OAQPS (15% of Maint. Labor) |  | 1012.1132
Annual Reagent Cost |  | 12738.3418 | - | q*Cost*[op hr/yr] | See parameters below |  | 12738.3418 |  |  | Eqn 2.47 (Section 4.2, Ch. 2)
Annual Electricity Cost |  | 11781.8059 | - | See parameters below | See parameters below |  | 11781.8059 |  |  | Eqn 2.49 (Section 4.2, Ch. 2)
Catalyst Replacement |  | 1888.7057 | - | See parameters below | See parameters below |  | 1888.7057
Catalyst Disposal Cost |  | 188.8706 | 10% | 0.100 x Cat Repl | Engineering Estimate |  | 188.8706
Fuel Penalty Costs (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Other Maintenance Cost (specify) |  |  | - |  | Vendor Supplied |  | 0 |  | Req'd | Need input
Total Direct Annual Costs | 28621.9505 |  | - | DAC |  |  | 28621.9505
Indirect Annual Costs
Indirect Annual Costs:
Overhead |  | 1214.5358 | 60% | 0.600 x Op/Super/Maint Labor & Mtls | OAQPS (60% of Op/Super/Maint. Labor & Mtls) |  | 1214.5358
Property Tax |  | 1012.1132 | 1.5% | 0.0150 x TCI | OAQPS (1%) |  | 1012.1132
Insurance |  | 674.7421 | 1% | 0.010 x TCI | OAQPS (1%) |  | 674.7421
General Administrative |  | 1349.4843 | 2% | 0.020 x TCI | OAQPS (2%) |  | 1349.4843
Total Indirect Annual Costs | 4250.8754 |  | - | DAC |  |  | 4250.8754
Capital Recovery Cost
Equipment Life (years) |  | 20 | - | n | Vendor Supplied |  | 20 | years | FALSE
Interest Rate | 7% | 7% | - | i | 7% per Agrium US Inc, Kenai Nitrogen Operations Facility Air Quality Control Construction Permit AQ0083CPT06 |  | 0.07 | % | FALSE
Capital Recovery Factor | 0.094393 |  | - | CRF = i/(1-(1+i)^-n) | -
Capital Recovery Cost (CRC) | 6369.0884 |  | - |  | OAQPS Eqn 2.54 (Section 4.2, Ch. 2) |  | 6369.0884 |  |  | Eqn 2.54 (Section 4.2, Ch. 2)
Total Annual Costs | 39241.9143 |  | - | TAC = DA + IDAC + CRC | OAQPS Eqn 2.56 (Section 4.2, Ch. 2) |  | 39241.9143 | $/yr |  | Eqn 2.56 (Section 4.2, Ch. 2)
Cost Effectiveness Analysis:
| NOx |  |  |  | Reference
Uncontrolled Emissions (tpy) | 0.31397 |  |  |  | PTE Calculations before add on emissions controls
Controlled NOx Emissions (tpy) | 0.021978 |  |  |  | Vendor Emissions Reduction Percentage
NOx Reduction (tpy) | 0.29199 |  |  |  | Calculated below
Total Annual Costs | 39241.9143 |  |  |  | Calculated above
Cost Effectiveness ($/ton/yr) | 134392.5675 |  |  |  | OAQPS Eqn 2.58 (Section 4.2, Ch. 2)
Cost Effectiveness Threshold ($/ton/yr) | [8 empty] | Req'd
Conclusion:
Project costs exceed BACT cost effectiveness threshold and may not be considered cost effective.
Design Parameters:
Enter values in boxes below. Where default value is available, entered value will override default.
Required data is highlighted yellow.
Combustion Unit Sizing | [5 empty] | Default | Final | Final Units | Cond Format | Notes
Reference
Turbine heat capacity: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | Req'd
Duct burner heat capacity, if applicable: |  | MMBtu/hr |  |  |  |  | 0 | MMBtu/hr | FALSE
NOx Emission Rates
Reference
Turbine uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | FALSE
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | FALSE
or |  | ppmv @ 15% O2 |  |  | Assumption for baseline/uncontrolled emissions | 0 |  |  | FALSE
or (default) |  | ppmv @ 15% O2 |  |  |  | 0 |  |  | FALSE
Duct burner uncontrolled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | N/A
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | N/A
or |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
or (default) |  | ppmv @ 3% O2 |  |  |  | 0 |  |  | N/A
Controlled NOx concentration: |  | lb NOx/MMBtu |  |  |  | 0 | 0 | lb/MMBtu | Req'd
or |  | lb NOx/MMscf |  |  |  | 0 |  |  | Req'd
or |  | ppmv @ 15% O2 |  |  | Most stringent limit identified as BACT | 0 |  |  | Req'd
Natural Gas Properties
Reference
HHV [Default: 1050 Btu/scf] |  | Btu/scf |  |  |  | 1050 | 1050 | Btu/scf | FALSE
F-factor (dry) [Default: 8710 dscf/MMBtu] |  | dscf/MMBtu |  |  | EPA 40 CFR Part 60 Appendix A, Method 19, Table 19-2 | 8710 | 8710 | dscf/MMBtu | FALSE
Operational Parameters
Reference
Max annual op hours [Default: 8760 hr/yr] | 500 | hr/yr |  |  |  | 8760 | 500 | hours | FALSE
Annual Electricity Costs: Enter values below. Where default value is available, entered number overrides default.
Reference
Power demand: | 149.8957 | kW |  |  | Calculated below | #DIV/0! | 149.8957 | kW |  | Eqn 2.48 (Section 4.2, Ch. 2)
If power demand is not known, estimate on the basis of the parameters below:
delta P duct [Default: 3 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 3 | 3 | in H2O | N/A
delta P catalyst (per layer) [Default: 1 in H2O] |  |  |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) | 1 | 1 | in H2O | N/A
number of layers of catalyst | [6 empty] | 0 | # layers | N/A
Calculated Power demand: | 149.8957 | kW |  |  | OAQPS Eqn 2.48 (Section 4.2, Ch. 2) |  |  |  | N/A
Electricity Cost [Default: 0.1572 $/kWh] | 0.1572 | $/kWh |  |  |  | 0.1572 | 0.1572 | $/kWh | FALSE
Aqueous Ammonia Costs: Enter values below or parameters to estimate.
Reference
Aqueous ammonia cost: | 5.67 | $/gallon |  |  |  |  | 5.67 | $/gallon | FALSE
Aqueous ammonia storage volume: |  | gallons |  |  | Calculated below |  | 0 | gallons | Req'd
or |  | days' worth |  |  | Engineering Estimate |  | 0 | gallons | Req'd
Aqueous ammonia consumption rate: |  | gal/hr |  |  | Calculated below | 4.4932 | 4.4932 | gal/hr
If aqueous ammonia consumption rate not known, estimate on the basis of the parameters below:
Stored NH3 concentration [Default: 19.4%] | 32.5% | wt% |  |  |  | 19.4% | 32.5% | wt% | FALSE | Eqn 2.34 (Section 4.2, Ch. 2)
NH3 solution mass flow rate (msol) | 33 | lb/hr |  |  | Calculated below | 0 | 33 | lb/hr | FALSE | Eqn 2.32, 2.33 (Section 4.2, Ch. 2)
NH3 solution density [Default: 7.344 lb/gal] |  | lb/gal |  |  | Engineeering Data | 7.3444 | 7.3444 | lb/gal | FALSE
Calculated Aqueous ammonia consumption rate: | 4.4932 | gal/hr |  |  | OAQPS Eqn 2.32-2.34 (Section 4.2, Ch. 2) |  |  |  | FALSE
Catalyst Costs:
Reference
Initial catalyst cost: | 6072 |  |  |  | Vendor Data |  | 6072 | $ | FALSE
Catalyst replacement frequency: | 3 | years |  |  |  |  | 3 | years | FALSE
Interest Rate | 7% | % |  |  | ADEC Default |  | 7% | % | FALSE
Annual Catalyst Replacement Cost | 1888.7057 |  |  |  | OAQPS Eqn 2.51 (Section 4.2, Ch. 2) | 1888.7057 | 1888.7057 | $ | FALSE | Eqn 2.51 (Section 4.2, Ch. 2)
* OAQPS refers to the EPA Air Pollution Control Cost Manual, Sixt Edition and subsequent revisions.
Note on A130: Note: Default cost from EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a
Note on I130: Note: From EIA data, Table 5.6.A Nov 2014 - Retail Price of Electricity to Industrial Customers in Alaska: http://www.eia.gov/electricity/monthly/epm_table_grapher.cfm?t=epmt_5_06_a