## PermitSearchResults (39)
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | Combustion Turbine | 15.21 | Natural Gas | 360 | MW | This process represents the GE option for the project - One GE 7FA.05 natural gas-fired combustion turbine generator with an 820.5 MMBTUH duct burner. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | EFFICIENT DESIGN AND COMBUSTION. | 1000 | LB/MW-HR | ANNUAL | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | COMBUSTION TURBINE | 15.21 | NATURAL GAS | 360 | MW | This process represents the Siemens option for the project - One Siemens SGT6-5000F5 natural gas-fired combustion turbine generator with an 820.3 MMBTUH duct burner. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | EFFICIENT DESIGN AND COMBUSTION. | 1000 | LB/MW-HR | ANNUAL | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITH DUCT FIRING | 15.21 | NATURAL GAS | 1000 | MW | TWO MITSUBISHI &lsquo;&lsquo;G&lsquo;&lsquo; MODEL COMBUSTION TURBINE GENERATORS (CTS) WITH A NOMINAL GENERATING CAPACITY OF 270 MW CAPACITY EACH, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR), OXIDATION CATALYST | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | EXCLUSIVE USE OF PIPELINE-QUALITY NATURAL GAS, AND INSTALLATION OF HIGH-EFFICIENCY CT MODEL (MITSUBISHI &lsquo;&lsquo;G&lsquo;&lsquo; MODEL) | 946 | LB/MW-H (AS CO2) | 12-MONTH ROLLING | BACT-PSD |  |  | 0 |  | 7500 | BTU/KWH (HEAT RATE) | AT ALL TIMES, EXCLUDING SU/SD | 0 |  |  | 0 | 0 | N |  | WITH AND WITHOUT DUCT FIRING
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | MR. RANDY THOMPSON | (615) 532-6825 | randall.thompson@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Natural Gas-Fired Combustion Turbine with HRSG | 15.21 | Natural Gas | 1339 | MMBtu/hr | Turbine throughput is 1019.7 MMBtu/hr when burning natural gas and 1083.7 MMBtu/hr when burning No. 2 oil. Duct burner throughput is 319.3 MMBtu/hr. Duct burner firing will occur during natural gas combustion only. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion design and practices | 1800 | LB/MWH | 12-MONTH MOVING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0805 | EAGLE MOUNTAIN STEAM ELECTRIC STATION | EAGLE MOUNTAIN POWER COMPANY | TARRANT | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joel Lunsford, x-1513, joel.lunsford@tceq.texas.gov | GHGPSDTX115, 107569, PSDTX1432 | 4911 | 221112 | 110005028638 | 11/04/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-14 | 2017-11-17 | B |  | Electric Generation |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 462 | MW |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 917 | LB/MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
TX-0787 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joel Lunsford, 512-239-1513, joel.lunsford@tceq.texas.gov | GHGPSDTX125, 111393, PSDTX1368 | 4911 | 221112 | unknown | 12/10/2015 &nbsp;ACT | 03/01/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | Electric Generation |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 497 | MW |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 937 | LB/MW HR |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD COMBUSTION PRACTICES | 924 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 megawatts (MW)) | 15.21 | natural gas | 889 | MW | (2) GE 7HA.01 in a 2x1 configuration and a 872 million British thermal units per hour (MMBtu/hr) duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 901 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Subparts KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 1127 | MW | (2) GE 7HA.02 in a 2x1 configuration and a 985 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 865 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Subparts KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 748 | MW | (2) GE 7FA.05 in a 2x1 configuration and a 826 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 944 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 889 | MW | (2) MHI 501GAC in a 2x1 configuration and a 221 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 929 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 889 | MW | (2) MHI 501GAC in (2) 1x1 configurations and a 221 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 929 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 915 | MW | (2) Siemens SCC6-8000H(1.4) in a 2x1 configuration and a 326 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 965 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and TTTT
NJ-0079 | WOODBRIDGE ENERGY CENTER | CPV SHORE, LLC | MIDDLESEX | NJ | 7095 | USA | MARK TURNER | (415)293-1463 | MTURNER@CPV.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Mr. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS, yogesh.doshi@dep.state.nj.us; phone 609-633-7249 | 18940 - BOP110003 | 4911 | 221112 | 110055590953 | 10/12/2011 &nbsp;ACT | 07/25/2012 &nbsp;ACT | 2012-11-27 | 2018-04-17 | A |  | Woodbridge Energy Center (WEC), proposed at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, would be a new, highly efficient, 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,307 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, one small dew point fuel gas heater (fuel gas heater), a mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Other Permitting Information: Facility-Wide Greenhouse Gas (GHG) emissions as CO2e emissions= 2,073,645 tons per year | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural gas | 40297.6 | mmcubic ft/year | Woodbridge Energy Center (WEC), located at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, will be a new 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) each with a maximum rated heat input of 2,307 million British thermal units per hour (MMBtu/hr), that will utilize pipeline natural gas only, with 2 HRSGs, 2 Duct Burners (each 500 MMbtu/hr). | Carbon Dioxide Equivalent (CO2e) | Other - CO2 Monitored by CO2 CEMs | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 925 | LB/MW-H | BASED ON 12 MONTH PERIOD, ROLLING 1 MNTH | BACT-PSD |  | U | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0080 | HESS NEWARK ENERGY CENTER | HESS NEWARK ENERGY CENTER, LLC | ESSEX | NJ | 7105 | USA | PETER HAID | (774) 750-7088 | PHAID@HESS.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Supervisor: Yogesh Doshi - yogesh.doshi@dep.state.nj.us Phone: 609-633-7249 Permit Evaluator: Michael Hogan - michael.hogan@dep.state.nj.us. Phone: (609)-633-1124 | 08857/BOP110001 | 4911 | 221112 | 110044839903 | 12/10/2011 &nbsp;ACT | 11/01/2012 &nbsp;ACT | 2013-04-04 | 2018-04-17 | A |  | Combined Cycle Electric Generating Facility HESS Newark Energy Center (Hess-NEC), proposed at City of Newark (Essex County), New Jersey, would be a new, highly efficient, 655 MW combined-cycle power generating facility. Hess-NEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,320 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, a 12-cell mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Facility-wide Greenhouse Gas (GHG) emissions as CO2e emissions = 2,003,654 tpy | Combined cylce turbine with duct burner | 15.21 | natural gas | 39463 | mmcubic ft/year* | * Annual throughput is for 2 turbines, 2 duct burners and 1 auxiliary boiler | Carbon Dioxide Equivalent (CO2e) | Other - CO2 Monitored by CO2 CEMs | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 887 | LB/MW-H | CONSCUTV 12 MONTH PERIOD ROLLING 1 MONTH | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO2 Monitored by CO2 CEMs, CH4 and Nitrous oxide monitored by calculations
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices and energy efficiency | 1071 | LB/MW-H | 12-MONTH ROLLING AVG. | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 is 1,071.0 LB/MW-H gross energy output based on a 12-month rolling average. Cost effectiveness information: The CO2e limit is based on 6% performance degradation for GE turbines. CCS is assumed to be about 90% effective, resulting in a reduction of approximately 2.3 million tons of CO2 emissions per year from the proposed CTGs at MCV. However, the use of CCS as a control method would also result in significant energy and environmental impacts due to the increased fuel usage required to operate the CCS systems. MCV estimated that to reduce the 2.3 million tons of CO2 per year from the proposed CTGs, an additional 181 MW of electric power and steam generation would be needed for capture, compression, and transport to an Enhanced Oil Recovery (EOR) for storage. That would result in air emission increases for an annualized cost of approximately $155 million per year, which is approximately $67 per ton to capture and store CO2. Therefore, MCV determined that CCS for emission reduction, as well as the environmental degradation due to increases in pollutants is not reasonable.
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices and energy efficiency. | 995 | LB/MW-H | 12-MO. ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is based on 6% performance degradation for GE turbines. CCS is assumed to be about 90% effective, resulting in a reduction of approximately 2.3 million tons of CO2 emissions per year from the proposed CTGs at MCV. However, the use of CCS as a control method would also result in significant energy and environmental impacts due to the increased fuel usage required to operate the CCS systems. MCV estimated that to reduce the 2.3 million tons of CO2 per year from the proposed CTGs, an additional 181 MW of electric power and steam generation would be needed for capture, compression and transport to an Enhanced Oil Recovery (EOR) for storage. That would result in air emissioin increases for an annualized cost of approximately $155 million per year, which is approximately $67 per ton to capture and store CO2. Therefore, MCV determined that CCS for emission reduction, as well as the environmental degradation due to increases in pollutant is not reasonable.
TX-0810 | DECORDOVA STEAM ELECTRIC STATION (DECORDOVA STATION) | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL BARNES | 214-875-8374 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5221 Ruth.Alvirez@tceq.texas.gov | 107569, PSDTX1432, GHGPSDTX124 | 4911 | 221112 | Not Found | 07/26/2016 &nbsp;ACT | 10/04/2016 &nbsp;ACT | 2016-10-04 | 2017-11-16 | C |  | two combustion turbines (CTGs) authorized to operate in simple cycle or combined cycle. | The simple cycle operations were issued in 2013, but the combined cycle criteria pollutant PSD permit / state amendment was issued on March 8, 2016. This GHG initial review is linked to the 2016 action which added combined cycle capability, it does not apply to the simple cycle operations which were authorized in 2013. | Combined Cycle and Cogeneration (&gt;25 MW) | 15.21 | natural gas | 213 | MW | Two turbine options: GE 7FA [210 megawatts (MW)] or Siemens 5000F (231MW) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices and firing low carbon fuel. | 966 | LB/MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two Combine Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 3001.57 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. . (Operational limits are for each CCCT NG-fired with duct burner) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Good combustion practices and oxidation catalyst | 883 | LB/MW-HR | EXPRESSED AS CO2E (NET) | BACT-PSD |  | U | 0 | U | 2896556 | TONS | YEAR (NET) EXPRESSED AS CO2E | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative emissions from both CCCT in any 12-month period expressed as CO2e
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices/energy efficiency | 1000 | LB/MW-H | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit is for each unit operating with or without DB. CCS technology for natural gas-fired combined cycle units entails significant economic, energy, and environmental impacts as a control method would also result in significant energy and environmental impacts due to the increased fuel usage required to operate the CCS systems. Renaissance referred to a detailed cost analysis conducted by Carnegie Mellon University (*) which specifically analyzed costs for plants using amine-based post-combustion CCS systems with 90% CO2 capture. The analysis found that CCS increases capital costs (in 2007 basis) by approximately $600/kW, which would result in an incremental capital cost of approximately $840 million for this project. The analysis also found the cost (in 2007 basis) of CO2 avoided, ranged from $74-$114 per ton CO2 which equates to annual costs of $400-$600 million. *Reference of analysis. The cost of Carbon Capture and Storage for Natural Gas Combined Cycle Power Plants, Rubin and Zhai, Department of Engineering and Public Policy, Carnegie Mellon University, http://www.wecc.biz/committees/BOD/TEPPC/SPSG/MDTF/120914/Lists/Minutes/1/CCS_Costs_for_Combined_Cycle.pdf
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices/energy efficiency | 1000 | LB/MW-H | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit applies for each unit operating with or without DB. CCS technology for natural gas-fired combined cycle units entails significant economic, energy, and environmental impacts as a control method would also result in significant energy and environmental impacts due to the increased fuel usage required to operate the CCS systems. Renaissance referred to a detailed cost analysis conducted by Carnegie Mellon University (*) which specifically analyzed costs for plants using amine-based post-combustion CCS systems with 90% CO2 capture. The anlaysis found that CCS increases capital costs (in 2007 basis) by approximately $600/kW, which would result in an incremental capital cost of approximately $840 million for this project. The analysis also found the cost (in 2007 basis) of CO2 avoided, ranged from $74 to $114 per ton CO2 which equates to annual costs of $400 to $600 million.
TX-0773 | FGE EAGLE PINES PROJECT | FGE EAGLE PINES, LLC | CHEROKEE | TX |  | USA | EMERSON FARRELL | 281-407-7749 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, 512-239-1095, Erik.Hendrickson@tceq.texas.gov | 131316, PSDTX1454, AND GHGPSDT | 4911 | 221112 | UNKNOWN | 09/10/2015 &nbsp;ACT | 11/04/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | The FGEEP Project will include three natural gas-fired combined cycle (NGCC) power blocks, each block comprised of two gas-fired combustion turbines, two supplemental fired duct burners (DBs) heat recovery steam generators (HRSGs), and one steam turbine. FGEEP selected Alstom GT36 combustion turbines (CTs), each nominally rated at 321 megawatts (MW). Each HRSG is equipped with DBs that will have a maximum design heat input capacity of 799 million British thermal units per hour (MMBtu/hr). The CTs and DBs are fueled with pipeline quality natural gas. Each power block will also have a steam turbine generator designed to produce approximately 502 MW with the additional duct firing. Each of the three blocks will include the following ancillary equipment: one multi-cell condenser/cooling tower, one emergency generator, one firewater pump, two diesel storage tanks, and pressurized aqueous ammonia storage tanks. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 321 | MW | Alstom GT36 combustion turbines (321 MW)+ 799 million British thermal units per hour (MMBtu/hr) duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Low carbon fuel, good combustion, efficient combined cycle design | 886 | LB/MW H | WITHOUT DUCT FIRING | BACT-PSD | NSPS | N | 0 | U | 816 | LB/MW H | WITH DUCT FIRING | 0 |  |  | 0 | 0 | N
*TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2018-05-11 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | PIPELINE QUALITY NATURAL GAS, GOOD COMBUSTION PRACTICES | 884 | LB/MWH |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | Mitsubishi M501-GAC combustion turbine, combined cycle configuration with duct burner. | 15.21 | natural gs | 2988 | MMBTU/H | or ULSD; Duct burner 499 MMBtu/hr, natural gas | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Thermal efficiency Clean fuels | 1000 | LB PER GROSS MWH | 365-DAY ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Carbon Dioxide Equivalent (CO2e) | Other - CO2 CEMS or fuel use monitoring | (Greenhouse Gasses (GHG)) | CO2e | P | Use of low-emitting fuels and technologies | 850 | LB/MWH | FOR GAS OPERATION, 12-MO ROLLING | BACT-PSD | NSPS | U | 0 | U | 1210 | LB/MWH | FOR ULSD OPERATION, 12-MO ROLLING | 0 |  |  | 0 | 0 | N |  | Also, limited to 500 hr/yr per turbine on ULSD. Standard is a weighted average of the gas and ULSD standards, depending on generation on the two fuels during the compliance period. Excludes startup, shutdown, and malfunction. NSPS Subpart TTTT adopted as &lsquo;&lsquo;Secondary BACT&lsquo;&lsquo; during SSM periods.
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas without Duct Burner | 15.21 | Natural Gas | 8040 | H/YR |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 888 | LB/MW-H | BASED ON CONSECUTIVE 12 MONTH ROLLING | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE: MONITORED BY CALCULATIONS. GHG as CO2e<= 888 LB/MW-H (GROSS OUTPUT) FOR TURBINE AND ITS ASSICIATED DUCT BURNER INCLUDING MWHs FROM ULSD FIRING AND STEAM TURBINE
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas with Duct Burner | 15.21 | natural gas | 4000 | h/yr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | USE OS NATURAL GAS A CLEAN BURNING FUEL | 888 | LB/MW-H | BASED ON CONSECUTIVE 12 MONTH ROLLING | BACT-PSD | NSPS , OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE: MONITORED BY CALCULATIONS. GHG as CO2e<= 888 LB/MW-H (GROSS OUTPUT) FOR TURBINE AND ITS ASSICIATED DUCT BURNER INCLUDING MWHs FROM ULSD FIRING AND STEAM TURBINE
TX-0817 | CHOCOLATE BAYOU STEAM GENERATING (CBSG) STATION | INEOS USALLC | BRAZORIA | TX |  | USA | THERESA VITEK | 281-581-3498 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | 123117, PSDTX1460, GHGPSDTX135 | 4911 | 221112 | Not Found | 12/22/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-28 | 2017-11-16 | A |  | support facility providing steam and electricity |  | Combined Cycle Cogeneration | 15.21 | NATURAL GAS | 50 | MW | 2 UNITS EACH 50 MW GE LM6000 | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1000 | LB/MW H |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | MACT TTTT
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Carbon Dioxide Equivalent (CO2e) | Other - EPA METHOD 3B | (Greenhouse Gasses (GHG)) | CO2e | N |  | 774 | LB/MW-H | 365-DAY ROLLING AVG (FACILITYWIDE) | BACT-PSD |  | U | 0 | U | 7319 | BTU/KW-H | 365-DAY ROLLING AVG (FACILITYWIDE) | 0 |  |  | 0 | 0 | N |  | USE EPA METHOD 3B FOR CO2 EMISSIONS.
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000310459 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 2449 | MMBTU/H | two 315 MW (nominal) GE Energy 7F Series 5 Rapid Response Combined Cycle Combustion Turbines with Duct Burners and 31 MW (estimated) steam turbine generators | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 825 | LB/MW-H | FULL LOAD WITHOUT DUCT FIRING | BACT-PSD | OPERATING PERMIT , SIP | U | 0 | U | 895 | LB/MW-H | 365 DAY ROLLING AVERAGE | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST. HEAT RATE LIMITED TO 6,793 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR MATTAWOMAN TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS MATTAWOMAN PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Carbon Dioxide Equivalent (CO2e) | Other - | (Greenhouse Gasses (GHG)) | CO2e | N |  | 865 | LB/MW-H | 12-MONTH ROLLING AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHOD: IF NO CEMS INSTALLED, EPA METHOD 3A . WITH AND WITHOUT DUCT FIRING AT ALL TIMES
MI-0402 | SUMPTER POWER PLANT | WOLVERINE POWER SUPPLY COOPERATIVE INC. | WAYNE | MI | 48111 | USA | BRIAN WARNER | 231-775-5700 | BWARNER@WPSCI.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Julie Brunner at 517-373-7088 or brunnerj1@michigan.gov for questions related to this permit. Thank you. | 81-11 | 4911 | 221112 | 2616305315 | 05/27/2011 &nbsp;ACT | 11/17/2011 &nbsp;ACT | 2012-11-30 | 2016-05-04 | D |  | Utility--Natural gas fired combustion turbine | Other Facility Wide Pollutants not listed below: PM10 = 14.8 tpy PM2.5 = 14.8 tpy CO2e = 232,639 tpy | Combined cycle combustion turbine w/ HRSG | 15.21 | Natural gas | 130 | MW electrical output | This is a combined-cycle combustion turbine with a non-fired heat recovery steam generator (HRSG). Natural gas-fired combustion turbine conversion to combined-cycle. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 954 | LB/MW-H | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | N | 49.6 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Estimated efficiency (above) is 49.6% thermal efficiency (design) Top ranking option--thermal efficiency (design is gross summer 87 F degrees ambient and includes 6% factor for performance degradation).
[40 empty] | Range Low | 774 | LB/MW-H
[40 empty] | Range High | 1000 | LB/MW-H
[40 empty] | Mean | 956.1875 | LB/MW-H
[40 empty] | Median | 929 | LB/MW-H
[40 empty] | Mode | 1000 | LB/MW-H

## Clean Fuels and Good Combustion
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | Combustion Turbine | 15.21 | Natural Gas | 360 | MW | This process represents the GE option for the project - One GE 7FA.05 natural gas-fired combustion turbine generator with an 820.5 MMBTUH duct burner. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | EFFICIENT DESIGN AND COMBUSTION. | 1000 | LB/MW-HR | ANNUAL | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | COMBUSTION TURBINE | 15.21 | NATURAL GAS | 360 | MW | This process represents the Siemens option for the project - One Siemens SGT6-5000F5 natural gas-fired combustion turbine generator with an 820.3 MMBTUH duct burner. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | EFFICIENT DESIGN AND COMBUSTION. | 1000 | LB/MW-HR | ANNUAL | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITH DUCT FIRING | 15.21 | NATURAL GAS | 1000 | MW | TWO MITSUBISHI &lsquo;&lsquo;G&lsquo;&lsquo; MODEL COMBUSTION TURBINE GENERATORS (CTS) WITH A NOMINAL GENERATING CAPACITY OF 270 MW CAPACITY EACH, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR), OXIDATION CATALYST | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | EXCLUSIVE USE OF PIPELINE-QUALITY NATURAL GAS, AND INSTALLATION OF HIGH-EFFICIENCY CT MODEL (MITSUBISHI &lsquo;&lsquo;G&lsquo;&lsquo; MODEL) | 946 | LB/MW-H (AS CO2) | 12-MONTH ROLLING | BACT-PSD |  |  | 0 |  | 7500 | BTU/KWH (HEAT RATE) | AT ALL TIMES, EXCLUDING SU/SD | 0 |  |  | 0 | 0 | N |  | WITH AND WITHOUT DUCT FIRING
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | MR. RANDY THOMPSON | (615) 532-6825 | randall.thompson@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Natural Gas-Fired Combustion Turbine with HRSG | 15.21 | Natural Gas | 1339 | MMBtu/hr | Turbine throughput is 1019.7 MMBtu/hr when burning natural gas and 1083.7 MMBtu/hr when burning No. 2 oil. Duct burner throughput is 319.3 MMBtu/hr. Duct burner firing will occur during natural gas combustion only. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion design and practices | 1800 | LB/MWH | 12-MONTH MOVING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0805 | EAGLE MOUNTAIN STEAM ELECTRIC STATION | EAGLE MOUNTAIN POWER COMPANY | TARRANT | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joel Lunsford, x-1513, joel.lunsford@tceq.texas.gov | GHGPSDTX115, 107569, PSDTX1432 | 4911 | 221112 | 110005028638 | 11/04/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-14 | 2017-11-17 | B |  | Electric Generation |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 462 | MW |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 917 | LB/MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
TX-0787 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joel Lunsford, 512-239-1513, joel.lunsford@tceq.texas.gov | GHGPSDTX125, 111393, PSDTX1368 | 4911 | 221112 | unknown | 12/10/2015 &nbsp;ACT | 03/01/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | Electric Generation |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 497 | MW |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 937 | LB/MW HR |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD COMBUSTION PRACTICES | 924 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 megawatts (MW)) | 15.21 | natural gas | 889 | MW | (2) GE 7HA.01 in a 2x1 configuration and a 872 million British thermal units per hour (MMBtu/hr) duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 901 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Subparts KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 1127 | MW | (2) GE 7HA.02 in a 2x1 configuration and a 985 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 865 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Subparts KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 748 | MW | (2) GE 7FA.05 in a 2x1 configuration and a 826 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 944 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 889 | MW | (2) MHI 501GAC in a 2x1 configuration and a 221 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 929 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 889 | MW | (2) MHI 501GAC in (2) 1x1 configurations and a 221 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 929 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 915 | MW | (2) Siemens SCC6-8000H(1.4) in a 2x1 configuration and a 326 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 965 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and TTTT
NJ-0079 | WOODBRIDGE ENERGY CENTER | CPV SHORE, LLC | MIDDLESEX | NJ | 7095 | USA | MARK TURNER | (415)293-1463 | MTURNER@CPV.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Mr. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS, yogesh.doshi@dep.state.nj.us; phone 609-633-7249 | 18940 - BOP110003 | 4911 | 221112 | 110055590953 | 10/12/2011 &nbsp;ACT | 07/25/2012 &nbsp;ACT | 2012-11-27 | 2018-04-17 | A |  | Woodbridge Energy Center (WEC), proposed at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, would be a new, highly efficient, 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,307 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, one small dew point fuel gas heater (fuel gas heater), a mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Other Permitting Information: Facility-Wide Greenhouse Gas (GHG) emissions as CO2e emissions= 2,073,645 tons per year | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural gas | 40297.6 | mmcubic ft/year | Woodbridge Energy Center (WEC), located at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, will be a new 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) each with a maximum rated heat input of 2,307 million British thermal units per hour (MMBtu/hr), that will utilize pipeline natural gas only, with 2 HRSGs, 2 Duct Burners (each 500 MMbtu/hr). | Carbon Dioxide Equivalent (CO2e) | Other - CO2 Monitored by CO2 CEMs | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 925 | LB/MW-H | BASED ON 12 MONTH PERIOD, ROLLING 1 MNTH | BACT-PSD |  | U | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0080 | HESS NEWARK ENERGY CENTER | HESS NEWARK ENERGY CENTER, LLC | ESSEX | NJ | 7105 | USA | PETER HAID | (774) 750-7088 | PHAID@HESS.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Supervisor: Yogesh Doshi - yogesh.doshi@dep.state.nj.us Phone: 609-633-7249 Permit Evaluator: Michael Hogan - michael.hogan@dep.state.nj.us. Phone: (609)-633-1124 | 08857/BOP110001 | 4911 | 221112 | 110044839903 | 12/10/2011 &nbsp;ACT | 11/01/2012 &nbsp;ACT | 2013-04-04 | 2018-04-17 | A |  | Combined Cycle Electric Generating Facility HESS Newark Energy Center (Hess-NEC), proposed at City of Newark (Essex County), New Jersey, would be a new, highly efficient, 655 MW combined-cycle power generating facility. Hess-NEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,320 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, a 12-cell mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Facility-wide Greenhouse Gas (GHG) emissions as CO2e emissions = 2,003,654 tpy | Combined cylce turbine with duct burner | 15.21 | natural gas | 39463 | mmcubic ft/year* | * Annual throughput is for 2 turbines, 2 duct burners and 1 auxiliary boiler | Carbon Dioxide Equivalent (CO2e) | Other - CO2 Monitored by CO2 CEMs | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 887 | LB/MW-H | CONSCUTV 12 MONTH PERIOD ROLLING 1 MONTH | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO2 Monitored by CO2 CEMs, CH4 and Nitrous oxide monitored by calculations
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices and energy efficiency | 1071 | LB/MW-H | 12-MONTH ROLLING AVG. | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 is 1,071.0 LB/MW-H gross energy output based on a 12-month rolling average. Cost effectiveness information: The CO2e limit is based on 6% performance degradation for GE turbines. CCS is assumed to be about 90% effective, resulting in a reduction of approximately 2.3 million tons of CO2 emissions per year from the proposed CTGs at MCV. However, the use of CCS as a control method would also result in significant energy and environmental impacts due to the increased fuel usage required to operate the CCS systems. MCV estimated that to reduce the 2.3 million tons of CO2 per year from the proposed CTGs, an additional 181 MW of electric power and steam generation would be needed for capture, compression, and transport to an Enhanced Oil Recovery (EOR) for storage. That would result in air emission increases for an annualized cost of approximately $155 million per year, which is approximately $67 per ton to capture and store CO2. Therefore, MCV determined that CCS for emission reduction, as well as the environmental degradation due to increases in pollutants is not reasonable.
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices and energy efficiency. | 995 | LB/MW-H | 12-MO. ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is based on 6% performance degradation for GE turbines. CCS is assumed to be about 90% effective, resulting in a reduction of approximately 2.3 million tons of CO2 emissions per year from the proposed CTGs at MCV. However, the use of CCS as a control method would also result in significant energy and environmental impacts due to the increased fuel usage required to operate the CCS systems. MCV estimated that to reduce the 2.3 million tons of CO2 per year from the proposed CTGs, an additional 181 MW of electric power and steam generation would be needed for capture, compression and transport to an Enhanced Oil Recovery (EOR) for storage. That would result in air emissioin increases for an annualized cost of approximately $155 million per year, which is approximately $67 per ton to capture and store CO2. Therefore, MCV determined that CCS for emission reduction, as well as the environmental degradation due to increases in pollutant is not reasonable.
TX-0810 | DECORDOVA STEAM ELECTRIC STATION (DECORDOVA STATION) | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL BARNES | 214-875-8374 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5221 Ruth.Alvirez@tceq.texas.gov | 107569, PSDTX1432, GHGPSDTX124 | 4911 | 221112 | Not Found | 07/26/2016 &nbsp;ACT | 10/04/2016 &nbsp;ACT | 2016-10-04 | 2017-11-16 | C |  | two combustion turbines (CTGs) authorized to operate in simple cycle or combined cycle. | The simple cycle operations were issued in 2013, but the combined cycle criteria pollutant PSD permit / state amendment was issued on March 8, 2016. This GHG initial review is linked to the 2016 action which added combined cycle capability, it does not apply to the simple cycle operations which were authorized in 2013. | Combined Cycle and Cogeneration (&gt;25 MW) | 15.21 | natural gas | 213 | MW | Two turbine options: GE 7FA [210 megawatts (MW)] or Siemens 5000F (231MW) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices and firing low carbon fuel. | 966 | LB/MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two Combine Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 3001.57 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. . (Operational limits are for each CCCT NG-fired with duct burner) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Good combustion practices and oxidation catalyst | 883 | LB/MW-HR | EXPRESSED AS CO2E (NET) | BACT-PSD |  | U | 0 | U | 2896556 | TONS | YEAR (NET) EXPRESSED AS CO2E | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative emissions from both CCCT in any 12-month period expressed as CO2e
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices/energy efficiency | 1000 | LB/MW-H | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit is for each unit operating with or without DB. CCS technology for natural gas-fired combined cycle units entails significant economic, energy, and environmental impacts as a control method would also result in significant energy and environmental impacts due to the increased fuel usage required to operate the CCS systems. Renaissance referred to a detailed cost analysis conducted by Carnegie Mellon University (*) which specifically analyzed costs for plants using amine-based post-combustion CCS systems with 90% CO2 capture. The analysis found that CCS increases capital costs (in 2007 basis) by approximately $600/kW, which would result in an incremental capital cost of approximately $840 million for this project. The analysis also found the cost (in 2007 basis) of CO2 avoided, ranged from $74-$114 per ton CO2 which equates to annual costs of $400-$600 million. *Reference of analysis. The cost of Carbon Capture and Storage for Natural Gas Combined Cycle Power Plants, Rubin and Zhai, Department of Engineering and Public Policy, Carnegie Mellon University, http://www.wecc.biz/committees/BOD/TEPPC/SPSG/MDTF/120914/Lists/Minutes/1/CCS_Costs_for_Combined_Cycle.pdf
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices/energy efficiency | 1000 | LB/MW-H | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit applies for each unit operating with or without DB. CCS technology for natural gas-fired combined cycle units entails significant economic, energy, and environmental impacts as a control method would also result in significant energy and environmental impacts due to the increased fuel usage required to operate the CCS systems. Renaissance referred to a detailed cost analysis conducted by Carnegie Mellon University (*) which specifically analyzed costs for plants using amine-based post-combustion CCS systems with 90% CO2 capture. The anlaysis found that CCS increases capital costs (in 2007 basis) by approximately $600/kW, which would result in an incremental capital cost of approximately $840 million for this project. The analysis also found the cost (in 2007 basis) of CO2 avoided, ranged from $74 to $114 per ton CO2 which equates to annual costs of $400 to $600 million.
TX-0773 | FGE EAGLE PINES PROJECT | FGE EAGLE PINES, LLC | CHEROKEE | TX |  | USA | EMERSON FARRELL | 281-407-7749 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, 512-239-1095, Erik.Hendrickson@tceq.texas.gov | 131316, PSDTX1454, AND GHGPSDT | 4911 | 221112 | UNKNOWN | 09/10/2015 &nbsp;ACT | 11/04/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | The FGEEP Project will include three natural gas-fired combined cycle (NGCC) power blocks, each block comprised of two gas-fired combustion turbines, two supplemental fired duct burners (DBs) heat recovery steam generators (HRSGs), and one steam turbine. FGEEP selected Alstom GT36 combustion turbines (CTs), each nominally rated at 321 megawatts (MW). Each HRSG is equipped with DBs that will have a maximum design heat input capacity of 799 million British thermal units per hour (MMBtu/hr). The CTs and DBs are fueled with pipeline quality natural gas. Each power block will also have a steam turbine generator designed to produce approximately 502 MW with the additional duct firing. Each of the three blocks will include the following ancillary equipment: one multi-cell condenser/cooling tower, one emergency generator, one firewater pump, two diesel storage tanks, and pressurized aqueous ammonia storage tanks. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 321 | MW | Alstom GT36 combustion turbines (321 MW)+ 799 million British thermal units per hour (MMBtu/hr) duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Low carbon fuel, good combustion, efficient combined cycle design | 886 | LB/MW H | WITHOUT DUCT FIRING | BACT-PSD | NSPS | N | 0 | U | 816 | LB/MW H | WITH DUCT FIRING | 0 |  |  | 0 | 0 | N
*TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2018-05-11 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | PIPELINE QUALITY NATURAL GAS, GOOD COMBUSTION PRACTICES | 884 | LB/MWH |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | Mitsubishi M501-GAC combustion turbine, combined cycle configuration with duct burner. | 15.21 | natural gs | 2988 | MMBTU/H | or ULSD; Duct burner 499 MMBtu/hr, natural gas | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Thermal efficiency Clean fuels | 1000 | LB PER GROSS MWH | 365-DAY ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Carbon Dioxide Equivalent (CO2e) | Other - CO2 CEMS or fuel use monitoring | (Greenhouse Gasses (GHG)) | CO2e | P | Use of low-emitting fuels and technologies | 850 | LB/MWH | FOR GAS OPERATION, 12-MO ROLLING | BACT-PSD | NSPS | U | 0 | U | 1210 | LB/MWH | FOR ULSD OPERATION, 12-MO ROLLING | 0 |  |  | 0 | 0 | N |  | Also, limited to 500 hr/yr per turbine on ULSD. Standard is a weighted average of the gas and ULSD standards, depending on generation on the two fuels during the compliance period. Excludes startup, shutdown, and malfunction. NSPS Subpart TTTT adopted as &lsquo;&lsquo;Secondary BACT&lsquo;&lsquo; during SSM periods.
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas without Duct Burner | 15.21 | Natural Gas | 8040 | H/YR |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 888 | LB/MW-H | BASED ON CONSECUTIVE 12 MONTH ROLLING | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE: MONITORED BY CALCULATIONS. GHG as CO2e<= 888 LB/MW-H (GROSS OUTPUT) FOR TURBINE AND ITS ASSICIATED DUCT BURNER INCLUDING MWHs FROM ULSD FIRING AND STEAM TURBINE
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas with Duct Burner | 15.21 | natural gas | 4000 | h/yr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | USE OS NATURAL GAS A CLEAN BURNING FUEL | 888 | LB/MW-H | BASED ON CONSECUTIVE 12 MONTH ROLLING | BACT-PSD | NSPS , OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE: MONITORED BY CALCULATIONS. GHG as CO2e<= 888 LB/MW-H (GROSS OUTPUT) FOR TURBINE AND ITS ASSICIATED DUCT BURNER INCLUDING MWHs FROM ULSD FIRING AND STEAM TURBINE
[40 empty] | Range Low | 850 | LB/MW-H
[40 empty] | Range High | 1000 | LB/MW-H
[40 empty] | Mean | 969.6296 | LB/MW-H
[40 empty] | Median | 929 | LB/MW-H
[40 empty] | Mode | 1000 | LB/MW-H

## No Controls
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
TX-0817 | CHOCOLATE BAYOU STEAM GENERATING (CBSG) STATION | INEOS USALLC | BRAZORIA | TX |  | USA | THERESA VITEK | 281-581-3498 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | 123117, PSDTX1460, GHGPSDTX135 | 4911 | 221112 | Not Found | 12/22/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-28 | 2017-11-16 | A |  | support facility providing steam and electricity |  | Combined Cycle Cogeneration | 15.21 | NATURAL GAS | 50 | MW | 2 UNITS EACH 50 MW GE LM6000 | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1000 | LB/MW H |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | MACT TTTT
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Carbon Dioxide Equivalent (CO2e) | Other - EPA METHOD 3B | (Greenhouse Gasses (GHG)) | CO2e | N |  | 774 | LB/MW-H | 365-DAY ROLLING AVG (FACILITYWIDE) | BACT-PSD |  | U | 0 | U | 7319 | BTU/KW-H | 365-DAY ROLLING AVG (FACILITYWIDE) | 0 |  |  | 0 | 0 | N |  | USE EPA METHOD 3B FOR CO2 EMISSIONS.
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000310459 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 2449 | MMBTU/H | two 315 MW (nominal) GE Energy 7F Series 5 Rapid Response Combined Cycle Combustion Turbines with Duct Burners and 31 MW (estimated) steam turbine generators | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 825 | LB/MW-H | FULL LOAD WITHOUT DUCT FIRING | BACT-PSD | OPERATING PERMIT , SIP | U | 0 | U | 895 | LB/MW-H | 365 DAY ROLLING AVERAGE | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST. HEAT RATE LIMITED TO 6,793 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR MATTAWOMAN TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS MATTAWOMAN PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Carbon Dioxide Equivalent (CO2e) | Other - | (Greenhouse Gasses (GHG)) | CO2e | N |  | 865 | LB/MW-H | 12-MONTH ROLLING AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHOD: IF NO CEMS INSTALLED, EPA METHOD 3A . WITH AND WITHOUT DUCT FIRING AT ALL TIMES
MI-0402 | SUMPTER POWER PLANT | WOLVERINE POWER SUPPLY COOPERATIVE INC. | WAYNE | MI | 48111 | USA | BRIAN WARNER | 231-775-5700 | BWARNER@WPSCI.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Julie Brunner at 517-373-7088 or brunnerj1@michigan.gov for questions related to this permit. Thank you. | 81-11 | 4911 | 221112 | 2616305315 | 05/27/2011 &nbsp;ACT | 11/17/2011 &nbsp;ACT | 2012-11-30 | 2016-05-04 | D |  | Utility--Natural gas fired combustion turbine | Other Facility Wide Pollutants not listed below: PM10 = 14.8 tpy PM2.5 = 14.8 tpy CO2e = 232,639 tpy | Combined cycle combustion turbine w/ HRSG | 15.21 | Natural gas | 130 | MW electrical output | This is a combined-cycle combustion turbine with a non-fired heat recovery steam generator (HRSG). Natural gas-fired combustion turbine conversion to combined-cycle. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 954 | LB/MW-H | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | N | 49.6 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Estimated efficiency (above) is 49.6% thermal efficiency (design) Top ranking option--thermal efficiency (design is gross summer 87 F degrees ambient and includes 6% factor for performance degradation).
[40 empty] | Range Low | 774 | LB/MW-H
[40 empty] | Range High | 1000 | LB/MW-H
[40 empty] | Mean | 883.6 | LB/MW-H
[40 empty] | Median | 865 | LB/MW-H
[40 empty] | Mode | #N/A | LB/MW-H