## PermitSearchResults (8)
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
TX-0618 | CHANNEL ENERGY CENTER LLC | CHANNEL ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX955M1 | 4911 | 221112 | 110034690564 | 11/03/2011 &nbsp;ACT | 10/15/2012 &nbsp;ACT | 2012-10-24 | 2014-01-06 | B |  | Combustion turbine (Siemens 501F)/duct burners (475 MMBtu/hr) with heat recovery steam generator | 42179 and N021M1 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | The turbine is a Siemens 501F rated at a nominal 180 MW and the duct burner will have a maximum design heat input of 475 MMBtu/hr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion | 4 | PPMVD | @ 15% O2 ON A 24-HR ROLLING AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0619 | DEER PARK ENERGY CENTER | DEER PARK ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX979M2 | 4911 | 221112 | 110017743254 | 09/01/2011 &nbsp;ACT | 09/26/2012 &nbsp;ACT | 2012-10-25 | 2013-09-25 | B |  | The Deer Park Energy Center is a combined cycle cogeneration facility consisting of five Siemens/Westinghouse 501F combustion turbine generators, each with a 725 MMBtu/hr duct burner and heat recovery steam generator. | 45642 and N036M2 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | natural gas-fired combined cycle turbine generator with a heat recovery steam generator equipped with a duct burner. The turbine is a Siemens 501F rated at a nominal 180 megawatts and the DB will have a maximum design rate capability of 725 million British thermal units per hour | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion | 4 | PPMVD | @15% O2, 24-HR ROLLING AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0620 | ES JOSLIN POWER PLANT | CALHOUN PORT AUTHORITY | CALHOUN | TX |  | USA | CHARLES HAUSMANN | 361-987-2813 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1256 | 4911 | 221112 | 110001866641 | 05/27/2011 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2012-11-14 | 2013-09-25 | B |  | Three gas-fired combined cycle turbine generators, including a steam turbine generator, to replace the existing steam boiler/turbine generator. | 96336 | Combined cycle gas turbine | 15.21 | natural gas | 195 | MW | The three combustion turbine generators (CTG) will be the General Electric 7FA, each with a maximum base-load electric power output of approximately 195 megawatts (MW). The steam turbine is rated at approximately 235 MW. This project also includes the installation of two emergency generators, one fire water pump, and auxiliary equipment. No duct burners. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion | 4 | PPMVD | @15% O2, 24-HR ROLLING AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0303 | FPL WEST COUNTY ENERGY CENTER UNIT 3 | FLORIDA POWER AND LIGHT COMPANY (FP&L) | PALM BEACH COUNTY | FL | 33470 | USA | RANDALL R. LABAUVE |  |  | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | AL LINERO, P.E. ADMINISTRATOR SPECIAL PROJECT SECTION BUREAU OF AIR REGULATION | 0990646-002-AC (PSD-FL-396) | 4911 | 221112 | 110028293674 | 12/06/2007 &nbsp;ACT | 07/30/2008 &nbsp;ACT | 2008-12-15 | 2011-01-05 | B |  | THE FP&amp;L WEST COUNTY ENERGY CENTER (WCEC) WAS PREVIOUSLY APPROVED FOR CONSTRUCTION AS A NOMINAL 2,500 MEGAWATT (MW) GREENFIELD POWER PLANT. THE PREVIOUSLY APPROVED CONSTRUCTION UNDERWAY (PHASE I) IS FOR TWO NOMINAL 1,250 MW GAS-FIRED COMBINED CYCLE UNITS (UNITS 1 AND 2) THAT WILL USE ULTRALOW SULFUR DIESEL (ULSD) FUEL OIL (FO) AS BACKUP FUEL. PHASE 2: UNITS 1 AND 2 WILL EACH CONSIST OF: THREE NOMINAL 250 MEGAWATT (MW) MODEL 501G COMBUSTION TURBINE-ELECTRICAL GENERATORS (CTG) WITH EVAPORATIVE INLET COOLING SYSTEMS; THREE SUPPLEMENTARY-FIRED HEAT RECOVERY STEAM GENERATORS (HRSG) WITH SELECTIVE CATALYTIC REDUCTION (SCR) REACTORS; ONE NOMINAL 428 MMBTU/HOUR (LOWER HEATING VALUE - LHV) GAS-FIRED DUCT BURNER (DB) LOCATED WITHIN EACH OF THE THREE HRSG; THREE 149 FEET EXHAUST STACKS; ONE 26 CELL MECHANICAL DRAFT COOLING TOWER; AND A COMMON NOMINAL 500 MW STEAM-ELECTRICAL GENERATOR (STG). PREVIOUSLY APPROVED ANCILLARY EQUIPMENT INCLUDES: FOUR EMERGENCY GENERATORS; TWO NATURAL GAS FIRED FUEL HEATERS; ONE EMERGENCY DIESEL FIRED PUMP; TWO DIESEL FUEL STORAGE TANKS; TWO AUXILIARY STEAM BOILERS; AND OTHER ASSOCIATED SUPPORT EQUIPMENT. THIS PERMIT AUTHORIZES CONSTRUCTION OF ANOTHER 1,250 MW GAS-FIRED COMBINED CYCLE UNIT (UNIT 3) IDENTICAL TO THE DESCRIPTION GIVEN ABOVE FOR UNITS 1 AND 2. ADDITIONAL ANCILLARY EQUIPMENT FOR UNIT 3 WILL INCLUDE TWO EMERGENCY GENERATORS, TWO NATURAL GAS FIRED FUEL HEATERS AND ASSOCIATED EQUIPMENT. UNIT 3 WILL USE SOME OF THE INFRASTRUCTURE AND ANCILLARY EQUIPMENT ALREADY UNDER CONSTRUCTION INCLUDING THE DIESEL STORAGE TANKS AND AUXILIARY BOILERS. | COMBINED CYCLE UNIT 3 WILL CONSIST OF: THREE NOMINAL 250 MEGAWATT (MW) Â¿GÂ¿ CLASS COMBUSTION TURBINE-ELECTRICAL GENERATORS (CTG) EVAPORATIVE INLET COOLING SYSTEMS; THREE SUPPLEMENTARY-FIRED HEAT RECOVERY STEAM GENERATORS (HRSG) WITH SELECTIVE CATALYTIC REDUCTION (SCR) REACTORS AND A NOMINAL 428 MMBTU/HOUR (LOWER HEATING VALUE Â¿ LHV) GAS-FIRED DB; THREE 149 FOOT EXHAUST STACKS; ONE 26-CELL MECHANICAL DRAFT COOLING TOWER; AND A COMMON NOMINAL 500 MW STEAM-ELECTRICAL GENERATOR. | THREE NOMINAL 250 MW CTG (EACH) WITH SUPPLEMENTARY-FIRED HRSG | 15.21 | NATURAL GAS | 2333 | MMBTU/H | FUEL HEAT INPUT RATE (LHV): OIL 2,117 MMBTU/H COMBINED CYCLE UNIT 3 WILL CONSIST OF: THREE NOMINAL 250 MW COMBUSTION TURBINE-ELECTRICAL GENERATORS (CTG) WITH EVAPORATIVE INLET COOLING SYSTEMS; THREE SUPPLEMENTARY-FIRED HEAT RECOVERY STEAM GENERATORS (HRSG) WITH SELECTIVE CATALYTIC REDUCTION (SCR) REACTORS AND A COMMON NOMINAL 500 MW STEAM-ELECTRICAL GENERATOR. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION | 6 | PPMVD (GAS) | 12-MONTH | BACT-PSD |  | U | 0 | U | 8 | PPMVD (OIL) | 24-HOUR | 0 |  |  | 0 | 0 | N |  | COMPLIANCE WITH THE CONTINUOUS 24-HOUR CO STANDARDS SHALL BE DEMONSTRATED BASED ON DATA COLLECTED BY THE REQUIRED CEMS. THE INITIAL AND ANNUAL EPA METHOD 10 TESTS ASSOCIATED WITH THE CERTIFICATION OF THE CEMS INSTRUMENTS SHALL ALSO BE USED TO DEMONSTRATE COMPLIANCE WITH THE INDIVIDUAL STANDARDS FOR NATURAL GAS, FO, AND BASIC DB MODE. THE STACKS TEST LIMITS APPLY ONLY AT HIGH LOAD (90-100% OF THE CTG CAPACITY).
OK-0129 | CHOUTEAU POWER PLANT | ASSOCIATED ELECTRIC COOPERATIVE INC | MAYES | OK | 74362 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2007-115-C(M-1)PSD | 4911 | 221112 | 4009700017 | 06/19/2008 &nbsp;ACT | 01/23/2009 &nbsp;ACT | 2009-11-20 | 2010-02-18 | B |  |  |  | COMBINED CYCLE COGENERATION &gt;25MW | 15.21 | NATURAL GAS | 1882 | MMBTU/H | SIEMENS V84.3A | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION | 8 | PPMV | 1-HR AVG | BACT-PSD | N/A | U | 0 | U | 51.32 | PPMV | 3-HR AVG | 0 |  |  | 0 | 0 | N
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Good Combustion & Clean Fuel | 4.3 | PPMVD@15% O2 | 3-HR AVERAGE, NATURAL GAS OPERATION | BACT-PSD |  | U | 0 | U | 10 | PPMVD@15% O2 | 3-HR AVERAGE, ULSD OPERATION | 0 |  |  | 0 | 0 | N |  | No CEMS required. Also subject to limits of 7.1 ppmvd @15% O2 for gas and 13.6 ppmvd@15%O2 for ULSD, at low loads. The lowest loads at which the facility can demonstrate compliance with these low-load limits determines the minimum permitted operating load for the CT. Compliance by stack test.
*FL-0363 | DANIA BEACH ENERGY CENTER | FLORIDA POWER AND LIGHT COMPANY | BROWARD | FL | 33314 | USA | JOHN HAMPP | 561-691-2894 | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-017-AC | 4911 | 221112 | 110002044065 | 07/27/2017 &nbsp;ACT | 12/04/2017 &nbsp;ACT | 2018-04-03 | 2018-04-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.F.ZIP | 1200 megawatt 2-on-1 combined cycle facility, natural gas-fired, with limited ULSD use. GE 7HA turbines | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.D.ZIP | 2-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural gas | 4000 | MMBtu/hr | Two nominal 430 MW combustion turbines, coupled to a steam turbine generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Good Combustion & Clean Fuel | 4.3 | PPMVD@15% O2 | AT LOADS > 90% | BACT-PSD |  | U | 0 | U | 7.2 | PPMVD@15% O2 | FOR LOADS < 90% | 0 |  |  | 0 | 0 | N |  | For oil, limit is 10.0 ppmvd @ 15% O2 for loads > 90%, and 14.6 ppmvd@15% O2 for loads < 90%. Compliance by annual stack test.
TX-0698 | BAYPORT COMPLEX | AIR LIQUIDE LARGE INDUSTRIES U.S., L.P. | HARRIS | TX |  | USA | JASON MILLER | (281) 474-8243 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 | 9346 PSDTX612M2 | 4931 | 325120 | 110000462758 | 07/27/2012 &nbsp;ACT | 09/05/2013 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | Air Liquid currently operates a cogeneration facility in Pasadena, Texas (Bayou Cogeneration Plant). The permit amendment submitted by Air Liquide will authorize a redevelopment project of its cogeneration plant. The proposed project will involve the replacement of four existing gas-fired turbines (GE 7EA) with similar gas-fired turbines (GE 7EA), the addition of three new gas-fired boilers rated at 550 MMBtu/hr and the removal of three existing gas-fired boilers rated at 443 MMBtu/hr. |  | (4) cogeneration turbines | 15.21 | natural gas | 90 | MW | (4) GE 7EA turbines providing power and process steam | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good Combustion & Clean Fuel | 15 | PPMVD | @15% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057188626 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.21 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (6) GE LM2500+ DLE turbines that drive the ethylene section compressors with waste heat recovery for amine solution regeneration. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good Combustion & Clean Fuel | 29 | PPMVD | @15% O2, 4 HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.21 | natural gas | 10 | M TONNES/YR | Four GE Frame 7E gas turbines for refrigeration and compression at the site | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good Combustion & Clean Fuel | 25 | PPM | ROLLING 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0104 | CPV VALLEY ENERGY CENTER | CPV VALLEY LLC | ORANGE | NY | 10940 | USA |  |  |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-335600136/00001 | 4911 | 221112 | 110043332471 | 08/01/2013 &nbsp;ACT | 08/01/2013 &nbsp;ACT | 2017-08-25 | 2017-09-28 | A |  | CPV Valley Energy Center is a 680 MW combined cycle electric generating facility located in Middletown, NY. The combustion turbines are rated at 2,234 MMBTU/H firing natural gas and 2,145 MMBTU/H firing diesel fuel. The duct burners are rated for 500 MMBTU/H firing natural gas. In addition to the turbines their emission limits for the auxiliary boiler (73.5 MMBTU/H), emergency generator, fire pump, and gas heater. | State Facility Permit | Turbines and duct burners - NG | 15.21 | natural gas | 0 |  | Combined cycle units heat rate 7,605 BTU/KW-H (HHV) or less without duct burner firing to achieve design thermal efficiency of 57.4% (LHV). | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Good combustion practice and oxidation catalyst. | 2 | PPMVD @ 15% O2 | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 2.0 PPVD @15% O2 without duct burners 3.4 PPVD @15% O2 with duct burners Applies to all operating loads, except during startup and shutdown.
FL-0304 | CANE ISLAND POWER PARK | FLORIDA MUNICIPAL POWER AGENCY (FMPA | OSCEOLA | FL | 33848 | USA | ROGER FONTES | 4073557767 | ROGER.FONTES@FMPA.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | ALVARO LINERO, PE. SPECIAL PROJECT SECTION ADMINISTRATOR BUREAU OF AIR REGULATION | PSD-FL-400 (0970043-014-AC) | 4911 | 221112 | 110013931308 | 04/01/2008 &nbsp;ACT | 09/08/2008 &nbsp;ACT | 2009-02-16 | 2009-04-20 | B |  | FMPA AND THE KISSIMMEE UTILITIES AUTHORITY (KUA) JOINTLY OWN THE CIPP, WHICH IS LOCATED IN OSCEOLA COUNTY AT 6075 OLD TAMPA HIGHWAY, INTERCESSION CITY, FLORIDA. THE CIPP PRESENTLY CONSISTS OF ONE 40 MEGAWATT (MW) SIMPLE CYCLE COMBUSTION TURBINE (UNIT 1), A 120 MW COMBINED CYCLE UNIT INCLUDING A HEAT RECOVERY STEAM GENERATOR (HRSG) (UNIT 2) AND A 250 MW COMBINED CYCLE UNIT (UNIT 3). THE THREE EXISTING UNITS FIRE NATURAL GAS AS THE PRIMARY FUEL, WITH DISTILLATE FUEL AS BACKUP. THE NEW UNIT WILL BE A NATURAL GAS 300 MW COMBINED CYCLE UNIT AND ASSOCIATED EQUIPMENT. | THE PROJECT WILL BE A Â¿ONE-ON-ONEÂ¿ 300 MW NATURAL GAS-FUELED COMBINED CYCLE UNIT (CIPP UNIT 4) AND ASSOCIATED AUXILIARY EQUIPMENT. UNIT 4 AND ASSOCIATED AUXILIARY EQUIPMENT WILL CONSIST OF: Â¿ A NOMINAL 150 MW GAS-FUELED GENERAL ELECTRIC 7241 FA CTG; Â¿ A SUPPLEMENTARY-FIRED HRSG WITH NATURAL GAS FUELED DUCT BURNERS (DB); Â¿ A NOMINAL 150 MW STG; Â¿ A NOMINAL 160-FOOT STACK; Â¿ AN EMERGENCY DIESEL ENGINE FIRE PUMP AND SMALL ULTRALOW SULFUR DIESEL (ULSD) FUEL OIL (FO)STORAGE TANK; Â¿ A NOMINAL 750 KILOWATTS (KW) SAFE SHUTDOWN DIESEL GENERATOR WITH A ULSD FO STORAGE TANK; AND Â¿ A MECHANICAL DRAFT COOLING TOWER WITH DRIFT ELIMINATORS. | 300 MW COMBINED CYCLE COMBUSTION TURBINE | 15.21 | NATURAL GAS | 1860 | MMBTU/H |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 6 | PPMVD | 12-MONTH | BACT-PSD | NSPS , NESHAP | U | 0 | U | 8 | PPMVD | 24-HR | 0 |  |  | 0 | 0 | N |  | CONTINOUS EMISSION MONITOR TO DETERMINE CONTINUOUS COMPLIANCE.
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 9 | PPM | EACH CTG; 24-H ROLLING AVG. | BACT-PSD | SIP | N | 0 | N | 43.9 | LB/H | EACH CTG; 24-H ROLLING AVG. | 0 |  |  | 10600 | 0 | N | 2012 | Emission limit 1 is 9.0 ppmv dry at 15% oxygen on a 24-hour rolling average as determined each hour the turbine operates; except during startup/shutdown. The limit applies to each unit. Emission limit 2 is 43.9 LB/H based on a 24-hour rolling average as determined each hour the turbine operates; except during startup/shutdown. The limit is for each unit. The cost information was estimated for a catalytic oxidation system (COS) CO = $10,600/ton CO+VOC = $8,948/ton
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 10.5 | PPM | EACH CTG/DB; 24-H ROLLING AVG. | BACT-PSD | SIP | N | 0 | N | 57.6 | LB/H | EACH CTG/DB; 24-H ROLLING AVG. | 0 |  |  | 10600 | 0 | N | 2012 | Emission limit 1 is 10.5 ppmv dry at 15% oxygen, for each CTG/DB, based on a 24-hour rolling average as determined each hour the turbine operates. Emission limit 2 is 57.6 LB/HR for each CTG/DB, based on a 24-hour rolling average as determined each hour the turbine operates. The cost effectiveness was estimated for a catalytic oxidation system (COS); CO = $10,600/ton CO + VOC = $8,948/ton
TX-0548 | MADISON BELL ENERGY CENTER | MADISON BELL PARTNERS LP | MADISON | TX | 77354 | USA |  |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | RANDY HAMILTON RHAMILTO@TCEQ.STATE.TX.US | 83378 | 4911 | 221122 | UNKNOWN | 10/31/2007 &nbsp;ACT | 08/18/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | THE PROJECT WOULD INCLUDE FOUR NATURAL GAS-FIRED COMBUSTION TURBINES (GE F7EA) AND FOUR HEAT RECOVERY STEAM GENERATORS (HRSGS) WITH PROVISIONS FOR DUCT FIRING. THE PROPOSED PROJECT WILL OPERATE THE COMBUSTION TURBINES IN COMBINED CYCLE MODE. THE COMBINED NOMINAL GENERATING CAPACITY OF THE PLANT IS APPROXIMATELY 550 MW IN COMBINED CYCLE MODE. | PSDTX1105 | ELECTRICITY GENERATION | 15.21 | NATURAL GAS | 275 | MW | FOUR GE PG7121(EA) COMBINE CYCLE TURBINES FIRING NATURAL GAS WILL DIRECTLY GENERATE 75 MW; EACH HAS A 165 MMBTU/HR DUCT BURNER AND A HEAT RECOVERY STEAM GENERATOR. TWO HRSGÂ¿S WILL TURN ONE 125 MW STEAM TURBINE AND THE OTHER TWO WILL TURN ANOTHER 125 MW STEAM TURBINE. THE TURBINE MAY OPERATE WITHOUT THE DUCT BURNER. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 17.5 | PPMVD | @ 15% O2, 1-HR ROLLING AVG | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0687 | WEST PLANT AND EAST PLANT CENTRAL HEAT AND POWER | UNIVERSITY OF TEXAS MEDICAL BRANCH AT GALVESTON | GALVESTON | TX |  | USA | JACK TARPLEY | 409-747-0515 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, 512-239-2175, laura.gibson@tceq.texas.gov | 56653, PSDTX1376 | 8221 | 611310 | 110017309615 | 08/23/2013 &nbsp;ACT | 10/13/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | UTMB Galveston has applied for an amendment to authorize two combined cycle natural gas fired Solar Taurus 60 combustion turbines. Each CTG will produce 13MW. |  | Two Combustion Turbine-Generators | 15.21 | Natural Gas | 13 | MW | Combined Cycle | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 50 | PPM | 15% O2, 24HR ROLLING AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0547 | NATURAL GAS-FIRED POWER GENERATION FACILITY | LAMAR POWER PARTNERS II LLC | LAMAR | TX | 75126 | USA |  |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | RANDY HAMILTON RHAMILTO@TCEQ.STATE.TX.US | 83207 | 4911 | 221122 | UNKNOWN | 10/25/2007 &nbsp;ACT | 06/22/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | THE NEW POWER BLOCK WILL BE CAPABLE OF PRODUCING EITHER 620 OR 910 MEGAWATTS OF ELECTRICITY, DEPENDING UPON WHICH COMBUSTION TURBINE MODEL OPTION IS CHOSEN. | PSDTX1106 | ELECTRICITY GENERATION | 15.21 | NATURAL GAS | 250 | MW | LAMAR POWER PARTNERS PROPOSES TO CONSTRUCT A NATURAL GAS-FIRED COMBINED-CYCLE POWER BLOCK TO BE BUILT AT THE EXISTING SITE IN LAMAR COUNTY, TEXAS. THE NEW POWER BLOCK WILL BE CAPABLE OF PRODUCING EITHER 620 OR 910 MEGAWATTS OF ELECTRICITY, DEPENDING UPON WHICH COMBUSTION TURBINE MODEL OPTION IS CHOSEN. THE PROPOSED PROJECT WOULD INCLUDE TWO COMBUSTION TURBINES (EITHER 170 MW GENERAL ELECTRIC 7FAS OR 250 MW MITSUBISHI 501GS), TWO HEAT RECOVERY STEAM GENERATORS WITH DUCT BURNERS AND ONE STEAM TURBINE. THE GE7FAS WOULD BE CAPABLE OF PRODUCING 620 MW OF ELECTRICITY IN COMBINED CYCLE MODE, WHILE THE M501GS WOULD PRODUCE 910 MW IN COMBINED CYCLE MODE. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRATICES | 15 | PPMVD | @ 15% O2, 24-HR ROLLING AVG | BACT-PSD |  |  | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055426409 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Four combined cycle combution turbines | 15.21 | natural gas | 373 | MMBTU/H | Three GE, LMS6000 PF, natural gas-fired, combined cycle CTG, rated at 373 MMBtu per hour each, based on HHV and one (1) HRSG each with no Duct Burners | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation Catalyst | 4 | PPMVD AT 15% O2 | 1-HR AVE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 3.3 | LB/H | 30-DAY ROLLING AVE | 0 |  |  | 0 | 0 | N |  | startup limit: 140.0 lb per event shutdown limit: 15.0 lb per event compliance is monitored with continuous emissions monitors
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | MR. RANDY THOMPSON | (615) 532-6825 | randall.thompson@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Natural Gas-Fired Combustion Turbine with HRSG | 15.21 | Natural Gas | 1339 | MMBtu/hr | Turbine throughput is 1019.7 MMBtu/hr when burning natural gas and 1083.7 MMBtu/hr when burning No. 2 oil. Duct burner throughput is 319.3 MMBtu/hr. Duct burner firing will occur during natural gas combustion only. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | oxidation catalyst | 2 | PPMVD @ 15% O2 | 30 UNIT-OPERATING-DAY MOVING AVERAGE | BACT-PSD |  | N | 90 | U | 10 | PPMVD @ 15% O2 | 15 UNIT-OPERATING-DAY MOVING AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission limit #1 is for natural gas combustion, emission limit #2 is for No. 2 oil combustion.
GA-0138 | LIVE OAKS POWER PLANT | LIVE OAKS COMPANY, LLC | GLYNN | GA | 31525 | USA | BURT WALLACE | 478 943-2331 | BURT_1@BELLSOUTH.NET | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-127-0075-P-02-0 | 4911 | 221122 | UNKNOWN | 11/19/2008 &nbsp;ACT | 04/08/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | A |  | LIVE OAKS POWER PLANT PROPOSED FACILITY WILL OPERATE AS A FULLY DISPATCHABLE ELECTRIC GENERATING FACILITY. THE COMBINED CYCLE SYSTEM WILL UTILIZE TWO COMBUSTION TURBINES AND ONE STEAM TURBINE, CONFIGURED IN A TWO-ON-ONE ARRANGEMENT. THE HEAT CONTENT OF THE EXHAUST GASSES WIL BE RECOVERED BY A HEAT RECOVERY STEAM GENERATOR (HRSG), AND USED TO DRIVE A STEAM TURBINE. DURING PEAK LOADS A DUCT BURNER IN THE HRSG CAN BE FIRED TO AD ADDITIONAL HEAT ENERGY TO THE GAS TURBINE EXHAUST, INCREASING THE PRODUCTION OF STEAM SENT TO THE STEAM TURBINE. THE COMBUSTION TURBINES (CTs) SELECTED ARE SIEMENS MODEL SGT6-5000F. EACH COMBUSTION TURBINE WILL GENERATE 200 MW OF ELECTRIC POWER. THE GROSS ELECTRICAL CAPACITY OF THE COMBINED CYCLE FACILITY FIRING NATURAL GAS WILL THEN BE 600 MW. | PM10 74.3(+) EMISSIONS (T/YR) | COMBINED CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.21 | NATURAL GAS | 600 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | oxidation Catalyst | 2 | PPM@15%02 | 3 HOUR AVERAGE WO/O DUCT FIRING/CONDITIO | BACT-PSD | OPERATING PERMIT , SIP | U | 0 | N | 3.2 | PPM@15%02 | 3 HOUR AVERAGE W/DUCT FIRING/CONDITION 2 | 208 | T/YR | 12 CONSECUTVE MONTH AVERAGE/CONDITION 2. | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST. HEAT RATE LIMITED TO 6,793 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR MATTAWOMAN TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS MATTAWOMAN PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | oxidation Catalyst | 2 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE (EXCLUDING SU/SD) | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | WITH AND WITHOUT DUCT FIRING, EXCLUDING SU/SD
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS. HEAT INPUT LIMITED TO 6,802 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR KEYS TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS KEYS PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | oxidation Catalyst | 2 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | WITH AND WITHOUT DUCT FIRING, EXCEPT DURING PERIODS OF STARTUP/SHUTDOWN
TX-0600 | THOMAS C. FERGUSON POWER PLANT | LOWER COLORADO RIVER AUTHORITY | LLANO | TX | 7657 | USA | JOE BENTLEY | 512-473-3272 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tan Nguyen 512-239-3445 tan.nguyen@tceq.texas.gov | PSDTX1244 | 4911 | 221112 | 110035336222 | 10/29/2010 &nbsp;ACT | 09/01/2011 &nbsp;ACT | 2011-09-02 | 2011-09-14 | B |  | Power Plant. Two natural gas-fired combined cycle turbine generators (GE 7FA) with unfired HRSG | 93938 | Natural gas-fired turbines | 15.21 | natural gas | 390 | MW | (2) GE7FA at 195 MW each, (1) steam turbine at 200 MW. Each turbine is equipped with an unfired heat recovery steam generator (HRSG), which provides steam for the steam turbine. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | oxidation Catalyst | 4 | PPMVD | ROLLING 3-HR AT 15% OXYGEN /LOAD >= 60% | BACT-PSD |  | N | 0 | U | 6 | PPMVD | ROLLING 3-HR AT 15% OXYGEN /LOAD < 60% | 0 |  |  | 0 | 0 | N
TX-0590 | KING POWER STATION | PONDERA CAPITAL MANAGEMENT GP INC | HARRIS | TX | 77044 | USA | MARK CHRISOS | (781) 993-3036 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Katherine Stinchcomb (512) 239-1583 katherine.stinchcomb@tceq.texas.gov | PSDTX1125 | 4911 | 221119 | 110040440902 | 03/07/2008 &nbsp;ACT | 08/05/2010 &nbsp;ACT | 2011-08-26 | 2011-09-14 | A |  | Four combined-cycle natural gas-fired combustion turbines | State permit number 84289 Nonattainment permit number N75 | Turbine | 15.21 | natural gas | 1350 | MW | The plant will be designed to generate 1,350 nominal megawatts of power. There are two configuration scenarios: either four Siemens SGT6-5000F CTGs in combined-cycle mode (Scenario A) or four GE Frame 7FA CTGs in combined cycle mode (Scenario B). Scenario B also includes one or two auxiliary boilers. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | oxidation Catalyst | 2 | PPMVD AT 15% O2 | THREE-HOUR ROLLING | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies with or without duct burners
TX-0689 | CEDAR BAYOU ELECTRIC GENERATION STATION | NRG TEXAS POWER | CHAMBERS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 105810, PSDTX1308 | 4911 | 221112 | 110015743301 | 09/12/2012 &nbsp;ACT | 08/29/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power gereration station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the combined cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The new units will produce between 215-263 MW each. |  | Combined cycle natural gas turbines | 15.21 | Natural Gas | 225 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation Catalyst | 2 | PPM | ROLLING 12 MONTHS | BACT-PSD |  | N | 0 | U | 4 | PPM | 1HR AVG. | 0 |  |  | 0 | 0 | N
TX-0709 | SAND HILL ENERGY CENTER | CITY OF AUSTIN | TRAVIS | TX |  | USA | JOSEPH RAVI | (512) 322-6284 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez (512) 239-5220 Ruth.alvirez@tceq.texas.gov | 48106, PSDTX1012M2 | 4911 | 221112 | 110008975804 | 03/20/2015 &nbsp;ACT | 09/13/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | GE 7FA Natural Gas-fired Combined Cycle Turbine with DB fired HRSG |  | Natural gas-fired combined cycle turbines | 15.21 | Natural Gas | 173.9 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation Catalyst | 2 | PPM | 1HR AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0018 | LANGLEY GULCH POWER PLANT | IDAHO POWER COMPANY | PAYETTE | ID |  | USA |  | 2083885820 | TMAHLUM@IDAHOPOWER.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2009.0092 | 4911 | 221112 | UNKNOWN | 06/07/2009 &nbsp;ACT | 06/25/2010 &nbsp;ACT | 2010-08-09 | 2010-10-05 | A |  | ONE-ON-ONE COMBINED CYCLE PLANT CONSISTING OF (1) NATURAL GAS-FIRED COMBUSTION TURBINE (CT) AND (1) STEAM TURBINE. THE CT IS EQUIPPED WITH (1) HEAT RECOVERY STEAM GENERATOR (HRSG) AND DUCT BURNER. ANCILLARY EQUIPMENT INCLUDES (1) DIESEL-FIRED EMERGENCY GENERATOR, (1) DIESEL-FIRED FIRE PUMP, (1) WET COOLING TOWER, AND (6) DRY CHEMICAL STORAGE SILOS. |  | COMBUSTION TURBINE, COMBINED CYCLE W/ DUCT BURNER | 15.21 | NATURAL GAS (ONLY) | 2375.28 | MMBTU/H | SIEMENS SGT6-5000F COMBUSTION TURBINE (NGCT, CCGT) FOR ELECTRICAL GENERATION, NOMINAL 269 MW AND 2.1466 MMSCF/HR | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst | 2 | PPMVD | 3-HR ROLLING / 15% O2 | BACT-PSD |  | N | 0 |  | 24.5 | PPMVD | 3-HR ROLLING / 15% O2 DURING LL | 2510 | LB/H | 1-HR / 15% O2 DURING SU/SD | 0 | 0 | N |  | LIMITS APPLY TO COMBUSTION TURBINE AND DUCT BURNER COMBINED EMISSIONS. SECONDARY LIMIT APPLIES DURING STARTUP, SHUTDOWN, AND LOW-LOAD EVENTS (SU/SD/LL).
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 3 | PPMVD | @15% O2, 3-HR ROLLING AVG | BACT-PSD |  | U | 0 | U | 17.9 | LB/H | 3-HR ROLLING AVG | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #1 - combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr | two identical Siemens SGT6-5000F combined cycle turbines without duct firing, each at 2258 mmBtu/hr generating approx. 300 MW each. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPM | 30-DAY ROLLING AVG. @15% O2 | BACT-PSD |  | U | 95 | U | 552.4 | TON/YR | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #2 -combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPM | 30-DAY ROLLING AVERAGE | BACT-PSD |  | N | 95 | U | 552.4 | TON/YR | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | 552.4 ton/yr limit includes startup, shutdown and malfunction
PA-0286 | MOXIE ENERGY LLC/PATRIOT GENERATION PLT | MOXIE ENERGY LLC | LYCOMING COUNTY | PA |  | USA | KENT MORTON | (571) 594 - 0150 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MUHAMMAD Q. ZAMAN, ENVIRONMENTAL PROGRAM MANAGER NORTHCENTRAL REGION 208 West Third St, Suite 101 Williamsport, PA 17701 570-327-3648 | 41-00084A | 4911 | 221112 | 45-2015223-2 | 07/18/2012 &nbsp;ACT | 01/31/2013 &nbsp;ACT | 2013-03-27 | 2016-05-27 | A |  | This plan approval is for the construction of two natural-gas-fired combined cycle powerblocks where each powerblock consists of a combustion turbine and heat recovery steam generator with duct burner. The two powerblocks constructed pursuant to this plan approval will be either the two powerblocks rated 472 megawatts (MW) (P101 and P102) or the powerblocks rated 458 MW (P103 and P104). Additionally, this plan approval is for the construction of a 1464 bhp diesel-fired emergency generator, 460 bhp dieselfired fire pump, 1600 gallon diesel tank, 300 gallon diesel tank, two 15,000 gallon (each) lube oil tanks and ancillary electrical equipment. |  | Combined Cycle Power Blocks 472 MW - (2) | 15.21 | Natural Gas | 0 |  | Two natural-gas-fired combined cycle powerblocks where each powerblock consists of a combustion turbine and heat recovery steam generator with duct burner. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPMDV |  | BACT-PSD | OTHER | U | 0 | U | 109.3 | T/YR | EACH UNIT | 0 |  |  | 0 | 0 | N
*PA-0298 | FUTURE POWER PA/GOOD SPRINGS NGCC FACILITY | FUTURE POWER PA INC | SCHUYLKILL | PA | 17980 | USA | JAMES PALUMBO | 570-342-5200 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MARK J. WEJKSZNER NORTHEAST REGION AIR PROGRAM MANAGER 2 Public Square Wilkes-Barre, PA 18711 570-826-2357 | 54-00082A | 4911 | 221112 | 26-3703407-1 | 05/03/2013 &nbsp;ACT | 03/04/2014 &nbsp;ACT | 2014-04-17 | 2018-03-23 | A |  | Natural gas-fired combined-cycle electric generation facility that is designed to generate up to 346 MW nominal, using a combustion turbine generator and a heat recovery steam generator that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. The Turbine is rated at 2,267 MMBTU/hr HHV (2,042 MMBTU/hr LHV). The Duct burner is rated at 134.3 MMBTU/hr HHV (120 MMBTU/hr LHV). The proposed project will also include a diesel engine-driven emergency generator; a diesel engine-driven firewater pump; a multi-cell evaporative cooling tower; and associated emission control systems, tanks, and other plant equipment. |  | Turbine, COMBINED CYCLE UNIT (Siemens 5000) | 15.21 | Natural Gas | 2267 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 3 | PPMVD | @ 15% OXYGEN | BACT-PSD | NSPS | U | 0 | U | 17.9 | LB/H | WITH DUCT BURNER | 84.8 | T/YR | BASED ON A 12-MONTH ROLLING TOTAL | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | Combined Cycle Combustion Turbine -Siemens turbine without Duct Burner | 15.21 | Natural gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each Siemens combustion turbine will be 2,356 MMBtu/hr(HHV) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPMVD@15% O2 | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 50 | U | 12 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITHOUT DUCT BURNER - GENERAL ELECTRIC | 15.21 | Natural Gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each General Electric combustion turbine will be 2,312 MMBtu/hr(HHV) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst | 2 | PPMVD@15%O2 | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 50 | N | 10.2 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITH DUCT BURNER - GENERAL ELECTRIC | 15.21 | Natural gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each General Electric combustion each turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 MMBtu/hr duct burner | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst | 2 | PPMVD@15%O2 | 3-HR ROLLING AVERAGE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 50 | N | 11.1 | LB/H | AVEARAGE OF THREE ONE HOUR TESTS | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst | 4 | PPMV | 24-H ROLL AVG DET. EACH H TURBINE OPERAT | BACT-PSD | N/A | U | 0 | U | 3159 | LB/H | 4-H ROLL AVG | 0 |  |  | 0 | 0 | N |  | The first limit is 4 ppmv based on a 24-H rolling average as determined each hour the turbine operates;/dry at 15% O2; except during startup and shutdown; each CTG/HRSG. The second limit is 3159 LB/H based on a 4-H rolling average as determined each hour the turbine operates. Applied on a per block basis (each CTG/HRSG pair combined). Combustion control and catalytic oxidation system (COS) selected based on outlet concentration, not% control efficiency. COS not fully functional at lower than optimum catalyst temperatures during startup/shutdown. CEMS monitoring.
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITHOUT DUCT FIRING | 15.21 | NATURAL GAS | 270 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Oxidation Catalyst | 1.5 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE, EXCLUDING SU/SD | BACT-PSD |  |  | 0 |  | 13767 | LB/EVENT | FOR ALL STARTUPS | 0 |  |  | 0 | 0 | N |  | 818 LB/EVENT FOR SHUTDOWNS. STARTUP AND SHUTDOWN LIMITS ARE TOTAL FOR BOTH CTS COMBINED
CT-0157 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo james.grillo@ct.cov 860-424-3570 | 144-0023 | 4911 | 221112 | 110040589672 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-03 | 2016-02-19 | A |  | 805 MW Combined Cycle Power Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/12 months |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 0.9 | PPMVD @15% O2 | 1 HR BLOCK | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.7 | PPMVD @15% O2 | 1 HR BLOCK | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
CT-0158 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo; james.grillo@ct.gov; 860-424-3570 | 144-0024 | 4911 | 221112 | 110040589672 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-04 | 2016-02-19 | A |  | 805 MW Combined Cycle Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/yr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 0.9 | PPMVD @15% O2 | 1 HR BLOCK | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.7 | PPMVD @15% O2 | 1 HR BLOCK | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/o Duct Firing | 15.21 | Natural Gas | 2969 | MMBtu/hr | Throughput is for turbine only | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 0.9 | PPMVD @15% O2 | 1 HOUR BLOCK | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
GA-0127 | PLANT MCDONOUGH COMBINED CYCLE | SOUTHERN COMPANY/GEORGIA POWER | COBB | GA | 30080 | USA |  |  |  | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us | JOHN YNTEMA 404-363-7117 JOHN.YNTEMA@DNR.STATE.GA.US | 4911-067-0003-V-02-2 | 4911 | 221112 | 110000355972 | 03/08/2007 &nbsp;ACT | 01/07/2008 &nbsp;ACT | 2008-06-17 | 2008-10-09 | B |  | THREE NATURAL GAS FIRED COMBINED CYCLE POWER BLOCKS. EACH BLOCK CONSISTS OF TWO COMBUSTION TURBINES, TWO HEAT RECOVERY STEAM GENERATORS WITH DUCT BURNERS AND A STEAM TURBINE. TWO TURBINES WILL BE CAPABLE OF FIRING ULTRA LOW SULFUR DIESEL AS BACKUP FUEL. EACH COMBINED-CYCLE BLOCK WILL HAVE OUTPUT OF 840 MW. TURBINES ARE REPLACING TWO COAL-FIRED UTILITY BOILERS |  | COMBINED CYCLE COMBUSTION TURBINE | 15.21 | NATURAL GAS | 254 | MW | 6 TURBINES, 254 MW EACH (NOT INCLUDING STEAM RECOVERY), LIMITS ARE FOR EACH TURBINE (MITSUBISHI MODEL M501G). BACKUP FUEL FOR TWO TURBINES IS ULTRA-LOW SULFUR FUEL OIL | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 1.8 | PPM @ 15% O2 | 3-HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 1750 | 0 | N |  | FUEL OIL HAS OWN LAER LIMITS FOR CO AND VOC
TX-0767 | LON C. HILL POWER STATION | LON C. HILL, L.P. | NUECES | TX |  | USA | MATTHEW LINDSEY | 713-358-9734 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem, 512-239-1310, Tzvi.Shalem@tceq.texas.gov | 114911 AND PSDTX1380 | 4911 | 221122 | 110000501127 | 07/15/2015 &nbsp;ACT | 10/02/2015 &nbsp;ACT | 2015-09-23 | 2016-07-06 | A |  | The Lon C. Hill Power Station (LCHP) will include two natural gas-fired combined cycle combustion turbines (CTGs) equipped with dry low NOx burners (DLNs), heat recovery steam generators (HRSG), and natural gas-fired duct burners (DBs). Ancillary equipment includes evaporative coolers or inlet chillers, a single steam turbine (ST), auxiliary boiler, emergency generator, firewater pump, two cooling towers, oil water separator, degreaser, two diesel storage tanks, gasoline storage tank, selective catalytic reduction (SCR) and ammonia (NH3) handling systems including an NH3 storage tank, and two water tanks. The LCHP will be a 2x1 combined cycle power plant consisting of two CTGs, two HRSGs and one ST. The CTGs and ST will be one of two options: two Siemens SCC6-5000 CTGs and a SST6-5000 ST, or two General Electric 7FA CTGs and a D-11 ST. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 195 | MW | Two power configuration options authorized Siemens â€“ 240 MW + 250 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 195 MW + 670 MMBtu/hr duct burner | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPM | ROLLING 24-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0773 | FGE EAGLE PINES PROJECT | FGE EAGLE PINES, LLC | CHEROKEE | TX |  | USA | EMERSON FARRELL | 281-407-7749 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, 512-239-1095, Erik.Hendrickson@tceq.texas.gov | 131316, PSDTX1454, AND GHGPSDT | 4911 | 221112 | UNKNOWN | 09/10/2015 &nbsp;ACT | 11/04/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | The FGEEP Project will include three natural gas-fired combined cycle (NGCC) power blocks, each block comprised of two gas-fired combustion turbines, two supplemental fired duct burners (DBs) heat recovery steam generators (HRSGs), and one steam turbine. FGEEP selected Alstom GT36 combustion turbines (CTs), each nominally rated at 321 megawatts (MW). Each HRSG is equipped with DBs that will have a maximum design heat input capacity of 799 million British thermal units per hour (MMBtu/hr). The CTs and DBs are fueled with pipeline quality natural gas. Each power block will also have a steam turbine generator designed to produce approximately 502 MW with the additional duct firing. Each of the three blocks will include the following ancillary equipment: one multi-cell condenser/cooling tower, one emergency generator, one firewater pump, two diesel storage tanks, and pressurized aqueous ammonia storage tanks. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 321 | MW | Alstom GT36 combustion turbines (321 MW)+ 799 million British thermal units per hour (MMBtu/hr) duct burner | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPM | 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 |  |  | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2017-11-17 | A |  | Combinec Cycle Electric Generating Plant | 103839 | combined cycle turbine | 15.21 | natural gas | 700 | MW | The generating equipment consists of two natural gas-fired combustion turbines (CTs), each exhausting to a fired heat recovery steam generator (HRSG) to produce steam to drive a shared steam turbine generator. The steam turbine is rated at 271 MW of electric output. Three models of combustion turbines are being considered for this site: the General Electric 7FA.05, the Siemens SGT6-5000F(4), and the Siemens SGT6-5000F(5). The final selection of the combustion turbine will not be made until after the permit is issued. Plant output will range between 637 and 735 MW, depending on the model turbine selected. Duct Burners are rated at 750 MMBtu/hr each. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 2 | PPMVD | 3-HR ROLL AVG, 15% OXYGEN, 80-100% LOAD | BACT-PSD |  | N | 0 | U | 4 | PPMVD | 3-HR ROLL AVG, 15% OXYGEN, 60-80% LOAD | 0 |  |  | 0 | 0 | N
*TX-0660 | FGE TEXAS POWER I AND FGE TEXAS POWER II | FGE POWER LLC | MITCHELL | TX | 79565 | USA | EMERSON FARRELL | 281-362-2830 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX1364 | 3511 |  |  | 05/06/2013 &nbsp;EST | 03/24/2014 &nbsp;ACT | 2014-06-13 | 2017-11-17 | U |  | Electric Generating Utility | TCEQ Permit No. 110025 | Alstom Turbine | 15.21 | Natural Gas | 230.7 | MW | Four (4) Alstom GT24 CTGs, each with a HRSG and DBs, max design capacity 409 MMBtu/hr | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst | 2 | PPMVD | CORRECTED TO 15% O2, ROLLING 3 HR AVE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2018-05-11 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 2 | PPMVD | 15% O2 3 HOUR AVERAGE | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 2 | PPMVD | 3 HOURS | BACT-PSD |  |  | 90 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LIMIT ONE IS USED WITH CONDITIONS AT 15% O2 WITH USING DUCT BURNERS.
NJ-0080 | HESS NEWARK ENERGY CENTER | HESS NEWARK ENERGY CENTER, LLC | ESSEX | NJ | 7105 | USA | PETER HAID | (774) 750-7088 | PHAID@HESS.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Supervisor: Yogesh Doshi - yogesh.doshi@dep.state.nj.us Phone: 609-633-7249 Permit Evaluator: Michael Hogan - michael.hogan@dep.state.nj.us. Phone: (609)-633-1124 | 08857/BOP110001 | 4911 | 221112 | 110044839903 | 12/10/2011 &nbsp;ACT | 11/01/2012 &nbsp;ACT | 2013-04-04 | 2018-04-17 | A |  | Combined Cycle Electric Generating Facility HESS Newark Energy Center (Hess-NEC), proposed at City of Newark (Essex County), New Jersey, would be a new, highly efficient, 655 MW combined-cycle power generating facility. Hess-NEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,320 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, a 12-cell mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Facility-wide Greenhouse Gas (GHG) emissions as CO2e emissions = 2,003,654 tpy | Combined cylce turbine with duct burner | 15.21 | natural gas | 39463 | mmcubic ft/year* | * Annual throughput is for 2 turbines, 2 duct burners and 1 auxiliary boiler | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst | 2 | PPMVD | 3-HR ROLLING AVERAGE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | U | 90 | N | 10.2 | LB/H | AVERAGE OF THREE TESTS | 0 |  |  | 0 | 0 | N
PA-0278 | MOXIE LIBERTY LLC/ASYLUM POWER PL T | MOXIE ENERGY LLC | BRADFORD COUNTY | PA |  | USA | KENT J MORTON | (571) 594 - 0150 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MUHAMMAD Q. ZAMAN, ENVIRONMENTAL PROGRAM MANAGER, NORTHCENTRAL REGION | 08Â·00045A | 491 | 221112 | 45-2015223-1 | 09/26/2011 &nbsp;ACT | 10/10/2012 &nbsp;ACT | 2012-12-03 | 2015-04-03 | A |  |  | The project consists of two identical 1 x 1 power blocks, and each block includes a combustion gas turbine and a steam turbine. Each combined-cycle process will also include a heat recovery steam generator and supplemental duct burners. Additionally, one diesel-fired emergency generator, one diesel-fired fire water pump, two diesel fuel storage tanks, two lube oil storage tanks, and one aqueous ammonia storage tank were proposed to be constructed and operated. Each combined-cycle process will be rated at 468 MW or less. | Combined-cycle Turbines (2) - Natural gas fired | 15.21 | Natural Gas | 3277 | MMBTU/H | Two combine cycle Turbines, each with a combustion turbine and heat recovery steam generator with duct burner. Each combined-cycle process will be rated at 468 MW or less. The heat input rating of each combustion gas turbine is 2890 MMBtu/hr (HHV) or less, and the heat input rating of each supplemental duct burner is equal to 387 MMBtu/hr (HHV) or less. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPMVD | @15% O2 | BACT-PSD |  | U | 80 | U | 15.3 | LB/H | 468 MW POWERBLOCK | 2 | PPMVD | @15% O2 | 0 | 0 | N |  | 1-hr CEMS monitoring and combustion controls for lean combustion. Other Limit: 15.0000 LB/H 454 MW POWERBLOCK
TX-0546 | PATTILLO BRANCH POWER PLANT | PATTILLO BRANCH POWER COMPANY LLC | FANNIN | TX |  | USA |  |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | RANDY HAMILTON RHAMILTO@TCEQ.STATE.TX.US | 83642 | 4911 | 221122 | TX0121997 | 12/13/2007 &nbsp;ACT | 06/17/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | 1400 MW POWER PLANT. 4 NATURAL GAS FIRED TURBINES PLUS HEAT RECOVERY STEAM GENERATORS (HRSG) | PSDTX1115 | ELECTRICITY GENERATION | 15.21 | NATURAL GAS | 350 | MW | EACH TURBINE/HRSG WILL BE DESIGNED TO OUTPUT 350 MW. TURBINES BEING CONSIDERED FOR THE PROJECT ARE GE 7FA, GE 7FB, AND SIEMENS SGT6-5000F. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 2 | PPMVD | @ 15% O2, 3-HR ROLLING AVG | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | (2) combined cycle turbines | 15.21 | natural gas | 650 | MW | The specific equipment includes two combustion turbines (CTs) connected to electric generators, producing between 183 and 232 MW of electricity, depending on ambient temperature and the selected CT. The two HRSGs use duct burners rated at 750 MMBtu/hr each to supplement the heat energy from the CTs. The steam from the two HRSGs is combined and routed to a single steam turbine driving a third electric generator with an electricity output capacity of 271 MW. Depending on the selected CT, total plant output at 59Â°F is between 637 MW and 735 MW. The applicant is considering three models of CT; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) Siemens SGT6-5000F(4); or (3) Siemens SGT6-5000F(5). | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 2 | PPMVD | @15% O2, 3-HR ROLLING, 80-100% LOAD | BACT-PSD |  | N | 0 | U | 4 | PPMVD | @15% O2, 3-HR ROLLING, 60-80% LOAD | 0 |  |  | 0 | 0 | N
TX-0713 | TENASKA BROWNSVILLE GENERATING STATION | TENASKA BROWNSVILLE PARTNERS, LLC | CAMERON | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 108411 PSDTX1350 | 4911 | 221112 | unknown | 02/21/2013 &nbsp;ACT | 04/29/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | Tenaska proposes a new electric power plant, using combined cycle gas turbine (CCGT) technology and fueled by pipeline quality natural gas. The proposed permit authorizes two CTs (2x1 CCGT), although the final design selected by Tenaska may only consist of one CT (1x1 CCGT). |  | (2) combined cycle turbines | 15.21 | natural gas | 274 | MW | Each CTG is site-rated at 274 MW gross electric output at 62Â°F ambient temperature. At this condition, two HRSGs with full duct burner firing produce enough steam to generate an additional 336 MW, for a total of 884 MW gross, or with about 5% losses, about 840 MW net electric output. Under summertime conditions, the net output is approximately 800 MW with the 2x1 CCGT configuration or about 400 MW with the 1x1 CCGT configuration. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 2 | PPMVD | @15% O2, 24-HR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 4 | PPM | HOURLY | BACT-PSD | NSPS | N | 0 | U | 2 | PPM | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N |  | NSPS KKKK AND TTTT
TX-0789 | DECORDOVA STEAM ELECTRIC STATION | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas.gov | 107569 AND PSDTX1432 | 4911 | 221112 | 110008149217 | 12/23/2015 &nbsp;ACT | 03/08/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | The DeCordova Station will consist of two combustion turbine generators (CTGs) operating in simple cycle or combined cycle modes. The gas turbines will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE). Simple cycle operations limited to 2,500 hr/yr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 4 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP01) | 15.21 | Natural Gas | 40 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 4 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD |  | U | 0 | U | 3.7 | LB/H | 30-DAY ROLLING AVERAGE | 32 | T/YR |  | 3307 | 5108 | N | 2011
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP02) | 15.21 | Natural Gas | 40 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 4 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD |  | N | 0 | U | 3.7 | LB/H | 30-DAY ROLLING AVERAGE | 32 | T/YR |  | 3307 | 5108 | N | 2011
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Combustion Turbine | 15.21 | natural gas | 87 | MW | The exhaust heat from the turbine will be used to heat a heating medium which is used to regenerate rich amine from the acid gas removal system. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 4 | PPMVD | @15% O2, 3 HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0710 | VICTORIA POWER STATION | VICTORIA WLE L.P. | VICTORIA | TX |  | USA | GARY CLARK | (361) 947-9934 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | 108258 PSDTX1348 | 4911 | 221112 | 110000501154 | 02/14/2013 &nbsp;ACT | 12/01/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | The facility is currently authorized under Standard Permit No. 80878 and several Permits by Rule (PBR), including Â§106.263 for maintenance, startup, and shutdown (MSS) (PBR Registration No. 94387) and Title V Permit No. O-35. Victoria proposes to install an additional natural gas-fired turbine (GT) and HRSG with duct burners at the Victoria Station. The resulting new facility will be a combined cycle generating facility in a 2x2x1 configuration (two combustion turbines, two HRSGs with duct burners, and one steam turbine). |  | combined cycle turbine | 15.21 | natural gas | 197 | MW | General Electric 7FA.04 at 197 MW nominal ouput. The duct burners will be capable of a maximum natural gas firing rate of up to 483 MMBtu/hr (HHV). The duct burners may be fired additional hours; however, total annual firing will not exceed the equivalent of 4,375 hours at maximum capacity per duct burner. The available capacity of the existing steam turbine will be increased from 125 MW in its existing 1x1x1 configuration to approximately 185 MW in the 2x2x1 configuration. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 4 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0712 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER COMPANY | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | (205) 257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tzvi Shalem 512-239-1310 tzvi.shalem@tceq.texas.gov | 111393 PSDTX1368 | 4911 | 221112 | 110007199735 | 06/27/2013 &nbsp;ACT | 11/20/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | Southern Power Company (SPC) is proposing to construct an electric generating facility near Trinidad, Henderson County, Texas. The Trinidad Generating Facility (TGF) will include a natural gas-fired combined cycle combustion turbine generator (CTG) equipped with heat recovery steam generator (HRSG) and duct burners (DB). |  | combined cycle turbine | 15.21 | natural gas | 497 | MW | The facility will consist of a Mitsubishi Heavy Industries (MHI) J model gas fired combustion turbine nominally rated at 497 megawatts (MW) equipped with a HRSG and DB with a maximum design capacity of 402 million British thermal units per hour (MMBtu/hr). The gross nominal output of the CTG with HRSG and DB is 530 MW. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 4 | PPMVD | @15% O2, 24-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0714 | S R BERTRON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | HARRIS | TX |  | USA | CRAIG ECKBERG | (713) 537-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | 102731 PSDTX1294 | 4911 | 221112 | 110034988413 | 05/10/2012 &nbsp;ACT | 12/19/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | NRG Texas is proposing to construct an additional electric power generation station at the Bertron Power Project which will generate electric power for sale on the wholesale electric market. The Bertron Power Project will include two power blocks that can be operated in combined cycle mode. |  | (2) combined cycle turbines | 15.21 | natural gas | 240 | MW | The gas turbines will be one of three options: (1) Two Siemens Model F5 (SF5) CTGs each rated at nominal capability of 225 megawatts (MW). Each CTG will have a duct fired HRSG with a maximum heat input of 688 million British thermal units per hour (MMBtu/hr). (2) Two General Electric Model 7FA (GE7FA) CTGs each rated at nominal capability of 215 MW. Each CTG will have a duct fired HRSG with a maximum heat input of 523 MMBtu/hr. (3) Two Mitsubishi Heavy Industry G Frame (MHI501G) CTGs each rated at a nominal electric output of 263 MW. Each CTG will have a duct fired HRSG with a maximum heat input of 686 MMBtu/hr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 4 | PPMVD | @15% O2, ONE HOUR | BACT-PSD |  | N | 0 | U | 2 | PPMVD | @15% O2, ROLLING 12-MONTH | 0 |  |  | 0 | 0 | N
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Simple Cycle Electrical Generation Gas Turbines 15.210 | 15.21 | natural gas | 34 | MW | Nine GE PGT25+G4 gas turbines for electrical generation at the site at 34 MW/turbine | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 9 | PPM | ROLLING 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041470431 | 04/18/2014 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2016-05-16 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 4 | PPMVD @ 15% O2 | 3-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Permit requires downward adjustment to CO limits based on first 30 months of operation
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | Combustion Turbine | 15.21 | Natural Gas | 360 | MW | This process represents the GE option for the project - One GE 7FA.05 natural gas-fired combustion turbine generator with an 820.5 MMBTUH duct burner. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practice. | 2 | PPMVD@15%O2 | 3-HR | BACT-PSD | N/A | U | 0 | U | 14 | LB/HR | 3-HR | 0 |  |  | 0 | 0 | N
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two Combine Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 3001.57 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. . (Operational limits are for each CCCT NG-fired with duct burner) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 2 | PPMDV @ 15% O2 |  | BACT-PSD |  | U | 0 | U | 1189.8 | TONS | YR | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative emissions from both CCCT in any 12-month period
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064098541 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine With Duct Burner | 15.21 | Natural Gas | 3727 | MMBtu/hr | DLN burner, SCR, Oxidation Catalyst and shall maintain and operate the sources and associated air cleaning devices in accordance with good engineering practice. shall install, certify, maintain and operate continuous emission monitoring systems (CEMS) for nitrogen oxides, carbon monoxide, carbon dioxide, and ammonia emissions on the exhaust of each combined-cycle powerblock. Emissions limits are for each combustion turbine/duct burner block. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 2 | PPMDV @ 15% O2 |  | BACT-PSD | NSPS | U | 0 | U | 15.6 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 105.1 tpy 12-month rolling basis
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 725 | MEGAWATT | TWO GENERAL ELECTRIC (GE) F-CLASS ADVANCED COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 725 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES | 2 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE, EXCLUDING SU/SD | BACT-PSD |  | U | 0 | U | 530 | LB | CEM | 0 |  |  | 0 | 0 | N |  | EMISSION #1 IS WITH AND WITHOUT DUCT FIRING EMISSION #2 APPLIES TO EACH STARTUP/SHUTDOWN EVENT
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas without Duct Burner | 15.21 | Natural Gas | 8040 | H/YR |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES | 2 | PPMVD@15% O2 | 3 H ROLLING AV BASED ON ONE H BLOCK AV | BACT-PSD | OPERATING PERMIT | N | 69 | N | 15.3 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY CEMS AND STACK TESTING
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas with Duct Burner | 15.21 | natural gas | 4000 | h/yr |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst and good combustion practices | 2 | PPMVD@15%O2 | 3 H ROLLING AV BASED ON ONE H BLOCK AV | BACT-PSD | OPERATING PERMIT | N | 69 | N | 18.1 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY CEMS AND STACK TESTING
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002049328 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | COMBINED CYCLE TURBINE GENERATORS (UNITS 6A &amp; 6B) | 15.21 | NATURAL GAS | 7146 | MMBTU/H | TURBINES ALSO PERMITTED TO BURN NO. 2 FUEL OIL AND ULTRA LOW SULFUR DIESEL. FUEL OIL USE IS LIMITED TO 1000 HOURS PER YEAR. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES | 3 | PPMVD @ 15% O2 | HOURLY AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 3 | PPMVD @ 15% O2 | HOURLY AVERAGE | 0 | 0 | N |  | CO MONITORED USING CEMS. 3 PPMVD @ 15% O2 LIMIT APPLIES WHEN OPERATING W/ AND W/O THE DUCT BURNER AND WHEN FIRING FUEL OIL. STARTUP/SHUTDOWN: PROGRESS THROUGH THE SU/SD EVENT AS QUICKLY AS POSSIBLE WHILE FOLLOWING THE MANUFACTURER'S RECOMMENDED PROCEDURES. SU/SD OPERATIONS LIMITED TO 1302 HR/YR. BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE).
*VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404-001 | 4911 | 221112 | 110055066440 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2016-07-07 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | Three Mitsubishi M501 GAC Turbines (3,442 mmBtu/hr each) | 15.21 | natural gas | 0 | s | combined fuel for three turbines as a 12-month rolling total | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices including the minimization of startup and shutdown emissions | 1.5 | PPMVD | 3-HOUR ROLLING AVG W/O DUCT BURNER | BACT-PSD | NSPS , SIP | U | 0 | Y | 2.4 | PPMVD | 3-HOUR ROLLING AVG W/O DUCT BURNER | 0 |  |  | 0 | 0 | N |  | CEMS will be used to monitor CO from the turbines Initial performance test continuous monitoring and recording of catalyst bed inlet and outlet temperature
VA-0315 | WARREN COUNTY POWER PLANT - DOMINION | VIRGINIA ELECTRIC AND POWER COMPANY | WARREN | VA | 22630 | USA | ROBERT BISHA | 804-273-3010 | ROBERT.M.BISHA@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Manager, Mr. Janardan Pandey, by phone at (540) 574-7817 or by e-mail: Janardan.Pandey@deq.virginia.gov | 81391-007 | 4911 | 221112 | 110040513110 | 09/03/2010 &nbsp;ACT | 12/17/2010 &nbsp;ACT | 2012-09-28 | 2015-03-30 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Virginia Electric and Power Company (Dominion) has proposed to construct and operate a combined-cycle electric power generating facility in Warren County with a nominal generating capacity of 1280 megawatts (MW) at ISO (International Organization for Standardization) conditions. | Equipment to be constructed at ths facility consists of: 3 Mitsubishi Model M501 GAC natural gas-fired combined-cylce turbines, each rated at 299,600 kW (2,996 MMBtu/hr. Each equipped with a heat recovery steam generator (HRSG) having a duct burner with a design rating of 500 MMBtu/hr. This permit supersedes the previous permit issued on 7/30/2004 to CPV Warren LLC. | COMBINED CYCLE TURBINE &amp; DUCT BURNER, 3 | 15.21 | Natural Gas | 2996 | MMBTU/H | Emissions are for one of three units (Mitsubishi natural gas-fired combustion turbine (CT) generator,Model M501 GAC). | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices. | 1.5 | PPMVD | ONE HR AVERAGE (W/O DUCT BURNER FIRING) | BACT-PSD |  | U | 0 | U | 2.4 | PPMVD | ONE HR AVERAGE (WITH DUCT BURNER FIRING) | 0 |  |  | 0 | 0 | N |  | Emissions are for one of three units. Emission 1: 9.9 LB/H ONE HR AVERAGE (W/O DUCT BURNER FIRING) Emission 2: 17.4 LB/H ONE HR AVERAGE (WITH DUCT BURNER FIRING)
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | COMBUSTION TURBINE | 15.21 | NATURAL GAS | 360 | MW | This process represents the Siemens option for the project - One Siemens SGT6-5000F5 natural gas-fired combustion turbine generator with an 820.3 MMBTUH duct burner. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES. | 2 | PPMVD@15% O2 | 3-HR | BACT-PSD | N/A | U | 0 | U | 14.5 | LB/HR | 3-HR | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine without Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burner. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst and Use of Natural gas a clean burning fuel | 0.9 | PPMVD@15%O2 | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 90 | U | 4.75 | LB/H | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burners. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and use of natural gas a clean burning fuel | 1.5 | PPMVD@15%O2 | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 90 | U | 10.5 | LB/H | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITH DUCT BURNER - SIEMENS | 15.21 | Natural Gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two Siemens turbines and two associated duct burners) The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst and use of only natural gas a clean burning fuel | 2 | PPMVD | 3-HR ROLLING AVE BASED ON 1-HR BLOCK AVE | BACT-PSD | OPERATING PERMIT | N | 50 | N | 14 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | 0 |  |  | 0 | 0 | N
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG with duct burner NG only | 15.21 | Natural Gas | 3338 | MMBtu/hr | Emission limits are for each turbine operating with duct burner and do not include startup/shutdown emissions. Tons per year limits is a cumulative value for all three CCCT. CEMS for NOx, CO, and O2. Each CCCT and duct burner have 5 operational scenarios: 1 CCCT with duct burner fired - fueled by NG only 2 CCCT with duct burner fired - fueled by NG blend with ethane 3 CCCT without duct burner fired - fueled by NG only 4 CCCT without duct burner fired - fueled by NG blend with ethane 5 CCCT without duct burner fired - fueled by ULSD (Limited to emergency use only) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst operated at all steady state operating loads and good combustion practices | 2 | PPMDV @ 15% O2 |  | BACT-PSD | NSPS | U | 0 | U | 84.9 | TONS | YEAR | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 1.5 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 6.27 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N |  | CO EMISSION LIMITS DURING 3-YR PERIOD IMMEDIATELY FOLLOWING COMMENCEMENT OF COMMERCIAL OPERATION: 2.0 PPMVD @15% O2 OR 8.35 LB/HR, 1-HR AVG (NO DUCT FIRING)
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 1.5 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 6.27 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N |  | CO EMISSION LIMITS DURING 3-YR PERIOD IMMEDIATELY FOLLOWING COMMENCEMENT OF COMMERCIAL OPERATION: 2.0 PPMVD @15% O2 OR 8.35 LB/HR, 1-HR AVG (NO DUCT FIRING)
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 1.5 | PPMVD | @15% O2, 1-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 2 | PPMVD | @15% O2, 1-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N |  | 2.0 PPMVD @15% O2, 1-HR AVG (NO DUCT BURNING) APPLIES DURING 3-YEAR DEMONSTRATION PERIOD
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 2 | PPMVD | @15% O2, 1-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 7.65 | LB/H | 1-HR AVG (NO DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | Natural Gas | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 2 | PPMVD | @15% O2, 1-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 7.65 | LB/H | 1-HR AVG (NO DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 2 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 10 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 2 | PPMVD | @15% O2, 1-HR AVG (W/ DUCT FIRING) | BACT-PSD |  | U | 0 | U | 10 | LB/H | 1-HR AVG (W/ DUCT FIRING) | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 3 | PPMVD | @15% O2, 1-HR AVG (W/ DUCT BURNING) | BACT-PSD |  | U | 0 | U | 13.35 | LB/H | 1-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 3 | PPMVD | @15% O2, 1-HR AVG (W/ DUCT BURNING) | BACT-PSD |  | U | 0 | U | 13.35 | LB/H | 1-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1209 | HIGH DESERT POWER PROJECT | HIGH DESERT POWER PROJECT LLC | SAN BERNADINO | CA | 92394 | USA | JON BOYER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 98-01 | 4911 | 221112 | 110014461420 | 09/25/2009 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-11 | 2014-01-15 | C | http://www.epa.gov/region09/air/permit/r9-permits-issued.html | 720 MW NATURAL GAS FIRED POWER PLANT | RBLC Management: There were many duplicate pollutant records Editor repeated all emission limits for each of the 3 types of operation, Start-up, Normal, and Shutdown. Record was edited and duplicate records were deleted. Original Note: PSD Permit amended to change the design of the power plant. These changes include a modification in the turbine configuration from 3x3x3 (i.e., three combustion turbines (CT), three heat recovery steam generators (HRSG), and three steam turbine generators (STG)) to a 3x3x1 configuration, reconfiguration of the cooling tower from three towers to one, addition of a diesel firewater pump engine, modification of the stack location, elevation, and diameter, and modification in the physical dimensions of the cooling tower, steam turbine, and HRSG structure. The terms and conditions included in the PSD permit issued February 15, 2001, and the modeling analyses on which the original determinations were based, remain valid and in effect. | COMBUSTION TURBINE GENERATORS (NORMAL OPERATION) | 15.21 | NATURAL GAS | 190 | MW | THREE (3) COMBUSTION TURBINE GENERATORS AT 190 MW EACH AND EQUIPPED WITH A 160 MMBTU/HR DUCT BURNER AND HRSG | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 4 | PPMVD | @15% O2, 24-HR AVG | BACT-PSD |  | U | 0 | U | 17.53 | LB/H | 24-HR AVG | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 4 | PPM | 24-H ROLL. AVG., NOT STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 85 | N | 5.31 | LB/H | 24-H ROLL. AVG., NOT STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | The CO limits apply to EACH CTGHRSG based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. The first CO limit is 4 ppmdv at 15%O2. Startup is defined as the period of time from synchronization to the grid (generator breaker closed) until the unit reaches steady state operation (loads greater than 50 percent of design capacity). Shutdown is defined as that period of time from the initial lowering of the turbine output below 50 percent of full operating load, with the intent to shut down, until the point at which the generator breaker opens.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 4 | PPM | EACH EU; 24-H ROLL AVG EXCEPT | BACT-PSD | SIP | N | 85 | N | 5.31 | LB/H | EACH EU; 24-H ROLL AVG EXCEPT | 0 |  |  | 0 | 0 | N |  | The emission limits above are for each CTG/HRSG and are as follows: 1) 4 ppmvd at 15% O2 based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. 2) 5.31 LB/H based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. There are separate limits for each of these emission units during startup and shutdown which will be identified as a separate process in this determination. Startup is defined as the period of time from synchronization to the grid (generator breaker closed) until the unit reaches steady state operation (loads greater than 50 percent design capacity). Shutdown is defined as that period of time from the initial lowering of the turbine output below 50 percent of full operating load, with the intent to shut down, until the point at which the generator breaker opens.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 4 | PPM | 24-H ROLL.AVG., EXCEPT STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 0 | N | 17.4 | LB/H | 24-H ROLL.AVG., EXCEPT STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above is 4 ppmvd at 15% O2. Also, each of the emission limits above are based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. There is a separate limit for each startup/shutdown event, which will be entered as a separate 'Process' in the RBLC determination.
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Combustion turbine with duct burner | 15.21 | Natural gas | 3304.3 | MMBtu/hr | Limits are for each CCCT and yearly limits are for cumulative turbine and duct burner. Duct burner throughput is 637.9 MMBtu/hr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst, combustion controls, exclusive natural gas | 2 | PPMDV @ 15 % O2 |  | BACT-PSD |  | U | 0 | U | 84.9 | TONS | YEAR | 0 |  |  | 0 | 0 | N |  | CO CEMS (1-hour average)
NJ-0079 | WOODBRIDGE ENERGY CENTER | CPV SHORE, LLC | MIDDLESEX | NJ | 7095 | USA | MARK TURNER | (415)293-1463 | MTURNER@CPV.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Mr. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS, yogesh.doshi@dep.state.nj.us; phone 609-633-7249 | 18940 - BOP110003 | 4911 | 221112 | 110055590953 | 10/12/2011 &nbsp;ACT | 07/25/2012 &nbsp;ACT | 2012-11-27 | 2018-04-17 | A |  | Woodbridge Energy Center (WEC), proposed at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, would be a new, highly efficient, 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,307 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, one small dew point fuel gas heater (fuel gas heater), a mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Other Permitting Information: Facility-Wide Greenhouse Gas (GHG) emissions as CO2e emissions= 2,073,645 tons per year | Combined Cycle Combustion Turbine w/o duct burner | 15.21 | natural gas | 40297.6 | mmcubic ft/year | The above natural gas use is combined for two GE 7FA CC turbines (each with a maximum heat input of 2, 307 MMBtu/hr)and two duct burners (each with a maximum heat input of 500 MMBtu/hr) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst, good combustion practices and use only natural gas a clean burning fuel | 2 | PPMVD | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | U | 77 | Y | 10.2 | LB/H | AVERAGE OF THREE TESTS | 0 |  |  | 0 | 0 | N |  | Compliance Verified by Stack test in 2016, CO Emission limit1 achieved was 0.0 PPMVD; Emission limit 2 achieved was 0.0 LB/H (no CO Emissions)
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064098541 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine without Duct Burner | 15.21 |  | 0 |  |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst, good engineering practice | 2 | PPMDV @ 15% O2 |  | BACT-PSD | NSPS | U | 0 | U | 14.7 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 105.1 tpy on 12-month rolling basis
*VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404-001 | 4911 | 221112 | 110055066440 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2016-07-07 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | COMBUSTION TURBINE GENERATORS, (3) | 15.21 | Natural Gas | 3442 | MMBTU/H | Three (3) Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners (natural gas-fired). | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst; good combustion practices. | 1.5 | PPMVD | 3 H AVG/WITHOUT DUCT BURNING | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | Mitsubishi M501-GAC combustion turbine, combined cycle configuration with duct burner. | 15.21 | natural gs | 2988 | MMBTU/H | or ULSD; Duct burner 499 MMBtu/hr, natural gas | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst; Limit the time in startup or shutdown. | 3.3 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON NG | BACT-PSD |  | U | 0 | U | 9 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON ULSD | 0 |  |  | 0 | 0 | N
TX-0727 | CEDAR BAYOU ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | CHAMBERS COUNTY | TX |  | USA | LINDSAY LITTLE | (713) 357-5291 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem, 512-239-1310, tzvi.shalem@tceq.texas.gov | 80289 & PSDTX1082M1 | 4911 | 221112 | 110037869456 | 07/09/2014 &nbsp;ACT | 03/31/2015 &nbsp;ACT | 2015-03-30 | 2016-05-16 | C |  | NRG operates the Cedar Bayou 4 Electric Generating Station in Chambers County, consisting of two natural gas-fired combustion turbines, Emission Point Numbers (EPNs) CBY41 and CBY42, and associated ancillary equipment. NRGâ€™s amendment application requests an increase in the annual carbon monoxide (CO) and a small increase in the volatile organic compounds (VOC) emission rates for both turbines, due to an increase in the number of startups per year. NRG requests to install oxidation catalysts to each unit. |  | Combined cycle turbines | 15.21 | Natural Gas | 187 | MW/turbine |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalysts | 15 | PPMVD | 15%O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
[40 empty] | Range Low | 0.9 | PPMV
[40 empty] | Range High | 50 | PPMV
[40 empty] | Mean | 4.4137 | PPMV
[40 empty] | Median | 2 | PPMV
[40 empty] | Mode | 2 | PPMV

## Oxidation Catalyst
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
CT-0157 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo james.grillo@ct.cov 860-424-3570 | 144-0023 | 4911 | 221112 | 110040589672 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-03 | 2016-02-19 | A |  | 805 MW Combined Cycle Power Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/12 months |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 0.9 | PPMVD @15% O2 | 1 HR BLOCK | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.7 | PPMVD @15% O2 | 1 HR BLOCK | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
CT-0158 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo; james.grillo@ct.gov; 860-424-3570 | 144-0024 | 4911 | 221112 | 110040589672 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-04 | 2016-02-19 | A |  | 805 MW Combined Cycle Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/yr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 0.9 | PPMVD @15% O2 | 1 HR BLOCK | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.7 | PPMVD @15% O2 | 1 HR BLOCK | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/o Duct Firing | 15.21 | Natural Gas | 2969 | MMBtu/hr | Throughput is for turbine only | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 0.9 | PPMVD @15% O2 | 1 HOUR BLOCK | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine without Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burner. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst and Use of Natural gas a clean burning fuel | 0.9 | PPMVD@15%O2 | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 90 | U | 4.75 | LB/H | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITHOUT DUCT FIRING | 15.21 | NATURAL GAS | 270 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Oxidation Catalyst | 1.5 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE, EXCLUDING SU/SD | BACT-PSD |  |  | 0 |  | 13767 | LB/EVENT | FOR ALL STARTUPS | 0 |  |  | 0 | 0 | N |  | 818 LB/EVENT FOR SHUTDOWNS. STARTUP AND SHUTDOWN LIMITS ARE TOTAL FOR BOTH CTS COMBINED
*VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404-001 | 4911 | 221112 | 110055066440 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2016-07-07 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | Three Mitsubishi M501 GAC Turbines (3,442 mmBtu/hr each) | 15.21 | natural gas | 0 | s | combined fuel for three turbines as a 12-month rolling total | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices including the minimization of startup and shutdown emissions | 1.5 | PPMVD | 3-HOUR ROLLING AVG W/O DUCT BURNER | BACT-PSD | NSPS , SIP | U | 0 | Y | 2.4 | PPMVD | 3-HOUR ROLLING AVG W/O DUCT BURNER | 0 |  |  | 0 | 0 | N |  | CEMS will be used to monitor CO from the turbines Initial performance test continuous monitoring and recording of catalyst bed inlet and outlet temperature
VA-0315 | WARREN COUNTY POWER PLANT - DOMINION | VIRGINIA ELECTRIC AND POWER COMPANY | WARREN | VA | 22630 | USA | ROBERT BISHA | 804-273-3010 | ROBERT.M.BISHA@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Manager, Mr. Janardan Pandey, by phone at (540) 574-7817 or by e-mail: Janardan.Pandey@deq.virginia.gov | 81391-007 | 4911 | 221112 | 110040513110 | 09/03/2010 &nbsp;ACT | 12/17/2010 &nbsp;ACT | 2012-09-28 | 2015-03-30 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Virginia Electric and Power Company (Dominion) has proposed to construct and operate a combined-cycle electric power generating facility in Warren County with a nominal generating capacity of 1280 megawatts (MW) at ISO (International Organization for Standardization) conditions. | Equipment to be constructed at ths facility consists of: 3 Mitsubishi Model M501 GAC natural gas-fired combined-cylce turbines, each rated at 299,600 kW (2,996 MMBtu/hr. Each equipped with a heat recovery steam generator (HRSG) having a duct burner with a design rating of 500 MMBtu/hr. This permit supersedes the previous permit issued on 7/30/2004 to CPV Warren LLC. | COMBINED CYCLE TURBINE &amp; DUCT BURNER, 3 | 15.21 | Natural Gas | 2996 | MMBTU/H | Emissions are for one of three units (Mitsubishi natural gas-fired combustion turbine (CT) generator,Model M501 GAC). | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices. | 1.5 | PPMVD | ONE HR AVERAGE (W/O DUCT BURNER FIRING) | BACT-PSD |  | U | 0 | U | 2.4 | PPMVD | ONE HR AVERAGE (WITH DUCT BURNER FIRING) | 0 |  |  | 0 | 0 | N |  | Emissions are for one of three units. Emission 1: 9.9 LB/H ONE HR AVERAGE (W/O DUCT BURNER FIRING) Emission 2: 17.4 LB/H ONE HR AVERAGE (WITH DUCT BURNER FIRING)
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burners. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and use of natural gas a clean burning fuel | 1.5 | PPMVD@15%O2 | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 90 | U | 10.5 | LB/H | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 1.5 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 6.27 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N |  | CO EMISSION LIMITS DURING 3-YR PERIOD IMMEDIATELY FOLLOWING COMMENCEMENT OF COMMERCIAL OPERATION: 2.0 PPMVD @15% O2 OR 8.35 LB/HR, 1-HR AVG (NO DUCT FIRING)
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 1.5 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 6.27 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N |  | CO EMISSION LIMITS DURING 3-YR PERIOD IMMEDIATELY FOLLOWING COMMENCEMENT OF COMMERCIAL OPERATION: 2.0 PPMVD @15% O2 OR 8.35 LB/HR, 1-HR AVG (NO DUCT FIRING)
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 1.5 | PPMVD | @15% O2, 1-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 2 | PPMVD | @15% O2, 1-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N |  | 2.0 PPMVD @15% O2, 1-HR AVG (NO DUCT BURNING) APPLIES DURING 3-YEAR DEMONSTRATION PERIOD
*VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404-001 | 4911 | 221112 | 110055066440 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2016-07-07 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | COMBUSTION TURBINE GENERATORS, (3) | 15.21 | Natural Gas | 3442 | MMBTU/H | Three (3) Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners (natural gas-fired). | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst; good combustion practices. | 1.5 | PPMVD | 3 H AVG/WITHOUT DUCT BURNING | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
GA-0127 | PLANT MCDONOUGH COMBINED CYCLE | SOUTHERN COMPANY/GEORGIA POWER | COBB | GA | 30080 | USA |  |  |  | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us | JOHN YNTEMA 404-363-7117 JOHN.YNTEMA@DNR.STATE.GA.US | 4911-067-0003-V-02-2 | 4911 | 221112 | 110000355972 | 03/08/2007 &nbsp;ACT | 01/07/2008 &nbsp;ACT | 2008-06-17 | 2008-10-09 | B |  | THREE NATURAL GAS FIRED COMBINED CYCLE POWER BLOCKS. EACH BLOCK CONSISTS OF TWO COMBUSTION TURBINES, TWO HEAT RECOVERY STEAM GENERATORS WITH DUCT BURNERS AND A STEAM TURBINE. TWO TURBINES WILL BE CAPABLE OF FIRING ULTRA LOW SULFUR DIESEL AS BACKUP FUEL. EACH COMBINED-CYCLE BLOCK WILL HAVE OUTPUT OF 840 MW. TURBINES ARE REPLACING TWO COAL-FIRED UTILITY BOILERS |  | COMBINED CYCLE COMBUSTION TURBINE | 15.21 | NATURAL GAS | 254 | MW | 6 TURBINES, 254 MW EACH (NOT INCLUDING STEAM RECOVERY), LIMITS ARE FOR EACH TURBINE (MITSUBISHI MODEL M501G). BACKUP FUEL FOR TWO TURBINES IS ULTRA-LOW SULFUR FUEL OIL | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 1.8 | PPM @ 15% O2 | 3-HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 1750 | 0 | N |  | FUEL OIL HAS OWN LAER LIMITS FOR CO AND VOC
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | MR. RANDY THOMPSON | (615) 532-6825 | randall.thompson@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Natural Gas-Fired Combustion Turbine with HRSG | 15.21 | Natural Gas | 1339 | MMBtu/hr | Turbine throughput is 1019.7 MMBtu/hr when burning natural gas and 1083.7 MMBtu/hr when burning No. 2 oil. Duct burner throughput is 319.3 MMBtu/hr. Duct burner firing will occur during natural gas combustion only. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | oxidation catalyst | 2 | PPMVD @ 15% O2 | 30 UNIT-OPERATING-DAY MOVING AVERAGE | BACT-PSD |  | N | 90 | U | 10 | PPMVD @ 15% O2 | 15 UNIT-OPERATING-DAY MOVING AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission limit #1 is for natural gas combustion, emission limit #2 is for No. 2 oil combustion.
GA-0138 | LIVE OAKS POWER PLANT | LIVE OAKS COMPANY, LLC | GLYNN | GA | 31525 | USA | BURT WALLACE | 478 943-2331 | BURT_1@BELLSOUTH.NET | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-127-0075-P-02-0 | 4911 | 221122 | UNKNOWN | 11/19/2008 &nbsp;ACT | 04/08/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | A |  | LIVE OAKS POWER PLANT PROPOSED FACILITY WILL OPERATE AS A FULLY DISPATCHABLE ELECTRIC GENERATING FACILITY. THE COMBINED CYCLE SYSTEM WILL UTILIZE TWO COMBUSTION TURBINES AND ONE STEAM TURBINE, CONFIGURED IN A TWO-ON-ONE ARRANGEMENT. THE HEAT CONTENT OF THE EXHAUST GASSES WIL BE RECOVERED BY A HEAT RECOVERY STEAM GENERATOR (HRSG), AND USED TO DRIVE A STEAM TURBINE. DURING PEAK LOADS A DUCT BURNER IN THE HRSG CAN BE FIRED TO AD ADDITIONAL HEAT ENERGY TO THE GAS TURBINE EXHAUST, INCREASING THE PRODUCTION OF STEAM SENT TO THE STEAM TURBINE. THE COMBUSTION TURBINES (CTs) SELECTED ARE SIEMENS MODEL SGT6-5000F. EACH COMBUSTION TURBINE WILL GENERATE 200 MW OF ELECTRIC POWER. THE GROSS ELECTRICAL CAPACITY OF THE COMBINED CYCLE FACILITY FIRING NATURAL GAS WILL THEN BE 600 MW. | PM10 74.3(+) EMISSIONS (T/YR) | COMBINED CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.21 | NATURAL GAS | 600 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | oxidation Catalyst | 2 | PPM@15%02 | 3 HOUR AVERAGE WO/O DUCT FIRING/CONDITIO | BACT-PSD | OPERATING PERMIT , SIP | U | 0 | N | 3.2 | PPM@15%02 | 3 HOUR AVERAGE W/DUCT FIRING/CONDITION 2 | 208 | T/YR | 12 CONSECUTVE MONTH AVERAGE/CONDITION 2. | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST. HEAT RATE LIMITED TO 6,793 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR MATTAWOMAN TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS MATTAWOMAN PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | oxidation Catalyst | 2 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE (EXCLUDING SU/SD) | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | WITH AND WITHOUT DUCT FIRING, EXCLUDING SU/SD
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS. HEAT INPUT LIMITED TO 6,802 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR KEYS TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS KEYS PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | oxidation Catalyst | 2 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | WITH AND WITHOUT DUCT FIRING, EXCEPT DURING PERIODS OF STARTUP/SHUTDOWN
TX-0590 | KING POWER STATION | PONDERA CAPITAL MANAGEMENT GP INC | HARRIS | TX | 77044 | USA | MARK CHRISOS | (781) 993-3036 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Katherine Stinchcomb (512) 239-1583 katherine.stinchcomb@tceq.texas.gov | PSDTX1125 | 4911 | 221119 | 110040440902 | 03/07/2008 &nbsp;ACT | 08/05/2010 &nbsp;ACT | 2011-08-26 | 2011-09-14 | A |  | Four combined-cycle natural gas-fired combustion turbines | State permit number 84289 Nonattainment permit number N75 | Turbine | 15.21 | natural gas | 1350 | MW | The plant will be designed to generate 1,350 nominal megawatts of power. There are two configuration scenarios: either four Siemens SGT6-5000F CTGs in combined-cycle mode (Scenario A) or four GE Frame 7FA CTGs in combined cycle mode (Scenario B). Scenario B also includes one or two auxiliary boilers. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | oxidation Catalyst | 2 | PPMVD AT 15% O2 | THREE-HOUR ROLLING | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies with or without duct burners
TX-0689 | CEDAR BAYOU ELECTRIC GENERATION STATION | NRG TEXAS POWER | CHAMBERS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 105810, PSDTX1308 | 4911 | 221112 | 110015743301 | 09/12/2012 &nbsp;ACT | 08/29/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power gereration station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the combined cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The new units will produce between 215-263 MW each. |  | Combined cycle natural gas turbines | 15.21 | Natural Gas | 225 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation Catalyst | 2 | PPM | ROLLING 12 MONTHS | BACT-PSD |  | N | 0 | U | 4 | PPM | 1HR AVG. | 0 |  |  | 0 | 0 | N
TX-0709 | SAND HILL ENERGY CENTER | CITY OF AUSTIN | TRAVIS | TX |  | USA | JOSEPH RAVI | (512) 322-6284 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez (512) 239-5220 Ruth.alvirez@tceq.texas.gov | 48106, PSDTX1012M2 | 4911 | 221112 | 110008975804 | 03/20/2015 &nbsp;ACT | 09/13/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | GE 7FA Natural Gas-fired Combined Cycle Turbine with DB fired HRSG |  | Natural gas-fired combined cycle turbines | 15.21 | Natural Gas | 173.9 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation Catalyst | 2 | PPM | 1HR AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0018 | LANGLEY GULCH POWER PLANT | IDAHO POWER COMPANY | PAYETTE | ID |  | USA |  | 2083885820 | TMAHLUM@IDAHOPOWER.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2009.0092 | 4911 | 221112 | UNKNOWN | 06/07/2009 &nbsp;ACT | 06/25/2010 &nbsp;ACT | 2010-08-09 | 2010-10-05 | A |  | ONE-ON-ONE COMBINED CYCLE PLANT CONSISTING OF (1) NATURAL GAS-FIRED COMBUSTION TURBINE (CT) AND (1) STEAM TURBINE. THE CT IS EQUIPPED WITH (1) HEAT RECOVERY STEAM GENERATOR (HRSG) AND DUCT BURNER. ANCILLARY EQUIPMENT INCLUDES (1) DIESEL-FIRED EMERGENCY GENERATOR, (1) DIESEL-FIRED FIRE PUMP, (1) WET COOLING TOWER, AND (6) DRY CHEMICAL STORAGE SILOS. |  | COMBUSTION TURBINE, COMBINED CYCLE W/ DUCT BURNER | 15.21 | NATURAL GAS (ONLY) | 2375.28 | MMBTU/H | SIEMENS SGT6-5000F COMBUSTION TURBINE (NGCT, CCGT) FOR ELECTRICAL GENERATION, NOMINAL 269 MW AND 2.1466 MMSCF/HR | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst | 2 | PPMVD | 3-HR ROLLING / 15% O2 | BACT-PSD |  | N | 0 |  | 24.5 | PPMVD | 3-HR ROLLING / 15% O2 DURING LL | 2510 | LB/H | 1-HR / 15% O2 DURING SU/SD | 0 | 0 | N |  | LIMITS APPLY TO COMBUSTION TURBINE AND DUCT BURNER COMBINED EMISSIONS. SECONDARY LIMIT APPLIES DURING STARTUP, SHUTDOWN, AND LOW-LOAD EVENTS (SU/SD/LL).
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #1 - combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr | two identical Siemens SGT6-5000F combined cycle turbines without duct firing, each at 2258 mmBtu/hr generating approx. 300 MW each. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPM | 30-DAY ROLLING AVG. @15% O2 | BACT-PSD |  | U | 95 | U | 552.4 | TON/YR | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #2 -combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPM | 30-DAY ROLLING AVERAGE | BACT-PSD |  | N | 95 | U | 552.4 | TON/YR | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | 552.4 ton/yr limit includes startup, shutdown and malfunction
PA-0286 | MOXIE ENERGY LLC/PATRIOT GENERATION PLT | MOXIE ENERGY LLC | LYCOMING COUNTY | PA |  | USA | KENT MORTON | (571) 594 - 0150 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MUHAMMAD Q. ZAMAN, ENVIRONMENTAL PROGRAM MANAGER NORTHCENTRAL REGION 208 West Third St, Suite 101 Williamsport, PA 17701 570-327-3648 | 41-00084A | 4911 | 221112 | 45-2015223-2 | 07/18/2012 &nbsp;ACT | 01/31/2013 &nbsp;ACT | 2013-03-27 | 2016-05-27 | A |  | This plan approval is for the construction of two natural-gas-fired combined cycle powerblocks where each powerblock consists of a combustion turbine and heat recovery steam generator with duct burner. The two powerblocks constructed pursuant to this plan approval will be either the two powerblocks rated 472 megawatts (MW) (P101 and P102) or the powerblocks rated 458 MW (P103 and P104). Additionally, this plan approval is for the construction of a 1464 bhp diesel-fired emergency generator, 460 bhp dieselfired fire pump, 1600 gallon diesel tank, 300 gallon diesel tank, two 15,000 gallon (each) lube oil tanks and ancillary electrical equipment. |  | Combined Cycle Power Blocks 472 MW - (2) | 15.21 | Natural Gas | 0 |  | Two natural-gas-fired combined cycle powerblocks where each powerblock consists of a combustion turbine and heat recovery steam generator with duct burner. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPMDV |  | BACT-PSD | OTHER | U | 0 | U | 109.3 | T/YR | EACH UNIT | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | Combined Cycle Combustion Turbine -Siemens turbine without Duct Burner | 15.21 | Natural gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each Siemens combustion turbine will be 2,356 MMBtu/hr(HHV) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPMVD@15% O2 | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 50 | U | 12 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITHOUT DUCT BURNER - GENERAL ELECTRIC | 15.21 | Natural Gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each General Electric combustion turbine will be 2,312 MMBtu/hr(HHV) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst | 2 | PPMVD@15%O2 | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 50 | N | 10.2 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITH DUCT BURNER - GENERAL ELECTRIC | 15.21 | Natural gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each General Electric combustion each turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 MMBtu/hr duct burner | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst | 2 | PPMVD@15%O2 | 3-HR ROLLING AVERAGE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 50 | N | 11.1 | LB/H | AVEARAGE OF THREE ONE HOUR TESTS | 0 |  |  | 0 | 0 | N
TX-0767 | LON C. HILL POWER STATION | LON C. HILL, L.P. | NUECES | TX |  | USA | MATTHEW LINDSEY | 713-358-9734 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem, 512-239-1310, Tzvi.Shalem@tceq.texas.gov | 114911 AND PSDTX1380 | 4911 | 221122 | 110000501127 | 07/15/2015 &nbsp;ACT | 10/02/2015 &nbsp;ACT | 2015-09-23 | 2016-07-06 | A |  | The Lon C. Hill Power Station (LCHP) will include two natural gas-fired combined cycle combustion turbines (CTGs) equipped with dry low NOx burners (DLNs), heat recovery steam generators (HRSG), and natural gas-fired duct burners (DBs). Ancillary equipment includes evaporative coolers or inlet chillers, a single steam turbine (ST), auxiliary boiler, emergency generator, firewater pump, two cooling towers, oil water separator, degreaser, two diesel storage tanks, gasoline storage tank, selective catalytic reduction (SCR) and ammonia (NH3) handling systems including an NH3 storage tank, and two water tanks. The LCHP will be a 2x1 combined cycle power plant consisting of two CTGs, two HRSGs and one ST. The CTGs and ST will be one of two options: two Siemens SCC6-5000 CTGs and a SST6-5000 ST, or two General Electric 7FA CTGs and a D-11 ST. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 195 | MW | Two power configuration options authorized Siemens â€“ 240 MW + 250 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 195 MW + 670 MMBtu/hr duct burner | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPM | ROLLING 24-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0773 | FGE EAGLE PINES PROJECT | FGE EAGLE PINES, LLC | CHEROKEE | TX |  | USA | EMERSON FARRELL | 281-407-7749 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, 512-239-1095, Erik.Hendrickson@tceq.texas.gov | 131316, PSDTX1454, AND GHGPSDT | 4911 | 221112 | UNKNOWN | 09/10/2015 &nbsp;ACT | 11/04/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | The FGEEP Project will include three natural gas-fired combined cycle (NGCC) power blocks, each block comprised of two gas-fired combustion turbines, two supplemental fired duct burners (DBs) heat recovery steam generators (HRSGs), and one steam turbine. FGEEP selected Alstom GT36 combustion turbines (CTs), each nominally rated at 321 megawatts (MW). Each HRSG is equipped with DBs that will have a maximum design heat input capacity of 799 million British thermal units per hour (MMBtu/hr). The CTs and DBs are fueled with pipeline quality natural gas. Each power block will also have a steam turbine generator designed to produce approximately 502 MW with the additional duct firing. Each of the three blocks will include the following ancillary equipment: one multi-cell condenser/cooling tower, one emergency generator, one firewater pump, two diesel storage tanks, and pressurized aqueous ammonia storage tanks. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 321 | MW | Alstom GT36 combustion turbines (321 MW)+ 799 million British thermal units per hour (MMBtu/hr) duct burner | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPM | 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 |  |  | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2017-11-17 | A |  | Combinec Cycle Electric Generating Plant | 103839 | combined cycle turbine | 15.21 | natural gas | 700 | MW | The generating equipment consists of two natural gas-fired combustion turbines (CTs), each exhausting to a fired heat recovery steam generator (HRSG) to produce steam to drive a shared steam turbine generator. The steam turbine is rated at 271 MW of electric output. Three models of combustion turbines are being considered for this site: the General Electric 7FA.05, the Siemens SGT6-5000F(4), and the Siemens SGT6-5000F(5). The final selection of the combustion turbine will not be made until after the permit is issued. Plant output will range between 637 and 735 MW, depending on the model turbine selected. Duct Burners are rated at 750 MMBtu/hr each. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 2 | PPMVD | 3-HR ROLL AVG, 15% OXYGEN, 80-100% LOAD | BACT-PSD |  | N | 0 | U | 4 | PPMVD | 3-HR ROLL AVG, 15% OXYGEN, 60-80% LOAD | 0 |  |  | 0 | 0 | N
*TX-0660 | FGE TEXAS POWER I AND FGE TEXAS POWER II | FGE POWER LLC | MITCHELL | TX | 79565 | USA | EMERSON FARRELL | 281-362-2830 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX1364 | 3511 |  |  | 05/06/2013 &nbsp;EST | 03/24/2014 &nbsp;ACT | 2014-06-13 | 2017-11-17 | U |  | Electric Generating Utility | TCEQ Permit No. 110025 | Alstom Turbine | 15.21 | Natural Gas | 230.7 | MW | Four (4) Alstom GT24 CTGs, each with a HRSG and DBs, max design capacity 409 MMBtu/hr | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst | 2 | PPMVD | CORRECTED TO 15% O2, ROLLING 3 HR AVE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2018-05-11 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 2 | PPMVD | 15% O2 3 HOUR AVERAGE | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 2 | PPMVD | 3 HOURS | BACT-PSD |  |  | 90 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LIMIT ONE IS USED WITH CONDITIONS AT 15% O2 WITH USING DUCT BURNERS.
NJ-0080 | HESS NEWARK ENERGY CENTER | HESS NEWARK ENERGY CENTER, LLC | ESSEX | NJ | 7105 | USA | PETER HAID | (774) 750-7088 | PHAID@HESS.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Supervisor: Yogesh Doshi - yogesh.doshi@dep.state.nj.us Phone: 609-633-7249 Permit Evaluator: Michael Hogan - michael.hogan@dep.state.nj.us. Phone: (609)-633-1124 | 08857/BOP110001 | 4911 | 221112 | 110044839903 | 12/10/2011 &nbsp;ACT | 11/01/2012 &nbsp;ACT | 2013-04-04 | 2018-04-17 | A |  | Combined Cycle Electric Generating Facility HESS Newark Energy Center (Hess-NEC), proposed at City of Newark (Essex County), New Jersey, would be a new, highly efficient, 655 MW combined-cycle power generating facility. Hess-NEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,320 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, a 12-cell mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Facility-wide Greenhouse Gas (GHG) emissions as CO2e emissions = 2,003,654 tpy | Combined cylce turbine with duct burner | 15.21 | natural gas | 39463 | mmcubic ft/year* | * Annual throughput is for 2 turbines, 2 duct burners and 1 auxiliary boiler | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst | 2 | PPMVD | 3-HR ROLLING AVERAGE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | U | 90 | N | 10.2 | LB/H | AVERAGE OF THREE TESTS | 0 |  |  | 0 | 0 | N
PA-0278 | MOXIE LIBERTY LLC/ASYLUM POWER PL T | MOXIE ENERGY LLC | BRADFORD COUNTY | PA |  | USA | KENT J MORTON | (571) 594 - 0150 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MUHAMMAD Q. ZAMAN, ENVIRONMENTAL PROGRAM MANAGER, NORTHCENTRAL REGION | 08Â·00045A | 491 | 221112 | 45-2015223-1 | 09/26/2011 &nbsp;ACT | 10/10/2012 &nbsp;ACT | 2012-12-03 | 2015-04-03 | A |  |  | The project consists of two identical 1 x 1 power blocks, and each block includes a combustion gas turbine and a steam turbine. Each combined-cycle process will also include a heat recovery steam generator and supplemental duct burners. Additionally, one diesel-fired emergency generator, one diesel-fired fire water pump, two diesel fuel storage tanks, two lube oil storage tanks, and one aqueous ammonia storage tank were proposed to be constructed and operated. Each combined-cycle process will be rated at 468 MW or less. | Combined-cycle Turbines (2) - Natural gas fired | 15.21 | Natural Gas | 3277 | MMBTU/H | Two combine cycle Turbines, each with a combustion turbine and heat recovery steam generator with duct burner. Each combined-cycle process will be rated at 468 MW or less. The heat input rating of each combustion gas turbine is 2890 MMBtu/hr (HHV) or less, and the heat input rating of each supplemental duct burner is equal to 387 MMBtu/hr (HHV) or less. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPMVD | @15% O2 | BACT-PSD |  | U | 80 | U | 15.3 | LB/H | 468 MW POWERBLOCK | 2 | PPMVD | @15% O2 | 0 | 0 | N |  | 1-hr CEMS monitoring and combustion controls for lean combustion. Other Limit: 15.0000 LB/H 454 MW POWERBLOCK
TX-0546 | PATTILLO BRANCH POWER PLANT | PATTILLO BRANCH POWER COMPANY LLC | FANNIN | TX |  | USA |  |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | RANDY HAMILTON RHAMILTO@TCEQ.STATE.TX.US | 83642 | 4911 | 221122 | TX0121997 | 12/13/2007 &nbsp;ACT | 06/17/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | 1400 MW POWER PLANT. 4 NATURAL GAS FIRED TURBINES PLUS HEAT RECOVERY STEAM GENERATORS (HRSG) | PSDTX1115 | ELECTRICITY GENERATION | 15.21 | NATURAL GAS | 350 | MW | EACH TURBINE/HRSG WILL BE DESIGNED TO OUTPUT 350 MW. TURBINES BEING CONSIDERED FOR THE PROJECT ARE GE 7FA, GE 7FB, AND SIEMENS SGT6-5000F. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 2 | PPMVD | @ 15% O2, 3-HR ROLLING AVG | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | (2) combined cycle turbines | 15.21 | natural gas | 650 | MW | The specific equipment includes two combustion turbines (CTs) connected to electric generators, producing between 183 and 232 MW of electricity, depending on ambient temperature and the selected CT. The two HRSGs use duct burners rated at 750 MMBtu/hr each to supplement the heat energy from the CTs. The steam from the two HRSGs is combined and routed to a single steam turbine driving a third electric generator with an electricity output capacity of 271 MW. Depending on the selected CT, total plant output at 59Â°F is between 637 MW and 735 MW. The applicant is considering three models of CT; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) Siemens SGT6-5000F(4); or (3) Siemens SGT6-5000F(5). | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 2 | PPMVD | @15% O2, 3-HR ROLLING, 80-100% LOAD | BACT-PSD |  | N | 0 | U | 4 | PPMVD | @15% O2, 3-HR ROLLING, 60-80% LOAD | 0 |  |  | 0 | 0 | N
TX-0713 | TENASKA BROWNSVILLE GENERATING STATION | TENASKA BROWNSVILLE PARTNERS, LLC | CAMERON | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 108411 PSDTX1350 | 4911 | 221112 | unknown | 02/21/2013 &nbsp;ACT | 04/29/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | Tenaska proposes a new electric power plant, using combined cycle gas turbine (CCGT) technology and fueled by pipeline quality natural gas. The proposed permit authorizes two CTs (2x1 CCGT), although the final design selected by Tenaska may only consist of one CT (1x1 CCGT). |  | (2) combined cycle turbines | 15.21 | natural gas | 274 | MW | Each CTG is site-rated at 274 MW gross electric output at 62Â°F ambient temperature. At this condition, two HRSGs with full duct burner firing produce enough steam to generate an additional 336 MW, for a total of 884 MW gross, or with about 5% losses, about 840 MW net electric output. Under summertime conditions, the net output is approximately 800 MW with the 2x1 CCGT configuration or about 400 MW with the 1x1 CCGT configuration. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 2 | PPMVD | @15% O2, 24-HR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | Combustion Turbine | 15.21 | Natural Gas | 360 | MW | This process represents the GE option for the project - One GE 7FA.05 natural gas-fired combustion turbine generator with an 820.5 MMBTUH duct burner. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practice. | 2 | PPMVD@15%O2 | 3-HR | BACT-PSD | N/A | U | 0 | U | 14 | LB/HR | 3-HR | 0 |  |  | 0 | 0 | N
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two Combine Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 3001.57 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. . (Operational limits are for each CCCT NG-fired with duct burner) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 2 | PPMDV @ 15% O2 |  | BACT-PSD |  | U | 0 | U | 1189.8 | TONS | YR | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative emissions from both CCCT in any 12-month period
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064098541 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine With Duct Burner | 15.21 | Natural Gas | 3727 | MMBtu/hr | DLN burner, SCR, Oxidation Catalyst and shall maintain and operate the sources and associated air cleaning devices in accordance with good engineering practice. shall install, certify, maintain and operate continuous emission monitoring systems (CEMS) for nitrogen oxides, carbon monoxide, carbon dioxide, and ammonia emissions on the exhaust of each combined-cycle powerblock. Emissions limits are for each combustion turbine/duct burner block. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 2 | PPMDV @ 15% O2 |  | BACT-PSD | NSPS | U | 0 | U | 15.6 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 105.1 tpy 12-month rolling basis
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 725 | MEGAWATT | TWO GENERAL ELECTRIC (GE) F-CLASS ADVANCED COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 725 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES | 2 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE, EXCLUDING SU/SD | BACT-PSD |  | U | 0 | U | 530 | LB | CEM | 0 |  |  | 0 | 0 | N |  | EMISSION #1 IS WITH AND WITHOUT DUCT FIRING EMISSION #2 APPLIES TO EACH STARTUP/SHUTDOWN EVENT
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas without Duct Burner | 15.21 | Natural Gas | 8040 | H/YR |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES | 2 | PPMVD@15% O2 | 3 H ROLLING AV BASED ON ONE H BLOCK AV | BACT-PSD | OPERATING PERMIT | N | 69 | N | 15.3 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY CEMS AND STACK TESTING
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas with Duct Burner | 15.21 | natural gas | 4000 | h/yr |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst and good combustion practices | 2 | PPMVD@15%O2 | 3 H ROLLING AV BASED ON ONE H BLOCK AV | BACT-PSD | OPERATING PERMIT | N | 69 | N | 18.1 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY CEMS AND STACK TESTING
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | COMBUSTION TURBINE | 15.21 | NATURAL GAS | 360 | MW | This process represents the Siemens option for the project - One Siemens SGT6-5000F5 natural gas-fired combustion turbine generator with an 820.3 MMBTUH duct burner. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES. | 2 | PPMVD@15% O2 | 3-HR | BACT-PSD | N/A | U | 0 | U | 14.5 | LB/HR | 3-HR | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITH DUCT BURNER - SIEMENS | 15.21 | Natural Gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two Siemens turbines and two associated duct burners) The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst and use of only natural gas a clean burning fuel | 2 | PPMVD | 3-HR ROLLING AVE BASED ON 1-HR BLOCK AVE | BACT-PSD | OPERATING PERMIT | N | 50 | N | 14 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | 0 |  |  | 0 | 0 | N
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG with duct burner NG only | 15.21 | Natural Gas | 3338 | MMBtu/hr | Emission limits are for each turbine operating with duct burner and do not include startup/shutdown emissions. Tons per year limits is a cumulative value for all three CCCT. CEMS for NOx, CO, and O2. Each CCCT and duct burner have 5 operational scenarios: 1 CCCT with duct burner fired - fueled by NG only 2 CCCT with duct burner fired - fueled by NG blend with ethane 3 CCCT without duct burner fired - fueled by NG only 4 CCCT without duct burner fired - fueled by NG blend with ethane 5 CCCT without duct burner fired - fueled by ULSD (Limited to emergency use only) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst operated at all steady state operating loads and good combustion practices | 2 | PPMDV @ 15% O2 |  | BACT-PSD | NSPS | U | 0 | U | 84.9 | TONS | YEAR | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 2 | PPMVD | @15% O2, 1-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 7.65 | LB/H | 1-HR AVG (NO DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | Natural Gas | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 2 | PPMVD | @15% O2, 1-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 7.65 | LB/H | 1-HR AVG (NO DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 2 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 10 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 2 | PPMVD | @15% O2, 1-HR AVG (W/ DUCT FIRING) | BACT-PSD |  | U | 0 | U | 10 | LB/H | 1-HR AVG (W/ DUCT FIRING) | 0 |  |  | 0 | 0 | N
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Combustion turbine with duct burner | 15.21 | Natural gas | 3304.3 | MMBtu/hr | Limits are for each CCCT and yearly limits are for cumulative turbine and duct burner. Duct burner throughput is 637.9 MMBtu/hr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst, combustion controls, exclusive natural gas | 2 | PPMDV @ 15 % O2 |  | BACT-PSD |  | U | 0 | U | 84.9 | TONS | YEAR | 0 |  |  | 0 | 0 | N |  | CO CEMS (1-hour average)
NJ-0079 | WOODBRIDGE ENERGY CENTER | CPV SHORE, LLC | MIDDLESEX | NJ | 7095 | USA | MARK TURNER | (415)293-1463 | MTURNER@CPV.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Mr. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS, yogesh.doshi@dep.state.nj.us; phone 609-633-7249 | 18940 - BOP110003 | 4911 | 221112 | 110055590953 | 10/12/2011 &nbsp;ACT | 07/25/2012 &nbsp;ACT | 2012-11-27 | 2018-04-17 | A |  | Woodbridge Energy Center (WEC), proposed at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, would be a new, highly efficient, 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,307 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, one small dew point fuel gas heater (fuel gas heater), a mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Other Permitting Information: Facility-Wide Greenhouse Gas (GHG) emissions as CO2e emissions= 2,073,645 tons per year | Combined Cycle Combustion Turbine w/o duct burner | 15.21 | natural gas | 40297.6 | mmcubic ft/year | The above natural gas use is combined for two GE 7FA CC turbines (each with a maximum heat input of 2, 307 MMBtu/hr)and two duct burners (each with a maximum heat input of 500 MMBtu/hr) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst, good combustion practices and use only natural gas a clean burning fuel | 2 | PPMVD | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | U | 77 | Y | 10.2 | LB/H | AVERAGE OF THREE TESTS | 0 |  |  | 0 | 0 | N |  | Compliance Verified by Stack test in 2016, CO Emission limit1 achieved was 0.0 PPMVD; Emission limit 2 achieved was 0.0 LB/H (no CO Emissions)
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064098541 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine without Duct Burner | 15.21 |  | 0 |  |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst, good engineering practice | 2 | PPMDV @ 15% O2 |  | BACT-PSD | NSPS | U | 0 | U | 14.7 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 105.1 tpy on 12-month rolling basis
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 3 | PPMVD | @15% O2, 3-HR ROLLING AVG | BACT-PSD |  | U | 0 | U | 17.9 | LB/H | 3-HR ROLLING AVG | 0 |  |  | 0 | 0 | N
*PA-0298 | FUTURE POWER PA/GOOD SPRINGS NGCC FACILITY | FUTURE POWER PA INC | SCHUYLKILL | PA | 17980 | USA | JAMES PALUMBO | 570-342-5200 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MARK J. WEJKSZNER NORTHEAST REGION AIR PROGRAM MANAGER 2 Public Square Wilkes-Barre, PA 18711 570-826-2357 | 54-00082A | 4911 | 221112 | 26-3703407-1 | 05/03/2013 &nbsp;ACT | 03/04/2014 &nbsp;ACT | 2014-04-17 | 2018-03-23 | A |  | Natural gas-fired combined-cycle electric generation facility that is designed to generate up to 346 MW nominal, using a combustion turbine generator and a heat recovery steam generator that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. The Turbine is rated at 2,267 MMBTU/hr HHV (2,042 MMBTU/hr LHV). The Duct burner is rated at 134.3 MMBTU/hr HHV (120 MMBTU/hr LHV). The proposed project will also include a diesel engine-driven emergency generator; a diesel engine-driven firewater pump; a multi-cell evaporative cooling tower; and associated emission control systems, tanks, and other plant equipment. |  | Turbine, COMBINED CYCLE UNIT (Siemens 5000) | 15.21 | Natural Gas | 2267 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 3 | PPMVD | @ 15% OXYGEN | BACT-PSD | NSPS | U | 0 | U | 17.9 | LB/H | WITH DUCT BURNER | 84.8 | T/YR | BASED ON A 12-MONTH ROLLING TOTAL | 0 | 0 | N
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002049328 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | COMBINED CYCLE TURBINE GENERATORS (UNITS 6A &amp; 6B) | 15.21 | NATURAL GAS | 7146 | MMBTU/H | TURBINES ALSO PERMITTED TO BURN NO. 2 FUEL OIL AND ULTRA LOW SULFUR DIESEL. FUEL OIL USE IS LIMITED TO 1000 HOURS PER YEAR. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES | 3 | PPMVD @ 15% O2 | HOURLY AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 3 | PPMVD @ 15% O2 | HOURLY AVERAGE | 0 | 0 | N |  | CO MONITORED USING CEMS. 3 PPMVD @ 15% O2 LIMIT APPLIES WHEN OPERATING W/ AND W/O THE DUCT BURNER AND WHEN FIRING FUEL OIL. STARTUP/SHUTDOWN: PROGRESS THROUGH THE SU/SD EVENT AS QUICKLY AS POSSIBLE WHILE FOLLOWING THE MANUFACTURER'S RECOMMENDED PROCEDURES. SU/SD OPERATIONS LIMITED TO 1302 HR/YR. BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE).
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 3 | PPMVD | @15% O2, 1-HR AVG (W/ DUCT BURNING) | BACT-PSD |  | U | 0 | U | 13.35 | LB/H | 1-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 3 | PPMVD | @15% O2, 1-HR AVG (W/ DUCT BURNING) | BACT-PSD |  | U | 0 | U | 13.35 | LB/H | 1-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | Mitsubishi M501-GAC combustion turbine, combined cycle configuration with duct burner. | 15.21 | natural gs | 2988 | MMBTU/H | or ULSD; Duct burner 499 MMBtu/hr, natural gas | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst; Limit the time in startup or shutdown. | 3.3 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON NG | BACT-PSD |  | U | 0 | U | 9 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON ULSD | 0 |  |  | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055426409 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Four combined cycle combution turbines | 15.21 | natural gas | 373 | MMBTU/H | Three GE, LMS6000 PF, natural gas-fired, combined cycle CTG, rated at 373 MMBtu per hour each, based on HHV and one (1) HRSG each with no Duct Burners | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation Catalyst | 4 | PPMVD AT 15% O2 | 1-HR AVE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 3.3 | LB/H | 30-DAY ROLLING AVE | 0 |  |  | 0 | 0 | N |  | startup limit: 140.0 lb per event shutdown limit: 15.0 lb per event compliance is monitored with continuous emissions monitors
TX-0600 | THOMAS C. FERGUSON POWER PLANT | LOWER COLORADO RIVER AUTHORITY | LLANO | TX | 7657 | USA | JOE BENTLEY | 512-473-3272 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tan Nguyen 512-239-3445 tan.nguyen@tceq.texas.gov | PSDTX1244 | 4911 | 221112 | 110035336222 | 10/29/2010 &nbsp;ACT | 09/01/2011 &nbsp;ACT | 2011-09-02 | 2011-09-14 | B |  | Power Plant. Two natural gas-fired combined cycle turbine generators (GE 7FA) with unfired HRSG | 93938 | Natural gas-fired turbines | 15.21 | natural gas | 390 | MW | (2) GE7FA at 195 MW each, (1) steam turbine at 200 MW. Each turbine is equipped with an unfired heat recovery steam generator (HRSG), which provides steam for the steam turbine. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | oxidation Catalyst | 4 | PPMVD | ROLLING 3-HR AT 15% OXYGEN /LOAD >= 60% | BACT-PSD |  | N | 0 | U | 6 | PPMVD | ROLLING 3-HR AT 15% OXYGEN /LOAD < 60% | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst | 4 | PPMV | 24-H ROLL AVG DET. EACH H TURBINE OPERAT | BACT-PSD | N/A | U | 0 | U | 3159 | LB/H | 4-H ROLL AVG | 0 |  |  | 0 | 0 | N |  | The first limit is 4 ppmv based on a 24-H rolling average as determined each hour the turbine operates;/dry at 15% O2; except during startup and shutdown; each CTG/HRSG. The second limit is 3159 LB/H based on a 4-H rolling average as determined each hour the turbine operates. Applied on a per block basis (each CTG/HRSG pair combined). Combustion control and catalytic oxidation system (COS) selected based on outlet concentration, not% control efficiency. COS not fully functional at lower than optimum catalyst temperatures during startup/shutdown. CEMS monitoring.
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 4 | PPM | HOURLY | BACT-PSD | NSPS | N | 0 | U | 2 | PPM | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N |  | NSPS KKKK AND TTTT
TX-0789 | DECORDOVA STEAM ELECTRIC STATION | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas.gov | 107569 AND PSDTX1432 | 4911 | 221112 | 110008149217 | 12/23/2015 &nbsp;ACT | 03/08/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | The DeCordova Station will consist of two combustion turbine generators (CTGs) operating in simple cycle or combined cycle modes. The gas turbines will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE). Simple cycle operations limited to 2,500 hr/yr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 4 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP01) | 15.21 | Natural Gas | 40 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 4 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD |  | U | 0 | U | 3.7 | LB/H | 30-DAY ROLLING AVERAGE | 32 | T/YR |  | 3307 | 5108 | N | 2011
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP02) | 15.21 | Natural Gas | 40 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 4 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD |  | N | 0 | U | 3.7 | LB/H | 30-DAY ROLLING AVERAGE | 32 | T/YR |  | 3307 | 5108 | N | 2011
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Combustion Turbine | 15.21 | natural gas | 87 | MW | The exhaust heat from the turbine will be used to heat a heating medium which is used to regenerate rich amine from the acid gas removal system. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 4 | PPMVD | @15% O2, 3 HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0710 | VICTORIA POWER STATION | VICTORIA WLE L.P. | VICTORIA | TX |  | USA | GARY CLARK | (361) 947-9934 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | 108258 PSDTX1348 | 4911 | 221112 | 110000501154 | 02/14/2013 &nbsp;ACT | 12/01/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | The facility is currently authorized under Standard Permit No. 80878 and several Permits by Rule (PBR), including Â§106.263 for maintenance, startup, and shutdown (MSS) (PBR Registration No. 94387) and Title V Permit No. O-35. Victoria proposes to install an additional natural gas-fired turbine (GT) and HRSG with duct burners at the Victoria Station. The resulting new facility will be a combined cycle generating facility in a 2x2x1 configuration (two combustion turbines, two HRSGs with duct burners, and one steam turbine). |  | combined cycle turbine | 15.21 | natural gas | 197 | MW | General Electric 7FA.04 at 197 MW nominal ouput. The duct burners will be capable of a maximum natural gas firing rate of up to 483 MMBtu/hr (HHV). The duct burners may be fired additional hours; however, total annual firing will not exceed the equivalent of 4,375 hours at maximum capacity per duct burner. The available capacity of the existing steam turbine will be increased from 125 MW in its existing 1x1x1 configuration to approximately 185 MW in the 2x2x1 configuration. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 4 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0712 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER COMPANY | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | (205) 257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tzvi Shalem 512-239-1310 tzvi.shalem@tceq.texas.gov | 111393 PSDTX1368 | 4911 | 221112 | 110007199735 | 06/27/2013 &nbsp;ACT | 11/20/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | Southern Power Company (SPC) is proposing to construct an electric generating facility near Trinidad, Henderson County, Texas. The Trinidad Generating Facility (TGF) will include a natural gas-fired combined cycle combustion turbine generator (CTG) equipped with heat recovery steam generator (HRSG) and duct burners (DB). |  | combined cycle turbine | 15.21 | natural gas | 497 | MW | The facility will consist of a Mitsubishi Heavy Industries (MHI) J model gas fired combustion turbine nominally rated at 497 megawatts (MW) equipped with a HRSG and DB with a maximum design capacity of 402 million British thermal units per hour (MMBtu/hr). The gross nominal output of the CTG with HRSG and DB is 530 MW. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 4 | PPMVD | @15% O2, 24-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0714 | S R BERTRON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | HARRIS | TX |  | USA | CRAIG ECKBERG | (713) 537-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | 102731 PSDTX1294 | 4911 | 221112 | 110034988413 | 05/10/2012 &nbsp;ACT | 12/19/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | NRG Texas is proposing to construct an additional electric power generation station at the Bertron Power Project which will generate electric power for sale on the wholesale electric market. The Bertron Power Project will include two power blocks that can be operated in combined cycle mode. |  | (2) combined cycle turbines | 15.21 | natural gas | 240 | MW | The gas turbines will be one of three options: (1) Two Siemens Model F5 (SF5) CTGs each rated at nominal capability of 225 megawatts (MW). Each CTG will have a duct fired HRSG with a maximum heat input of 688 million British thermal units per hour (MMBtu/hr). (2) Two General Electric Model 7FA (GE7FA) CTGs each rated at nominal capability of 215 MW. Each CTG will have a duct fired HRSG with a maximum heat input of 523 MMBtu/hr. (3) Two Mitsubishi Heavy Industry G Frame (MHI501G) CTGs each rated at a nominal electric output of 263 MW. Each CTG will have a duct fired HRSG with a maximum heat input of 686 MMBtu/hr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 4 | PPMVD | @15% O2, ONE HOUR | BACT-PSD |  | N | 0 | U | 2 | PPMVD | @15% O2, ROLLING 12-MONTH | 0 |  |  | 0 | 0 | N
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041470431 | 04/18/2014 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2016-05-16 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 4 | PPMVD @ 15% O2 | 3-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Permit requires downward adjustment to CO limits based on first 30 months of operation
CA-1209 | HIGH DESERT POWER PROJECT | HIGH DESERT POWER PROJECT LLC | SAN BERNADINO | CA | 92394 | USA | JON BOYER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 98-01 | 4911 | 221112 | 110014461420 | 09/25/2009 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-11 | 2014-01-15 | C | http://www.epa.gov/region09/air/permit/r9-permits-issued.html | 720 MW NATURAL GAS FIRED POWER PLANT | RBLC Management: There were many duplicate pollutant records Editor repeated all emission limits for each of the 3 types of operation, Start-up, Normal, and Shutdown. Record was edited and duplicate records were deleted. Original Note: PSD Permit amended to change the design of the power plant. These changes include a modification in the turbine configuration from 3x3x3 (i.e., three combustion turbines (CT), three heat recovery steam generators (HRSG), and three steam turbine generators (STG)) to a 3x3x1 configuration, reconfiguration of the cooling tower from three towers to one, addition of a diesel firewater pump engine, modification of the stack location, elevation, and diameter, and modification in the physical dimensions of the cooling tower, steam turbine, and HRSG structure. The terms and conditions included in the PSD permit issued February 15, 2001, and the modeling analyses on which the original determinations were based, remain valid and in effect. | COMBUSTION TURBINE GENERATORS (NORMAL OPERATION) | 15.21 | NATURAL GAS | 190 | MW | THREE (3) COMBUSTION TURBINE GENERATORS AT 190 MW EACH AND EQUIPPED WITH A 160 MMBTU/HR DUCT BURNER AND HRSG | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 4 | PPMVD | @15% O2, 24-HR AVG | BACT-PSD |  | U | 0 | U | 17.53 | LB/H | 24-HR AVG | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 4 | PPM | 24-H ROLL. AVG., NOT STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 85 | N | 5.31 | LB/H | 24-H ROLL. AVG., NOT STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | The CO limits apply to EACH CTGHRSG based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. The first CO limit is 4 ppmdv at 15%O2. Startup is defined as the period of time from synchronization to the grid (generator breaker closed) until the unit reaches steady state operation (loads greater than 50 percent of design capacity). Shutdown is defined as that period of time from the initial lowering of the turbine output below 50 percent of full operating load, with the intent to shut down, until the point at which the generator breaker opens.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 4 | PPM | EACH EU; 24-H ROLL AVG EXCEPT | BACT-PSD | SIP | N | 85 | N | 5.31 | LB/H | EACH EU; 24-H ROLL AVG EXCEPT | 0 |  |  | 0 | 0 | N |  | The emission limits above are for each CTG/HRSG and are as follows: 1) 4 ppmvd at 15% O2 based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. 2) 5.31 LB/H based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. There are separate limits for each of these emission units during startup and shutdown which will be identified as a separate process in this determination. Startup is defined as the period of time from synchronization to the grid (generator breaker closed) until the unit reaches steady state operation (loads greater than 50 percent design capacity). Shutdown is defined as that period of time from the initial lowering of the turbine output below 50 percent of full operating load, with the intent to shut down, until the point at which the generator breaker opens.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 4 | PPM | 24-H ROLL.AVG., EXCEPT STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 0 | N | 17.4 | LB/H | 24-H ROLL.AVG., EXCEPT STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above is 4 ppmvd at 15% O2. Also, each of the emission limits above are based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. There is a separate limit for each startup/shutdown event, which will be entered as a separate 'Process' in the RBLC determination.
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Simple Cycle Electrical Generation Gas Turbines 15.210 | 15.21 | natural gas | 34 | MW | Nine GE PGT25+G4 gas turbines for electrical generation at the site at 34 MW/turbine | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 9 | PPM | ROLLING 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0727 | CEDAR BAYOU ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | CHAMBERS COUNTY | TX |  | USA | LINDSAY LITTLE | (713) 357-5291 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem, 512-239-1310, tzvi.shalem@tceq.texas.gov | 80289 & PSDTX1082M1 | 4911 | 221112 | 110037869456 | 07/09/2014 &nbsp;ACT | 03/31/2015 &nbsp;ACT | 2015-03-30 | 2016-05-16 | C |  | NRG operates the Cedar Bayou 4 Electric Generating Station in Chambers County, consisting of two natural gas-fired combustion turbines, Emission Point Numbers (EPNs) CBY41 and CBY42, and associated ancillary equipment. NRGâ€™s amendment application requests an increase in the annual carbon monoxide (CO) and a small increase in the volatile organic compounds (VOC) emission rates for both turbines, due to an increase in the number of startups per year. NRG requests to install oxidation catalysts to each unit. |  | Combined cycle turbines | 15.21 | Natural Gas | 187 | MW/turbine |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalysts | 15 | PPMVD | 15%O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
[40 empty] | Range Low | 0.9 | PPMV
[40 empty] | Range High | 15 | PPMV
[40 empty] | Mean | 2.6372 | PPMV
[40 empty] | Median | 2 | PPMV
[40 empty] | Mode | 2 | PPMV

## Good Combustion and Clean Fuels
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
NY-0104 | CPV VALLEY ENERGY CENTER | CPV VALLEY LLC | ORANGE | NY | 10940 | USA |  |  |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-335600136/00001 | 4911 | 221112 | 110043332471 | 08/01/2013 &nbsp;ACT | 08/01/2013 &nbsp;ACT | 2017-08-25 | 2017-09-28 | A |  | CPV Valley Energy Center is a 680 MW combined cycle electric generating facility located in Middletown, NY. The combustion turbines are rated at 2,234 MMBTU/H firing natural gas and 2,145 MMBTU/H firing diesel fuel. The duct burners are rated for 500 MMBTU/H firing natural gas. In addition to the turbines their emission limits for the auxiliary boiler (73.5 MMBTU/H), emergency generator, fire pump, and gas heater. | State Facility Permit | Turbines and duct burners - NG | 15.21 | natural gas | 0 |  | Combined cycle units heat rate 7,605 BTU/KW-H (HHV) or less without duct burner firing to achieve design thermal efficiency of 57.4% (LHV). | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Good combustion practice and oxidation catalyst. | 2 | PPMVD @ 15% O2 | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 2.0 PPVD @15% O2 without duct burners 3.4 PPVD @15% O2 with duct burners Applies to all operating loads, except during startup and shutdown.
TX-0618 | CHANNEL ENERGY CENTER LLC | CHANNEL ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX955M1 | 4911 | 221112 | 110034690564 | 11/03/2011 &nbsp;ACT | 10/15/2012 &nbsp;ACT | 2012-10-24 | 2014-01-06 | B |  | Combustion turbine (Siemens 501F)/duct burners (475 MMBtu/hr) with heat recovery steam generator | 42179 and N021M1 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | The turbine is a Siemens 501F rated at a nominal 180 MW and the duct burner will have a maximum design heat input of 475 MMBtu/hr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion | 4 | PPMVD | @ 15% O2 ON A 24-HR ROLLING AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0619 | DEER PARK ENERGY CENTER | DEER PARK ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX979M2 | 4911 | 221112 | 110017743254 | 09/01/2011 &nbsp;ACT | 09/26/2012 &nbsp;ACT | 2012-10-25 | 2013-09-25 | B |  | The Deer Park Energy Center is a combined cycle cogeneration facility consisting of five Siemens/Westinghouse 501F combustion turbine generators, each with a 725 MMBtu/hr duct burner and heat recovery steam generator. | 45642 and N036M2 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | natural gas-fired combined cycle turbine generator with a heat recovery steam generator equipped with a duct burner. The turbine is a Siemens 501F rated at a nominal 180 megawatts and the DB will have a maximum design rate capability of 725 million British thermal units per hour | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion | 4 | PPMVD | @15% O2, 24-HR ROLLING AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0620 | ES JOSLIN POWER PLANT | CALHOUN PORT AUTHORITY | CALHOUN | TX |  | USA | CHARLES HAUSMANN | 361-987-2813 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1256 | 4911 | 221112 | 110001866641 | 05/27/2011 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2012-11-14 | 2013-09-25 | B |  | Three gas-fired combined cycle turbine generators, including a steam turbine generator, to replace the existing steam boiler/turbine generator. | 96336 | Combined cycle gas turbine | 15.21 | natural gas | 195 | MW | The three combustion turbine generators (CTG) will be the General Electric 7FA, each with a maximum base-load electric power output of approximately 195 megawatts (MW). The steam turbine is rated at approximately 235 MW. This project also includes the installation of two emergency generators, one fire water pump, and auxiliary equipment. No duct burners. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion | 4 | PPMVD | @15% O2, 24-HR ROLLING AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Good Combustion & Clean Fuel | 4.3 | PPMVD@15% O2 | 3-HR AVERAGE, NATURAL GAS OPERATION | BACT-PSD |  | U | 0 | U | 10 | PPMVD@15% O2 | 3-HR AVERAGE, ULSD OPERATION | 0 |  |  | 0 | 0 | N |  | No CEMS required. Also subject to limits of 7.1 ppmvd @15% O2 for gas and 13.6 ppmvd@15%O2 for ULSD, at low loads. The lowest loads at which the facility can demonstrate compliance with these low-load limits determines the minimum permitted operating load for the CT. Compliance by stack test.
*FL-0363 | DANIA BEACH ENERGY CENTER | FLORIDA POWER AND LIGHT COMPANY | BROWARD | FL | 33314 | USA | JOHN HAMPP | 561-691-2894 | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-017-AC | 4911 | 221112 | 110002044065 | 07/27/2017 &nbsp;ACT | 12/04/2017 &nbsp;ACT | 2018-04-03 | 2018-04-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.F.ZIP | 1200 megawatt 2-on-1 combined cycle facility, natural gas-fired, with limited ULSD use. GE 7HA turbines | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.D.ZIP | 2-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural gas | 4000 | MMBtu/hr | Two nominal 430 MW combustion turbines, coupled to a steam turbine generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Good Combustion & Clean Fuel | 4.3 | PPMVD@15% O2 | AT LOADS > 90% | BACT-PSD |  | U | 0 | U | 7.2 | PPMVD@15% O2 | FOR LOADS < 90% | 0 |  |  | 0 | 0 | N |  | For oil, limit is 10.0 ppmvd @ 15% O2 for loads > 90%, and 14.6 ppmvd@15% O2 for loads < 90%. Compliance by annual stack test.
FL-0303 | FPL WEST COUNTY ENERGY CENTER UNIT 3 | FLORIDA POWER AND LIGHT COMPANY (FP&L) | PALM BEACH COUNTY | FL | 33470 | USA | RANDALL R. LABAUVE |  |  | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | AL LINERO, P.E. ADMINISTRATOR SPECIAL PROJECT SECTION BUREAU OF AIR REGULATION | 0990646-002-AC (PSD-FL-396) | 4911 | 221112 | 110028293674 | 12/06/2007 &nbsp;ACT | 07/30/2008 &nbsp;ACT | 2008-12-15 | 2011-01-05 | B |  | THE FP&amp;L WEST COUNTY ENERGY CENTER (WCEC) WAS PREVIOUSLY APPROVED FOR CONSTRUCTION AS A NOMINAL 2,500 MEGAWATT (MW) GREENFIELD POWER PLANT. THE PREVIOUSLY APPROVED CONSTRUCTION UNDERWAY (PHASE I) IS FOR TWO NOMINAL 1,250 MW GAS-FIRED COMBINED CYCLE UNITS (UNITS 1 AND 2) THAT WILL USE ULTRALOW SULFUR DIESEL (ULSD) FUEL OIL (FO) AS BACKUP FUEL. PHASE 2: UNITS 1 AND 2 WILL EACH CONSIST OF: THREE NOMINAL 250 MEGAWATT (MW) MODEL 501G COMBUSTION TURBINE-ELECTRICAL GENERATORS (CTG) WITH EVAPORATIVE INLET COOLING SYSTEMS; THREE SUPPLEMENTARY-FIRED HEAT RECOVERY STEAM GENERATORS (HRSG) WITH SELECTIVE CATALYTIC REDUCTION (SCR) REACTORS; ONE NOMINAL 428 MMBTU/HOUR (LOWER HEATING VALUE - LHV) GAS-FIRED DUCT BURNER (DB) LOCATED WITHIN EACH OF THE THREE HRSG; THREE 149 FEET EXHAUST STACKS; ONE 26 CELL MECHANICAL DRAFT COOLING TOWER; AND A COMMON NOMINAL 500 MW STEAM-ELECTRICAL GENERATOR (STG). PREVIOUSLY APPROVED ANCILLARY EQUIPMENT INCLUDES: FOUR EMERGENCY GENERATORS; TWO NATURAL GAS FIRED FUEL HEATERS; ONE EMERGENCY DIESEL FIRED PUMP; TWO DIESEL FUEL STORAGE TANKS; TWO AUXILIARY STEAM BOILERS; AND OTHER ASSOCIATED SUPPORT EQUIPMENT. THIS PERMIT AUTHORIZES CONSTRUCTION OF ANOTHER 1,250 MW GAS-FIRED COMBINED CYCLE UNIT (UNIT 3) IDENTICAL TO THE DESCRIPTION GIVEN ABOVE FOR UNITS 1 AND 2. ADDITIONAL ANCILLARY EQUIPMENT FOR UNIT 3 WILL INCLUDE TWO EMERGENCY GENERATORS, TWO NATURAL GAS FIRED FUEL HEATERS AND ASSOCIATED EQUIPMENT. UNIT 3 WILL USE SOME OF THE INFRASTRUCTURE AND ANCILLARY EQUIPMENT ALREADY UNDER CONSTRUCTION INCLUDING THE DIESEL STORAGE TANKS AND AUXILIARY BOILERS. | COMBINED CYCLE UNIT 3 WILL CONSIST OF: THREE NOMINAL 250 MEGAWATT (MW) Â¿GÂ¿ CLASS COMBUSTION TURBINE-ELECTRICAL GENERATORS (CTG) EVAPORATIVE INLET COOLING SYSTEMS; THREE SUPPLEMENTARY-FIRED HEAT RECOVERY STEAM GENERATORS (HRSG) WITH SELECTIVE CATALYTIC REDUCTION (SCR) REACTORS AND A NOMINAL 428 MMBTU/HOUR (LOWER HEATING VALUE Â¿ LHV) GAS-FIRED DB; THREE 149 FOOT EXHAUST STACKS; ONE 26-CELL MECHANICAL DRAFT COOLING TOWER; AND A COMMON NOMINAL 500 MW STEAM-ELECTRICAL GENERATOR. | THREE NOMINAL 250 MW CTG (EACH) WITH SUPPLEMENTARY-FIRED HRSG | 15.21 | NATURAL GAS | 2333 | MMBTU/H | FUEL HEAT INPUT RATE (LHV): OIL 2,117 MMBTU/H COMBINED CYCLE UNIT 3 WILL CONSIST OF: THREE NOMINAL 250 MW COMBUSTION TURBINE-ELECTRICAL GENERATORS (CTG) WITH EVAPORATIVE INLET COOLING SYSTEMS; THREE SUPPLEMENTARY-FIRED HEAT RECOVERY STEAM GENERATORS (HRSG) WITH SELECTIVE CATALYTIC REDUCTION (SCR) REACTORS AND A COMMON NOMINAL 500 MW STEAM-ELECTRICAL GENERATOR. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION | 6 | PPMVD (GAS) | 12-MONTH | BACT-PSD |  | U | 0 | U | 8 | PPMVD (OIL) | 24-HOUR | 0 |  |  | 0 | 0 | N |  | COMPLIANCE WITH THE CONTINUOUS 24-HOUR CO STANDARDS SHALL BE DEMONSTRATED BASED ON DATA COLLECTED BY THE REQUIRED CEMS. THE INITIAL AND ANNUAL EPA METHOD 10 TESTS ASSOCIATED WITH THE CERTIFICATION OF THE CEMS INSTRUMENTS SHALL ALSO BE USED TO DEMONSTRATE COMPLIANCE WITH THE INDIVIDUAL STANDARDS FOR NATURAL GAS, FO, AND BASIC DB MODE. THE STACKS TEST LIMITS APPLY ONLY AT HIGH LOAD (90-100% OF THE CTG CAPACITY).
FL-0304 | CANE ISLAND POWER PARK | FLORIDA MUNICIPAL POWER AGENCY (FMPA | OSCEOLA | FL | 33848 | USA | ROGER FONTES | 4073557767 | ROGER.FONTES@FMPA.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | ALVARO LINERO, PE. SPECIAL PROJECT SECTION ADMINISTRATOR BUREAU OF AIR REGULATION | PSD-FL-400 (0970043-014-AC) | 4911 | 221112 | 110013931308 | 04/01/2008 &nbsp;ACT | 09/08/2008 &nbsp;ACT | 2009-02-16 | 2009-04-20 | B |  | FMPA AND THE KISSIMMEE UTILITIES AUTHORITY (KUA) JOINTLY OWN THE CIPP, WHICH IS LOCATED IN OSCEOLA COUNTY AT 6075 OLD TAMPA HIGHWAY, INTERCESSION CITY, FLORIDA. THE CIPP PRESENTLY CONSISTS OF ONE 40 MEGAWATT (MW) SIMPLE CYCLE COMBUSTION TURBINE (UNIT 1), A 120 MW COMBINED CYCLE UNIT INCLUDING A HEAT RECOVERY STEAM GENERATOR (HRSG) (UNIT 2) AND A 250 MW COMBINED CYCLE UNIT (UNIT 3). THE THREE EXISTING UNITS FIRE NATURAL GAS AS THE PRIMARY FUEL, WITH DISTILLATE FUEL AS BACKUP. THE NEW UNIT WILL BE A NATURAL GAS 300 MW COMBINED CYCLE UNIT AND ASSOCIATED EQUIPMENT. | THE PROJECT WILL BE A Â¿ONE-ON-ONEÂ¿ 300 MW NATURAL GAS-FUELED COMBINED CYCLE UNIT (CIPP UNIT 4) AND ASSOCIATED AUXILIARY EQUIPMENT. UNIT 4 AND ASSOCIATED AUXILIARY EQUIPMENT WILL CONSIST OF: Â¿ A NOMINAL 150 MW GAS-FUELED GENERAL ELECTRIC 7241 FA CTG; Â¿ A SUPPLEMENTARY-FIRED HRSG WITH NATURAL GAS FUELED DUCT BURNERS (DB); Â¿ A NOMINAL 150 MW STG; Â¿ A NOMINAL 160-FOOT STACK; Â¿ AN EMERGENCY DIESEL ENGINE FIRE PUMP AND SMALL ULTRALOW SULFUR DIESEL (ULSD) FUEL OIL (FO)STORAGE TANK; Â¿ A NOMINAL 750 KILOWATTS (KW) SAFE SHUTDOWN DIESEL GENERATOR WITH A ULSD FO STORAGE TANK; AND Â¿ A MECHANICAL DRAFT COOLING TOWER WITH DRIFT ELIMINATORS. | 300 MW COMBINED CYCLE COMBUSTION TURBINE | 15.21 | NATURAL GAS | 1860 | MMBTU/H |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 6 | PPMVD | 12-MONTH | BACT-PSD | NSPS , NESHAP | U | 0 | U | 8 | PPMVD | 24-HR | 0 |  |  | 0 | 0 | N |  | CONTINOUS EMISSION MONITOR TO DETERMINE CONTINUOUS COMPLIANCE.
OK-0129 | CHOUTEAU POWER PLANT | ASSOCIATED ELECTRIC COOPERATIVE INC | MAYES | OK | 74362 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2007-115-C(M-1)PSD | 4911 | 221112 | 4009700017 | 06/19/2008 &nbsp;ACT | 01/23/2009 &nbsp;ACT | 2009-11-20 | 2010-02-18 | B |  |  |  | COMBINED CYCLE COGENERATION &gt;25MW | 15.21 | NATURAL GAS | 1882 | MMBTU/H | SIEMENS V84.3A | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION | 8 | PPMV | 1-HR AVG | BACT-PSD | N/A | U | 0 | U | 51.32 | PPMV | 3-HR AVG | 0 |  |  | 0 | 0 | N
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 9 | PPM | EACH CTG; 24-H ROLLING AVG. | BACT-PSD | SIP | N | 0 | N | 43.9 | LB/H | EACH CTG; 24-H ROLLING AVG. | 0 |  |  | 10600 | 0 | N | 2012 | Emission limit 1 is 9.0 ppmv dry at 15% oxygen on a 24-hour rolling average as determined each hour the turbine operates; except during startup/shutdown. The limit applies to each unit. Emission limit 2 is 43.9 LB/H based on a 24-hour rolling average as determined each hour the turbine operates; except during startup/shutdown. The limit is for each unit. The cost information was estimated for a catalytic oxidation system (COS) CO = $10,600/ton CO+VOC = $8,948/ton
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 10.5 | PPM | EACH CTG/DB; 24-H ROLLING AVG. | BACT-PSD | SIP | N | 0 | N | 57.6 | LB/H | EACH CTG/DB; 24-H ROLLING AVG. | 0 |  |  | 10600 | 0 | N | 2012 | Emission limit 1 is 10.5 ppmv dry at 15% oxygen, for each CTG/DB, based on a 24-hour rolling average as determined each hour the turbine operates. Emission limit 2 is 57.6 LB/HR for each CTG/DB, based on a 24-hour rolling average as determined each hour the turbine operates. The cost effectiveness was estimated for a catalytic oxidation system (COS); CO = $10,600/ton CO + VOC = $8,948/ton
TX-0698 | BAYPORT COMPLEX | AIR LIQUIDE LARGE INDUSTRIES U.S., L.P. | HARRIS | TX |  | USA | JASON MILLER | (281) 474-8243 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 | 9346 PSDTX612M2 | 4931 | 325120 | 110000462758 | 07/27/2012 &nbsp;ACT | 09/05/2013 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | Air Liquid currently operates a cogeneration facility in Pasadena, Texas (Bayou Cogeneration Plant). The permit amendment submitted by Air Liquide will authorize a redevelopment project of its cogeneration plant. The proposed project will involve the replacement of four existing gas-fired turbines (GE 7EA) with similar gas-fired turbines (GE 7EA), the addition of three new gas-fired boilers rated at 550 MMBtu/hr and the removal of three existing gas-fired boilers rated at 443 MMBtu/hr. |  | (4) cogeneration turbines | 15.21 | natural gas | 90 | MW | (4) GE 7EA turbines providing power and process steam | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good Combustion & Clean Fuel | 15 | PPMVD | @15% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0547 | NATURAL GAS-FIRED POWER GENERATION FACILITY | LAMAR POWER PARTNERS II LLC | LAMAR | TX | 75126 | USA |  |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | RANDY HAMILTON RHAMILTO@TCEQ.STATE.TX.US | 83207 | 4911 | 221122 | UNKNOWN | 10/25/2007 &nbsp;ACT | 06/22/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | THE NEW POWER BLOCK WILL BE CAPABLE OF PRODUCING EITHER 620 OR 910 MEGAWATTS OF ELECTRICITY, DEPENDING UPON WHICH COMBUSTION TURBINE MODEL OPTION IS CHOSEN. | PSDTX1106 | ELECTRICITY GENERATION | 15.21 | NATURAL GAS | 250 | MW | LAMAR POWER PARTNERS PROPOSES TO CONSTRUCT A NATURAL GAS-FIRED COMBINED-CYCLE POWER BLOCK TO BE BUILT AT THE EXISTING SITE IN LAMAR COUNTY, TEXAS. THE NEW POWER BLOCK WILL BE CAPABLE OF PRODUCING EITHER 620 OR 910 MEGAWATTS OF ELECTRICITY, DEPENDING UPON WHICH COMBUSTION TURBINE MODEL OPTION IS CHOSEN. THE PROPOSED PROJECT WOULD INCLUDE TWO COMBUSTION TURBINES (EITHER 170 MW GENERAL ELECTRIC 7FAS OR 250 MW MITSUBISHI 501GS), TWO HEAT RECOVERY STEAM GENERATORS WITH DUCT BURNERS AND ONE STEAM TURBINE. THE GE7FAS WOULD BE CAPABLE OF PRODUCING 620 MW OF ELECTRICITY IN COMBINED CYCLE MODE, WHILE THE M501GS WOULD PRODUCE 910 MW IN COMBINED CYCLE MODE. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRATICES | 15 | PPMVD | @ 15% O2, 24-HR ROLLING AVG | BACT-PSD |  |  | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0548 | MADISON BELL ENERGY CENTER | MADISON BELL PARTNERS LP | MADISON | TX | 77354 | USA |  |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | RANDY HAMILTON RHAMILTO@TCEQ.STATE.TX.US | 83378 | 4911 | 221122 | UNKNOWN | 10/31/2007 &nbsp;ACT | 08/18/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | THE PROJECT WOULD INCLUDE FOUR NATURAL GAS-FIRED COMBUSTION TURBINES (GE F7EA) AND FOUR HEAT RECOVERY STEAM GENERATORS (HRSGS) WITH PROVISIONS FOR DUCT FIRING. THE PROPOSED PROJECT WILL OPERATE THE COMBUSTION TURBINES IN COMBINED CYCLE MODE. THE COMBINED NOMINAL GENERATING CAPACITY OF THE PLANT IS APPROXIMATELY 550 MW IN COMBINED CYCLE MODE. | PSDTX1105 | ELECTRICITY GENERATION | 15.21 | NATURAL GAS | 275 | MW | FOUR GE PG7121(EA) COMBINE CYCLE TURBINES FIRING NATURAL GAS WILL DIRECTLY GENERATE 75 MW; EACH HAS A 165 MMBTU/HR DUCT BURNER AND A HEAT RECOVERY STEAM GENERATOR. TWO HRSGÂ¿S WILL TURN ONE 125 MW STEAM TURBINE AND THE OTHER TWO WILL TURN ANOTHER 125 MW STEAM TURBINE. THE TURBINE MAY OPERATE WITHOUT THE DUCT BURNER. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 17.5 | PPMVD | @ 15% O2, 1-HR ROLLING AVG | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.21 | natural gas | 10 | M TONNES/YR | Four GE Frame 7E gas turbines for refrigeration and compression at the site | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good Combustion & Clean Fuel | 25 | PPM | ROLLING 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057188626 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.21 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (6) GE LM2500+ DLE turbines that drive the ethylene section compressors with waste heat recovery for amine solution regeneration. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good Combustion & Clean Fuel | 29 | PPMVD | @15% O2, 4 HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0687 | WEST PLANT AND EAST PLANT CENTRAL HEAT AND POWER | UNIVERSITY OF TEXAS MEDICAL BRANCH AT GALVESTON | GALVESTON | TX |  | USA | JACK TARPLEY | 409-747-0515 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, 512-239-2175, laura.gibson@tceq.texas.gov | 56653, PSDTX1376 | 8221 | 611310 | 110017309615 | 08/23/2013 &nbsp;ACT | 10/13/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | UTMB Galveston has applied for an amendment to authorize two combined cycle natural gas fired Solar Taurus 60 combustion turbines. Each CTG will produce 13MW. |  | Two Combustion Turbine-Generators | 15.21 | Natural Gas | 13 | MW | Combined Cycle | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 50 | PPM | 15% O2, 24HR ROLLING AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
[40 empty] | Range Low | 2 | PPMV
[40 empty] | Range High | 50 | PPMV
[40 empty] | Mean | 12.5647 | PPMV
[40 empty] | Median | 8 | PPMV
[40 empty] | Mode | 4 | PPMV