## Combined Cycle Turbines 15.210
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Carbon Dioxide Equivalent (CO2e) | Other - EPA METHOD 3B | (Greenhouse Gasses (GHG)) | CO2e | N |  | 774 | LB/MW-H | 365-DAY ROLLING AVG (FACILITYWIDE) | BACT-PSD |  | U | 0 | U | 7319 | BTU/KW-H | 365-DAY ROLLING AVG (FACILITYWIDE) | 0 |  |  | 0 | 0 | N |  | USE EPA METHOD 3B FOR CO2 EMISSIONS.
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/o Duct Firing | 15.21 | Natural Gas | 2969 | MMBtu/hr | Throughput is for turbine only | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of low carbon fuel | 7273 | BTU/KW-HR | 12-MONTH ROLLING (NET PLANT, GAS ONLY) | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 0 | U | 816 | LB/MW-HR | (NET, GAS ONLY) | 0 |  |  | 0 | 0 | N
DE-0023 | NRG ENERGY CENTER DOVER | NRG ENERGY CENTER DOVER LLC | USA | DE | 19901 | USA | WILLIAM GROW | 302-678-4666 |  | 3 | DE001 | DELAWARE DEPT OF NATURAL RES & ENV CTRL | MR. PAUL FOSTER | (302)323-4542 | PAUL.FOSTER@STATE.DE.US |  | AQM-001/00127(R-2)(REV-1) | 4911 | 221119 | 110043806931 | 11/17/2011 &nbsp;ACT | 10/31/2012 &nbsp;ACT | 2013-05-07 | 2016-05-13 | U |  | The facility operates two electric generation units and an auxilliliary steam boiler. |  | UNIT 2- KD1 | 15.21 | Natural Gas | 655 | MMBTU/H | 500 MMBTU/hr Gas Turbine (Model: GE LM6000) rated at 52 MW and 155 MMBTU/hr Heat Recovery Steam Generator rated at 18 MW. The unit is required to operate a certified CEMS and COMS. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1085 | LB/GROSS MWH | 12 MONTH ROLLING AVERAGE | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
DE-0024 | GARRISON ENERGY CENTER | GARRISON ENERGY CENTER, LLC/ CALPINE CORPORATION | KENT COUNTY | DE | 19901 | USA | STUART WIDOM | 302-468-5324 | STUART.WIDOM@CALPINE.COM | 3 | DE001 | DELAWARE DEPT OF NATURAL RES & ENV CTRL | MR. PAUL FOSTER | (302)323-4542 | PAUL.FOSTER@STATE.DE.US |  | APC-2012/0098 | 4911 | 221112 | 110043806931 | 04/04/2012 &nbsp;ACT | 01/30/2013 &nbsp;ACT | 2013-05-13 | 2014-01-28 | A |  | one (1) 309 MW GE Combined Cycle Combustion Turbine Generating system fired principally on Natural Gas, one (1) 86,000 GPM Cooling Tower, one (1) 1,400,000 ULSD Storage Tank |  | Unit 1 | 15.21 | Natural Gas | 2260 | million BTUs |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N | Fuel Usage Restriction to natural gas and low sulfur distillate fuel | 1006304 | TONS | 12 MONTH ROLLING AVERAGE | BACT-PSD | SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Carbon Dioxide Equivalent (CO2e) | Other - CO2 CEMS or fuel use monitoring | (Greenhouse Gasses (GHG)) | CO2e | P | Use of low-emitting fuels and technologies | 850 | LB/MWH | FOR GAS OPERATION, 12-MO ROLLING | BACT-PSD | NSPS | U | 0 | U | 1210 | LB/MWH | FOR ULSD OPERATION, 12-MO ROLLING | 0 |  |  | 0 | 0 | N |  | Also, limited to 500 hr/yr per turbine on ULSD. Standard is a weighted average of the gas and ULSD standards, depending on generation on the two fuels during the compliance period. Excludes startup, shutdown, and malfunction. NSPS Subpart TTTT adopted as &lsquo;&lsquo;Secondary BACT&lsquo;&lsquo; during SSM periods.
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #1 - combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr | two identical Siemens SGT6-5000F combined cycle turbines without duct firing, each at 2258 mmBtu/hr generating approx. 300 MW each. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1318647 | TON/YR | 12-MONTH ROLLING | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #2 -combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1318647 | TON/YR | 12-MONTH ROLLING TOTAL | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0129 | CPV THREE RIVERS ENERGY CENTER | CPV THREE RIVERS, LLC | GRUNDY | IL | 60450 | USA | MIKE BRUNO | 781-817-8972 | MBRUNO@CPV.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Illinois EPA, Bureau of Air Permit Section | 16060032 | 4911 | 221112 | Not Found | 06/10/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2019-01-02 | 2019-02-19 | A |  | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, each with a combustion turbine and associated heat recovery steam generator (HRSG). The turbines would burn natural gas and ultra-low sulfur diesel (ULSD) as a backup fuel. Other units include an auxiliary boiler, fuel heater, engines, natural gas piping and components, circuit breakers and roadways. |  | Combined Cycle Combustion Turbines | 15.21 | Natural Gas | 3474 | mmBtu/hr | Throughput of ultra-low sulfur diesel (ULSD) is 3798 mmBtu/hr. Combined cycle combustion turbines w/ heat recovery steam generator (HRSG). Turbine inlets will have inlet evaporative cooling systems to cool inlet air during warm weather to increase power output. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Equipment design and proper operation | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Permit limit: 4,026,300 ton/yr, 12-month rolling average. See also Condition 2.1.2(h) of the issued permit.
IL-0130 | JACKSON ENERGY CENTER | JACKSON GENERATION, LLC | WILL | IL | 60421 | USA | JAMES KIEFER | 847-908-2833 | JKEIFER@POWERUSA.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov |  | 17040013 | 4911 | 221112 | Not Found | 04/04/2017 &nbsp;ACT | 12/31/2018 &nbsp;ACT | 2019-07-23 | 2020-04-16 | A |  | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, each with a combustion turbine and associated heat recovery steam generator (HRSG). The turbines would only burn natural gas. Other units include an auxiliary boiler, fuel heater, emergency engines, natural gas piping and components, circuit breakers and roadways | Additional pollutants: Sulfuric Acid Mist: 48 tons/year; GHG as CO2e: 4,752,085 tons/year | Combined-Cycle Combustion Turbine | 15.21 | Natural Gas | 3864 | mmBtu/hr | Combined-cycle combustion turbines with heat recovery steam generator (HRSG). Turbines will have inlet evaporative cooling systems to cool inlet air during warm weather to increase power output. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Equipment design and proper operation | 4733910 | TONS/YEAR | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO2 emissions of each turbine shall not exceed 1,000 lb/MWh of gross energy output, or, alternatively, 1,030 lb/MWh of net energy output on a 12-month rolling average basis.
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | HIGH THERMAL EFFICIENCY DESIGN | 7646 | BTU/KW-H |  | BACT-PSD |  |  | 0 |  | 4885000 | TONS | 12 CONSECUTIVE MONTH PERIOD | 0 |  |  | 0 | 0 | N |  | LIMIT ONE IS FOR EACH CCCT BLOCK. LIMIT TWO IS FOR ALL FOUR (4) COMBINED.
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Combined cycle combustion turbine | 15.21 | Natural gas | 250 | MW | Combined cycle combustion unit; this unit includes a heat recovery steam generator (HRSG) with supplemental natural gas duct firing (duct burners) and a condensing steam turbine generator with SCR and CO catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1022755.9 | TONS PER YEAR | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0256 | COGENERATION PLANT | WESTLAKE VINYLS COMPANY LP | ASCENSION | LA | 70734 | USA | KAREN KHONSARI | (225) 673-0647 | KKHONSARI@WESTLAKE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: DAN NGUYEN, 225-219-3417 | PSD-LA-754 | 4939 | 221112 | 110000746328 | 01/12/2011 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2011-12-21 | 2012-04-03 | B |  | COGENERATION PLANT AT SYNTHETIC ORGANIC CHEMICAL MANUFACTURING FACILITY | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS &lsquo;&lsquo;FWE&lsquo;&lsquo; REPRESENT POTENTIAL EMISSIONS ASSOCIATED WITH THE COGENERATION PLANT. NOX &lsquo;&lsquo;NETTED OUT&lsquo;&lsquo; OF PSD/NNSR. | COGENERATION TRAINS 1-3 (1-10, 2-10, 3-10) | 15.21 | NATURAL GAS | 475 | MMBTU/H | EACH COGEN TRAIN CONSISTS OF A 50 MW GE LM6000 PF SPRINT TURBINE AND A HEAT RECOVERY STEAM GENERATOR EQUIPPED WITH A 70 MM BTU/HR DUCT BURNER. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | USE OF NATURAL GAS AS FUEL AND GOOD COMBUSTION PRACTICES | 55576.77 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | IN ADDITION, AN ANNUAL LIMIT OF 243,426.26 TPY WAS ESTABLISHED BY THE ACCOMPANYING TITLE V PERMIT (3090-V0).
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Combined Cycle Refrigeration Compressor Turbines (8) | 15.21 | natural gas | 286 | MMBTU/H | GE LM2500+G4 | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion/operating practices and fueled by natural gas - use GE LM2500+G4 turbines | 4872107 | TONS/YEAR | ANNUAL MAXIMUM FROM THE FACILITYWIDE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | co2(e)
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1A | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Thermally efficient combustion turbines and good combustion practices | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT Limit = 1000 LB/MWh
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1B | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Thermally efficient combustion turbines and good combustion practices | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT Limit = 1000 LB/MWh
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Combust low carbon fuel gas and good combustion practices | 2602275 | T/YR | ANNUAL TOTAL | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Annual Total for 5 Combined Cycle Turbines
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000310459 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 2449 | MMBTU/H | two 315 MW (nominal) GE Energy 7F Series 5 Rapid Response Combined Cycle Combustion Turbines with Duct Burners and 31 MW (estimated) steam turbine generators | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 825 | LB/MW-H | FULL LOAD WITHOUT DUCT FIRING | BACT-PSD | OPERATING PERMIT , SIP | U | 0 | U | 895 | LB/MW-H | 365 DAY ROLLING AVERAGE | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 725 | MEGAWATT | TWO GENERAL ELECTRIC (GE) F-CLASS ADVANCED COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 725 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 7109 | BTU/KWH | @ ISO CONDITIONS | BACT-PSD | NSPS | U | 0 | U | 878 | LB/MWH | @ ISO CONDITIONS | 0 |  |  | 0 | 0 | N |  | EMISSION LIMIT (EL) 1 IS HEAT RATE; EMISSION LIMIT (EL) 2 IS GROSS HEAT THERMAL RATE EFFICIENCY. ANNUAL EMISSIONS LIMITED TO 2,665,914, 12 MONTH ROLLING AVERAGE
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITH DUCT FIRING | 15.21 | NATURAL GAS | 1000 | MW | TWO MITSUBISHI &lsquo;&lsquo;G&lsquo;&lsquo; MODEL COMBUSTION TURBINE GENERATORS (CTS) WITH A NOMINAL GENERATING CAPACITY OF 270 MW CAPACITY EACH, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR), OXIDATION CATALYST | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | EXCLUSIVE USE OF PIPELINE-QUALITY NATURAL GAS, AND INSTALLATION OF HIGH-EFFICIENCY CT MODEL (MITSUBISHI &lsquo;&lsquo;G&lsquo;&lsquo; MODEL) | 946 | LB/MW-H (AS CO2) | 12-MONTH ROLLING | BACT-PSD |  |  | 0 |  | 7500 | BTU/KWH (HEAT RATE) | AT ALL TIMES, EXCLUDING SU/SD | 0 |  |  | 0 | 0 | N |  | WITH AND WITHOUT DUCT FIRING
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST. HEAT RATE LIMITED TO 6,793 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR MATTAWOMAN TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS MATTAWOMAN PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Carbon Dioxide Equivalent (CO2e) | Other - | (Greenhouse Gasses (GHG)) | CO2e | N |  | 865 | LB/MW-H | 12-MONTH ROLLING AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHOD: IF NO CEMS INSTALLED, EPA METHOD 3A . WITH AND WITHOUT DUCT FIRING AT ALL TIMES
MI-0402 | SUMPTER POWER PLANT | WOLVERINE POWER SUPPLY COOPERATIVE INC. | WAYNE | MI | 48111 | USA | BRIAN WARNER | 231-775-5700 | BWARNER@WPSCI.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Julie Brunner at 517-373-7088 or brunnerj1@michigan.gov for questions related to this permit. Thank you. | 81-11 | 4911 | 221112 | 2616305315 | 05/27/2011 &nbsp;ACT | 11/17/2011 &nbsp;ACT | 2012-11-30 | 2016-05-04 | D |  | Utility--Natural gas fired combustion turbine | Other Facility Wide Pollutants not listed below: PM10 = 14.8 tpy PM2.5 = 14.8 tpy CO2e = 232,639 tpy | Combined cycle combustion turbine w/ HRSG | 15.21 | Natural gas | 130 | MW electrical output | This is a combined-cycle combustion turbine with a non-fired heat recovery steam generator (HRSG). Natural gas-fired combustion turbine conversion to combined-cycle. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 954 | LB/MW-H | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | N | 49.6 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Estimated efficiency (above) is 49.6% thermal efficiency (design) Top ranking option--thermal efficiency (design is gross summer 87 F degrees ambient and includes 6% factor for performance degradation).
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices and energy efficiency. | 995 | LB/MW-H | 12-MO. ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is based on 6% performance degradation for GE turbines. CCS is assumed to be about 90% effective, resulting in a reduction of approximately 2.3 million tons of CO2 emissions per year from the proposed CTGs at MCV. However, the use of CCS as a control method would also result in significant energy and environmental impacts due to the increased fuel usage required to operate the CCS systems. MCV estimated that to reduce the 2.3 million tons of CO2 per year from the proposed CTGs, an additional 181 MW of electric power and steam generation would be needed for capture, compression and transport to an Enhanced Oil Recovery (EOR) for storage. That would result in air emissioin increases for an annualized cost of approximately $155 million per year, which is approximately $67 per ton to capture and store CO2. Therefore, MCV determined that CCS for emission reduction, as well as the environmental degradation due to increases in pollutant is not reasonable.
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices and energy efficiency | 1071 | LB/MW-H | 12-MONTH ROLLING AVG. | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 is 1,071.0 LB/MW-H gross energy output based on a 12-month rolling average. Cost effectiveness information: The CO2e limit is based on 6% performance degradation for GE turbines. CCS is assumed to be about 90% effective, resulting in a reduction of approximately 2.3 million tons of CO2 emissions per year from the proposed CTGs at MCV. However, the use of CCS as a control method would also result in significant energy and environmental impacts due to the increased fuel usage required to operate the CCS systems. MCV estimated that to reduce the 2.3 million tons of CO2 per year from the proposed CTGs, an additional 181 MW of electric power and steam generation would be needed for capture, compression, and transport to an Enhanced Oil Recovery (EOR) for storage. That would result in air emission increases for an annualized cost of approximately $155 million per year, which is approximately $67 per ton to capture and store CO2. Therefore, MCV determined that CCS for emission reduction, as well as the environmental degradation due to increases in pollutants is not reasonable.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices/energy efficiency | 1000 | LB/MW-H | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit is for each unit operating with or without DB. CCS technology for natural gas-fired combined cycle units entails significant economic, energy, and environmental impacts as a control method would also result in significant energy and environmental impacts due to the increased fuel usage required to operate the CCS systems. Renaissance referred to a detailed cost analysis conducted by Carnegie Mellon University (*) which specifically analyzed costs for plants using amine-based post-combustion CCS systems with 90% CO2 capture. The analysis found that CCS increases capital costs (in 2007 basis) by approximately $600/kW, which would result in an incremental capital cost of approximately $840 million for this project. The analysis also found the cost (in 2007 basis) of CO2 avoided, ranged from $74-$114 per ton CO2 which equates to annual costs of $400-$600 million. *Reference of analysis. The cost of Carbon Capture and Storage for Natural Gas Combined Cycle Power Plants, Rubin and Zhai, Department of Engineering and Public Policy, Carnegie Mellon University, http://www.wecc.biz/committees/BOD/TEPPC/SPSG/MDTF/120914/Lists/Minutes/1/CCS_Costs_for_Combined_Cycle.pdf
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices/energy efficiency | 1000 | LB/MW-H | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit applies for each unit operating with or without DB. CCS technology for natural gas-fired combined cycle units entails significant economic, energy, and environmental impacts as a control method would also result in significant energy and environmental impacts due to the increased fuel usage required to operate the CCS systems. Renaissance referred to a detailed cost analysis conducted by Carnegie Mellon University (*) which specifically analyzed costs for plants using amine-based post-combustion CCS systems with 90% CO2 capture. The anlaysis found that CCS increases capital costs (in 2007 basis) by approximately $600/kW, which would result in an incremental capital cost of approximately $840 million for this project. The analysis also found the cost (in 2007 basis) of CO2 avoided, ranged from $74 to $114 per ton CO2 which equates to annual costs of $400 to $600 million.
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | No info was entered on type of add-on control. Contact permitting agency. | 1386286 | T/YR | 12-MO ROLL TIME PERIOD DETER EACH MONTH | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is 1,386,286 T/Y based on a 12-month rolling time period as determined at the end of each calendar month. The limit is for each of the four CTG/HRSGs.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures and the use of a low carbon fuel (pipeline quality natural gas). | 339125 | T/YR | 12-MO ROLL TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The proposed permit also contains a net heat rate limit of 8361 Btu/kW-hr per 2x1 block. The tons per year and net heat rate value equate to 992 lb CO2 per MW-hour (lb/MWh). CCS is assumed to be about 90 percent effective. However, the use of CCS technology creates a significant increase in parasitic electrical load, which would decrease the net plant output of the proposed plant from 115 MW to 106 MW, and the technology entails a significant economic impact on the proposed facility. Holland BPW reviewed the documents and utilized the costs provided for different plants at base case and with potential CCS control. The amine-based CCS technologies were used since these had the lowest estimated costs of the CCS technologies considred in the reports. An incremental cost of $800/kW was scaled based on relative gas flows, CO2 removal rates, and net megawatt output. The resulting incremental cost, scaled from these variables is $1,410/kW. When applying a CCS technology to a plant, there would be a significant increase in parasitic electrical load, as well as an impact oon plant output due to the steam demand by the steam stripping towers. As such, the net plant output of hte proposed CHP with CCS is 106 MW. This was applied to the $1,410/kW incremental captial rate. The cost of a pipeline to transport the CO2 was added to the result to estimate the total capital cost of the CCS system. The resulting cost is in excess of $60/ton and is not considered to be economically feasible.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures and the use of a low carbon fuel (pipeline quality natural gas). | 2097001 | T/YR | 12-MONTH ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is for EACH CTGHRSG. The proposed permit also contains a 802 lb CO2 per MW-hour (lb/MWh) emission limit that serves as BACT due to energy efficiency, which is equivalent to a net heat rate of 6,855 Btu/kW-hr per 2x1 block and is more stringent than the required NSPS limit of the same units. The amine-based CCS technologies were used since these are generally considered to be the most feasible near-term deployable technology for possible future CO2 removal. CCS is assumed to be about 90 percent effective. Using the lowest capital cost range, the estimated capital cost for CCS for the proposed project is approximately $629,000,000. The cost of a pipeline to transport the CO2 was added to the result to estimate the total capital cost of the CO2 control system. The operating and maintenance and indirect operating costs were estimated to be around $53,000,000. Based on 90 percent CO2 removal and the control being applied to the facility-wide emissions, not just the CTG/HRSG trains, the resulting cost is estimated to be $30/ton and was not considered economically feasible.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures and the use of a low carbon fuel (pipeline quality natural gas). | 312321 | T/YR | 12-MO. ROLLING TIME PERIOD; EACH EU. | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is for each CTGHRSG and is 312,321 tons per year based upon a 12-month rolling time period as determined at the end of each calendar month. The proposed permit also contains a net heat rate limit of 8,361 BTU/KW-H per CTG/HRSG pair (2x1 block). The tons per year and net heat rate value equate to 992 lb CO2 per MW-H (lb/MW-H). CCS is assumed to be about 90 percent effective. However, the use of CCS technology creates a significant increase in parasitic electrical load, which would decrease the net plant output of the proposed plant from 115 MW to 106 MW, and the technology entails a significant economic impact on the proposed facility. Holland BPW reviewed the documents and utilized the costs provided for different plants at base case and with potential CCS control. The amine-based CCS technologies were used since these had the lowest estimated costs of the CCS technologies considered in the reports. An incremental cost of $800/kW capital cost rate was derived based on an average of several of these estimates scaled to 2010 dollars. This value is in the range of other CCS BACT analyses. For costs specific to Holland BPW, the $800/kW was scaled based on relative gas flows, CO2 removal rates, and net megawatt output. The resulting incremental cost, scaled from these variables, is $1410/kW. When applying a CCS technology to a plant, there would be a significant increase in parasitic electrical load, as well as an impact on plant output due to the steam demand by the steam stripping towers. As such, the net plant output of the proposed CHP with CCS is 106 MW. This was applied to the $1410/kW incremental capital rate. The cost of a pipeline to transport the CO2 was added to the result to estimate the total capital cost of the CCS system. The resulting cost is in excess of $60/ton and is not considered to be economically feasible.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures and the use of a low carbon fuel (pipeline quality natural gas). | 992286 | T/YR | 12-MO.ROLL.TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CCS was estimated to cost over $240 per ton of CO2 removed, with an estimated annual cost of over $246 million. Terrestrial sequestration was estimated to cost over $160 per ton of CO2 removed, with an estimated annual cost of over $160 million. Thus, both of these options are ruled out, as they are not economically feasible.
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Several energy efficiency measures and the use of natural gas. | 1425081 | T/YR | EACH CT/HRSG TRAIN; 12-MO. ROLL TIME PER | BACT-PSD |  | N | 0 | N | 7978 | BTU/KW-H | EACH CT/HRSG TRAIN; 12-MO ROLL AVG | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above is 1,425,081 T/YR based on a 12-month rolling time period as determined at the end of each calendar month for each individual CT/HRSG. Emission limit 2 above is 7,978 BTU/KW-H (HHV) and is the Net Heat Rate on a 12-month rolling average basis for each individual CT/HRSG. CCS was estimated to cost over $75 per ton of CO2 removed, with an estimated annual cost of over $321 million to remove 4.24 million tons per year. Thus, this option was ruled out as economically infeasible.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures and the use of a low carbon fuel (pipeline quality natural gas). | 1978297 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 806 | LB/MW-H | 12-OPERATING MONTH ROLL AVG BASIS | 0 |  |  | 0 | 0 | N |  | For emission limit 2 (806 LB/MW-H) it is based on a 12-operating month rolling average basis as determined at the end of each operating calendar month (basis is BACT & NSPS TTTT). Compliance is determined monthly at the end of the initial and each subsequent 12-operating month period. The first month of the initial compliance period is defined in 40 CFR 60.5525(c)(1)(i). The amine-based CCS technologies were used since these are generally considered to be the most feasible near-term deployable technology for possible future CO2 removal. CCS is assumed to be about 90 percent effective. Using the lowest capital cost range, the estimated capital cost for CCS for the proposed project is approximately $393 million, including the cost of a pipeline to transport the CO2 and the cost of the CO2 control system. The cost per ton was close to $100/ton, which was not considered economically feasible.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures and the use of a low carbon fuel (pipeline quality natural gas). | 1978297 | T/YR | 12-MO ROLL TIME PERIOD | BACT-PSD |  | N | 0 | N | 806 | LB/MWH | 12- OPERATING MONTH ROLL AVG | 0 |  |  | 0 | 0 | N |  | Emission limit 2 is 806 LB/MWH based on 12-operating month rolling average basis as determined at the end of each operating calendar month. Compliance is determined monthly at the end of the initial and each subsequent 12-operating month period. The first month of the initial compliance period is defined in 40 CFR 60.5525(c)(1)(i). The amine-based CCS technologies were used since these are generally considered to be the most feasible near-term deployable technology for possible future CO2 removal. CCS is assumed to be about 90 percent effective. Using the lowest capital cost range, the estimated capital cost for CCS for the proposed project is approximately $393 million, including the cost of a pipeline to transport the CO2 and the cost of the CO2 control system. The cost per ton was close to $100/ton, which was not considered economically feasible.
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures | 2042773 | T/YR | 12-MO ROLLING TIME PERIOD; EACH UNIT | BACT-PSD | NSPS | N | 0 | N | 794 | LB/MW-H | 12-OPER MO ROLL AVG; EACH UNIT | 0 |  |  | 0 | 0 | N |  | The estimated cost of CCS is over $70,000,000 per year. This does not take into account the large parasitic load caused by a CCS system. For emission limit 2 above (794 LB/MW-H), compliance is determined monthly at the end of the initial and each subsequent 12-operating month period. The first month of the initial compliance period is defined in 40 CFR 60.5525(c)(1)(i).
MI-0439 | JACKSON GENERATING STATION | CONSUMERS ENERGY COMPANY | JACKSON | MI | 49203-2174 | USA | BRIAN LABBY | 989-667-5008 | BRIAN.LABBY@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, at 517-284-6790 or at byrnesm@michigan.gov, for technical questions regarding this permit. Thank you. | 118-18 | 4911 | 221112 | 110015804511 | 11/29/2018 &nbsp;ACT | 04/02/2019 &nbsp;ACT | 2019-05-20 | 2019-06-19 | C |  | Natural gas combined-cycle power plant |  | FGLMDB1-6 (6 combined cycle natural gas fired CTG each equipped with a HRSG) | 15.21 | natural gas | 420 | MW | FGLMDB1-6 is 6 combined cycle natural gas fired combustion turbine generators (CTG) each equipped with a heat recovery steam generator (HRSG). Nominal rating 420 MW. Each combustion turbine (CT) is a GE LM6000 with a rating of 440 MMBTU/HR (HHV) and a duct burner rating of 222 MMBTU/HR (HHV). A combined cycle natural gas fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 420 MW electricity production. The HRSG is not capable of operating independently from the CTG. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of low carbon fuel (natural gas), good combustion practices, and energy efficiency measures. | 1000257 | T/YR | 12-MONTH ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Energy efficiency measures involve the installation of combined cycle units, following vendor recommended maintenance practices, the minimization of heat loss, and automated instrumentation and controls for efficient combustion. Emission limit = 1,000,257 tons/yr applied to all stacks combined on a 12-month rolling time period basis. This limit applies during periods of startup and shutdown.
*MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2019-10-22 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2--A 667 MMBTU/H natural gas fired CTG with a HRSG. | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2 is a nominally rated 667 MMBTU/H natural gas fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas fired duct burner rated at 204 MMBTU/h to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR and oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | low carbon fuel (pipeline quality natural gas), good combustion practices and energy efficiency measures. | 430349 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Carbon capture and sequestration (CCS) would not be economically feasible based upon a qualitative assessment based upon the CTG/HRSG train analysis.
*MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2019-10-22 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1--A 667 MMBTU/H NG fired combustion turbine generator coupled with a heat recovery steam generator (HRSG) | 15.21 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR) and oxidation catalyst. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Low carbon fuel (pipeline quality natural gas), good combustion practices and energy efficiency measures. | 430349 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit applies during all operating modes. Carbon capture and sequestration (CCS) would not be economically feasible based upon a qualitative assessment based upon the CTG/HRSG train analysis.
*MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2019-12-19 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures | 2739722 | T/YR | 12-MONTH ROLLING TIME PERIOD; EACH UNIT | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CCS was ruled out as economically infeasible.
NJ-0079 | WOODBRIDGE ENERGY CENTER | CPV SHORE, LLC | MIDDLESEX | NJ | 7095 | USA | MARK TURNER | (415)293-1463 | MTURNER@CPV.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Mr. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS, yogesh.doshi@dep.state.nj.us; phone 609-633-7249 | 18940 - BOP110003 | 4911 | 221112 | 110055590953 | 10/12/2011 &nbsp;ACT | 07/25/2012 &nbsp;ACT | 2012-11-27 | 2018-04-17 | A |  | Woodbridge Energy Center (WEC), proposed at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, would be a new, highly efficient, 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,307 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, one small dew point fuel gas heater (fuel gas heater), a mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Other Permitting Information: Facility-Wide Greenhouse Gas (GHG) emissions as CO2e emissions= 2,073,645 tons per year | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural gas | 40297.6 | mmcubic ft/year | Woodbridge Energy Center (WEC), located at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, will be a new 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) each with a maximum rated heat input of 2,307 million British thermal units per hour (MMBtu/hr), that will utilize pipeline natural gas only, with 2 HRSGs, 2 Duct Burners (each 500 MMbtu/hr). | Carbon Dioxide Equivalent (CO2e) | Other - CO2 Monitored by CO2 CEMs | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 925 | LB/MW-H | BASED ON 12 MONTH PERIOD, ROLLING 1 MNTH | BACT-PSD |  | U | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0080 | HESS NEWARK ENERGY CENTER | HESS NEWARK ENERGY CENTER, LLC | ESSEX | NJ | 7105 | USA | PETER HAID | (774) 750-7088 | PHAID@HESS.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Supervisor: Yogesh Doshi - yogesh.doshi@dep.state.nj.us Phone: 609-633-7249 Permit Evaluator: Michael Hogan - michael.hogan@dep.state.nj.us. Phone: (609)-633-1124 | 08857/BOP110001 | 4911 | 221112 | 110044839903 | 12/10/2011 &nbsp;ACT | 11/01/2012 &nbsp;ACT | 2013-04-04 | 2018-04-17 | A |  | Combined Cycle Electric Generating Facility HESS Newark Energy Center (Hess-NEC), proposed at City of Newark (Essex County), New Jersey, would be a new, highly efficient, 655 MW combined-cycle power generating facility. Hess-NEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,320 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, a 12-cell mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Facility-wide Greenhouse Gas (GHG) emissions as CO2e emissions = 2,003,654 tpy | Combined cylce turbine with duct burner | 15.21 | natural gas | 39463 | mmcubic ft/year* | * Annual throughput is for 2 turbines, 2 duct burners and 1 auxiliary boiler | Carbon Dioxide Equivalent (CO2e) | Other - CO2 Monitored by CO2 CEMs | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 887 | LB/MW-H | CONSCUTV 12 MONTH PERIOD ROLLING 1 MONTH | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO2 Monitored by CO2 CEMs, CH4 and Nitrous oxide monitored by calculations
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burners. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Turbine efficiency and Use of Natural gas a clean burning fuel | 1237923 | TONS/YEAR | CONSECUTIVE 12 MONTH (ROLLING 1 MONTH) | BACT-PSD | OPERATING PERMIT | N | 0 | U | 947 | LB/MW-H | CONSECUTIVE 12 MONTH (ROLLING 1 MONTH) | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas with Duct Burner | 15.21 | natural gas | 4000 | h/yr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | USE OS NATURAL GAS A CLEAN BURNING FUEL | 888 | LB/MW-H | BASED ON CONSECUTIVE 12 MONTH ROLLING | BACT-PSD | NSPS , OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE: MONITORED BY CALCULATIONS. GHG as CO2e<= 888 LB/MW-H (GROSS OUTPUT) FOR TURBINE AND ITS ASSICIATED DUCT BURNER INCLUDING MWHs FROM ULSD FIRING AND STEAM TURBINE
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas without Duct Burner | 15.21 | Natural Gas | 8040 | H/YR |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 888 | LB/MW-H | BASED ON CONSECUTIVE 12 MONTH ROLLING | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE: MONITORED BY CALCULATIONS. GHG as CO2e<= 888 LB/MW-H (GROSS OUTPUT) FOR TURBINE AND ITS ASSICIATED DUCT BURNER INCLUDING MWHs FROM ULSD FIRING AND STEAM TURBINE
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Siemens, without duct burners | 15.21 | Natural Gas | 515600 | MMSCF/rolling 12-months | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process without duct burners. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A | (Greenhouse Gasses (GHG)) | CO2e | P | state-of-the-art high efficiency combustion technology | 318404 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1435847 | T/YR | PER ROLLING 12-MONTHS | 840 | LB/MW-H | GROSS OUTPUT | 0 | 0 | N |  | Additional limit: 840 LB/MW-H gross output. BACT is compliance with the proposed NSPS: 1000 LB CO2/MW-H gross output. 99% of the CO2e is CO2. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Siemens, with duct burners | 15.21 | Natural Gas | 51560 | MMSCF/rolling 12-MO | Two Siemens 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process with duct burners. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A | (Greenhouse Gasses (GHG)) | CO2e | P | state-of-the-art high efficiency combustion technology | 318404 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1435847 | T/YR | PER ROLLING 12-MONTHS | 0 |  | SEE NOTES | 0 | 0 | N |  | Additional limit: 840 LB/MW-H gross output. BACT is compliance with the proposed NSPS: 1000 LB CO2/MW-H gross output. 99% of the CO2e is CO2. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Mitsubishi, without duct burners | 15.21 | Natural Gas | 47917 | MMSCF/rolling 12-MO | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process without duct burners. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A | (Greenhouse Gasses (GHG)) | CO2e | P | state-of-the-art high efficiency combustion technology | 318404 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1394611 | T/YR | PER ROLLING 12-MONTHS | 0 |  | SEE NOTES | 0 | 0 | N |  | Additional limit: 840 LB/MW-H gross output. BACT is compliance with the proposed NSPS: 1000 LB CO2/MW-H gross output. 99% of the CO2e is CO2. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Mitsubishi, with duct burners | 15.21 | Natural Gas | 47917 | MMSCF/rolling 12-MO | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process with duct burners. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A | (Greenhouse Gasses (GHG)) | CO2e | P | state-of-the-art high efficiency combustion technology | 318404 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1394611 | T/YR | PER ROLLING 12-MONTHS | 0 |  | SEE NOTES | 0 | 0 | N |  | Additional limit: 840 LB/MW-H gross output. BACT is compliance with the proposed NSPS: 1000 LB CO2/MW-H gross output. 99% of the CO2e is CO2. T/YR limit is for 2 turbines.
OH-0360 | CARROLL COUNTY ENERGY | CARROLL COUNTY ENERGY | CARROLL | OH | 44615 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0113762 | 4911 | 221112 | 110064671127 | 04/11/2013 &nbsp;ACT | 11/05/2013 &nbsp;ACT | 2015-12-30 | 2019-04-01 | A |  | Natural gas fired combined cycle gas turbine electric generating station of nominal capacity of 742 MW | Installation of a natural gas-fired combined cycle combustion turbine electric utility power plant, nominally rated at 742 MW. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural Gas | 2045 | MMBTU/H | Two identical General Electric 7FA combined cycle combustion turbine (each at 2,045 mmBtu/hr heat input turbine at ISO conditions and 566 mmBtu/hr heat input duct burner, HHV) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. All throughputs and emission limits are for each turbine. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A | (Greenhouse Gasses (GHG)) | CO2e | P | state-of-the-art high efficiency combustion technology and natural gas fuel only | 307279 | LB/H |  | BACT-PSD |  | U | 0 | U | 1345883.48 | T/YR | PER ROLLING 12 MONTH PERIOD | 0 |  | SEE NOTES | 0 | 0 | N |  | 859 lb/MW-hr at ISO conditions and without duct firing and 307,279 lb/hr gross energy output value at ISO conditions and with duct firing. Limits are for each turbine.
OH-0363 | NTE OHIO, LLC |  | BUTLER | OH | 45044 | USA | MICHAEL SCHUSTER | (904)436-6896 | MSCHUSTER@NTEENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0116610 | 4911 | 221112 | 110070379584 | 04/07/2014 &nbsp;ACT | 11/05/2014 &nbsp;ACT | 2019-02-22 | 2019-04-01 | A |  | Combined-cycle, natural gas-fired power plant | Initial installation of either one (1) Mitsubishi Hitachi Power Systems Americas M501JAC or one (1) Mitsubishi Hitachi Power Systems Americas M501GAC single power block in a 1x1 combined-cycle multi-shaft configuration, including a combustion turbine and heat recovery steam generator with duct burners and a steam turbine to be known as the Middletown Energy Center. | Turbine generator with HRSG and duct burners (P001) | 15.21 | Natural gas | 3278.5 | MMBTU/H | Combined-cycle combustion turbine generator (CTG) with heat recovery steam generator (HRSG), natural gas-fired, including duct burners (DB). Permit was for either Mitsubishi Hitachi Power Systems America M501GAC or M501JAC. The M501GAC was installed. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A for CO2 | (Greenhouse Gasses (GHG)) | CO2e | B | Good combustion, oxidation catalysts, used of natural gas, energy efficiency. | 880 | LB/MW-H | SEE NOTES. | BACT-PSD |  | U | 0 | U | 375130 | LB/H | SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | CO2e emissions shall not exceed 880 Lb/MW-hr and 375,130 Lbs/hr gross energy output, @ ISO conditions, 100% load, without duct firing, and 1,626,781 tons per rolling, 12-month period.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 1 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2022 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Carbon Dioxide Equivalent (CO2e) | Other - ASME PTC 46-1996 | (Greenhouse Gasses (GHG)) | CO2e | P | high efficiency | 7471 | BTU/KW-H | HHV NET PER EACH CCT BLOCK. SEE NOTES. | BACT-PSD |  | U | 0 | U | 4898977 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  |  | 0 | 0 | N |  | 7,471 Btu/kW-hr (HHV, net) for each CCT block (ISO conditions corrected for plant elevation, without duct firing or inlet evaporative cooling, baseload, and not accounting for transformer losses). 4,898,977 tons of CO2e (total combined for the four CCTs) as a rolling, 12-month basis under Scenario 1.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 2 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2144 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Carbon Dioxide Equivalent (CO2e) | Other - ASME PTC 46-1996 | (Greenhouse Gasses (GHG)) | CO2e | P | high efficiency | 7471 | BTU/KW-H | HHV NET PER EACH CCT BLOCK. SEE NOTES. | BACT-PSD |  | U | 0 | U | 5174943 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  |  | 0 | 0 | N |  | 7,471 Btu/kW-hr (HHV, net) for each CCT block (ISO conditions corrected for plant elevation, without duct firing or inlet evaporative cooling, baseload, and not accounting for transformer losses). 5,174,943 tons of CO2e (total combined for the four CCTs) as a rolling, 12-month basis under Scenario 1.
OH-0366 | CLEAN ENERGY FUTURE - LORDSTOWN, LLC | CLEAN ENERGY FUTURE - LORDSTOWN, LLC | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0117655 | 4911 | 221112 | 110070396317 | 09/17/2014 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2019-02-27 | 2019-06-19 | A |  | 962 MW (gross winter output) combined cycle gas turbine (CCGT) facility | Initial installation permit for the construction of the Lordstown Energy Center - a nominal 940 MW combined cycle gas turbine (CCGT) facility. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 2725 | MMBTU/H | Combined cycle combustion turbine (2,725 MMBtu/hr heat input turbine at ISO conditions and 179 MMBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Limits and throughputs are for single turbine. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A for CO2 | (Greenhouse Gasses (GHG)) | CO2e | P | High efficient combustion technology | 833 | LB/MW-H | WITHOUT DUCT BURNERS. SEE NOTES. | BACT-PSD |  | U | 0 | U | 369700 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | Carbon dioxide equivalent (CO2e) emissions shall not exceed 833 lb/MW-hr gross energy output (at full load ISO conditions without duct firing) and 369,700 lbs/hr (maximum under any condition with duct firing). 1,510,526.6 t/yr per rolling 12 month period for all operating modes, including startup periods.
OH-0367 | SOUTH FIELD ENERGY LLC | SOUTH FIELD ENERGY LLC | COLUMBIANA | OH | 43968 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0119495 | 4911 | 221112 | Not Found | 09/14/2015 &nbsp;ACT | 09/23/2016 &nbsp;ACT | 2019-02-28 | 2019-06-19 | A |  | 1150 MW combined-cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the South Field Energy facility, a nominal 1,150 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in Wellsville, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3131 | MMBTU/H | Two identical combined cycle combustion turbine (3,131 MMBtu/hr heat input turbine at ISO conditions, natural gas firing with evaporative cooler on and 800 MMBtu/hr maximum heat input natural gas-fired duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), catalytic oxidizer, and wet injection for ULSD firing. Heat input for ULSD firing at ISO conditions, with evaporative cooler on is 3,173 MMBtu/hr. Throughputs and limits are for single turbine except as noted. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A for CO2 | (Greenhouse Gasses (GHG)) | CO2e | P | High efficient combustion technology | 481301 | LB/H | NAT GAS, WITH DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 2045634.5 | T/YR | PER ROLLING 12 MONTH PERIOD. | 0 |  | SEE NOTES | 0 | 0 | N |  | 481,301 lbs/hr for natural gas (maximum under any condition with duct firing). 546,182 lbs/hr for ultra low sulfur diesel (maximum under any condition with duct firing). Facility heat rate shall not exceed 7,165 Btu/net kW-hr energy output (at full load ISO conditions, natural gas firing, without duct firing).
OH-0370 | TRUMBULL ENERGY CENTER | TRUMBULL ENERGY CENTER | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122331 | 4911 | 221112 | Not Found | 03/23/2017 &nbsp;ACT | 09/07/2017 &nbsp;ACT | 2019-03-05 | 2019-06-19 | A |  | 940 MW combined cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the Trumbull Energy Center, a nominal 940 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in the Village of Lordstown, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3025 | MMBTU/H | Two identical combined cycle combustion turbine (3,025 mmBtu/hr heat input turbine at ISO conditions and 237 mmBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Throughputs and limits are for single turbine except as noted. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A for CO2 | (Greenhouse Gasses (GHG)) | CO2e | P | High efficient combustion technology | 833 | LB/MW-H | SEE NOTES. | BACT-PSD |  | U | 0 | U | 1683213 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 833 lb/MW-hr gross energy output (at full load ISO conditions without duct firing). 884 lbs/ MW-hr gross energy output (maximum under any full load condition with duct firing). 401,084 lb/hr (maximum under any condition with duct firing). 1,683,213 T/YR per rolling 12 month period all operating modes, including startup and shutdown periods.
OH-0372 | OREGON ENERGY CENTER | OREGON ENERGY CENTER | LUCAS | OH | 43616 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0121049 | 4911 | 221112 | Not Found | 06/27/2016 &nbsp;ACT | 09/27/2017 &nbsp;ACT | 2019-03-06 | 2019-06-19 | A |  | Combined cycle gas turbine (CCGT) facility | Installation of natural gas-fired combined cycle combustion turbine power plant. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3055 | MMBTU/H | Combined cycle combustion turbine (3,055 mmBtu/hr heat input turbine at ISO conditions and 221.3 mmBtu/hr heat input duct burner) with dry low NOX combustors, selective catalytic reduction (SCR), and catalytic oxidation. All heat values are on a HHV basis. Throughputs and limits are for single turbine except as noted. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A for CO2 | (Greenhouse Gasses (GHG)) | CO2e | P | high efficiency combustion design | 401921 | LB/H | SEE NOTES. | BACT-PSD |  | U | 0 | U | 1689461 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  |  | 0 | 0 | N |  | 833 lb/MW-hr (pounds per megawatt-hour) gross energy output (at full load ISO conditions without duct firing) and 401,921 lb/hr (maximum under any condition with duct firing). 1,689,461 t/yr per rolling 12 month period for all operating modes, including startup and shutdown.
OH-0374 | GUERNSEY POWER STATION LLC | GUERNSEY POWER STATION LLC | GUERNSEY | OH | 43723 | USA | MARY KING | (317)447-4513 | MARY@APEXPOWERGROUP.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122594 | 4911 | 221112 | 110070379546 | 04/14/2017 &nbsp;ACT | 10/23/2017 &nbsp;ACT | 2019-03-08 | 2019-06-19 | A |  | 1,650 MW combined cycle combustion turbine electrical generating facility | Installation PTI for a new 1,650 MW combined cycle natural-gas fired turbine plant and associated auxiliary boiler, firewater pumps, emergency generators and fuel gas heaters | Combined Cycle Combustion Turbines (3, identical) (P001 to P003) | 15.21 | Natural gas | 3516 | MMBTU/H | Three identical Combustion Turbines; GE 7HA.02 natural gas-fired lean pre-mix combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,516 MMBtu/hr HHV at 100% load and -18Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 997 MMBtu/hr HHV controlled with catalytic oxidation and selective catalytic reduction (SCR) and cooled with an air-cooled condenser (ACC) used to generate electricity. Throughputs and limits are for a single turbine except as noted. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A for CO2 | (Greenhouse Gasses (GHG)) | CO2e | P | high efficiency combustion practices as recommended by the manufacturer | 846 | LB/MW-H | WITHOUT DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 1000 | LB/MW-H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | Limits are for single turbine except as noted. 846 lb/MW-hr gross energy output at full load ISO conditions without duct burner. 450 kg per MW-h of gross energy output (1,000 lbs/MW-h) on a 12-operating-month rolling average basis with duct burner. 7,056,798 t/yr per rolling 12 month period for all 3 turbines.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | General Electric Combustion Turbine (P004) | 15.21 | Natural gas | 3544 | MMBTU/H | General Electric model 7HA.02 natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,544 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A for CO2 | (Greenhouse Gasses (GHG)) | CO2e | P | high efficiency combustion practices as recommended by the manufacturer | 775 | LB/MW-H | SEE NOTES. | BACT-PSD |  | U | 0 | U | 1915689 | T/YR | PER ROLLING 12 MONTH PERIOD | 0 |  |  | 0 | 0 | N |  | 775 lb/MW-hr gross energy output at full load ISO conditions when firing natural gas. Gross energy output is defined as the gross power output of the generators before accounting for any balance of plant loads.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Mitsubishi Combustion Turbine (P005) | 15.21 | Natural gas | 3320 | MMBTU/H | Mitsubishi Model 501JAC natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,320 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 108 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A for CO2 | (Greenhouse Gasses (GHG)) | CO2e | P | high efficiency combustion practices as recommended by the manufacturer | 1000 | LB/MW-H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 775 | LB/MW-H | WITHOUT DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | With duct burners: 450 kg per MW-h of gross energy output (1,000 lbs/MW-h) on a 12-operating-month rolling average basis, or, if a petition is granted, CO2 emissions shall not exceed 470 kg per MW-h of net energy output (1,030 lbs/MW-h) on a 12-operating- month rolling average basis. [40 CFR 60.5520(a)-(c) and Table 2 of 40 CFR Part 60, Subpart TTTT] Without duct burners: 775 lb/MW-hr gross energy output at full load ISO conditions when firing natural gas. Gross energy output is defined as the gross power output of the generators before accounting for any balance of plant loads. 1,811,235 t/yr per rolling, 12-month period.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Siemens Combustion Turbine (P006) | 15.21 | Natural gas | 3602 | MMBTU/H | Siemens Model SCC6-8000H natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,602 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 667 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A for CO2 | (Greenhouse Gasses (GHG)) | CO2e | P | high efficiency combustion practices as recommended by the manufacturer | 1000 | LB/MW-H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 775 | LB/MW-H | WITHOUT DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 450 kg per MW-h of gross energy output (1,000 lbs/MW-h) on a 12-operating-month rolling average basis, or, if a petition is granted, CO2 emissions shall not exceed 470 kg per MW-h of net energy output (1,030 lbs/MW-h) on a 12-operating- month rolling average basis. [40 CFR 60.5520(a)-(c) and Table 2 of 40 CFR Part 60, Subpart TTTT] 775 lb/MW-hr gross energy output at full load ISO conditions when firing natural gas. Gross energy output is defined as the gross power output of the generators before accounting for any balance of plant loads. 1,962,130 tons of CO2e emissions per rolling, 12-month period.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A for CO2 | (Greenhouse Gasses (GHG)) | CO2e | P | High efficient combustion technology | 1000 | LB/MW-H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 1012.4 | LB/MW-H | WITHOUT DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | With duct burners: 450 kg per MW-h of gross energy output (1,000 lbs/MW-h) on a 12-operating-month rolling average basis, or, if a petition is granted, CO2 emissions shall not exceed 470 kg per MW-h of net energy output (1,030 lbs/MW-h) on a 12-operating-month rolling average basis. [40 CFR 60.5520(a)-(c) and Table 2 of 40 CFR Part 60, Subpart TTTT] Without duct burners: 1,012.4 lbs/MW-hr gross energy output at full load ISO conditions when firing natural gas. Gross energy output is defined as the gross power output of the generators before accounting for any balance of plant loads. 2,499,820 t/yr of CO2e emissions per rolling, 12-month period.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3A for CO2 | (Greenhouse Gasses (GHG)) | CO2e | P | High efficient combustion technology | 1000 | LB/MW-H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 976 | LB/MW-H | WITHOUT DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | With duct burners: 450 kg per MW-h of gross energy output (1,000 lbs/MW-h) on a 12-operating-month rolling average basis, or, if a petition is granted, CO2 emissions shall not exceed 470 kg per MW-h of net energy output (1,030 lbs/MW-h) on a 12-operating-month rolling average basis. [40 CFR 60.5520(a)-(c) and Table 2 of 40 CFR Part 60, Subpart TTTT] Without duct burners: 976.0 lbs/MW-hr gross energy output at full load ISO conditions when firing natural gas. Gross energy output is defined as the gross power output of the generators before accounting for any balance of plant loads. 2,342,643 tons of CO2e emissions per rolling, 12-month period.
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | Combustion Turbine | 15.21 | Natural Gas | 360 | MW | This process represents the GE option for the project - One GE 7FA.05 natural gas-fired combustion turbine generator with an 820.5 MMBTUH duct burner. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | EFFICIENT DESIGN AND COMBUSTION. | 1000 | LB/MW-HR | ANNUAL | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | COMBUSTION TURBINE | 15.21 | NATURAL GAS | 360 | MW | This process represents the Siemens option for the project - One Siemens SGT6-5000F5 natural gas-fired combustion turbine generator with an 820.3 MMBTUH duct burner. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | EFFICIENT DESIGN AND COMBUSTION. | 1000 | LB/MW-HR | ANNUAL | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
PA-0278 | MOXIE LIBERTY LLC/ASYLUM POWER PL T | MOXIE ENERGY LLC | BRADFORD COUNTY | PA |  | USA | KENT J MORTON | (571) 594 - 0150 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MUHAMMAD Q. ZAMAN, ENVIRONMENTAL PROGRAM MANAGER, NORTHCENTRAL REGION | 08Â·00045A | 491 | 221112 | 45-2015223-1 | 09/26/2011 &nbsp;ACT | 10/10/2012 &nbsp;ACT | 2012-12-03 | 2015-04-03 | A |  |  | The project consists of two identical 1 x 1 power blocks, and each block includes a combustion gas turbine and a steam turbine. Each combined-cycle process will also include a heat recovery steam generator and supplemental duct burners. Additionally, one diesel-fired emergency generator, one diesel-fired fire water pump, two diesel fuel storage tanks, two lube oil storage tanks, and one aqueous ammonia storage tank were proposed to be constructed and operated. Each combined-cycle process will be rated at 468 MW or less. | Combined-cycle Turbines (2) - Natural gas fired | 15.21 | Natural Gas | 3277 | MMBTU/H | Two combine cycle Turbines, each with a combustion turbine and heat recovery steam generator with duct burner. Each combined-cycle process will be rated at 468 MW or less. The heat input rating of each combustion gas turbine is 2890 MMBtu/hr (HHV) or less, and the heat input rating of each supplemental duct burner is equal to 387 MMBtu/hr (HHV) or less. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices. | 1480086 | T/YR | 468 MW POWERBLOCK | BACT-PSD |  | U | 0 | U | 1388540 | T/YR | 454 MW POWERBLOCK | 0 |  |  | 0 | 0 | N
PA-0296 | BERKS HOLLOW ENERGY ASSOC LLC/ONTELAUNEE | BERKS HOLLOW ENERGY ASSOC LLC | BERKS | PA | 19605 | USA | BRADLEY J COOLEY | 636-534-3268 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | WILLIAM R. WEAVER, SOUTHCENTRAL REGION AIR PROGRAM MANAGER 909 Elmerton Ave, Harrisburg, PA 17701 717-705-4868 | 06-05150A | 4931 | 221112 | 110056155342 | 05/08/2012 &nbsp;ACT | 12/17/2013 &nbsp;ACT | 2014-04-17 | 2020-03-02 | A |  | This application is for the construction of a natural gas-fired combined-cycle electric generation facility that is designed to generate up to 855 MW nominal, using 2 combustion turbine generators and 2 heat recovery steam generators that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. | This application is for the construction of a natural gas-fired combined-cycle electric generation facility that is designed to generate up to 855 MW nominal, using 2 combustion turbine generators and 2 heat recovery steam generators that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. | Turbine, Combined Cycle, #1 and #2 | 15.21 | Natural Gas | 3046 | MMBTU/H | Equipped with SCR and Oxidation Catalyst | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1380899 | T/YR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2018-12-21 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large combustion turbine | 15.21 | Natural Gas | 0 |  | This process entry is for operations with the duct burner. Limits entered are for each turbine. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 1881905 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2018-12-21 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two Combine Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 3001.57 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. . (Operational limits are for each CCCT NG-fired with duct burner) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Good combustion practices and oxidation catalyst | 883 | LB/MW-HR | EXPRESSED AS CO2E (NET) | BACT-PSD |  | U | 0 | U | 2896556 | TONS | YEAR (NET) EXPRESSED AS CO2E | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative emissions from both CCCT in any 12-month period expressed as CO2e
PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Combustion turbine with duct burner | 15.21 | Natural gas | 3304.3 | MMBtu/hr | Limits are for each CCCT and yearly limits are for cumulative turbine and duct burner. Duct burner throughput is 637.9 MMBtu/hr. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1629115 | TONS | YEAR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG with duct burner NG only | 15.21 | Natural Gas | 3338 | MMBtu/hr | Emission limits are for each turbine operating with duct burner and do not include startup/shutdown emissions. Tons per year limits is a cumulative value for all three CCCT. CEMS for NOx, CO, and O2. Each CCCT and duct burner have 5 operational scenarios: 1 CCCT with duct burner fired - fueled by NG only 2 CCCT with duct burner fired - fueled by NG blend with ethane 3 CCCT without duct burner fired - fueled by NG only 4 CCCT without duct burner fired - fueled by NG blend with ethane 5 CCCT without duct burner fired - fueled by ULSD (Limited to emergency use only) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | low sulfur fuel and good combustion practices | 3352086 | TONS | 12-MONTH ROLLING BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064098541 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2018-12-21 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine With Duct Burner | 15.21 | Natural Gas | 3727 | MMBtu/hr | DLN burner, SCR, Oxidation Catalyst and shall maintain and operate the sources and associated air cleaning devices in accordance with good engineering practice. shall install, certify, maintain and operate continuous emission monitoring systems (CEMS) for nitrogen oxides, carbon monoxide, carbon dioxide, and ammonia emissions on the exhaust of each combined-cycle powerblock. Emissions limits are for each combustion turbine/duct burner block. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1000 | LB CO2/MWH | GROSS ON A 12-MONTH ROLLING BASIS | BACT-PSD | NSPS | U | 0 | U | 1828492 | TPY |  | 0 |  |  | 0 | 0 | N
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Natural Gas-Fired Combustion Turbine with HRSG | 15.21 | Natural Gas | 1339 | MMBtu/hr | Turbine throughput is 1019.7 MMBtu/hr when burning natural gas and 1083.7 MMBtu/hr when burning No. 2 oil. Duct burner throughput is 319.3 MMBtu/hr. Duct burner firing will occur during natural gas combustion only. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion design and practices | 1800 | LB/MWH | 12-MONTH MOVING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TN-0164 | TVA - JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134 | USA | JACK BYARS | (423) 751-2666 | JGBYARS@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov |  | 972969 | 4911 | 221112 | 110070502905 | 09/26/2017 &nbsp;ACT | 02/01/2018 &nbsp;ACT | 2019-03-21 | 2019-03-21 | D |  | Combustion turbines and combined cycle plant | Permit 972969 adds startup and shutdown limits to the requirements established in PSD permit 970816F. | Dual-fuel CT and HRSG with duct burner | 15.21 | Natural Gas | 1020 | MMBtu/hr | Rated input capacity is 1020 MMBtu/hr (CT) and 319 MMBtu/hr (duct burner) when burning natural gas and 1084 MMBtu/hr when burning #2 oil. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion design & practices | 1800 | LB/MWH | 12-MONTH MOVING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0612 | THOMAS C. FERGUSON POWER PLANT | LOWER COLORADO RIVER AUTHORITY | LLANO | TX | 78767-7041 | USA | KENNETH TAYLOR | 979-249-8377 | KEN.TAYLOR@LCRA.ORG | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | Melanie Magee, 6PD-R Air Permit Section EPA Region VI (214)665-7161 | PSD-TX-1244-GHG | 4911 | 221122 | 110000456620 | 04/14/2011 &nbsp;ACT | 11/10/2011 &nbsp;ACT | 2012-02-08 | 2013-09-25 | D |  | Install 2 new natural gas-fired combined-cycle combustion turbine units (U1-STKand U2-STK) with a generating capacity of approximately 590 MW. The steam produced from the two new combustion turbines will exhaust to two dedicated Heat Recovery Steam Generators (HRSG) to produce steam. The steam produced from the two HRSGs is routed to the new shared steam turbine unit to produce electricity for sale to the Electric Reliability Council of Texas (ERCOT) power grid. |  | COMBINED CYCLE TURBINE GENERATOR U1-STK | 15.21 | Natural Gas | 1746 | MMBTU/H | Natural gas-fired GE 7FA combustion turbine unit, U1-STK. and is rated at Max. based-load output of 195 MW and vented to a Heat Recovery Steam Generator(HRSG) that is equipped with a SCR and an Oxidation Catalyst(OC). | Carbon Dioxide Equivalent (CO2e) | Other - EPA Method 3a or 3b | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 908957.6 | LB/H | 30-DAY ROLLING AVERAGE | BACT-PSD | OTHER | U | 0 | U | 153392.1 | LB/H | STARTUP AND SHUTDOWN (ONLY) | 0 |  |  | 0 | 0 | N
TX-0679 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | GHGPSDTX123 | 4925 | 221210 | 110057188626 | 12/12/2014 &nbsp;ACT | 02/27/2015 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. The LNG terminal will operate three trains continuously (8,760 hours per year) using eighteen (18) GE LM2500+G4 (with dry low NOx emissions) gas-fired refrigeration compressor turbines, six on each train. There are two methane, two ethylene, and two propane refrigeration turbines per train. |  | Refrigeration Compressor Turbine | 15.21 | natural gas | 40000 | hp | There are three LNG trains. In total there are (6) GE LM2500+ DLE turbines driving the compressors in the ethylene refrigeration sections. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | install efficient turbines, follow the turbine manufacturerâ€™s emission-related written instructions for maintenance activities including prescribed maintenance intervals to assure good combustion and efficient operation. Compressors shall be inspected and maintained according to a written maintenance plan to maintain efficiency. | 146754 | TPY | 12-MONTH ROLLING BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is for each turbine.
TX-0743 | AUSTIN ENERGY, SAND HILL ENERGY CENTER | CITY OF AUSTIN | TRAVIS | TX | 78617 | USA | RAVI JOSEPH | 512-322-6284 | RAVI.JOSEPH@AUSTINENERGY.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Tracie Donaldson, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, Texas 75202 | PSD-TX-1012-GHG | 4911 | 221112 | 110038018383 | 08/06/2014 &nbsp;ACT | 09/29/2014 &nbsp;ACT | 2015-05-29 | 2016-07-06 | B | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | This project authorizes the construction of an additional combined cycle unit at the existing Sand Hill Energy Center (SHEC). The SHEC operates in a 1x1x1 configuration and the new unit will allow the SHEC to operate in a 2x2x1 configuration. New unit will generate an additional 222 MW of gross electrical power. | The Texas Commission on Environmental Quality is the permitting authority for non-GHG emissions associated with this project. See: CN600129118; RN100215052 | Combustion Turbine with HRSG, Duct Burners, and SCR | 15.21 | Natural Gas | 7943 | Btu/kWh (HHV, gross) | GE 7FA.04 Gross Heat Rate is with and without duct burner firing and includes MSS. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 930 | LB CO2/MWH | 365-DAY ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 1461908 | TPY CO2E | 365-DAY ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | Emission limits include MSS and duct burner firing. Initial performance test for CO2 is required. CH4, N2O and CO2e are calculated.
TX-0748 | FGE POWER, FGE TEXAS PROJECT | FGE POWER, LLC | MITCHELL | TX | 79565 | USA | EMERSON FARRELL | 281-362-2830 | EFARRELL@FGEPOWER.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | EPA Region 6 Permit Writer: Aimee Wilson, Air Permitting Section (6PD-R), EPA Region 6, 1445 Ross Avenue, Dallas, Tx 75202 | PSD-TX-1364-GHG | 4911 | 221112 | Not Assigned | 03/20/2014 &nbsp;ACT | 04/28/2014 &nbsp;ACT | 2015-06-09 | 2016-07-06 | A | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | Authorizes FGE to construct a new combined cycle electric generating plant (FGETP) in Mitchell County, Texas. FGETP will generate 1,620 megawatts (MW) of gross electrical power near the City of Westbrook. The gross electrical power output is based on four combined cycle combustion turbines rated at nominal 230.7 MW each and two steam turbines with duct burner firing that are designed to produce an additional 336 MW each. FGEâ€™s rated output for a single power block is 810 MW of gross electrical output. FGETP will consist of the following sources of GHG emissions: â€¢ Four natural gas-fired CTGs (Alstom GT24) equipped with lean pre-mix low-NOx combustors; â€¢ Four natural gas-fired duct burner system equipped heat recovery steam generators (HRSGs); â€¢ Natural gas piping and metering; â€¢ Two diesel fuel-fired emergency electrical generator engines; â€¢ Two diesel fuel-fired fire water pump engines; and â€¢ Electrical equipment insulated with sulfur hexafluoride (SF6). | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. The CN and RN have not been assigned. | Combined Cycle Combustion Turbine with DB, HRSG and SCR | 15.21 | Natural Gas | 7625 | Btu/kWh | The plant will consist of four identical Alstom GT24 natural gas-fired CTGs. The CTGs will burn pipeline quality natural gas to rotate an electrical generator to generate electricity. The exhaust gas will exit the CTG and be routed to the heat recovery steam generator (HRSG) for steam production. Steam produced by each of the two HRSGs will be routed to the steam turbine. The two CTGs and one steam turbine will be coupled to electric generators to produce electricity for sale to the Electric Reliability Council of Texas (ERCOT) power grid. Each CTG has an approximate maximum base-load electric power output of 230.7 MW. The maximum electric power output from each steam turbine is approximately 336 MW. The units may operate at reduced load to respond to changes in system power requirements and/or stability. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 889 | LB CO2/MWH, GROSS | APPLIES WITH OR WITHOUT DB; INCLUDES MSS | BACT-PSD |  | U | 0 | U | 48 | TON CO2/HR PER EVENT | MSS | 0 |  |  | 0 | 0 | N |  | FGE will demonstrate compliance with the CO2 limit established as BACT by the use of a CO2 CEMS and also by recording the heat input to and the net power output from the generating station to demonstrate on an ongoing basis the 7,625 Btu/kWh GHG BACT limit. The CO2 CEMS shall measure and record the CO2 emissions. To demonstrate compliance with the CO2 BACT limit using CO2 CEMS, the measured hourly CO2 emissions are divided by the net hourly energy output and averaged daily. An initial stack test demonstration will be required for CO2 emissions from GT-1, GT-2, GT-3, and GT-4. FGE proposes to demonstrate compliance with the proposed heat rate with an annual compliance test at 90% load, corrected to ISO conditions. An initial stack test demonstration for CH4 and N2O emissions is not required. An annual compliance test, at or above 90% max load is also required. -A startup is defined as the period that begins when fuel is first fired. A planned startup for each combustion turbine is limited to 180 minutes (cold startup) per event. -A planned shutdown is defined as the period that begins when the gas turbine passes below 50% of full load and fuel flow ceases. The shutdown shall not exceed 60 minutes. -Startup and shutdown activities are limited to 1,460 hours per year per turbine on a 12-month rolling total basis.
TX-0766 | GOLDEN PASS LNG EXPORT TERMINAL | GOLDEN PASS PRODUCTS, LLC | JEFFERSON | TX |  | USA | BOB TOMLINSON | 713-860-6348 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 116055, PSDTX1386, GHGPSDTX100 | 4922 | 486210 | UNKNOWN | 04/03/2015 &nbsp;ACT | 09/11/2015 &nbsp;ACT | 2015-09-21 | 2016-07-06 | B |  | Liquefied natural gas (LNG) export terminal. |  | Refrigeration Compression Turbines | 15.21 | natural gas | 15.6 | MMtpy | Six GE Frame 7 Turbines at site. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Equipment specifications & work practices - Good combustion practices and use of low carbon fuel | 614533 | TPY |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0773 | FGE EAGLE PINES PROJECT | FGE EAGLE PINES, LLC | CHEROKEE | TX |  | USA | EMERSON FARRELL | 281-407-7749 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, 512-239-1095, Erik.Hendrickson@tceq.texas.gov | 131316, PSDTX1454, AND GHGPSDT | 4911 | 221112 | UNKNOWN | 09/10/2015 &nbsp;ACT | 11/04/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | The FGEEP Project will include three natural gas-fired combined cycle (NGCC) power blocks, each block comprised of two gas-fired combustion turbines, two supplemental fired duct burners (DBs) heat recovery steam generators (HRSGs), and one steam turbine. FGEEP selected Alstom GT36 combustion turbines (CTs), each nominally rated at 321 megawatts (MW). Each HRSG is equipped with DBs that will have a maximum design heat input capacity of 799 million British thermal units per hour (MMBtu/hr). The CTs and DBs are fueled with pipeline quality natural gas. Each power block will also have a steam turbine generator designed to produce approximately 502 MW with the additional duct firing. Each of the three blocks will include the following ancillary equipment: one multi-cell condenser/cooling tower, one emergency generator, one firewater pump, two diesel storage tanks, and pressurized aqueous ammonia storage tanks. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 321 | MW | Alstom GT36 combustion turbines (321 MW)+ 799 million British thermal units per hour (MMBtu/hr) duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Low carbon fuel, good combustion, efficient combined cycle design | 886 | LB/MW H | WITHOUT DUCT FIRING | BACT-PSD | NSPS | N | 0 | U | 816 | LB/MW H | WITH DUCT FIRING | 0 |  |  | 0 | 0 | N
TX-0787 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joel Lunsford, 512-239-1513, joel.lunsford@tceq.texas.gov | GHGPSDTX125, 111393, PSDTX1368 | 4911 | 221112 | unknown | 12/10/2015 &nbsp;ACT | 03/01/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | Electric Generation |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 497 | MW |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 937 | LB/MW HR |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD COMBUSTION PRACTICES | 924 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.21 | natural gas | 10 | M TONNES/YR | Four GE Frame 7E gas turbines for refrigeration and compression at the site | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Equipment specifications & work practices - Good combustion practices and use of low carbon fuel | 504517 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Simple Cycle Electrical Generation Gas Turbines 15.210 | 15.21 | natural gas | 34 | MW | Nine GE PGT25+G4 gas turbines for electrical generation at the site at 34 MW/turbine | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Equipment specifications & work practices - Good combustion practices and use of low carbon, low sulfur fuel | 156912 | T/YR |  | BACT-PSD |  | N | 0 | U | 1060 | LB/MW |  | 0 |  |  | 0 | 0 | N
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 megawatts (MW)) | 15.21 | natural gas | 889 | MW | (2) GE 7HA.01 in a 2x1 configuration and a 872 million British thermal units per hour (MMBtu/hr) duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 901 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Subparts KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 1127 | MW | (2) GE 7HA.02 in a 2x1 configuration and a 985 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 865 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Subparts KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 748 | MW | (2) GE 7FA.05 in a 2x1 configuration and a 826 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 944 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 889 | MW | (2) MHI 501GAC in a 2x1 configuration and a 221 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 929 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 889 | MW | (2) MHI 501GAC in (2) 1x1 configurations and a 221 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 929 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and TTTT
TX-0791 | ROCKWOOD ENERGY CENTER | ROCKWOOD ENERGY CENTER, LLC | COLORADO | TX |  | USA | JASON TUNDERMANN | 303-755-2358 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean Oâ€™Brien 512-239-1137 Sean.obrien@tceq.texas.gov | GHGPSDTX122, 122003, PSDTX1424 | 4911 | 221112 | UNKNOWN | 12/14/2015 &nbsp;ACT | 03/18/2016 &nbsp;ACT | 2016-03-21 | 2016-07-29 | A |  | power plant operating in combined cycle mode consisting of two turbines each with duct burners, both fired on natural gas, and a heat recovery steam generator. The applicant has proposed six potential turbine models with different duct burner maximum heat input rates for each option. Only one will be constructed. |  | Combined Cycle &amp; Cogeneration (&gt; 25 MW) | 15.21 | natural gas | 915 | MW | (2) Siemens SCC6-8000H(1.4) in a 2x1 configuration and a 326 MMBtu/hr duct burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 965 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and TTTT
TX-0805 | EAGLE MOUNTAIN STEAM ELECTRIC STATION | EAGLE MOUNTAIN POWER COMPANY | TARRANT | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joel Lunsford, x-1513, joel.lunsford@tceq.texas.gov | GHGPSDTX115, 107569, PSDTX1432 | 4911 | 221112 | 110005028638 | 11/04/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-14 | 2017-11-17 | B |  | Electric Generation |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 462 | MW |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 917 | LB/MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
TX-0810 | DECORDOVA STEAM ELECTRIC STATION (DECORDOVA STATION) | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL BARNES | 214-875-8374 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5221 Ruth.Alvirez@tceq.texas.gov | 107569, PSDTX1432, GHGPSDTX124 | 4911 | 221112 | Not Found | 07/26/2016 &nbsp;ACT | 10/04/2016 &nbsp;ACT | 2016-10-04 | 2017-11-16 | C |  | two combustion turbines (CTGs) authorized to operate in simple cycle or combined cycle. | The simple cycle operations were issued in 2013, but the combined cycle criteria pollutant PSD permit / state amendment was issued on March 8, 2016. This GHG initial review is linked to the 2016 action which added combined cycle capability, it does not apply to the simple cycle operations which were authorized in 2013. | Combined Cycle and Cogeneration (&gt;25 MW) | 15.21 | natural gas | 213 | MW | Two turbine options: GE 7FA [210 megawatts (MW)] or Siemens 5000F (231MW) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices and firing low carbon fuel. | 966 | LB/MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
TX-0817 | CHOCOLATE BAYOU STEAM GENERATING (CBSG) STATION | INEOS USALLC | BRAZORIA | TX |  | USA | THERESA VITEK | 281-581-3498 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | 123117, PSDTX1460, GHGPSDTX135 | 4911 | 221112 | Not Found | 12/22/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-28 | 2017-11-16 | A |  | support facility providing steam and electricity |  | Combined Cycle Cogeneration | 15.21 | NATURAL GAS | 50 | MW | 2 UNITS EACH 50 MW GE LM6000 | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1000 | LB/MW H |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | MACT TTTT
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Combined Cycle Turbine with Heat Recovery Steam Generator, fired Duct Burners, and Steam Turbine Generator | 15.21 | NATURAL GAS | 426 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines with HRSGs and Steam Turbine Generators | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Pipeline quality natural gas | 960 | LB / MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | PIPELINE QUALITY NATURAL GAS, GOOD COMBUSTION PRACTICES | 884 | LB/MWH |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | COMBINED CYCLE TURBINE MSS REDUCED LOAD | 15.21 | NATURAL GAS | 0 |  | 9 HOURS STARTUP, 1 HOUR SHUTDOWN | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | minimizing duration of startup / shutdown events, engaging the pollution control equipment as soon as practicable (based on vendor recommendations and guarantees), and meeting the emissions limits on the MAERT | 223 | TON/H |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
VA-0319 | GATEWAY COGENERATION 1, LLC - SMART WATER PROJECT | GATEWAY GREEN ENERGY | PRINCE GEORGE | VA | 23875-3000 | USA | T. EDWARD MCDANIEL | 972-638-8798 | EMCDANIEL@GGEHLLC.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52375-002 | 4911 | 221112 | 110045446718 | 01/11/2012 &nbsp;ACT | 08/27/2012 &nbsp;ACT | 2013-01-16 | 2015-05-29 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Combined cycle electrical power generating facility (160 MW), consisting of two combusion turbines (Rolls Royce Trent 60 WLE) with associated HRSG and no duct burning. |  | COMBUSTION TURBINES, (2) | 15.21 | Natural Gas | 593 | MMBTU/H | Burns primarily natural gas but has the capacity to burn up to 500 hours of ultra low sulfur diesel fuel (ULSD) as backup. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Controlled by the use of low carbon fuels and high efficiency design. The heat rate shall be no greater than 8,983 Btu/kW-h (HHV, gross). | 295961 | T/YR | 12 MO ROLLING AVG | BACT-PSD | NSPS | Y | 0 | U | 1050 | LB/MWH | 12 MO AVERAGE | 0 |  |  | 0 | 0 | N |  | Initial compliance testing, using ASME Performance Test Code on Overall Plant Performance (ASME PTC 46-1996).
VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404 | 4911 | 221112 | 110055066440 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2019-06-19 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | COMBUSTION TURBINE GENERATORS, (3) | 15.21 | Natural Gas | 3442 | MMBTU/H | Three (3) Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners (natural gas-fired). | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficient combustion practices and low GHG fuels. | 7500 | BTU/KW-H |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Option 1 - Normal Operation | 15.21 | natural gas | 34000 | MMCF/YR | Option 1: Two on one configuration: 3,482 MMBtu/hr combustion turbine with 475 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficient combustion practices and low GHG fuels | 883 | LB CO2E/MW-H | 12 MO ROLLING TOTAL | BACT-PSD | NSPS , SIP | N | 0 | N | 6745 | BTU/KW-H NET HHV | INITIAL HEAT RATE TEST | 0 |  |  | 0 | 0 | N |  | Compliance with the lb/Mw-hr limit can be based on CO2 CEMs or calculations, monthly by summing the CO2e emissions and dividing by the electrical energy output. Complianc with the heat rate limit (Btu/kW-hr) is based on an initial heat rate test on power block.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combusion Turbine - Option 2 - Normal Operation | 15.21 | Natural Gas | 35000 | MMCF/YR | Option 2: Two on one configuration: 3,116 MMBtu/hr combustion turbine with 991 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficient combustion practices and low GHG fuels | 883 | LB CO2E/MW H | 12 MO ROLLING TOTAL | BACT-PSD | NSPS , SIP | N | 0 | N | 6625 | BTU/KW H NET HHV | INITIAL HEAT RATE TEST | 0 |  |  | 0 | 0 | N |  | Compliance with the LB/MW H limit can be based on CO2 CEMS or calculations, monthly by summing the CO2e emissions & dividing the electrical energy output. Compliance with the heat rate limit (BTU/KW H) is based on an initial heat rate test on power block.
*VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2020-03-18 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/hr natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/hr combustion turbine. Emission limits reflect the operation of each of the three turbines. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficient combustion practices and low GHG fuels | 812 | LB/CO2E/MW-HR | 12 MO ROLLING TOTAL | BACT-PSD | NSPS , SIP | N | 0 | N | 6452 | BTU/KW-HR NET HHV | INITIAL HEAR RATE TEST | 0 |  |  | 0 | 0 | N |  | Compliance with the lb/Mw-hr limit can be based on CO2 CEMs or calculations, monthly by summing the CO2e emissions and dividing by the electrical energy output. Compliance with the heat rate limit (Btu/kW-hr) is based on an initial heat rate test on power block. Additional, incremental heat rate values and emission limits apply during the life of the turbines. Annual CO2-e emission limits for each turbine are 2,123,519 tons/year.
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Combined Cycle Turbine/Duct Burner | 15.21 | Natural Gas | 2419.61 | mmBtu/Hr | This entry is for both of two identical units at the facility. Nominal 197 mW General Electric Frame 7FA.04 Turbine w/ Duct Burner - throughput denotes aggregate heat input of turbine and duct burner (HHV). | Carbon Dioxide Equivalent (CO2e) | Other - Test Method 3A/B (CO2) | (Greenhouse Gasses (GHG)) | CO2e | P | Use of GE Frame 7EA CT Low Carbon Fuel | 272556 | LB/H |  | BACT-PSD |  | U | 0 | U | 792 | LB/MW/H |  | 0 |  |  | 0 | 0 | N |  | CO2e limit is applicable with and without duct firing.
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2018-06-25 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.02 Turbine | 15.21 | Natural Gas | 3496.2 | mmBtu/hr | Nominal 640 mWe All emission limits steady-state and include 1000 mmBtu/hr Duct Burner in operation Short Term startup and shutdown limits in lb/event given in permit. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of Natural Gas, Model GE7HA | 528543 | LB/HR |  | BACT-PSD | NSPS | U | 0 | U | 2315020 | TONS/YEAR |  | 826 | LB/MW-HR |  | 0 | 0 | N
*WV-0032 | BROOKE COUNTY POWER PLANT | ESC BROOKE COUNTY POWER I, LLC | BROOKE | WV | 26035 | USA | ANDREW DORN | 7163121042 | DREW.DORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 Steven.R.Pursley@wv.gov | R14-0035 | 4911 | 221112 | Not Found | 03/30/2018 &nbsp;ACT | 09/18/2018 &nbsp;ACT | 2018-12-20 | 2019-01-02 | A |  | Nominal 925 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.01 Turbine | 15.21 | Natural Gas/Ethane | 2737.7 | mmBtu/hr | Facility has 2 identical units, only 1 entry in RBLC. Nominal 462.5 mWe. All emission limits steady-state and include 424 mmBtu/hr Duct Burner in operation. Short Term startup and shutdown limits in lb/event given in permit. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of Natural Gas, Model GE7HA | 417382 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 829 | LB/MW-HR |  | 0 | 0 | N
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | Mitsubishi M501-GAC combustion turbine, combined cycle configuration with duct burner. | 15.21 | natural gs | 2988 | MMBTU/H | or ULSD; Duct burner 499 MMBtu/hr, natural gas | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Thermal efficiency Clean fuels | 1000 | PER GROSS MWH | 365-DAY ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0739 | AIR LIQUIDE, BAYOU COGENERATION PLANT | AIR LIQUIDE LARGE INDUSTRIES U.S., L.P. | HARRIS | TX | 77507 | USA | ASWATH KALAPPA | 713-402-2396 | ASWATH.KALAPPA@AIRLIQUIDE.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Aimee Wilson, US EPA Region 6, Air Permitting Section (6PD-R) 1445 Ross Avenue,Dallas, TX 75202 | PSD-TX-612-GHG | 4931 | 221112 | 110000462758 | 08/29/2013 &nbsp;ACT | 11/21/2013 &nbsp;ACT | 2015-05-28 | 2016-07-06 | D | http://yosemite.epa.gov/r6/Apermit.nsf/AirP#A | The redevelopment project at the Bayou Cogeneration Plant consists of replacing components of the power block and the boilers at the existing facility. | The Texas Commission on Environmental Quality (TCEQ) reviewed and issued the associated permitting action for the non-GHG emissions. CN600300693; RN100233998 | Combustion Turbine with HRSG and Duct Burners | 15.21 | Pipeline Nat Gas and 90/10 blend | 11988 | Btu/kWhr (HHV, gross) | Does not include a steam cycle condensing turbine and is not a combined cycle plant. Fuel is limited to pipeline quality natural gas or a max of 90/10 ratio of pipeline quality natural gas blended with off-gas based on an annual average. CO2 CEMS and Fuel Flow Meter are required. Stack sampling is required for CO2 using 40 CFR 60.8 and Method 3a or 3b and calculation for CH4, N2O and CO2e. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 7720 | BTU/KWH (HHV, GROSS) | 365-DAY ROLLING AVERAGE INCLUDES MSS | BACT-PSD |  | U | 0 | U | 485588 | TPY CO2E | 12-MONTH TOTAL, ROLLING MONTHLY | 0 |  |  | 0 | 0 | N |  | CO2 CEMS and Flow Meter required. Performance stack sampling required in accordance with 40 CFR 60.8 and Method 3a or 3b for CO2 emissions. Calculation for CH4, N2O and CO2e are required. Thermal Efficiency is is calculated daily based on monitoring fuel gas low, fuel HHV, and gross power production. Startup limited to 240 min per event and Shutdown is limited to 60 min per event.
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (COLD STARTUP PERIODS) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 224 | LB/H | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 410 | LB/EVENT | COLD STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | COLD STARTUP PERIODS SHALL NOT EXCEED 1.8 HR/EVENT OR 50 EVENTS/YR
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (WARM &amp; HOT STARTUP PERIODS) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 247 | LB/H | WARM & HOT STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 329 | LB/EVENT | WARM & HOT STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | WARM & HOT STARTUP PERIODS SHALL NOT EXCEED 1.3 HR/EVENT OR 260 EVENTS/YR
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 674 | LB/H | SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 337 | LB/EVENT | SHUTDOWN PERIODS | 0 |  |  | 0 | 0 | N |  | SHUTDOWN PERIODS SHALL NOT EXCEED 0.5 HR/EVENT OR 310 EVENTS/YR
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 2 | PPMVD | @15% O2, 1-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 7.65 | LB/H | 1-HR AVG (NO DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (COLD STARTUP PERIODS) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 224 | LB/H | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 410 | LB/EVENT | COLD STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | COLD STARTUP PERIODS SHALL NOT EXCEED 1.8 HR/EVENT OR 50 EVENTS/YR
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (WARM &amp; HOT STARTUP PERIODS) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 247 | LB/H | WARM & HOW STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 329 | LB/EVENT | WARM & HOW STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | WARM & HOT STARTUP PERIODS SHALL NOT EXCEED 1.3 HR/EVENT OR 260 EVENTS/YR
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 674 | LB/H | SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 337 | LB/H | SHUTDOWN PERIODS | 0 |  |  | 0 | 0 | N |  | SHUTDOWN PERIODS SHALL NOT EXCEED 0.5 HR/EVENT OR 310 EVENTS/YR
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 3 | PPMVD | @15% O2, 1-HR AVG (W/ DUCT BURNING) | BACT-PSD |  | U | 0 | U | 13.35 | LB/H | 1-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | Natural Gas | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 2 | PPMVD | @15% O2, 1-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 7.65 | LB/H | 1-HR AVG (NO DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 3 | PPMVD | @15% O2, 1-HR AVG (W/ DUCT BURNING) | BACT-PSD |  | U | 0 | U | 13.35 | LB/H | 1-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 1.5 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 6.27 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N |  | CO EMISSION LIMITS DURING 3-YR PERIOD IMMEDIATELY FOLLOWING COMMENCEMENT OF COMMERCIAL OPERATION: 2.0 PPMVD @15% O2 OR 8.35 LB/HR, 1-HR AVG (NO DUCT FIRING)
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 2 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 10 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (STARTUP &amp; SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 180 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 1000 | LB/H | EACH TURBINE & HRSG | BACT-PSD |  | U | 0 | U | 1932 | LB/H | BOTH TURBINES & HRSGS | 0 |  |  | 0 | 0 | N |  | 1) STARTUP FOR EACH TURBINE & HRSG NOT TO EXCEED 4.5 HOURS; 2) SHUTDOWN FOR EACH TURBINE & HRSG NOT TO EXCEED 0.5 HOURS; 3) ANNUAL LIMIT FOR BOTH TURBINES NOT TO EXCEED 1248 HRS/YR
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 1.5 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 6.27 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N |  | CO EMISSION LIMITS DURING 3-YR PERIOD IMMEDIATELY FOLLOWING COMMENCEMENT OF COMMERCIAL OPERATION: 2.0 PPMVD @15% O2 OR 8.35 LB/HR, 1-HR AVG (NO DUCT FIRING)
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 2 | PPMVD | @15% O2, 1-HR AVG (W/ DUCT FIRING) | BACT-PSD |  | U | 0 | U | 10 | LB/H | 1-HR AVG (W/ DUCT FIRING) | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (STARTUP &amp; SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 180 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 1000 | LB/H | EACH TURBINE & HRSG | BACT-PSD |  | U | 0 | U | 1902 | LB/H | BOTH TURBINES & HRSGS | 0 |  |  | 0 | 0 | N |  | 1) STARTUP FOR EACH TURBINE & HRSG NOT TO EXCEED 4.5 HOURS; 2) SHUTDOWN FOR EACH TURBINE & HRSG NOT TO EXCEED 0.5 HOURS; 3) ANNUAL LIMIT FOR BOTH TURBINES NOT TO EXCEED 1248 HRS/YR
CA-1209 | HIGH DESERT POWER PROJECT | HIGH DESERT POWER PROJECT LLC | SAN BERNADINO | CA | 92394 | USA | JON BOYER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 98-01 | 4911 | 221112 | 110014461420 | 09/25/2009 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-11 | 2014-01-15 | C | http://www.epa.gov/region09/air/permit/r9-permits-issued.html | 720 MW NATURAL GAS FIRED POWER PLANT | RBLC Management: There were many duplicate pollutant records Editor repeated all emission limits for each of the 3 types of operation, Start-up, Normal, and Shutdown. Record was edited and duplicate records were deleted. Original Note: PSD Permit amended to change the design of the power plant. These changes include a modification in the turbine configuration from 3x3x3 (i.e., three combustion turbines (CT), three heat recovery steam generators (HRSG), and three steam turbine generators (STG)) to a 3x3x1 configuration, reconfiguration of the cooling tower from three towers to one, addition of a diesel firewater pump engine, modification of the stack location, elevation, and diameter, and modification in the physical dimensions of the cooling tower, steam turbine, and HRSG structure. The terms and conditions included in the PSD permit issued February 15, 2001, and the modeling analyses on which the original determinations were based, remain valid and in effect. | COMBUSTION TURBINE GENERATORS (NORMAL OPERATION) | 15.21 | NATURAL GAS | 190 | MW | THREE (3) COMBUSTION TURBINE GENERATORS AT 190 MW EACH AND EQUIPPED WITH A 160 MMBTU/HR DUCT BURNER AND HRSG | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 4 | PPMVD | @15% O2, 24-HR AVG | BACT-PSD |  | U | 0 | U | 17.53 | LB/H | 24-HR AVG | 0 |  |  | 0 | 0 | N
CA-1209 | HIGH DESERT POWER PROJECT | HIGH DESERT POWER PROJECT LLC | SAN BERNADINO | CA | 92394 | USA | JON BOYER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 98-01 | 4911 | 221112 | 110014461420 | 09/25/2009 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-11 | 2014-01-15 | C | http://www.epa.gov/region09/air/permit/r9-permits-issued.html | 720 MW NATURAL GAS FIRED POWER PLANT | RBLC Management: There were many duplicate pollutant records Editor repeated all emission limits for each of the 3 types of operation, Start-up, Normal, and Shutdown. Record was edited and duplicate records were deleted. Original Note: PSD Permit amended to change the design of the power plant. These changes include a modification in the turbine configuration from 3x3x3 (i.e., three combustion turbines (CT), three heat recovery steam generators (HRSG), and three steam turbine generators (STG)) to a 3x3x1 configuration, reconfiguration of the cooling tower from three towers to one, addition of a diesel firewater pump engine, modification of the stack location, elevation, and diameter, and modification in the physical dimensions of the cooling tower, steam turbine, and HRSG structure. The terms and conditions included in the PSD permit issued February 15, 2001, and the modeling analyses on which the original determinations were based, remain valid and in effect. | COMBUSTION TURBINE GENERATOR (STARTUP PERIODS) | 15.21 | NATURAL GAS | 190 | MW | THREE (3) COMBUSTION TURBINE GENERATORS AT 190 MW EACH AND EQUIPPED WITH A 160 MMBTU/HR DUCT BURNER AND HRSG | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 183 | LB/COLD STARTUP | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 168 | LB/WARM STARTUP | WARM STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | RBLC Management: Limit Moved from Standard Limit Fields: &lsquo;&lsquo;138.0 LB.Hot Startup, Hot Startup Periods&lsquo;&lsquo; Remember, the Standard Limit fields may be used only when the process and pollutant match the information in Volume 3 of the RBLC User's Manual, Appendix E. The Standard Limit fields should not be used to list a third emission limit. If there are more than 2 emission limits, the additional information must be entered in the pollutant notes field. Original Note: OTHER REQUIREMENTS: 1) COLD STARTUP NOT TO EXCEED 4.5 HRS; 2) WARM STARTUP NOT TO EXCEED 2.6 HRS; 3) HOT STARTUP NOT TO EXCEED 1.9 HRS; 4) SEE PERMIT FOR ALTERNATIVE COLD STARTUP SCENARIO REQUIREMENTS
CA-1209 | HIGH DESERT POWER PROJECT | HIGH DESERT POWER PROJECT LLC | SAN BERNADINO | CA | 92394 | USA | JON BOYER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 98-01 | 4911 | 221112 | 110014461420 | 09/25/2009 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-11 | 2014-01-15 | C | http://www.epa.gov/region09/air/permit/r9-permits-issued.html | 720 MW NATURAL GAS FIRED POWER PLANT | RBLC Management: There were many duplicate pollutant records Editor repeated all emission limits for each of the 3 types of operation, Start-up, Normal, and Shutdown. Record was edited and duplicate records were deleted. Original Note: PSD Permit amended to change the design of the power plant. These changes include a modification in the turbine configuration from 3x3x3 (i.e., three combustion turbines (CT), three heat recovery steam generators (HRSG), and three steam turbine generators (STG)) to a 3x3x1 configuration, reconfiguration of the cooling tower from three towers to one, addition of a diesel firewater pump engine, modification of the stack location, elevation, and diameter, and modification in the physical dimensions of the cooling tower, steam turbine, and HRSG structure. The terms and conditions included in the PSD permit issued February 15, 2001, and the modeling analyses on which the original determinations were based, remain valid and in effect. | COMBUSTION TURBINE GENERATOR (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 190 | MW | THREE (3) COMBUSTION TURBINE GENERATORS AT 190 MW EACH AND EQUIPPED WITH A 160 MMBTU/HR DUCT BURNER AND HRSG | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 239 | LB/SHUTDOWN | SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | SHUTDOWN NOT TO EXCEED 1 HR
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (WARM STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | CATALYTIC OXIDATION SYSTEM | 373.6 | LB/H | WARM STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 790.5 | LB/EVENT | WARM STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF WARM STARTUPS NOT TO EXCEED 180 MINUTES; 2) WARM STARTUP MEANS A STARTUP THAT IS NOT A HOT OR COLD STARTUP
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (HOT STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | CATALYTIC OXIDATION SYSTEM | 370.3 | LB/H | HOT STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 679.6 | LB/EVENT | HOT STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF HOT STARTUPS NOT TO EXCEED 90 MINUTES; 2) HOT STARTUP MEANS A STARTUP WHEN THE COMBUSTION TURBINE HAS BEEN IN OPERATION DURING THE PRECEDING 8 HOURS
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | CATALYTIC OXIDATION SYSTEM | 483.5 | LB/H | TURBINE SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 483.5 | LB/EVENT | TURBINE SHUTDOWN PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF SHUTDOWN NOT TO EXCEED 30 MINUTES; 2) SHUTDOWN MEANS THE PERIOD BEGINNING WITH THE LOWERING OF EQUIPMENT FROM BASE LOAD AND LASTING UNTIL FUEL FLOW IS COMPLETELY OFF AND COMBUSTION HAS CEASED
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | CATALYTIC OXIDATION SYSTEM | 3 | PPMVD | @15% O2, 3-HR ROLLING AVG | BACT-PSD |  | U | 0 | U | 17.9 | LB/H | 3-HR ROLLING AVG | 0 |  |  | 0 | 0 | N
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (COLD STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | CATALYTIC OXIDATION SYSTEM | 429.6 | LB/H | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 1355.6 | LB/EVENT | COLD STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF COLD STARTUPS NOT TO EXCEED 270 MINUTES; 2) COLD STARTUP MEANS STARTUP WHEN THE COMBUSTION TURBINE HAS NOT BEEN IN OPERATION DURING THE PRECEDING 72 HOURS
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 1.5 | PPMVD | @15% O2, 1-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 2 | PPMVD | @15% O2, 1-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N |  | 2.0 PPMVD @15% O2, 1-HR AVG (NO DUCT BURNING) APPLIES DURING 3-YEAR DEMONSTRATION PERIOD
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (STARTUP PERIODS) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | CATALYST OXIDATION SYSTEM | 410 | LB/EVENT | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 329 | LB/EVENT | WARM & HOT STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | DURING STARTUP OR SHUTDOWN, EMISSIONS OF CO FROM BOTH CTGS COMBINED SHALL NOT EXCEED 790 LB/HR; DURATION OF COLD STARTUP NOT TO EXCEED 110 MIN; DURATION OF WARM & HOT STARTUP NOT TO EXCEED 80 MIN
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 110 | MMBTU/H | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST SYSTEM | 337 | LB/EVENT | SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | DURING STARTUP OR SHUTDOWN, EMISSIONS OF CO FROM BOTH CTGS COMBINED SHALL NOT EXCEED 790 LB/HR; SHUTDOWN NOT TO EXCEED 30 MIN
CA-1251 | PALMDALE ENERGY PROJECT | PALMDALE ENERGY, LLC | LOS ANGELES | CA | 93551 | USA | TOM CAMERON |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov | Staff Contact: Lisa Beckham beckham.lisa@epa.gov (415) 972-3811 | SE 17-01 | 4911 | 221122 | Not Found | 08/16/2017 &nbsp;ACT | 04/25/2018 &nbsp;ACT | 2018-10-25 | 2020-01-31 | A | https://www.epa.gov/caa-permitting/palmdale-energy-project-prevention-significant-deterioration-psd-permit | 645 MW (nominal) Natural Gas-fired Combined Cycle Power Plant, 2 x 1 configuration, auxiliary boiler for faster startup | See also docket: https://www.regulations.gov/docket?D=EPA-R09-OAR-2017-0473. Permit decision was appealed to EPA's Environmental Appeals Board. Board denied review on October 23, 2018. Information available through www.epa.gov/eab and https://yosemite.epa.gov/oa/EAB_Web_Docket.nsf/f22b4b245fab46c6852570e6004df1bd/ad735c0b822500258525829d004217eb!OpenDocument. 1/31/20 -- SYS MGR -- Link to permit is <https://www.regulations.gov/document?D=EPA-R09-OAR-2017-0473-0028> | Combustion Turbines (GEN1 and GEN2) | 15.21 | Natural Gas | 2217 | MMBTU/H | Each combustion turbine rated at 214 MW, with a maximum heat input rate of 2,217 MMBtu/H (HHV, at ISO conditions); natural gas-fired Siemens SGT6-5000F; each vents to dedicated Heat Recovery Steam Generator and a shared 276 MW Steam Turbine Generator; 160-ft stack height; 22-ft stack diameter | Carbon Monoxide | Other - CEMS | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 1.5 | PPM @ 15% O2 | 1-HR, DEMO LIMIT, W/O DUCT FIRING | BACT-PSD |  | N | 0 | U | 2 | PPM @ 15% O2 | 1-HR W/DUCT FIRING | 0 |  |  | 0 | 0 | N |  | During demonstration period, limit without duct firing is 2.0 ppm Mass Emission Limits: w/o duct firing: 7.8 lb/hr (10.4 lb/hr during demonstration period) w/ ducting firing: 11.3 lb/hr Startup/Shutdown Limits: Cold Start: 416 lb/event, 39 minutes Warm Start: 378 lb/event, 35 minutes Hot Start: 305 lb/event, 30 minutes Shutdown: 75.9 lb/event, 25 minutes NAAQS modeling-based limit: 419 lb/hr during SU/SD
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055426409 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Four combined cycle combution turbines | 15.21 | natural gas | 373 | MMBTU/H | Three GE, LMS6000 PF, natural gas-fired, combined cycle CTG, rated at 373 MMBtu per hour each, based on HHV and one (1) HRSG each with no Duct Burners | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Good combustion control and catalytic oxidation | 4 | PPMVD AT 15% O2 | 1-HR AVE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 3.3 | LB/H | 30-DAY ROLLING AVE | 0 |  |  | 0 | 0 | N |  | startup limit: 140.0 lb per event shutdown limit: 15.0 lb per event compliance is monitored with continuous emissions monitors
CO-0076 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110058377830 | 06/16/2014 &nbsp;ACT | 12/11/2014 &nbsp;ACT | 2014-12-31 | 2016-02-19 | C |  | Electric generation | Permit modification to convert startup and shutdown BACT limits to an hourly basis (from event based). | Four combined cycle combution turbines | 15.21 | natural gas | 373 | MMBTU/H each | GE, LM6000 PF, natural gas fired, combined cycle combustion turbines, with HRSG and no duct burners. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Catalytic Oxidation. | 38 | LB/H | 4-HR ROLLING AVE / STARTUP AND SHUTDOWN | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The CO limit was converted to an equivalent hourly based limit (the original permit included an event based limit) for periods of startup and shutdown.
CT-0157 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo james.grillo@ct.cov 860-424-3570 | 144-0023 | 4911 | 221112 | 110040589672 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-03 | 2016-02-19 | A |  | 805 MW Combined Cycle Power Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/12 months |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 0.9 | PPMVD @15% O2 | 1 HR BLOCK | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.7 | PPMVD @15% O2 | 1 HR BLOCK | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
CT-0158 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo; james.grillo@ct.gov; 860-424-3570 | 144-0024 | 4911 | 221112 | 110040589672 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-04 | 2016-02-19 | A |  | 805 MW Combined Cycle Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/yr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 0.9 | PPMVD @15% O2 | 1 HR BLOCK | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.7 | PPMVD @15% O2 | 1 HR BLOCK | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/o Duct Firing | 15.21 | Natural Gas | 2969 | MMBtu/hr | Throughput is for turbine only | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 0.9 | PPMVD @15% O2 | 1 HOUR BLOCK | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/Duct Firing | 15.21 | Natural Gas | 2639 | MMBtu/hr | Duct burner MRC is 946 MMbtu/hr | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 1.7 | LB/MMBTU | 1 HOUR BLOCK | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Clean burners that prevent CO formation | 4.3 | PPMVD@15% O2 | 3-HR AVERAGE, NATURAL GAS OPERATION | BACT-PSD |  | U | 0 | U | 10 | PPMVD@15% O2 | 3-HR AVERAGE, ULSD OPERATION | 0 |  |  | 0 | 0 | N |  | No CEMS required. Also subject to limits of 7.1 ppmvd @15% O2 for gas and 13.6 ppmvd@15%O2 for ULSD, at low loads. The lowest loads at which the facility can demonstrate compliance with these low-load limits determines the minimum permitted operating load for the CT. Compliance by stack test.
*FL-0363 | DANIA BEACH ENERGY CENTER | FLORIDA POWER AND LIGHT COMPANY | BROWARD | FL | 33314 | USA | JOHN HAMPP | 561-691-2894 | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-017-AC | 4911 | 221112 | 110002044065 | 07/27/2017 &nbsp;ACT | 12/04/2017 &nbsp;ACT | 2018-04-03 | 2018-04-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.F.ZIP | 1200 megawatt 2-on-1 combined cycle facility, natural gas-fired, with limited ULSD use. GE 7HA turbines | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.D.ZIP | 2-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural gas | 4000 | MMBtu/hr | Two nominal 430 MW combustion turbines, coupled to a steam turbine generator | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Clean burning fuel with lean pre-mix turbines | 4.3 | PPMVD@15% O2 | AT LOADS > 90% | BACT-PSD |  | U | 0 | U | 7.2 | PPMVD@15% O2 | FOR LOADS < 90% | 0 |  |  | 0 | 0 | N |  | For oil, limit is 10.0 ppmvd @ 15% O2 for loads > 90%, and 14.6 ppmvd@15% O2 for loads < 90%. Compliance by annual stack test.
*FL-0367 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 36410 | USA | ROY BELDEN | (203) 357-6820 | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-001-AC | 4911 | 221112 | 110012581820 | 02/16/2018 &nbsp;ACT | 07/27/2018 &nbsp;ACT | 2019-03-19 | 2019-03-19 | B | https://arm-permit2k.dep.state.fl.us/nontv/1010524.001.AC.F.ZIP | A 573-megawatt (MW) (winter) 1-on-1 combined cycle plant which includes a heat recovery steam generator with duct firing, along with supporting equipment. Natural gas is the only permitted fuel for the combined cycle unit. | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/1010524.001.AC.R.ZIP | 1-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural Gas | 3266.9 | MMBtu/hour | One nominal 385 MW GE 7HA.02 CTG and one HRSG with duct firing [approximately 210 MMBtu/hour], and one nominal 210 MW steam turbine generator (STG) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Clean burning fuel with good combustion practices | 4.3 | PPMVD @15% O2 | (TURBINE LOADS â‰¥ 90%); THREE 1-HR RUNS | BACT-PSD | SIP | U | 0 | U | 7.1 | PPMVD @15% O2 | (TURBINE LOADS < 90%); THREE 1-HR RUNS | 6.5 | PPMVD @15% O2 | (WHEN DUCT FIRING); THREE 1-HR RUNS | 0 | 0 | N |  | Initial and annual stack testing required.
GA-0138 | LIVE OAKS POWER PLANT | LIVE OAKS COMPANY, LLC | GLYNN | GA | 31525 | USA | BURT WALLACE | 478 943-2331 | BURT_1@BELLSOUTH.NET | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-127-0075-P-02-0 | 4911 | 221122 | UNKNOWN | 11/19/2008 &nbsp;ACT | 04/08/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | A |  | LIVE OAKS POWER PLANT PROPOSED FACILITY WILL OPERATE AS A FULLY DISPATCHABLE ELECTRIC GENERATING FACILITY. THE COMBINED CYCLE SYSTEM WILL UTILIZE TWO COMBUSTION TURBINES AND ONE STEAM TURBINE, CONFIGURED IN A TWO-ON-ONE ARRANGEMENT. THE HEAT CONTENT OF THE EXHAUST GASSES WIL BE RECOVERED BY A HEAT RECOVERY STEAM GENERATOR (HRSG), AND USED TO DRIVE A STEAM TURBINE. DURING PEAK LOADS A DUCT BURNER IN THE HRSG CAN BE FIRED TO AD ADDITIONAL HEAT ENERGY TO THE GAS TURBINE EXHAUST, INCREASING THE PRODUCTION OF STEAM SENT TO THE STEAM TURBINE. THE COMBUSTION TURBINES (CTs) SELECTED ARE SIEMENS MODEL SGT6-5000F. EACH COMBUSTION TURBINE WILL GENERATE 200 MW OF ELECTRIC POWER. THE GROSS ELECTRICAL CAPACITY OF THE COMBINED CYCLE FACILITY FIRING NATURAL GAS WILL THEN BE 600 MW. | PM10 74.3(+) EMISSIONS (T/YR) | COMBINED CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.21 | NATURAL GAS | 600 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | GOOD COMBUSTION PRACTICES AND CATALYTIC OXIDATION | 2 | PPM@15%02 | 3 HOUR AVERAGE WO/O DUCT FIRING/CONDITIO | BACT-PSD | OPERATING PERMIT , SIP | U | 0 | N | 3.2 | PPM@15%02 | 3 HOUR AVERAGE W/DUCT FIRING/CONDITION 2 | 208 | T/YR | 12 CONSECUTVE MONTH AVERAGE/CONDITION 2. | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #1 - combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr | two identical Siemens SGT6-5000F combined cycle turbines without duct firing, each at 2258 mmBtu/hr generating approx. 300 MW each. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | catalytic oxidizer | 2 | PPM | 30-DAY ROLLING AVG. @15% O2 | BACT-PSD |  | U | 95 | U | 552.4 | TON/YR | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #2 -combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | CO catalyst | 2 | PPM | 30-DAY ROLLING AVERAGE | BACT-PSD |  | N | 95 | U | 552.4 | TON/YR | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | 552.4 ton/yr limit includes startup, shutdown and malfunction
IL-0112 | NELSON ENERGY CENTER | INVENERGY NELSON, LLC | LEE | IL | 61071-9722 | USA | JOEL SCHROEDER | 312-224-1417 | JSCHROEDER@INVENERGYLLC.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Manish Patel, Permit Analyst Manish.Patel@illinois.gov 217-785-1722 | 98080039 | 4911 | 221112 | 110007399644 | 11/19/2010 &nbsp;ACT | 12/28/2010 &nbsp;ACT | 2013-02-21 | 2020-04-16 | A |  | Natural gas-fired electic power generation facility with two &quot;combined cycle&quot; turbines followed by heat recovery steam generators (HRSG) and the capability for supplemental fuel firing in the HRSG for each turbine using duct burners. NOx emissions will be controlled by SCR and low NOx combustors. | LSP-Nelson Energy started construction pursuant to a permit issued in year 2000 for a facility that was not completed due to financial difficulties, which eventually resulted in LSP-Nelson entering bankruptcy. Substantial construction of foundations and infrastructure for all units and physical installation of one turbine were completed, including construction of HRSGs. | Electric Generation Facility | 15.21 | Natural Gas | 220 | MW each | Two combined cycle combustion turbines followed by HRSGs with capability for supplemental fuel firing in HRSG for each combustion turbine using duct burners. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | N |  | 5 | PPMVD @ 15% O2 | HOURLY AVG EXCEPT DURING SSM OR TUNING | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0129 | CPV THREE RIVERS ENERGY CENTER | CPV THREE RIVERS, LLC | GRUNDY | IL | 60450 | USA | MIKE BRUNO | 781-817-8972 | MBRUNO@CPV.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Illinois EPA, Bureau of Air Permit Section | 16060032 | 4911 | 221112 | Not Found | 06/10/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2019-01-02 | 2019-02-19 | A |  | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, each with a combustion turbine and associated heat recovery steam generator (HRSG). The turbines would burn natural gas and ultra-low sulfur diesel (ULSD) as a backup fuel. Other units include an auxiliary boiler, fuel heater, engines, natural gas piping and components, circuit breakers and roadways. |  | Combined Cycle Combustion Turbines | 15.21 | Natural Gas | 3474 | mmBtu/hr | Throughput of ultra-low sulfur diesel (ULSD) is 3798 mmBtu/hr. Combined cycle combustion turbines w/ heat recovery steam generator (HRSG). Turbine inlets will have inlet evaporative cooling systems to cool inlet air during warm weather to increase power output. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst | 2 | PPMV @ 15 % O2 | 3 OPERATING-HOUR, ROLLED HOURLY, AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 is not applicable during periods of startup, shutdown, tuning and commissioning. Permit limits are as follows, applicable on a per-turbine basis: For natural gas: Without duct burner: 15.4 lb/hr With duct burner: 19.0 lb/hr For ULSD: 17.0 lb/hr For periods of startup, shutdown and commissioning: Extended startups using natural gas: 1522 lb/hr Commissioning and other than extended startups using natural gas: 204 lb/hr ULSD: 231 lb/hr For periods of tuning: Natural Gas: 204 lb/hr ULSD: 231 lb/hr Averaging period for the above permit limits is 3-hour average. Also see Condition 2.1.6(a)(iv) of the issued permit for operation during transitions.
IL-0130 | JACKSON ENERGY CENTER | JACKSON GENERATION, LLC | WILL | IL | 60421 | USA | JAMES KIEFER | 847-908-2833 | JKEIFER@POWERUSA.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov |  | 17040013 | 4911 | 221112 | Not Found | 04/04/2017 &nbsp;ACT | 12/31/2018 &nbsp;ACT | 2019-07-23 | 2020-04-16 | A |  | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, each with a combustion turbine and associated heat recovery steam generator (HRSG). The turbines would only burn natural gas. Other units include an auxiliary boiler, fuel heater, emergency engines, natural gas piping and components, circuit breakers and roadways | Additional pollutants: Sulfuric Acid Mist: 48 tons/year; GHG as CO2e: 4,752,085 tons/year | Combined-Cycle Combustion Turbine | 15.21 | Natural Gas | 3864 | mmBtu/hr | Combined-cycle combustion turbines with heat recovery steam generator (HRSG). Turbines will have inlet evaporative cooling systems to cool inlet air during warm weather to increase power output. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst | 2 | PPMV | 3 OPERATING HOUR AVERAGE @ 15% O2 | BACT-PSD |  | U | 0 | U | 211.5 | PPMV | 3 OPERATING HOUR AVERAGE @ 15% O2 | 0 |  |  | 0 | 0 | N |  | Emission Limits 1 is applicable when operating with duct burner. Emission Limit 2 is applicable without the duct burner, after 36 months from initial operation. Pounds/hour limit without duct burner is 30.5, 3-hour average. Pounds/hour limit with duct burner is 33,9, 3-hour average. Emission Limits 1 and 2 and pounds/hour limits do not apply during startup/shutdown/commissioning and tuning. Pounds/hour limit for startup/shutdown/commissioning is 483.5. Pounds/hour limit for tuning is 239. Pounds/hour limit for period of very low load is 20.6
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 2 | PPMVD | 3 HOURS | BACT-PSD |  |  | 90 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LIMIT ONE IS USED WITH CONDITIONS AT 15% O2 WITH USING DUCT BURNERS.
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES - START UP/SHUTDOWN CYCLE | 15.21 | NATURAL GAS | 2300 | MMBTU/H | A STARTUP/SHUTDOWN CYCLE IS A PAIR OF SUBSEQUENT SHUTDOWN AND STARTUP EVENTS (I.E., ONE STARTUP FOLLOWED BY ONE SHUTDOWN REPRESENTS ONE STARTUP/SHUTDOWN CYCLE). | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 2125 | LB | *EVENT | BACT-PSD |  |  | 0 |  | 407.5 | TONS | 12 CONSECUTIVE MONTH PERIOD | 0 |  |  | 0 | 0 | N |  | LIMIT ONE USES THE COLD START EMISSION TOTALS, PER CCCT AS A SHORT-TERM LIMIT DURING STARTUP/SHUTDOWN EVENTS. LIMIT TWO IS COMBINED EMISSIONS FROM CCCT1 THROUGH CCCT4 FOR THE DURATION OF THE COMBINED STARTUP/SHUTDOWN EVENT. *EVENT = ONE STARTUP OR ONE SHUTDOWN
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002049328 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | COMBINED CYCLE TURBINE GENERATORS (UNITS 6A &amp; 6B) | 15.21 | NATURAL GAS | 7146 | MMBTU/H | TURBINES ALSO PERMITTED TO BURN NO. 2 FUEL OIL AND ULTRA LOW SULFUR DIESEL. FUEL OIL USE IS LIMITED TO 1000 HOURS PER YEAR. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES | 3 | PPMVD @ 15% O2 | HOURLY AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 3 | PPMVD @ 15% O2 | HOURLY AVERAGE | 0 | 0 | N |  | CO MONITORED USING CEMS. 3 PPMVD @ 15% O2 LIMIT APPLIES WHEN OPERATING W/ AND W/O THE DUCT BURNER AND WHEN FIRING FUEL OIL. STARTUP/SHUTDOWN: PROGRESS THROUGH THE SU/SD EVENT AS QUICKLY AS POSSIBLE WHILE FOLLOWING THE MANUFACTURER'S RECOMMENDED PROCEDURES. SU/SD OPERATIONS LIMITED TO 1302 HR/YR. BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE).
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Combined Cycle Refrigeration Compressor Turbines (8) | 15.21 | natural gas | 286 | MMBTU/H | GE LM2500+G4 | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices and fueled by natural gas | 43.6 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 58.4 | PPMV | AT 15% O2 | 0 | 0 | N
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1A | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Catalytic Oxidation and good combustion practices during normal operations, and good combustion practices during startup/shutdown operations. | 125.21 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 388.55 | T/YR | ANNUAL MAXIMUM | 2 | PPM@15% O2 | 24-HOUR ROLLING AVERAGE | 0 | 0 | N
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1B | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Catalytic oxidation and good combustion practices during normal operations, and good combustion practices during startup/shutdown operations. | 125.21 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 388.55 | T/YR | ANNUAL MAXIMUM | 2 | PPM@15% O2 | 24-HOURLY ROLLING AVERAGE | 0 | 0 | N |  | BACT Limit = 2.0 PPM@15% O2 (24-hour rolling average)
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst, Proper Design, Good Combustion Practices. | 5 | PPMV | 30 DAY ROLLING AVERAGE | BACT-PSD | OPERATING PERMIT , NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Units are ppmv @15% O2; Averaging time is 30 Day Rolling Average During Normal Operations.
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 725 | MEGAWATT | TWO GENERAL ELECTRIC (GE) F-CLASS ADVANCED COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 725 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES | 2 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE, EXCLUDING SU/SD | BACT-PSD |  | U | 0 | U | 530 | LB | CEM | 0 |  |  | 0 | 0 | N |  | EMISSION #1 IS WITH AND WITHOUT DUCT FIRING EMISSION #2 APPLIES TO EACH STARTUP/SHUTDOWN EVENT
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITHOUT DUCT FIRING | 15.21 | NATURAL GAS | 270 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS, USE OF AN OXIDATION CATALYST AND EFFICIENT CT DESIGN | 1.5 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE, EXCLUDING SU/SD | BACT-PSD |  |  | 0 |  | 13767 | LB/EVENT | FOR ALL STARTUPS | 0 |  |  | 0 | 0 | N |  | 818 LB/EVENT FOR SHUTDOWNS. STARTUP AND SHUTDOWN LIMITS ARE TOTAL FOR BOTH CTS COMBINED
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES - COLD STARTUP | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | GOOD COMBUSTION PRACTICES AND OXIDATION CATALYST | 1772 | LB/EVENT | COLD STARTUP | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST. HEAT RATE LIMITED TO 6,793 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR MATTAWOMAN TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS MATTAWOMAN PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | GOOD COMBUSTION PRACTICES AND OXIDATION CATALYST | 2 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE (EXCLUDING SU/SD) | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | WITH AND WITHOUT DUCT FIRING, EXCLUDING SU/SD
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES - WARM STARTUP | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | GOOD COMBUSTION PRACTICES AND OXIDATION CATALYST | 1461 | LB/EVENT | WARM STARTUP | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES - HOT STARTUP | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | GOOD COMBUSTION PRACTICES AND OXIDATION CATALYST | 1216 | LB/EVENT | HOT STARTUP | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES - SHUTDOWN | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | GOOD COMBUSTION PRACTICES AND OXIDATION CATALYST | 156 | LB/EVENT | SHUTDOWN | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS. HEAT INPUT LIMITED TO 6,802 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR KEYS TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS KEYS PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | GOOD COMBUSTION PRACTICES AND OXIDATION CATALYST | 2 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | WITH AND WITHOUT DUCT FIRING, EXCEPT DURING PERIODS OF STARTUP/SHUTDOWN
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES - COLD STARTUP | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | GOOD COMBUSTION PRACTICES AND OXIDATION CATALYST | 1064 | LB/EVENT | COLD STARTUP | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KEYS IS PROHIBITED FROM OPERATING BOTH CTS IN A CONCURRENT STARTUP MODE AS DEFINED IN CONDITION B-II-4. ADDITIONALLY, THE START-UP OF A SECOND CT SHALL NOT COMMENCE UNTIL THE START-UP OF THE FIRST CT IS COMPLETE.
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES - WARM STARTUP | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | GOOD COMBUSTION PRACTICES AND OXIDATION CATALYST | 311 | LB/EVENT | WARM STARTUP | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KEYS IS PROHIBITED FROM OPERATING BOTH CTS IN A CONCURRENT STARTUP MODE AS DEFINED IN CONDITION B-II-4. ADDITIONALLY, THE START-UP OF A SECOND CT SHALL NOT COMMENCE UNTIL THE START-UP OF THE FIRST CT IS COMPLETE.
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES - HOT STARTUP | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS.KEYS IS PROHIBITED FROM OPERATING BOTH CTS IN A CONCURRENT STARTUP MODE. ADDITIONALLY, THE START-UP OF A SECOND CT SHALL NOT COMMENCE UNTIL THE START-UP OF THE FIRST CT IS COMPLETE. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | GOOD COMBUSTION PRACTICES AND OXIDATION CATALYST | 269 | LB/EVENT | HOT STARTUP | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KEYS IS PROHIBITED FROM OPERATING BOTH CTS IN A CONCURRENT STARTUP MODE AS DEFINED IN CONDITION B-II-4. ADDITIONALLY, THE START-UP OF A SECOND CT SHALL NOT COMMENCE UNTIL THE START-UP OF THE FIRST CT IS COMPLETE.
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES - SHUTDOWN | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | GOOD COMBUSTION PRACTICES AND OXIDATION CATALYST | 60 | LB/EVENT | SHUTDOWN | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 9 | PPM | EACH CTG; 24-H ROLLING AVG. | BACT-PSD | SIP | N | 0 | N | 43.9 | LB/H | EACH CTG; 24-H ROLLING AVG. | 0 |  |  | 10600 | 0 | N | 2012 | Emission limit 1 is 9.0 ppmv dry at 15% oxygen on a 24-hour rolling average as determined each hour the turbine operates; except during startup/shutdown. The limit applies to each unit. Emission limit 2 is 43.9 LB/H based on a 24-hour rolling average as determined each hour the turbine operates; except during startup/shutdown. The limit is for each unit. The cost information was estimated for a catalytic oxidation system (COS) CO = $10,600/ton CO+VOC = $8,948/ton
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 10.5 | PPM | EACH CTG/DB; 24-H ROLLING AVG. | BACT-PSD | SIP | N | 0 | N | 57.6 | LB/H | EACH CTG/DB; 24-H ROLLING AVG. | 0 |  |  | 10600 | 0 | N | 2012 | Emission limit 1 is 10.5 ppmv dry at 15% oxygen, for each CTG/DB, based on a 24-hour rolling average as determined each hour the turbine operates. Emission limit 2 is 57.6 LB/HR for each CTG/DB, based on a 24-hour rolling average as determined each hour the turbine operates. The cost effectiveness was estimated for a catalytic oxidation system (COS); CO = $10,600/ton CO + VOC = $8,948/ton
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG--Startup/Shutdown | 15.21 | Natural gas | 2237 | MMBTU/H each | Two (2) natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. This entry is for the startup/shutdown operations. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 3123 | LB/H | HOURLY DURING STARTUP | BACT-PSD | SIP | N | 0 | N | 2240 | LB/H | HOURLY DURING SHUTDOWN | 0 |  |  | 10600 | 0 | N | 2012 | Cost was estimated for a catalytic oxidation system (COS) CO = $10,600/ton CO + VOC = $8,948/ton
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Catalytic oxidation system | 11.4 | LB/H | 24-H ROLL.AVG; EACH HR OPERATE; NOT SS | BACT-PSD | SIP | N | 0 | N | 2 | PPMVOL | 3-H ROLL.AVG;EACH HR OPERATE; NOT SS | 0 |  |  | 0 | 0 | N |  | Emission limit 1 is 11.4 lb/hr based on a 24-hour rolling average as determined each hour the turbine operates, except during startup and shutdown. Emission limit 2 is 2.0 ppmv dry at 15% oxygen based on a 3-hour rolling average as determined each hour the turbine operates, except during startup and shutdown.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Catalytic oxidation system (COS) | 14.5 | LB/H | 24-H ROLL.AVG.; EACH HR TURBINE OPERATES | BACT-PSD | SIP | N | 0 | N | 2 | PPMVOL | 24-H ROLL.AVG.; EACH HR TURBINE OPERATES | 0 |  |  | 0 | 0 | N |  | Emission limit 1is 14.5 lb/hr based on a 24-hour rolling average as detrmined each hour the turbine operates. Emission limit 2 is 2.0 ppmv dry at 15% oxygen based on a 24-hour rolling average as determined each hour the turbine operates.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Startup/Shutdown | 15.21 | Natural gas | 2147 | MMBTU/H | Four natural gas-fired CTGs operating in startup/shutdown mode. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Catalytic oxidation system (COS) | 456.3 | LB/H | HOURLY DURING STARTUP | BACT-PSD | SIP | N | 0 | N | 360 | LB/H | HURLY DURING SHUTDOWN | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Efficient combustion control plus catalytic oxidation system. | 4 | PPMV | 24-H ROLL AVG DET. EACH H TURBINE OPERAT | BACT-PSD | N/A | U | 0 | U | 3159 | LB/H | 4-H ROLL AVG | 0 |  |  | 0 | 0 | N |  | The first limit is 4 ppmv based on a 24-H rolling average as determined each hour the turbine operates;/dry at 15% O2; except during startup and shutdown; each CTG/HRSG. The second limit is 3159 LB/H based on a 4-H rolling average as determined each hour the turbine operates. Applied on a per block basis (each CTG/HRSG pair combined). Combustion control and catalytic oxidation system (COS) selected based on outlet concentration, not% control efficiency. COS not fully functional at lower than optimum catalyst temperatures during startup/shutdown. CEMS monitoring.
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB: 4 nat gas fired CTG with DB for HRSG: Startup/shutdown events | 15.21 | natural gas | 2587 | MMBTU/H design heat input, each | *There are 4 total natural gas fired CTG with DB for HRSG. *They are identified in the permit as either flexible group FGCCA or FGCCB. *Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. *Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Efficient combustion control plus catalytic oxidation system. | 694 | T/YR | 12-MO ROLL TIME PERIOD STARTUP/SHUTDOWN | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is 694 T/Y based on a 12-month rolling time period for startup and shutdown events. It is applied on a per block basis (each CTG/HRSG pair combined). Combustion control and catalytic oxidation system (COS) selected based on outlet concentration, not % control efficiency. COS not fully functional at lower than optimum catalyst temperatures during startup/shutdown.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 4 | PPM | 24-H ROLL. AVG., NOT STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 85 | N | 5.31 | LB/H | 24-H ROLL. AVG., NOT STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | The CO limits apply to EACH CTGHRSG based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. The first CO limit is 4 ppmdv at 15%O2. Startup is defined as the period of time from synchronization to the grid (generator breaker closed) until the unit reaches steady state operation (loads greater than 50 percent of design capacity). Shutdown is defined as that period of time from the initial lowering of the turbine output below 50 percent of full operating load, with the intent to shut down, until the point at which the generator breaker opens.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: Startup &amp; Shutdown | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified seperately for the startup and shutdown periods associated with the process equipment included in FG-CTGHRSG. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 247.3 | LB/H | OPERATING HOUR DURING STARTUP | BACT-PSD | SIP | N | 85 | N | 551.3 | LB/H | OPERATING HOUR DURING SHUTDOWN | 0 |  |  | 0 | 0 | N |  | The CO limits above apply to EACH CTGHRSG. Startup is defined as the period of time from synchronization to the grid (generator breaker closed) until the unit reaches steady state operation (loads greater than 50 percent of design capacity). Shutdown is defined as that period of time from the initial lowering of the turbine output below 50 percent of full operating load, with the intent to shut down, until the point at which the generator breaker opens.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 24.7 | LB/H | 24-H ROLLING AVG | BACT-PSD | SIP | N | 85 | N | 3537 | LB/H | OPERATING HR. DURING STARTUP OR SHUTDOWN | 0 |  |  | 0 | 0 | N |  | There are 3 emission limits and they are for EACH CTGHRSG, as follows: Emission Limit 1 = 4 ppmvd at 15%O2 based on a 24-H rolling average as determined each operating hour except during startup and shutdown. Emission Limit 2 = 24.7 LB/H based on a 24-H rolling average as determined each operating hour except during startup and shutdown. Emission Limit 3 = 3537 LB/H based on an operating hour during startup or shutdown. Startup and shutdown operations are limited to 500 hours per 12-month rolling time period for each CTGHRSG train. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the startup and shutdown emission minimization plan. The efficiency range is 85-90 percent.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 4 | PPM | EACH EU; 24-H ROLL AVG EXCEPT | BACT-PSD | SIP | N | 85 | N | 5.31 | LB/H | EACH EU; 24-H ROLL AVG EXCEPT | 0 |  |  | 0 | 0 | N |  | The emission limits above are for each CTG/HRSG and are as follows: 1) 4 ppmvd at 15% O2 based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. 2) 5.31 LB/H based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. There are separate limits for each of these emission units during startup and shutdown which will be identified as a separate process in this determination. Startup is defined as the period of time from synchronization to the grid (generator breaker closed) until the unit reaches steady state operation (loads greater than 50 percent design capacity). Shutdown is defined as that period of time from the initial lowering of the turbine output below 50 percent of full operating load, with the intent to shut down, until the point at which the generator breaker opens.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG--Startup/Shutdown (2 combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H; EACH | Two combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. This process group is to identify emission limits during startup and shutdown. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 247.3 | LB/H | OPERATING HOUR DURING STARTUP | BACT-PSD | SIP | N | 85 | N | 551.3 | LB/H | OPERATING HOUR DURING SHUTDOWN | 0 |  |  | 0 | 0 | N |  | The emission limits above are during startup/shutdown. Startup is defined as the period of time from synchronization to the grid (generator breaker closed) until the unit reaches steady state operation (loads greater than 50 percent of design capacity). Shutdown is defined as that period of time from the initial lowering of the turbine output below 50 percent of full operating load, with the intent to shut down, until the point at which the generator breaker opens.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 4 | PPM | 24-H ROLL.AVG., EXCEPT STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 0 | N | 17.4 | LB/H | 24-H ROLL.AVG., EXCEPT STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above is 4 ppmvd at 15% O2. Also, each of the emission limits above are based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. There is a separate limit for each startup/shutdown event, which will be entered as a separate 'Process' in the RBLC determination.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Startup/Shutdown) | 15.21 | Natural gas | 1934.7 | MMBTU/H | This emission unit is being entered as a separate process to account for the emission limits associated with startup/shutdown events, which could not be included within the previous EUCCT original process name. A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 1580 | POUNDS | POUNDS PER EVENT | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is 1,580 pounds per event and applies to each startup or shutdown event. Startup is defined as the period of time from initiation of the combustion process (flame-on) and continues until the unit reaches 50% load. Shutdown is defined as that period of time from the lowering of the turbine output below 50% load, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated.
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 2 | PPMVD | EACH CT/HRSG TRAIN; 24-HR ROLL AVG | BACT-PSD | SIP | N | 0 | N | 357 | T/YR | EACH CT/HRSG TRAIN; 12-MO ROLL TIME PER. | 0 |  |  | 0 | 0 | N |  | Emission limits above are for each individual CT/HRSG train in FG-TURB/DB1-3. Startup/shutdown emissions are not included. They will be identified separately. Emission limit 1 above is 2.0 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. Emission limit 2 above is 357 ton/year based on a 12-month rolling time period as determined at the end of each calendar month.
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3--Startup/Shutdown Operations | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBTU/Hr heat input capacity and a dry low NOx burner. This scenario identifies the emission limits applicable during startup and shutdown operations. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 1164 | LB/H | EACH CT/HRSG TRAIN; STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above is 1164 lb/hr each operating hour during startup or shutdown for each individual CT/HRSG train in the flexible group. Startup is defined as the period of time from detection of a flame signal until the unit reaches steady state operation (i.e. loads greater than 50 percent). Shutdown is defined as beginning when the turbine output is lowered to the point that steady state operation can no longer be assured (i.e. loads less than 50 percent), and ending when a flame-off signal is detected.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 4 | PPMV | AT 15%O2; 240HR ROLL AVG; NOT S.S. | BACT-PSD | SIP | N | 0 | N | 788.6 | LB/H | OPERATING HR DURING STARTUP OR SHUTDOWN | 0 |  |  | 0 | 0 | N |  | The first emission limit above is 4 PPMVD at 15%O2 based on a 24-hour rolling average as determined each operating hour EXCEPT during startup and shutdown. Emission limit 2 above is 788.6 LB/H during each operating hour during startup or shutdown (S.S.). Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 4 | PPMVD | AT 15%O2; 24-H ROLL AVG; NOT INCL ST/SH | BACT-PSD | SIP | N | 0 | N | 788.6 | LB/H | OPERATING HR DURING STARTUP OR SHUTDOWN | 0 |  |  | 0 | 0 | N |  | There are two emission limits: Emission limit 1 = 4 ppmvd at 15%O2 based on a 24-hr rolling average as determined each operating hour, except during startup or shutdown. Emission limit 2 = 788.6 lb/h each operating hour during startup or shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from teh lowering of teh turbine output below the demonstrated steady state level, with teh intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2. Startup and shutdown hours are limits to 300 hours per 12-month rolling time period.
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 0.0045 | LB/MMBTU | EACH UNIT; 24-H ROLL AVG; NOT S.S. | BACT-PSD |  | N | 85 | N | 17.59 | LB/H | EACH UNIT; 24-H ROLL AVG; NOT S.S. | 0 |  |  | 0 | 0 | N |  | There are 3 CO emission limits in the permit; as follows: Emission limit 1 = 0.0045 LB/MMBTU based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown (S.S.). The limit applies to each unit. Emission limit 2 = 17.59 LB/H based on a 24-hour rolling average as determined each operating hour except during startup and shutdown (S.S.). The limit applies to each unit. Emission limit 3 = 791.5 LB/H each operating hour during startup or shutdown. Oxidation catalyst reduction is expected to reduce CO by 85-90%. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit.
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2)--Startup &amp; Shutdown | 15.21 | Natural gas | 0 |  | This section is the startup and shutdown emission limits for FGCTGHRSG. Two 3,658 MMBTU/H natural gas-fired combustion turbine generators (CTGs) coupled with heat recovery steam generators (HRSGs). The HRSGs are equipped with natural gas-fired duct burners rated at 800 MMBTU/H to provide heat for additional steam production. The HRSGs are not capable of operating independently from the CTGs. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst technology and good combustion practices. | 791.5 | LB/H | EACH UNIT; OPERATING HOUR DURING S.S. | BACT-PSD |  | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 791.5 LB/H, per operating hour during startup or shutdown. The limit applies to each unit. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit.
*MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2019-10-22 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2--A 667 MMBTU/H natural gas fired CTG with a HRSG. | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2 is a nominally rated 667 MMBTU/H natural gas fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas fired duct burner rated at 204 MMBTU/h to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR and oxidation catalyst. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | An oxidation catalyst for CO control for each CTG/HRSG unit, good combustion practices. | 4 | PPM | PPMVD@15%O2; 24-H AVG; SEE NOTES | BACT-PSD | SIP | N | 0 | U | 9 | LB/H | HOURLY EXCEPT STARTUP/SHUTDOWN; SEE NOTE | 0 |  |  | 17102 | 0 | N | 2017 | There are 3 CO emission limits in the permit. Emission limit 1 is 4 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. The limit applies when the unit is in combined cycle mode. Emission limit 2 is 9 lb/h and is an hourly limit except during startup and shutdown. The limit applies when the unit is in HRSG bypass mode. Emission limit 3 is 289 lb/h and is an hourly limit including startup and shutdown. The limit applies when the unit is in combined cycle mode. Thermal oxidation and NSCR were considered not technically feasible for these applications.
*MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2019-10-22 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1--A 667 MMBTU/H NG fired combustion turbine generator coupled with a heat recovery steam generator (HRSG) | 15.21 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR) and oxidation catalyst. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | An oxidation catalyst for CO control for each CTG/HRSG unit; good combustion practices. | 4 | PPM | PPMVD@15%O2;24-H ROLL AVG; SEE NOTES | BACT-PSD | SIP | N | 0 | U | 9 | LB/H | HOURLY EXCEPT STARTUP/SHUTDOWN; SEE NOTE | 0 |  |  | 17102 | 0 | N | 2017 | There are 3 CO emission limits in the permit as follows: Emission limit 1 is 4 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. Applies when the unit is in combined cycle mode. Emission limit 2 is 9 lb/h when the unit is in HRSG bypass mode. The limit is hourly except during startup and shutdown. Emission limit 3 is 289 lb/h when the unit is in combined cycle mode and is hourly including startup and shutdown. Thermal oxidation and NSCR were considered not technically feasible for these applications.
*MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2019-12-19 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 2 | PPM | PPMVD; EACH UNIT; 24-HR AVG, NO START/SH | BACT-PSD |  | N | 0 | U | 2106 | LB/H | HOURLY; INCLUD. START/SHUTDOWN; EACH | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 is 2 ppmvd, applies to each unit, and is based on a 24-hour rolling average as determined each hour, except during startup and shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from teh lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the combustion process ends at flame-off. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in special condition (SC) III.2 of the permit. Emission Limit 2 is 2,106 lb/hour, applies to each unit, and is hourly including startup and shutdown. NSCR and EMxGT were ruled out as technically infeasible. A oxidation catalysts typically has a reduction of 85-90 percent for CO emissions.
NJ-0079 | WOODBRIDGE ENERGY CENTER | CPV SHORE, LLC | MIDDLESEX | NJ | 7095 | USA | MARK TURNER | (415)293-1463 | MTURNER@CPV.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Mr. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS, yogesh.doshi@dep.state.nj.us; phone 609-633-7249 | 18940 - BOP110003 | 4911 | 221112 | 110055590953 | 10/12/2011 &nbsp;ACT | 07/25/2012 &nbsp;ACT | 2012-11-27 | 2018-04-17 | A |  | Woodbridge Energy Center (WEC), proposed at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, would be a new, highly efficient, 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,307 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, one small dew point fuel gas heater (fuel gas heater), a mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Other Permitting Information: Facility-Wide Greenhouse Gas (GHG) emissions as CO2e emissions= 2,073,645 tons per year | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural gas | 40297.6 | mmcubic ft/year | Woodbridge Energy Center (WEC), located at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, will be a new 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) each with a maximum rated heat input of 2,307 million British thermal units per hour (MMBtu/hr), that will utilize pipeline natural gas only, with 2 HRSGs, 2 Duct Burners (each 500 MMbtu/hr). | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst; Good Combustion Practices | 12.1 | LB/H | AVERAGE OF THREE 1-HOUR TESTS | BACT-PSD | OPERATING PERMIT | U | 77 | Y | 2 | PPMVD | 3-HR ROLLING AVERAGE BASED ON 1-HR BLOCK | 0 |  |  | 0 | 0 | N |  | Compliance Verified by Stack test in 2016, CO Emission limit 1 achieved was 0 LB/H; Emission limit 2 achieved was 0.0 PPMVD (no CO emissions)
NJ-0079 | WOODBRIDGE ENERGY CENTER | CPV SHORE, LLC | MIDDLESEX | NJ | 7095 | USA | MARK TURNER | (415)293-1463 | MTURNER@CPV.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Mr. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS, yogesh.doshi@dep.state.nj.us; phone 609-633-7249 | 18940 - BOP110003 | 4911 | 221112 | 110055590953 | 10/12/2011 &nbsp;ACT | 07/25/2012 &nbsp;ACT | 2012-11-27 | 2018-04-17 | A |  | Woodbridge Energy Center (WEC), proposed at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, would be a new, highly efficient, 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,307 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, one small dew point fuel gas heater (fuel gas heater), a mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Other Permitting Information: Facility-Wide Greenhouse Gas (GHG) emissions as CO2e emissions= 2,073,645 tons per year | Combined Cycle Combustion Turbine w/o duct burner | 15.21 | natural gas | 40297.6 | mmcubic ft/year | The above natural gas use is combined for two GE 7FA CC turbines (each with a maximum heat input of 2, 307 MMBtu/hr)and two duct burners (each with a maximum heat input of 500 MMBtu/hr) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst, good combustion practices and use only natural gas a clean burning fuel | 2 | PPMVD | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | U | 77 | Y | 10.2 | LB/H | AVERAGE OF THREE TESTS | 0 |  |  | 0 | 0 | N |  | Compliance Verified by Stack test in 2016, CO Emission limit1 achieved was 0.0 PPMVD; Emission limit 2 achieved was 0.0 LB/H (no CO Emissions)
NJ-0080 | HESS NEWARK ENERGY CENTER | HESS NEWARK ENERGY CENTER, LLC | ESSEX | NJ | 7105 | USA | PETER HAID | (774) 750-7088 | PHAID@HESS.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Supervisor: Yogesh Doshi - yogesh.doshi@dep.state.nj.us Phone: 609-633-7249 Permit Evaluator: Michael Hogan - michael.hogan@dep.state.nj.us. Phone: (609)-633-1124 | 08857/BOP110001 | 4911 | 221112 | 110044839903 | 12/10/2011 &nbsp;ACT | 11/01/2012 &nbsp;ACT | 2013-04-04 | 2018-04-17 | A |  | Combined Cycle Electric Generating Facility HESS Newark Energy Center (Hess-NEC), proposed at City of Newark (Essex County), New Jersey, would be a new, highly efficient, 655 MW combined-cycle power generating facility. Hess-NEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,320 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, a 12-cell mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Facility-wide Greenhouse Gas (GHG) emissions as CO2e emissions = 2,003,654 tpy | Combined cylce turbine with duct burner | 15.21 | natural gas | 39463 | mmcubic ft/year* | * Annual throughput is for 2 turbines, 2 duct burners and 1 auxiliary boiler | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst | 2 | PPMVD | 3-HR ROLLING AVERAGE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | U | 90 | N | 10.2 | LB/H | AVERAGE OF THREE TESTS | 0 |  |  | 0 | 0 | N
NJ-0080 | HESS NEWARK ENERGY CENTER | HESS NEWARK ENERGY CENTER, LLC | ESSEX | NJ | 7105 | USA | PETER HAID | (774) 750-7088 | PHAID@HESS.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Supervisor: Yogesh Doshi - yogesh.doshi@dep.state.nj.us Phone: 609-633-7249 Permit Evaluator: Michael Hogan - michael.hogan@dep.state.nj.us. Phone: (609)-633-1124 | 08857/BOP110001 | 4911 | 221112 | 110044839903 | 12/10/2011 &nbsp;ACT | 11/01/2012 &nbsp;ACT | 2013-04-04 | 2018-04-17 | A |  | Combined Cycle Electric Generating Facility HESS Newark Energy Center (Hess-NEC), proposed at City of Newark (Essex County), New Jersey, would be a new, highly efficient, 655 MW combined-cycle power generating facility. Hess-NEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,320 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, a 12-cell mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Facility-wide Greenhouse Gas (GHG) emissions as CO2e emissions = 2,003,654 tpy | Combined Cycle Combustion Turbine | 15.21 | natural gas | 39463 | MMCubic ft/yr | Fuel: Annual throughput is for 2 turbines, 2 duct burners and 1 auxiliary boiler CO2e = 2,000,268 t/yr for the facility (2 turbines, 2 duct burners and 1 auxiliary boiler, 1 emergency generator and 1 fire pump) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst and Good combustion Practices and use of natural gas a clean burning fuel | 10.2 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | U | 90 | U | 2 | PPMVD | 3-HR ROLLING AVE BASED ON 1-HR BLOCK AVE | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | Combined Cycle Combustion Turbine -Siemens turbine without Duct Burner | 15.21 | Natural gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each Siemens combustion turbine will be 2,356 MMBtu/hr(HHV) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | CO Oxidation Catalyst and Good Combustion Practices and use of Natural gas as a clean burning fuel | 2 | PPMVD@15% O2 | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 50 | U | 12 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITH DUCT BURNER - SIEMENS | 15.21 | Natural Gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two Siemens turbines and two associated duct burners) The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst and use of only natural gas a clean burning fuel | 2 | PPMVD | 3-HR ROLLING AVE BASED ON 1-HR BLOCK AVE | BACT-PSD | OPERATING PERMIT | N | 50 | N | 14 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITH DUCT BURNER - GENERAL ELECTRIC | 15.21 | Natural gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each General Electric combustion each turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 MMBtu/hr duct burner | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | CO Oxidation catalyst and good combustion practices and use of natural gas only as a clean burning fuel | 2 | PPMVD@15%O2 | 3-HR ROLLING AVERAGE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 50 | N | 11.1 | LB/H | AVEARAGE OF THREE ONE HOUR TESTS | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITHOUT DUCT BURNER - GENERAL ELECTRIC | 15.21 | Natural Gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each General Electric combustion turbine will be 2,312 MMBtu/hr(HHV) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | CO Oxidation Catalyst and Good Combustion Practices and use of Natural gas as a clean burning fuel | 2 | PPMVD@15%O2 | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 50 | N | 10.2 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine without Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burner. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst and Use of Natural gas a clean burning fuel | 0.9 | PPMVD@15%O2 | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 90 | U | 4.75 | LB/H | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burners. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and use of natural gas a clean burning fuel | 1.5 | PPMVD@15%O2 | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | BACT-PSD | OPERATING PERMIT | N | 90 | U | 10.5 | LB/H | 3-HR ROLLING AVE BASED ON 1-HR BLOCK | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas with Duct Burner | 15.21 | natural gas | 4000 | h/yr |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst and good combustion practices | 2 | PPMVD@15%O2 | 3 H ROLLING AV BASED ON ONE H BLOCK AV | BACT-PSD | OPERATING PERMIT | N | 69 | N | 18.1 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY CEMS AND STACK TESTING
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas without Duct Burner | 15.21 | Natural Gas | 8040 | H/YR |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES | 2 | PPMVD@15% O2 | 3 H ROLLING AV BASED ON ONE H BLOCK AV | BACT-PSD | OPERATING PERMIT | N | 69 | N | 15.3 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY CEMS AND STACK TESTING
NY-0104 | CPV VALLEY ENERGY CENTER | CPV VALLEY LLC | ORANGE | NY | 10940 | USA |  |  |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-335600136/00001 | 4911 | 221112 | 110043332471 | 08/01/2013 &nbsp;ACT | 08/01/2013 &nbsp;ACT | 2017-08-25 | 2017-09-28 | A |  | CPV Valley Energy Center is a 680 MW combined cycle electric generating facility located in Middletown, NY. The combustion turbines are rated at 2,234 MMBTU/H firing natural gas and 2,145 MMBTU/H firing diesel fuel. The duct burners are rated for 500 MMBTU/H firing natural gas. In addition to the turbines their emission limits for the auxiliary boiler (73.5 MMBTU/H), emergency generator, fire pump, and gas heater. | State Facility Permit | Turbines and duct burners - NG | 15.21 | natural gas | 0 |  | Combined cycle units heat rate 7,605 BTU/KW-H (HHV) or less without duct burner firing to achieve design thermal efficiency of 57.4% (LHV). | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Good combustion practice and oxidation catalyst. | 2 | PPMVD @ 15% O2 | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 2.0 PPVD @15% O2 without duct burners 3.4 PPVD @15% O2 with duct burners Applies to all operating loads, except during startup and shutdown.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Siemens, without duct burners | 15.21 | Natural Gas | 515600 | MMSCF/rolling 12-months | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process without duct burners. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 13 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 72.2 | T/YR | PER ROLLING 12-MONTHS | 2 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | BACT: 2.0 ppmvd at 15% O2. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Siemens, with duct burners | 15.21 | Natural Gas | 51560 | MMSCF/rolling 12-MO | Two Siemens 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process with duct burners. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 13 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 72.2 | T/YR | PER ROLLING 12-MONTHS | 2 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | BACT: 2.0 ppmvd at 15% O2. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Mitsubishi, without duct burners | 15.21 | Natural Gas | 47917 | MMSCF/rolling 12-MO | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process without duct burners. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 13.7 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 183.9 | T/YR | PER ROLLING 12-MONTHS | 2 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | BACT: 2.0 ppmvd at 15% O2. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Mitsubishi, with duct burners | 15.21 | Natural Gas | 47917 | MMSCF/rolling 12-MO | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process with duct burners. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 12.7 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 183.9 | T/YR | PER ROLLING 12-MONTHS | 2 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | BACT: 2.0 ppmvd at 15% O2. T/YR limit is for 2 turbines.
OH-0356 | DUKE ENERGY HANGING ROCK ENERGY | DUKE ENERGY HANGING ROCK, LLC | LAWRENCE | OH | 28207 | USA | ANDREW ROEBEL | 513-287-2356 | ANDREW.ROEBEL@DUKE-ENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110487 | 4911 | 221112 | 110012567203 | 07/17/2012 &nbsp;ACT | 12/18/2012 &nbsp;ACT | 2013-10-01 | 2016-05-04 | C |  | Four Natural Gas Fired Combustion Turbines, with Duct Burners; Combined Cycle, each 172 MW | This is a modification of RBLC OH-0252 to remove operating hour restrictions on duct burners, with changes to hourly limits without increasing the annual emission limitations. Original PTI # was 07-00503 | Turbines (4) (model GE 7FA) Duct Burners Off | 15.21 | NATURAL GAS | 172 | MW | Four GE 7FA combined cycle turbines, dry low NOx burners and selective catalytic reduction. These limits are for each of the 4 turbines individually, while operating with the duct burners off. This permit is a modification to RBLC OH-0252 to remove hourly restrictions on duct burners. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices burning natural gas | 25.7 | LB/H |  | BACT-PSD | SIP | U | 0 | Y | 278 | T/YR | PER ROLLING 12 MONTHS | 6 | PPM | PPMVD AT 15% O2 ON 24-H BLOCK AVERAGE | 0 | 0 | N |  | Limits are for each individual turbine. CEMS for CO and O2.
OH-0356 | DUKE ENERGY HANGING ROCK ENERGY | DUKE ENERGY HANGING ROCK, LLC | LAWRENCE | OH | 28207 | USA | ANDREW ROEBEL | 513-287-2356 | ANDREW.ROEBEL@DUKE-ENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110487 | 4911 | 221112 | 110012567203 | 07/17/2012 &nbsp;ACT | 12/18/2012 &nbsp;ACT | 2013-10-01 | 2016-05-04 | C |  | Four Natural Gas Fired Combustion Turbines, with Duct Burners; Combined Cycle, each 172 MW | This is a modification of RBLC OH-0252 to remove operating hour restrictions on duct burners, with changes to hourly limits without increasing the annual emission limitations. Original PTI # was 07-00503 | Turbines (4) (model GE 7FA) Duct Burners On | 15.21 | NATURAL GAS | 172 | MW | Four GE 7FA combined cycle turbines, dry low NOx burners and selective catalytic reduction. These limits are for each of the 4 turbines individually, while operating with the duct burners on. This permit is a modification to RBLC OH-0252 to remove hourly restrictions on duct burners. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices burning natural gas | 45.9 | LB/H |  | BACT-PSD | SIP | U | 0 | Y | 278 | T/YR | PER ROLLING 12 MONTHS | 8 | PPM | PPMVD AT 15% O2 ON 24-H BLOCK AVERAGE | 0 | 0 | N |  | Limits are for each individual turbine. CEMS for CO and O2.
OH-0360 | CARROLL COUNTY ENERGY | CARROLL COUNTY ENERGY | CARROLL | OH | 44615 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0113762 | 4911 | 221112 | 110064671127 | 04/11/2013 &nbsp;ACT | 11/05/2013 &nbsp;ACT | 2015-12-30 | 2019-04-01 | A |  | Natural gas fired combined cycle gas turbine electric generating station of nominal capacity of 742 MW | Installation of a natural gas-fired combined cycle combustion turbine electric utility power plant, nominally rated at 742 MW. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural Gas | 2045 | MMBTU/H | Two identical General Electric 7FA combined cycle combustion turbine (each at 2,045 mmBtu/hr heat input turbine at ISO conditions and 566 mmBtu/hr heat input duct burner, HHV) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. All throughputs and emission limits are for each turbine. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 12.5 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 213.2 | T/YT/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | Limits are for each turbine. 12.5 lb/h with duct burner and 9.9 lb/h turbine only (except startup and shutdown). 213.2 t/yr per rolling 12 month period including startup and shutdown. 869.5 lb/h for cold startup, 627.9 lb/h for hot startup, 801.4 lb/h for warm startup and 243.0 lb/hr for shutdown. Pound per hour emissions rates as presented are averaged over the duration of the event where (for the lead/lag turbine) the duration of a cold start is 245/220 minutes, the duration of a warm start is 140/115 minutes, the duration of a hot start is 83/58 minutes, and the duration of a shutdown is less than 1 hour. Emissions reflect the higher of the lead or lag turbine, on a pollutant-specific basis.
OH-0363 | NTE OHIO, LLC |  | BUTLER | OH | 45044 | USA | MICHAEL SCHUSTER | (904)436-6896 | MSCHUSTER@NTEENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0116610 | 4911 | 221112 | 110070379584 | 04/07/2014 &nbsp;ACT | 11/05/2014 &nbsp;ACT | 2019-02-22 | 2019-04-01 | A |  | Combined-cycle, natural gas-fired power plant | Initial installation of either one (1) Mitsubishi Hitachi Power Systems Americas M501JAC or one (1) Mitsubishi Hitachi Power Systems Americas M501GAC single power block in a 1x1 combined-cycle multi-shaft configuration, including a combustion turbine and heat recovery steam generator with duct burners and a steam turbine to be known as the Middletown Energy Center. | Turbine generator with HRSG and duct burners (P001) | 15.21 | Natural gas | 3278.5 | MMBTU/H | Combined-cycle combustion turbine generator (CTG) with heat recovery steam generator (HRSG), natural gas-fired, including duct burners (DB). Permit was for either Mitsubishi Hitachi Power Systems America M501GAC or M501JAC. The M501GAC was installed. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Used of natural gas, combustion controls, and catalytic oxidation | 16.8 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 249.1 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen. 16.8 lb/h with duct burner, except startup and shutdown. 13.2 lb/h turbine only, except startup and shutdown. 249.1 tons per rolling 12 month period for all operating modes, including startup. 1762.8 lb/h during cold startup, 1108.0 lb/h during hot startup, 1432.9 lb/h during warm startup, and 602.0 lb/h during shutdown. Pound per hour emissions rates as presented are averaged over the duration of the event where the duration of a cold start is 142.5 minutes, the duration of a warm start is 103 minutes, and it has been assumed that the CTs are at their respective maximum potential emission rates (100% load) for the balance of the averaging period that they are not in start-up or shutdown mode. The duration of a hot start is 22.8 minutes, and the duration of a shutdown is 12.5 minutes.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 1 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2022 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst | 10.4 | LB/H | WITHOUT DUCT BURNERS. SEE NOTES. | BACT-PSD |  | U | 0 | U | 5074.08 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | Limits are for single turbine except as noted. 2.0 ppm by volume, dry basis (ppmvd) at 15% oxygen, 3-hour average, turbine with duct burners and turbine only. 10.4 lb/h per 3 hour average without duct burners. 12.95 lb/h per 3 hour average with duct burners. 10506 lb/cold startup, 4531 lb/hot startup, 7699 lb/warm startup and 2776 lb/shutdown. 5074.08 t/yr per rolling 12 month period total for all 4 turbines.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 2 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2144 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst | 12 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 5101.7 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | Limits are for single turbine except as noted. 2.0 ppm by volume, dry basis (ppmvd) at 15% oxygen, 3-hour average, turbine with duct burners and turbine only. 12.0 lb/h per 3 hour average without duct burners. 14.9 lb/h per 3 hour average with duct burners. 10506 lb/cold startup, 4531 lb/hot startup, 7699 lb/warm startup and 2776 lb/shutdown. 5101.7 t/yr per rolling 12 month period total for all 4 turbines.
OH-0366 | CLEAN ENERGY FUTURE - LORDSTOWN, LLC | CLEAN ENERGY FUTURE - LORDSTOWN, LLC | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0117655 | 4911 | 221112 | 110070396317 | 09/17/2014 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2019-02-27 | 2019-06-19 | A |  | 962 MW (gross winter output) combined cycle gas turbine (CCGT) facility | Initial installation permit for the construction of the Lordstown Energy Center - a nominal 940 MW combined cycle gas turbine (CCGT) facility. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 2725 | MMBTU/H | Combined cycle combustion turbine (2,725 MMBtu/hr heat input turbine at ISO conditions and 179 MMBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Limits and throughputs are for single turbine. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Good combustion controls and oxidation catalyst | 14.3 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 128.5 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen. 14.3 lb/h with duct burner (except startup and shutdown). 13.6 lb/h without duct burner (except startup and shutdown). 128.5 t/yr per rolling 12 month period for all operating modes, including startup. 526.0 lb/h during cold startup, 436.1 lb/h during hot startup, 496.0 lb/h during warm startup, and 150.3 lb/h during shutdown.
OH-0367 | SOUTH FIELD ENERGY LLC | SOUTH FIELD ENERGY LLC | COLUMBIANA | OH | 43968 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0119495 | 4911 | 221112 | Not Found | 09/14/2015 &nbsp;ACT | 09/23/2016 &nbsp;ACT | 2019-02-28 | 2019-06-19 | A |  | 1150 MW combined-cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the South Field Energy facility, a nominal 1,150 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in Wellsville, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3131 | MMBTU/H | Two identical combined cycle combustion turbine (3,131 MMBtu/hr heat input turbine at ISO conditions, natural gas firing with evaporative cooler on and 800 MMBtu/hr maximum heat input natural gas-fired duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), catalytic oxidizer, and wet injection for ULSD firing. Heat input for ULSD firing at ISO conditions, with evaporative cooler on is 3,173 MMBtu/hr. Throughputs and limits are for single turbine except as noted. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Good combustion controls and oxidation catalyst | 18.57 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 108.1 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen, hourly average, all fuels, with and without duct burner. 18.57 lb/h with duct burner (except startup and shutdown). 15.17 lb/h without duct burner (except startup and shutdown). 16.15 lb/h for ultra low sulfur diesel (except startup and shutdown). 108.1 t/yr per rolling 12 month period for all operating modes, including startup and shutdown. When firing natural gas, 158.3 lb/h during startup and 160.1 lb/h during shutdown. When firing ultra low sulfur diesel, 356.6 lb/h during startup and 132.3 lb/h during shutdown.
OH-0370 | TRUMBULL ENERGY CENTER | TRUMBULL ENERGY CENTER | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122331 | 4911 | 221112 | Not Found | 03/23/2017 &nbsp;ACT | 09/07/2017 &nbsp;ACT | 2019-03-05 | 2019-06-19 | A |  | 940 MW combined cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the Trumbull Energy Center, a nominal 940 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in the Village of Lordstown, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3025 | MMBTU/H | Two identical combined cycle combustion turbine (3,025 mmBtu/hr heat input turbine at ISO conditions and 237 mmBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Throughputs and limits are for single turbine except as noted. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Good combustion controls and oxidation catalyst | 15.5 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 135.2 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen. 15.5 lb/h with duct burner. 14.6 lb/h without duct burner. Each limit except startup and shutdown). 135.2 t/yr per rolling 12 month period for all operating modes, including startup and shutdown. 526.0 lb/h during cold startup, 436.0 lb/h during hot startup, 496.0 lb/h during warm startup, and 159.0 lb/h during shutdown.
OH-0372 | OREGON ENERGY CENTER | OREGON ENERGY CENTER | LUCAS | OH | 43616 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0121049 | 4911 | 221112 | Not Found | 06/27/2016 &nbsp;ACT | 09/27/2017 &nbsp;ACT | 2019-03-06 | 2019-06-19 | A |  | Combined cycle gas turbine (CCGT) facility | Installation of natural gas-fired combined cycle combustion turbine power plant. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3055 | MMBTU/H | Combined cycle combustion turbine (3,055 mmBtu/hr heat input turbine at ISO conditions and 221.3 mmBtu/hr heat input duct burner) with dry low NOX combustors, selective catalytic reduction (SCR), and catalytic oxidation. All heat values are on a HHV basis. Throughputs and limits are for single turbine except as noted. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | oxidation catalyst and good combustion control | 15.5 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 135.19 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen. 15.5 lb/h with duct burner (except startup and shutdown). 14.6 lb/h without duct burner (except startup and shutdown). 135.19 t/yr per rolling 12 month period for all operating modes, including startup. 526 lb/h during cold startup, 436 lb/h during hot startup, 496 lb/h during warm startup, and 150 lb/h during shutdown.
OH-0374 | GUERNSEY POWER STATION LLC | GUERNSEY POWER STATION LLC | GUERNSEY | OH | 43723 | USA | MARY KING | (317)447-4513 | MARY@APEXPOWERGROUP.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122594 | 4911 | 221112 | 110070379546 | 04/14/2017 &nbsp;ACT | 10/23/2017 &nbsp;ACT | 2019-03-08 | 2019-06-19 | A |  | 1,650 MW combined cycle combustion turbine electrical generating facility | Installation PTI for a new 1,650 MW combined cycle natural-gas fired turbine plant and associated auxiliary boiler, firewater pumps, emergency generators and fuel gas heaters | Combined Cycle Combustion Turbines (3, identical) (P001 to P003) | 15.21 | Natural gas | 3516 | MMBTU/H | Three identical Combustion Turbines; GE 7HA.02 natural gas-fired lean pre-mix combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,516 MMBtu/hr HHV at 100% load and -18Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 997 MMBtu/hr HHV controlled with catalytic oxidation and selective catalytic reduction (SCR) and cooled with an air-cooled condenser (ACC) used to generate electricity. Throughputs and limits are for a single turbine except as noted. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | oxidation catalyst and good combustion practices as recommended by the manufacturer | 20.76 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 16.17 | LB/H | WITHOUT DUCT BURNERS. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | Limits are for single turbine except as noted. 2.0 ppm by volume, dry basis (ppmvd) at 15% oxygen turbine with duct burners and turbine only, both excluding startup and shutdown. 16.17 lb/h without duct burners. 20.76 lb/h with duct burners. Both excluding startup and shutdown 791.6 lb/cold startup, 161.5 lb/hot startup, 133.0 lb/warm startup and 139.6 lb/shutdown. 300.61 t/yr per rolling 12 month period total for all 3 turbines.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | General Electric Combustion Turbine (P004) | 15.21 | Natural gas | 3544 | MMBTU/H | General Electric model 7HA.02 natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,544 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices as recommended by the manufacturer. | 15.9 | LB/H | EXCEPT STARTUP AND SHUTDOWN. SEE NOTES | BACT-PSD |  | U | 0 | U | 123.8 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppmvd at 15% oxygen (O2) and 15.9 pounds per hour, excluding periods of startup and shutdown. 123.8 tons of NOx per rolling, 12-month period, including start-up and shutdown emissions. 877.0 lb/h during cold startup, 145.3 lb/h during hot startup, 130.6 lb/h during warm startup, and 137.7 lb/h during shutdown.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Mitsubishi Combustion Turbine (P005) | 15.21 | Natural gas | 3320 | MMBTU/H | Mitsubishi Model 501JAC natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,320 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 108 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | oxidation catalyst and shall operate the emissions unit in accordance with good combustion practices as recommended by the manufacturer | 15.3 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 121.2 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen. 15.30 lb/h with duct burner (except startup and shutdown). 16.1 lb/h without duct burner (except startup and shutdown). 121.2 t/yr per rolling 12 month period for all operating modes, including startup. 538.6 lb/h during cold startup, 449.4 lb/h during warm startup, 140.7 lb/h during hot startup, and 162.7 lb/h during shutdown.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Siemens Combustion Turbine (P006) | 15.21 | Natural gas | 3602 | MMBTU/H | Siemens Model SCC6-8000H natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,602 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 667 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | oxidation catalyst and shall operate the emissions unit in accordance with good combustion practices as recommended by the manufacturer | 16.5 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 142.6 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen. 16.5 lb/h with duct burner (except startup and shutdown). 13.6 lb/h without duct burner (except startup and shutdown). 142.6 t/yr per rolling 12 month period for all operating modes, including startup. 447.9 lb/h during cold startup, 439.9 lb/h during warm startup, 370.3 lb/h during hot startup, and 118.5 lb/h during shutdown.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Good combustion practices and oxidation catalyst | 17.9 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 112.8 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen on a 24-hr block averaging period. 17.9 lb/h with duct burner, except startup and shutdown. 15.3 lb/h without duct burner, except startup and shutdown. 112.8 tons per rolling 12 month period for all operating modes, including startup and shutdown. 35.85 tons per rolling 12 month period for startup and shutdown periods.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Good combustion practices and oxidation catalyst | 17.1 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 109.1 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen on a 24-hr block averaging period. 17.1 lb/h with duct burner, except startup and shutdown. 16.3 lb/h without duct burner, except startup and shutdown. 109.1 tons per rolling 12 month period for all operating modes, including startup and shutdown. 35.40 tons per rolling 12 month period for startup and shutdown periods.
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | Combustion Turbine | 15.21 | Natural Gas | 360 | MW | This process represents the GE option for the project - One GE 7FA.05 natural gas-fired combustion turbine generator with an 820.5 MMBTUH duct burner. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practice. | 2 | PPMVD@15%O2 | 3-HR | BACT-PSD | N/A | U | 0 | U | 14 | LB/HR | 3-HR | 0 |  |  | 0 | 0 | N
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | COMBUSTION TURBINE | 15.21 | NATURAL GAS | 360 | MW | This process represents the Siemens option for the project - One Siemens SGT6-5000F5 natural gas-fired combustion turbine generator with an 820.3 MMBTUH duct burner. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES. | 2 | PPMVD@15% O2 | 3-HR | BACT-PSD | N/A | U | 0 | U | 14.5 | LB/HR | 3-HR | 0 |  |  | 0 | 0 | N
OK-0157 | CHOUTEAU POWER PLANT | ASSOCIATED ELECTRIC COOPERATIVE INC | MAYES | OK | 74337 | USA | TADD HENRY | 918-475-4806 | THENRY@AECI.ORG | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2007-115-C(M-3)PSD | 4911 | 221112 | 097-00017 | 03/05/2013 &nbsp;ACT | 09/05/2013 &nbsp;ACT | 2014-06-19 | 2016-07-29 | C |  | The facility contains four combined cycle gas turbines (CCGT) firing exclusively natural gas. Hot exhaust gases from the gas turbines are passed through separate drum-type heat recovery steam generators (HRSG) where the heat is converted to steam. Steam from paired CCGT (EU 1-01 &amp; 1-02, and EU 1-03 &amp; 1-04) drive two separate conventional steam turbines. Waste heat is rejected through a condenser and mechanical draft-cooling tower. | This modification requires reevaluation of the CO BACT analysis for startup and shutdown and an air quality impact evaluation for the increase in CO emissions. | LARGE COMBUSTION TURBINES-COMBINED CYCLE &amp; COGEN | 15.21 | NATURAL GAS | 182 | MMBTU | STARTUP/SHUTDOWN | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 1750 | LB/EVENT | 2-HRS/HOT STARTUP | BACT-PSD | N/A | U | 0 | U | 450 | LB/EVENT | 2-HRS/COLD STARTUP | 750 | LB/EVENT | 1-HR/SHUTDOWN | 0 | 0 | N
OK-0157 | CHOUTEAU POWER PLANT | ASSOCIATED ELECTRIC COOPERATIVE INC | MAYES | OK | 74337 | USA | TADD HENRY | 918-475-4806 | THENRY@AECI.ORG | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2007-115-C(M-3)PSD | 4911 | 221112 | 097-00017 | 03/05/2013 &nbsp;ACT | 09/05/2013 &nbsp;ACT | 2014-06-19 | 2016-07-29 | C |  | The facility contains four combined cycle gas turbines (CCGT) firing exclusively natural gas. Hot exhaust gases from the gas turbines are passed through separate drum-type heat recovery steam generators (HRSG) where the heat is converted to steam. Steam from paired CCGT (EU 1-01 &amp; 1-02, and EU 1-03 &amp; 1-04) drive two separate conventional steam turbines. Waste heat is rejected through a condenser and mechanical draft-cooling tower. | This modification requires reevaluation of the CO BACT analysis for startup and shutdown and an air quality impact evaluation for the increase in CO emissions. | Turbine | 15.21 | Natural Gas | 178 | MW | Startup/Shutdown | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Minimize time spent in startup/shutdown. | 4500 | LB/EVENT | 2 HOURS / COLD STARTUP | BACT-PSD | N/A | U | 0 | U | 1750 | LB/EVENT | 2 HOURS / HOT STARTUP | 750 | LB/EVENT | 1 HOUR / SHUTDOWN | 0 | 0 | N
OK-0169 | PSO COMANCHE POWER STATION | PUBLIC SERVICE COMPANY OF OKLAHOMA | COMANCHE | OK | 73501 | USA | WILLIAM HILDESON | 214-777-1412 | WLHILDESON@AEP.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2010-496-C(M-2)PSD | 4911 | 221112 | 031-00007 | 08/18/2014 &nbsp;ACT | 10/08/2015 &nbsp;ACT | 2015-12-02 | 2016-07-06 | C |  | The facility is an electric utility plant, which burns natural gas to generate electricity. The Comanche Power Plant was constructed in 1971 and has operated continuously since that time without significant modification. The facility produces power using two Westinghouse gas combustion turbines(94 MW), Model W-501B, to supply a single steam turbine(120 MW). The turbines are fueled by Natural Gas and operate continuously. | American Electric Power (AEP) has requested a construction permit for their Comanche Power Station (SIC 4911, NAIC Code 221112) to install Dry Low-NOX burners (DLNB) to Units No. 1 and No. 2 to reduce emissions of NOX for the purpose of meeting Best Available Retrofit Technology (BART) requirements and Regional Haze Rule. | COMBINED CYCLE COMBUSTION TURBINE | 15.21 | NATURAL GAS | 1250 | MMBTUH | Two (2) turbines without duct burner that support one (1) steam turbine. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Controlled Startup and Shutdown procedures with respect to Dry Low NOx Burners. | 0.0785 | LB/MMBTU | 3-HR AVG NORMAL OPERATION | BACT-PSD | NESHAP , OTHER | U | 0 | Y | 98.13 | LB/HR | 3-HR AVG NORMAL OPERATION | 0 |  |  | 0 | 0 | N |  | Startup limited to 9 hours and 1077 pounds, Shutdown limited to 3 hours and 364 pounds, and No more than 75 Startup/Shutdowns per year.
PA-0278 | MOXIE LIBERTY LLC/ASYLUM POWER PL T | MOXIE ENERGY LLC | BRADFORD COUNTY | PA |  | USA | KENT J MORTON | (571) 594 - 0150 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MUHAMMAD Q. ZAMAN, ENVIRONMENTAL PROGRAM MANAGER, NORTHCENTRAL REGION | 08Â·00045A | 491 | 221112 | 45-2015223-1 | 09/26/2011 &nbsp;ACT | 10/10/2012 &nbsp;ACT | 2012-12-03 | 2015-04-03 | A |  |  | The project consists of two identical 1 x 1 power blocks, and each block includes a combustion gas turbine and a steam turbine. Each combined-cycle process will also include a heat recovery steam generator and supplemental duct burners. Additionally, one diesel-fired emergency generator, one diesel-fired fire water pump, two diesel fuel storage tanks, two lube oil storage tanks, and one aqueous ammonia storage tank were proposed to be constructed and operated. Each combined-cycle process will be rated at 468 MW or less. | Combined-cycle Turbines (2) - Natural gas fired | 15.21 | Natural Gas | 3277 | MMBTU/H | Two combine cycle Turbines, each with a combustion turbine and heat recovery steam generator with duct burner. Each combined-cycle process will be rated at 468 MW or less. The heat input rating of each combustion gas turbine is 2890 MMBtu/hr (HHV) or less, and the heat input rating of each supplemental duct burner is equal to 387 MMBtu/hr (HHV) or less. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPMVD | @15% O2 | BACT-PSD |  | U | 80 | U | 15.3 | LB/H | 468 MW POWERBLOCK | 2 | PPMVD | @15% O2 | 0 | 0 | N |  | 1-hr CEMS monitoring and combustion controls for lean combustion. Other Limit: 15.0000 LB/H 454 MW POWERBLOCK
PA-0286 | MOXIE ENERGY LLC/PATRIOT GENERATION PLT | MOXIE ENERGY LLC | LYCOMING COUNTY | PA |  | USA | KENT MORTON | (571) 594 - 0150 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MUHAMMAD Q. ZAMAN, ENVIRONMENTAL PROGRAM MANAGER NORTHCENTRAL REGION 208 West Third St, Suite 101 Williamsport, PA 17701 570-327-3648 | 41-00084A | 4911 | 221112 | 110057116124 | 07/18/2012 &nbsp;ACT | 01/31/2013 &nbsp;ACT | 2013-03-27 | 2020-03-02 | A |  | This plan approval is for the construction of two natural-gas-fired combined cycle powerblocks where each powerblock consists of a combustion turbine and heat recovery steam generator with duct burner. The two powerblocks constructed pursuant to this plan approval will be either the two powerblocks rated 472 megawatts (MW) (P101 and P102) or the powerblocks rated 458 MW (P103 and P104). Additionally, this plan approval is for the construction of a 1464 bhp diesel-fired emergency generator, 460 bhp dieselfired fire pump, 1600 gallon diesel tank, 300 gallon diesel tank, two 15,000 gallon (each) lube oil tanks and ancillary electrical equipment. |  | Combined Cycle Power Blocks 472 MW - (2) | 15.21 | Natural Gas | 0 |  | Two natural-gas-fired combined cycle powerblocks where each powerblock consists of a combustion turbine and heat recovery steam generator with duct burner. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | CO Catalyst | 2 | PPMDV |  | BACT-PSD | OTHER | U | 0 | U | 109.3 | T/YR | EACH UNIT | 0 |  |  | 0 | 0 | N
PA-0296 | BERKS HOLLOW ENERGY ASSOC LLC/ONTELAUNEE | BERKS HOLLOW ENERGY ASSOC LLC | BERKS | PA | 19605 | USA | BRADLEY J COOLEY | 636-534-3268 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | WILLIAM R. WEAVER, SOUTHCENTRAL REGION AIR PROGRAM MANAGER 909 Elmerton Ave, Harrisburg, PA 17701 717-705-4868 | 06-05150A | 4931 | 221112 | 110056155342 | 05/08/2012 &nbsp;ACT | 12/17/2013 &nbsp;ACT | 2014-04-17 | 2020-03-02 | A |  | This application is for the construction of a natural gas-fired combined-cycle electric generation facility that is designed to generate up to 855 MW nominal, using 2 combustion turbine generators and 2 heat recovery steam generators that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. | This application is for the construction of a natural gas-fired combined-cycle electric generation facility that is designed to generate up to 855 MW nominal, using 2 combustion turbine generators and 2 heat recovery steam generators that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. | Turbine, Combined Cycle, #1 and #2 | 15.21 | Natural Gas | 3046 | MMBTU/H | Equipped with SCR and Oxidation Catalyst | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | CO Catalyst | 211.92 | TPY | 12-MONTH ROLLING TOTAL | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0298 | FUTURE POWER PA/GOOD SPRINGS NGCC FACILITY | FUTURE POWER PA INC | SCHUYLKILL | PA | 17980 | USA | JAMES PALUMBO | 570-342-5200 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MARK J. WEJKSZNER NORTHEAST REGION AIR PROGRAM MANAGER 2 Public Square Wilkes-Barre, PA 18711 570-826-2357 | 54-00082A | 4911 | 221112 | 110062854870 | 05/03/2013 &nbsp;ACT | 03/04/2014 &nbsp;ACT | 2014-04-17 | 2020-02-19 | A |  | Natural gas-fired combined-cycle electric generation facility that is designed to generate up to 346 MW nominal, using a combustion turbine generator and a heat recovery steam generator that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. The Turbine is rated at 2,267 MMBTU/hr HHV (2,042 MMBTU/hr LHV). The Duct burner is rated at 134.3 MMBTU/hr HHV (120 MMBTU/hr LHV). The proposed project will also include a diesel engine-driven emergency generator; a diesel engine-driven firewater pump; a multi-cell evaporative cooling tower; and associated emission control systems, tanks, and other plant equipment. |  | Turbine, COMBINED CYCLE UNIT (Siemens 5000) | 15.21 | Natural Gas | 2267 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | CO Catalyst | 3 | PPMVD | @ 15% OXYGEN | BACT-PSD | NSPS | U | 0 | U | 17.9 | LB/H | WITH DUCT BURNER | 84.8 | T/YR | BASED ON A 12-MONTH ROLLING TOTAL | 0 | 0 | N
PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2018-12-21 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large combustion turbine | 15.21 | Natural Gas | 0 |  | This process entry is for operations with the duct burner. Limits entered are for each turbine. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst and good combustion practice | 15.9 | LB/HR | 3 HR AVERAGE | BACT-PSD |  | U | 0 | U | 318.6 | TPY | 12 MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2018-12-21 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two Combine Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 3001.57 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. . (Operational limits are for each CCCT NG-fired with duct burner) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 2 | PPMDV @ 15% O2 |  | BACT-PSD |  | U | 0 | U | 1189.8 | TONS | YR | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative emissions from both CCCT in any 12-month period
PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Combustion turbine with duct burner | 15.21 | Natural gas | 3304.3 | MMBtu/hr | Limits are for each CCCT and yearly limits are for cumulative turbine and duct burner. Duct burner throughput is 637.9 MMBtu/hr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst, combustion controls, exclusive natural gas | 2 | PPMDV @ 15 % O2 |  | BACT-PSD |  | U | 0 | U | 84.9 | TONS | YEAR | 0 |  |  | 0 | 0 | N |  | CO CEMS (1-hour average)
PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG with duct burner NG only | 15.21 | Natural Gas | 3338 | MMBtu/hr | Emission limits are for each turbine operating with duct burner and do not include startup/shutdown emissions. Tons per year limits is a cumulative value for all three CCCT. CEMS for NOx, CO, and O2. Each CCCT and duct burner have 5 operational scenarios: 1 CCCT with duct burner fired - fueled by NG only 2 CCCT with duct burner fired - fueled by NG blend with ethane 3 CCCT without duct burner fired - fueled by NG only 4 CCCT without duct burner fired - fueled by NG blend with ethane 5 CCCT without duct burner fired - fueled by ULSD (Limited to emergency use only) | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst operated at all steady state operating loads and good combustion practices | 2 | PPMDV @ 15% O2 |  | BACT-PSD | NSPS | U | 0 | U | 84.9 | TONS | YEAR | 0 |  |  | 0 | 0 | N
PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064098541 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2018-12-21 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine With Duct Burner | 15.21 | Natural Gas | 3727 | MMBtu/hr | DLN burner, SCR, Oxidation Catalyst and shall maintain and operate the sources and associated air cleaning devices in accordance with good engineering practice. shall install, certify, maintain and operate continuous emission monitoring systems (CEMS) for nitrogen oxides, carbon monoxide, carbon dioxide, and ammonia emissions on the exhaust of each combined-cycle powerblock. Emissions limits are for each combustion turbine/duct burner block. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 2 | PPMDV @ 15% O2 |  | BACT-PSD | NSPS | U | 0 | U | 15.6 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 105.1 tpy 12-month rolling basis
*PA-0315 | HILLTOP ENERGY CENTER, LLC | HILLTOP ENERGY CENTER, LLC | GREENE | PA | 15351 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 30-00233B | 4911 | 221112 | 110066828222 | &nbsp; | 04/12/2017 &nbsp;ACT | 2018-12-21 | 2019-03-26 | U |  | The project consists of a single power block in a one-on-one (1x1), combined cycle, single shaft configuration, including a combustion turbine (CT) and heat recovery steam generator (HRSG) with a steam turbine (ST). â€¢ One (1) 3,509 MMBtu/hr General Electric International, Inc. (GE) model no. GE 7HA.02 natural gas-fired combined cycle combustion turbine equipped with a heat recovery steam generator (HRSG) with supplemental 981.4 MMBtu/hr natural gas fired duct burners; controlled by selective catalytic reduction and oxidation catalyst. â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. â€¢ One (1) 500 gallon firewater pump diesel storage tank. â€¢ One (1) 35,000 gallon 19% aqueous ammonia storage tank. â€¢ Lubricating oil storage tanks. â€¢ Miscellaneous components in natural gas service, and SF6 containing circuit breakers; controlled by leak detection and repair (LDAR). â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. | The project consists of a single power block in a one-on-one (1x1), combined cycle, single shaft configuration, including a combustion turbine (CT) and heat recovery steam generator (HRSG) with a steam turbine (ST). â€¢ One (1) 3,509 MMBtu/hr General Electric International, Inc. (GE) model no. GE 7HA.02 natural gas-fired combined cycle combustion turbine equipped with a heat recovery steam generator (HRSG) with supplemental 981.4 MMBtu/hr natural gas fired duct burners; controlled by selective catalytic reduction and oxidation catalyst. â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. â€¢ One (1) 500 gallon firewater pump diesel storage tank. â€¢ One (1) 35,000 gallon 19% aqueous ammonia storage tank. â€¢ Lubricating oil storage tanks. â€¢ Miscellaneous components in natural gas service, and SF6 containing circuit breakers; controlled by leak detection and repair (LDAR). â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. | Combustion Turbine without Duct Burner | 15.21 | Natural Gas | 3509 | MMBtu/hr |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst | 2 | PPMDV | CORRECTED TO 15% O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0319 | RENAISSANCE ENERGY CENTER | APV RENAISSANCE PARTNERS | GREENE | PA | 15320 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 30-00235A | 4911 | 221112 | Not Found | 03/17/2017 &nbsp;ACT | 08/27/2018 &nbsp;ACT | 2019-03-26 | 2019-10-11 | U |  | This Plan Approval is to allow the construction and temporary operation of a natural gas-fired combined cycle power plant to be located in Monongahela Township, Greene County. with Two (2) Siemens, SGT6-8000H (or equivalent), natural gas-fired combustion turbines 3,580 MMBtu/hr heat input rating (LHV) each (controlled with low NOx burners), including natural gas-fired duct burners, 914.1 MMBtu/hr heat input rating each; controlled by Ultra-low NOx combustors, SCR, and oxidation catalysts; 1,127 MW total net generating capacity. One (1) natural gas-fired auxiliary boiler, 90 MMBtu/hr heat input rating. One (1) Cummins model #CFP15E-F20 (or equivalent), diesel-fired fire pump engine, 411 bhp rating; including One (1) diesel fuel storage tank, 2,175 gallons One (1) Caterpillar 3516 (or equivalent), diesel-fired emergency generator engine rated at 2000 kW. Miscellaneous components in natural gas service, and circuit breakers; controlled by leak detection and repair (â€œLDARâ€). One (1) aqueous ammonia (19%) storage vessel rated at 19,000 gallons (or as determined during final design). |  | COMBUSTION TURBINE UNIT w/o DUCT BURNERS UNIT | 15.21 | Natural Gas | 2665.9 | MMBtu/hr |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPPDV | @15% O2 | BACT-PSD |  | U | 0 | U | 187.44 | TPY |  | 0 |  |  | 0 | 0 | N
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Natural Gas-Fired Combustion Turbine with HRSG | 15.21 | Natural Gas | 1339 | MMBtu/hr | Turbine throughput is 1019.7 MMBtu/hr when burning natural gas and 1083.7 MMBtu/hr when burning No. 2 oil. Duct burner throughput is 319.3 MMBtu/hr. Duct burner firing will occur during natural gas combustion only. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Good combustion design and practices, oxidation catalyst | 2 | PPMVD @ 15% O2 | 30 UNIT-OPERATING-DAY MOVING AVERAGE | BACT-PSD |  | N | 90 | U | 10 | PPMVD @ 15% O2 | 15 UNIT-OPERATING-DAY MOVING AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission limit #1 is for natural gas combustion, emission limit #2 is for No. 2 oil combustion.
*TN-0164 | TVA - JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134 | USA | JACK BYARS | (423) 751-2666 | JGBYARS@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov |  | 972969 | 4911 | 221112 | 110070502905 | 09/26/2017 &nbsp;ACT | 02/01/2018 &nbsp;ACT | 2019-03-21 | 2019-03-21 | D |  | Combustion turbines and combined cycle plant | Permit 972969 adds startup and shutdown limits to the requirements established in PSD permit 970816F. | Dual-fuel CT and HRSG with duct burner | 15.21 | Natural Gas | 1020 | MMBtu/hr | Rated input capacity is 1020 MMBtu/hr (CT) and 319 MMBtu/hr (duct burner) when burning natural gas and 1084 MMBtu/hr when burning #2 oil. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst, good combustion design & practice | 2 | PPMVD @ 15% O2 | 30-DAY AVG WHEN BURNING NATURAL GAS | BACT-PSD |  | N | 0 | U | 10 | PPMVD @ 15% O2 | 30-DAY AVG WHEN BURNING #2 OIL | 0 |  |  | 0 | 0 | N |  | Startup & Shutdown: 1,760 lb/startup and 22 lb/shutdown when firing natural gas; 3,000 lb/startup and 12.8 lb/shutdown when firing #2 oil
TX-0590 | KING POWER STATION | PONDERA CAPITAL MANAGEMENT GP INC | HARRIS | TX | 77044 | USA | MARK CHRISOS | (781) 993-3036 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Katherine Stinchcomb (512) 239-1583 katherine.stinchcomb@tceq.texas.gov | PSDTX1125 AND N75, 84289 | 4911 | 221119 | 110040440902 | 04/05/2010 &nbsp;ACT | 08/05/2010 &nbsp;ACT | 2011-08-26 | 2020-02-03 | A |  | Four combined-cycle natural gas-fired combustion turbines | State permit number 84289 Nonattainment permit number N75 | Turbine | 15.21 | natural gas | 1350 | MW | The plant will be designed to generate 1,350 nominal megawatts of power. There are two configuration scenarios: either four Siemens SGT6-5000F CTGs in combined-cycle mode (Scenario A) or four GE Frame 7FA CTGs in combined cycle mode (Scenario B). Scenario B also includes one or two auxiliary boilers. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | good combustion practices with an oxidation catalyst | 2 | PPMVD AT 15% O2 | THREE-HOUR ROLLING | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies with or without duct burners
TX-0600 | THOMAS C. FERGUSON POWER PLANT | LOWER COLORADO RIVER AUTHORITY | LLANO | TX | 7657 | USA | JOE BENTLEY | 512-473-3272 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tan Nguyen 512-239-3445 tan.nguyen@tceq.texas.gov | PSDTX1244 & 93938 | 4911 | 221112 | 110035336222 | 07/27/2011 &nbsp;ACT | 09/01/2011 &nbsp;ACT | 2011-09-02 | 2020-02-03 | B |  | Power Plant. Two natural gas-fired combined cycle turbine generators (GE 7FA) with unfired HRSG | 93938 | Natural gas-fired turbines | 15.21 | natural gas | 390 | MW | (2) GE7FA at 195 MW each, (1) steam turbine at 200 MW. Each turbine is equipped with an unfired heat recovery steam generator (HRSG), which provides steam for the steam turbine. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Good combustion practices and oxidation catalyst | 4 | PPMVD | ROLLING 3-HR AT 15% OXYGEN /LOAD >= 60% | BACT-PSD |  | N | 0 | U | 6 | PPMVD | ROLLING 3-HR AT 15% OXYGEN /LOAD < 60% | 0 |  |  | 0 | 0 | N
TX-0618 | CHANNEL ENERGY CENTER LLC | CHANNEL ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX955M1, N021M1, 42179 | 4911 | 221112 | 110034690564 | 09/04/2012 &nbsp;ACT | 10/15/2012 &nbsp;ACT | 2012-10-24 | 2020-02-03 | B |  | Combustion turbine (Siemens 501F)/duct burners (475 MMBtu/hr) with heat recovery steam generator | 42179 and N021M1 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | The turbine is a Siemens 501F rated at a nominal 180 MW and the duct burner will have a maximum design heat input of 475 MMBtu/hr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion | 4 | PPMVD | @ 15% O2 ON A 24-HR ROLLING AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0619 | DEER PARK ENERGY CENTER | DEER PARK ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX979M2, N036M2, 45642 | 4911 | 221112 | 110017743254 | 08/13/2012 &nbsp;ACT | 09/26/2012 &nbsp;ACT | 2012-10-25 | 2020-02-03 | B |  | The Deer Park Energy Center is a combined cycle cogeneration facility consisting of five Siemens/Westinghouse 501F combustion turbine generators, each with a 725 MMBtu/hr duct burner and heat recovery steam generator. | 45642 and N036M2 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | natural gas-fired combined cycle turbine generator with a heat recovery steam generator equipped with a duct burner. The turbine is a Siemens 501F rated at a nominal 180 megawatts and the DB will have a maximum design rate capability of 725 million British thermal units per hour | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion | 4 | PPMVD | @15% O2, 24-HR ROLLING AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0620 | ES JOSLIN POWER PLANT | CALHOUN PORT AUTHORITY | CALHOUN | TX |  | USA | CHARLES HAUSMANN | 361-987-2813 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1256, 96336 | 4911 | 221112 | 110001866641 | 05/31/2012 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2012-11-14 | 2020-02-03 | B |  | Three gas-fired combined cycle turbine generators, including a steam turbine generator, to replace the existing steam boiler/turbine generator. | 96336 | Combined cycle gas turbine | 15.21 | natural gas | 195 | MW | The three combustion turbine generators (CTG) will be the General Electric 7FA, each with a maximum base-load electric power output of approximately 195 megawatts (MW). The steam turbine is rated at approximately 235 MW. This project also includes the installation of two emergency generators, one fire water pump, and auxiliary equipment. No duct burners. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion | 4 | PPMVD | @15% O2, 24-HR ROLLING AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 | 221122 | Not Found | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2019-03-06 | A |  | Combinec Cycle Electric Generating Plant | 103839 | combined cycle turbine | 15.21 | natural gas | 700 | MW | The generating equipment consists of two natural gas-fired combustion turbines (CTs), each exhausting to a fired heat recovery steam generator (HRSG) to produce steam to drive a shared steam turbine generator. The steam turbine is rated at 271 MW of electric output. Three models of combustion turbines are being considered for this site: the General Electric 7FA.05, the Siemens SGT6-5000F(4), and the Siemens SGT6-5000F(5). The final selection of the combustion turbine will not be made until after the permit is issued. Plant output will range between 637 and 735 MW, depending on the model turbine selected. Duct Burners are rated at 750 MMBtu/hr each. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 2 | PPMVD | 3-HR ROLL AVG, 15% OXYGEN, 80-100% LOAD | BACT-PSD |  | N | 0 | U | 4 | PPMVD | 3-HR ROLL AVG, 15% OXYGEN, 60-80% LOAD | 0 |  |  | 0 | 0 | N
*TX-0660 | FGE TEXAS POWER I AND FGE TEXAS POWER II | FGE POWER LLC | MITCHELL | TX | 79565 | USA | EMERSON FARRELL | 281-362-2830 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX1364 & 110025 | 3511 | 221112 | NOT FOUND | 10/23/2013 &nbsp;ACT | 03/24/2014 &nbsp;ACT | 2014-06-13 | 2020-03-05 | U |  | Electric Generating Utility | TCEQ Permit No. 110025 | Alstom Turbine | 15.21 | Natural Gas | 230.7 | MW | Four (4) Alstom GT24 CTGs, each with a HRSG and DBs, max design capacity 409 MMBtu/hr | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalyst | 2 | PPMVD | CORRECTED TO 15% O2, ROLLING 3 HR AVE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057188626 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.21 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (6) GE LM2500+ DLE turbines that drive the ethylene section compressors with waste heat recovery for amine solution regeneration. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | dry low emission combustors | 29 | PPMVD | @15% O2, 4 HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Combustion Turbine | 15.21 | natural gas | 87 | MW | The exhaust heat from the turbine will be used to heat a heating medium which is used to regenerate rich amine from the acid gas removal system. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 4 | PPMVD | @15% O2, 3 HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0687 | WEST PLANT AND EAST PLANT CENTRAL HEAT AND POWER | UNIVERSITY OF TEXAS MEDICAL BRANCH AT GALVESTON | GALVESTON | TX |  | USA | JACK TARPLEY | 409-747-0515 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, 512-239-2175, laura.gibson@tceq.texas.gov | 56653, PSDTX1376 | 8221 | 611310 | 110017309615 | 08/23/2013 &nbsp;ACT | 10/13/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | UTMB Galveston has applied for an amendment to authorize two combined cycle natural gas fired Solar Taurus 60 combustion turbines. Each CTG will produce 13MW. |  | Two Combustion Turbine-Generators | 15.21 | Natural Gas | 13 | MW | Combined Cycle | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 50 | PPM | 15% O2, 24HR ROLLING AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0689 | CEDAR BAYOU ELECTRIC GENERATION STATION | NRG TEXAS POWER | CHAMBERS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 105810, PSDTX1308 | 4911 | 221112 | 110015743301 | 09/12/2012 &nbsp;ACT | 08/29/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power gereration station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the combined cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The new units will produce between 215-263 MW each. |  | Combined cycle natural gas turbines | 15.21 | Natural Gas | 225 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OC | 2 | PPM | ROLLING 12 MONTHS | BACT-PSD |  | N | 0 | U | 4 | PPM | 1HR AVG. | 0 |  |  | 0 | 0 | N
TX-0698 | BAYPORT COMPLEX | AIR LIQUIDE LARGE INDUSTRIES U.S., L.P. | HARRIS | TX |  | USA | JASON MILLER | (281) 474-8243 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 | 9346 PSDTX612M2 | 4931 | 325120 | 110000462758 | 07/27/2012 &nbsp;ACT | 09/05/2013 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | Air Liquid currently operates a cogeneration facility in Pasadena, Texas (Bayou Cogeneration Plant). The permit amendment submitted by Air Liquide will authorize a redevelopment project of its cogeneration plant. The proposed project will involve the replacement of four existing gas-fired turbines (GE 7EA) with similar gas-fired turbines (GE 7EA), the addition of three new gas-fired boilers rated at 550 MMBtu/hr and the removal of three existing gas-fired boilers rated at 443 MMBtu/hr. |  | (4) cogeneration turbines | 15.21 | natural gas | 90 | MW | (4) GE 7EA turbines providing power and process steam | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | DLN and Closed Loop Emissions Controls (CLEC) | 15 | PPMVD | @15% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | (2) combined cycle turbines | 15.21 | natural gas | 650 | MW | The specific equipment includes two combustion turbines (CTs) connected to electric generators, producing between 183 and 232 MW of electricity, depending on ambient temperature and the selected CT. The two HRSGs use duct burners rated at 750 MMBtu/hr each to supplement the heat energy from the CTs. The steam from the two HRSGs is combined and routed to a single steam turbine driving a third electric generator with an electricity output capacity of 271 MW. Depending on the selected CT, total plant output at 59Â°F is between 637 MW and 735 MW. The applicant is considering three models of CT; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) Siemens SGT6-5000F(4); or (3) Siemens SGT6-5000F(5). | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 2 | PPMVD | @15% O2, 3-HR ROLLING, 80-100% LOAD | BACT-PSD |  | N | 0 | U | 4 | PPMVD | @15% O2, 3-HR ROLLING, 60-80% LOAD | 0 |  |  | 0 | 0 | N
TX-0709 | SAND HILL ENERGY CENTER | CITY OF AUSTIN | TRAVIS | TX |  | USA | JOSEPH RAVI | (512) 322-6284 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez (512) 239-5220 Ruth.alvirez@tceq.texas.gov | 48106, PSDTX1012M2 | 4911 | 221112 | 110008975804 | 03/20/2015 &nbsp;ACT | 09/13/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | GE 7FA Natural Gas-fired Combined Cycle Turbine with DB fired HRSG |  | Natural gas-fired combined cycle turbines | 15.21 | Natural Gas | 173.9 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OC | 2 | PPM | 1HR AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0710 | VICTORIA POWER STATION | VICTORIA WLE L.P. | VICTORIA | TX |  | USA | GARY CLARK | (361) 947-9934 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | 108258 PSDTX1348 | 4911 | 221112 | 110000501154 | 02/14/2013 &nbsp;ACT | 12/01/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | The facility is currently authorized under Standard Permit No. 80878 and several Permits by Rule (PBR), including Â§106.263 for maintenance, startup, and shutdown (MSS) (PBR Registration No. 94387) and Title V Permit No. O-35. Victoria proposes to install an additional natural gas-fired turbine (GT) and HRSG with duct burners at the Victoria Station. The resulting new facility will be a combined cycle generating facility in a 2x2x1 configuration (two combustion turbines, two HRSGs with duct burners, and one steam turbine). |  | combined cycle turbine | 15.21 | natural gas | 197 | MW | General Electric 7FA.04 at 197 MW nominal ouput. The duct burners will be capable of a maximum natural gas firing rate of up to 483 MMBtu/hr (HHV). The duct burners may be fired additional hours; however, total annual firing will not exceed the equivalent of 4,375 hours at maximum capacity per duct burner. The available capacity of the existing steam turbine will be increased from 125 MW in its existing 1x1x1 configuration to approximately 185 MW in the 2x2x1 configuration. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 4 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0712 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER COMPANY | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | (205) 257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tzvi Shalem 512-239-1310 tzvi.shalem@tceq.texas.gov | 111393 PSDTX1368 | 4911 | 221112 | 110007199735 | 06/27/2013 &nbsp;ACT | 11/20/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | Southern Power Company (SPC) is proposing to construct an electric generating facility near Trinidad, Henderson County, Texas. The Trinidad Generating Facility (TGF) will include a natural gas-fired combined cycle combustion turbine generator (CTG) equipped with heat recovery steam generator (HRSG) and duct burners (DB). |  | combined cycle turbine | 15.21 | natural gas | 497 | MW | The facility will consist of a Mitsubishi Heavy Industries (MHI) J model gas fired combustion turbine nominally rated at 497 megawatts (MW) equipped with a HRSG and DB with a maximum design capacity of 402 million British thermal units per hour (MMBtu/hr). The gross nominal output of the CTG with HRSG and DB is 530 MW. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 4 | PPMVD | @15% O2, 24-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0713 | TENASKA BROWNSVILLE GENERATING STATION | TENASKA BROWNSVILLE PARTNERS, LLC | CAMERON | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 108411 PSDTX1350 | 4911 | 221112 | unknown | 02/21/2013 &nbsp;ACT | 04/29/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | Tenaska proposes a new electric power plant, using combined cycle gas turbine (CCGT) technology and fueled by pipeline quality natural gas. The proposed permit authorizes two CTs (2x1 CCGT), although the final design selected by Tenaska may only consist of one CT (1x1 CCGT). |  | (2) combined cycle turbines | 15.21 | natural gas | 274 | MW | Each CTG is site-rated at 274 MW gross electric output at 62Â°F ambient temperature. At this condition, two HRSGs with full duct burner firing produce enough steam to generate an additional 336 MW, for a total of 884 MW gross, or with about 5% losses, about 840 MW net electric output. Under summertime conditions, the net output is approximately 800 MW with the 2x1 CCGT configuration or about 400 MW with the 1x1 CCGT configuration. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 2 | PPMVD | @15% O2, 24-HR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0714 | S R BERTRON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | HARRIS | TX |  | USA | CRAIG ECKBERG | (713) 537-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | 102731 PSDTX1294 | 4911 | 221112 | 110034988413 | 05/10/2012 &nbsp;ACT | 12/19/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | NRG Texas is proposing to construct an additional electric power generation station at the Bertron Power Project which will generate electric power for sale on the wholesale electric market. The Bertron Power Project will include two power blocks that can be operated in combined cycle mode. |  | (2) combined cycle turbines | 15.21 | natural gas | 240 | MW | The gas turbines will be one of three options: (1) Two Siemens Model F5 (SF5) CTGs each rated at nominal capability of 225 megawatts (MW). Each CTG will have a duct fired HRSG with a maximum heat input of 688 million British thermal units per hour (MMBtu/hr). (2) Two General Electric Model 7FA (GE7FA) CTGs each rated at nominal capability of 215 MW. Each CTG will have a duct fired HRSG with a maximum heat input of 523 MMBtu/hr. (3) Two Mitsubishi Heavy Industry G Frame (MHI501G) CTGs each rated at a nominal electric output of 263 MW. Each CTG will have a duct fired HRSG with a maximum heat input of 686 MMBtu/hr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | oxidation catalyst | 4 | PPMVD | @15% O2, ONE HOUR | BACT-PSD |  | N | 0 | U | 2 | PPMVD | @15% O2, ROLLING 12-MONTH | 0 |  |  | 0 | 0 | N
TX-0727 | CEDAR BAYOU ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | CHAMBERS COUNTY | TX |  | USA | LINDSAY LITTLE | (713) 357-5291 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem, 512-239-1310, tzvi.shalem@tceq.texas.gov | 80289 & PSDTX1082M1 | 4911 | 221112 | 110037869456 | 01/07/2015 &nbsp;ACT | 03/31/2015 &nbsp;ACT | 2015-03-30 | 2020-01-31 | C |  | NRG operates the Cedar Bayou 4 Electric Generating Station in Chambers County, consisting of two natural gas-fired combustion turbines, Emission Point Numbers (EPNs) CBY41 and CBY42, and associated ancillary equipment. NRGâ€™s amendment application requests an increase in the annual carbon monoxide (CO) and a small increase in the volatile organic compounds (VOC) emission rates for both turbines, due to an increase in the number of startups per year. NRG requests to install oxidation catalysts to each unit. |  | Combined cycle turbines | 15.21 | Natural Gas | 187 | MW/turbine |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation catalysts | 15 | PPMVD | 15%O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041470431 | 02/24/2015 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2020-01-31 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | SCR and oxidation catalyst | 4 | PPMVD @ 15% O2 | 3-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Permit requires downward adjustment to CO limits based on first 30 months of operation
TX-0767 | LON C. HILL POWER STATION | LON C. HILL, L.P. | NUECES | TX |  | USA | MATTHEW LINDSEY | 713-358-9734 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem, 512-239-1310, Tzvi.Shalem@tceq.texas.gov | 114911 AND PSDTX1380 | 4911 | 221122 | 110000501127 | 07/15/2015 &nbsp;ACT | 10/02/2015 &nbsp;ACT | 2015-09-23 | 2016-07-06 | A |  | The Lon C. Hill Power Station (LCHP) will include two natural gas-fired combined cycle combustion turbines (CTGs) equipped with dry low NOx burners (DLNs), heat recovery steam generators (HRSG), and natural gas-fired duct burners (DBs). Ancillary equipment includes evaporative coolers or inlet chillers, a single steam turbine (ST), auxiliary boiler, emergency generator, firewater pump, two cooling towers, oil water separator, degreaser, two diesel storage tanks, gasoline storage tank, selective catalytic reduction (SCR) and ammonia (NH3) handling systems including an NH3 storage tank, and two water tanks. The LCHP will be a 2x1 combined cycle power plant consisting of two CTGs, two HRSGs and one ST. The CTGs and ST will be one of two options: two Siemens SCC6-5000 CTGs and a SST6-5000 ST, or two General Electric 7FA CTGs and a D-11 ST. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 195 | MW | Two power configuration options authorized Siemens â€“ 240 MW + 250 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 195 MW + 670 MMBtu/hr duct burner | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPM | ROLLING 24-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0773 | FGE EAGLE PINES PROJECT | FGE EAGLE PINES, LLC | CHEROKEE | TX |  | USA | EMERSON FARRELL | 281-407-7749 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, 512-239-1095, Erik.Hendrickson@tceq.texas.gov | 131316, PSDTX1454, AND GHGPSDT | 4911 | 221112 | UNKNOWN | 09/10/2015 &nbsp;ACT | 11/04/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | The FGEEP Project will include three natural gas-fired combined cycle (NGCC) power blocks, each block comprised of two gas-fired combustion turbines, two supplemental fired duct burners (DBs) heat recovery steam generators (HRSGs), and one steam turbine. FGEEP selected Alstom GT36 combustion turbines (CTs), each nominally rated at 321 megawatts (MW). Each HRSG is equipped with DBs that will have a maximum design heat input capacity of 799 million British thermal units per hour (MMBtu/hr). The CTs and DBs are fueled with pipeline quality natural gas. Each power block will also have a steam turbine generator designed to produce approximately 502 MW with the additional duct firing. Each of the three blocks will include the following ancillary equipment: one multi-cell condenser/cooling tower, one emergency generator, one firewater pump, two diesel storage tanks, and pressurized aqueous ammonia storage tanks. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 321 | MW | Alstom GT36 combustion turbines (321 MW)+ 799 million British thermal units per hour (MMBtu/hr) duct burner | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 2 | PPM | 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 4 | PPM | HOURLY | BACT-PSD | NSPS | N | 0 | U | 2 | PPM | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N |  | NSPS KKKK AND TTTT
TX-0789 | DECORDOVA STEAM ELECTRIC STATION | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas.gov | 107569 AND PSDTX1432 | 4911 | 221112 | 110008149217 | 12/23/2015 &nbsp;ACT | 03/08/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | The DeCordova Station will consist of two combustion turbine generators (CTGs) operating in simple cycle or combined cycle modes. The gas turbines will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE). Simple cycle operations limited to 2,500 hr/yr. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 4 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.21 | natural gas | 10 | M TONNES/YR | Four GE Frame 7E gas turbines for refrigeration and compression at the site | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Dry low NOx burners and good combustion practices | 25 | PPM | ROLLING 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Simple Cycle Electrical Generation Gas Turbines 15.210 | 15.21 | natural gas | 34 | MW | Nine GE PGT25+G4 gas turbines for electrical generation at the site at 34 MW/turbine | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 9 | PPM | ROLLING 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Combined Cycle Turbine with Heat Recovery Steam Generator, fired Duct Burners, and Steam Turbine Generator | 15.21 | NATURAL GAS | 426 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines with HRSGs and Steam Turbine Generators | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Selective Catalytic Reduction (SCR) and Dry Low NOx burners | 2 | PPMVD | 15% O2 3-H AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 2 | PPMVD | 15% O2 3 HOUR AVERAGE | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | COMBINED CYCLE TURBINE MSS REDUCED LOAD | 15.21 | NATURAL GAS | 0 |  | 9 HOURS STARTUP, 1 HOUR SHUTDOWN | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | minimizing duration of startup / shutdown events, engaging the pollution control equipment as soon as practicable (based on vendor recommendations and guarantees), and meeting the emissions limits on the MAERT | 8000 | LB/H |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
VA-0315 | WARREN COUNTY POWER PLANT - DOMINION | VIRGINIA ELECTRIC AND POWER COMPANY | WARREN | VA | 22630 | USA | ROBERT BISHA | 804-273-3010 | ROBERT.M.BISHA@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Manager, Mr. Janardan Pandey, by phone at (540) 574-7817 or by e-mail: Janardan.Pandey@deq.virginia.gov | 81391-007 | 4911 | 221112 | 110040513110 | 09/03/2010 &nbsp;ACT | 12/17/2010 &nbsp;ACT | 2012-09-28 | 2015-03-30 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Virginia Electric and Power Company (Dominion) has proposed to construct and operate a combined-cycle electric power generating facility in Warren County with a nominal generating capacity of 1280 megawatts (MW) at ISO (International Organization for Standardization) conditions. | Equipment to be constructed at ths facility consists of: 3 Mitsubishi Model M501 GAC natural gas-fired combined-cylce turbines, each rated at 299,600 kW (2,996 MMBtu/hr. Each equipped with a heat recovery steam generator (HRSG) having a duct burner with a design rating of 500 MMBtu/hr. This permit supersedes the previous permit issued on 7/30/2004 to CPV Warren LLC. | COMBINED CYCLE TURBINE &amp; DUCT BURNER, 3 | 15.21 | Natural Gas | 2996 | MMBTU/H | Emissions are for one of three units (Mitsubishi natural gas-fired combustion turbine (CT) generator,Model M501 GAC). | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices. | 1.5 | PPMVD | ONE HR AVERAGE (W/O DUCT BURNER FIRING) | BACT-PSD |  | U | 0 | U | 2.4 | PPMVD | ONE HR AVERAGE (WITH DUCT BURNER FIRING) | 0 |  |  | 0 | 0 | N |  | Emissions are for one of three units. Emission 1: 9.9 LB/H ONE HR AVERAGE (W/O DUCT BURNER FIRING) Emission 2: 17.4 LB/H ONE HR AVERAGE (WITH DUCT BURNER FIRING)
VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404 | 4911 | 221112 | 110055066440 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2019-06-19 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | COMBUSTION TURBINE GENERATORS, (3) | 15.21 | Natural Gas | 3442 | MMBTU/H | Three (3) Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners (natural gas-fired). | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst; good combustion practices. | 1.5 | PPMVD | 3 H AVG/WITHOUT DUCT BURNING | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404 | 4911 | 221112 | 110055066440 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2019-06-19 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | Three Mitsubishi M501 GAC Turbines (3,442 mmBtu/hr each) | 15.21 | natural gas | 0 | s | combined fuel for three turbines as a 12-month rolling total | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices including the minimization of startup and shutdown emissions | 1.5 | PPMVD | 3-HOUR ROLLING AVG W/O DUCT BURNER | BACT-PSD | NSPS , SIP | U | 0 | Y | 2.4 | PPMVD | 3-HOUR ROLLING AVG W/O DUCT BURNER | 0 |  |  | 0 | 0 | N |  | CEMS will be used to monitor CO from the turbines Initial performance test continuous monitoring and recording of catalyst bed inlet and outlet temperature
VA-0322 | GREEN ENERGY PARTNERS/ STONEWALL, LLC | GREEN ENERGY PARTNERS/ STONEWALL, LLC | LOUDOUN | VA | 20147 | USA | JOHN ANDREWS | 703-508-3619 | ADNCOMINV@AOL.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Mr. Thomas Valentour, by phone at (703) 583-3931 or by e-mail: Thomas.Valentour@deq.virginia.gov | 73826-001 | 4911 | 221112 | 110041353834 | 02/26/2013 &nbsp;ACT | 04/30/2013 &nbsp;ACT | 2013-04-30 | 2016-05-04 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Green Energy Partners / Stonewall, LLC has proposed to construct and operate a combined-cycle electric power generating facility in Loudoun County with a nominal generating capacity of 750 megawatts (MW). The proposed facility is comprised of two combusion turbine generators each having a heat recovery steam generator (HRSG) driving a common steam turbine. Each HRSG has a duct burner for supplemental firing. The facility also includes an auxilliary boiler, an emergency fire water pump, an emergency generator and a fuel gas heater. | GEP/S has requested that the proposed permit allow two optional plant configurations, each having a different combustion turbine manufacturer. The two combustion turbine configuration options currently being considered are the General Electric GE7FA.05 and Siemens SGT6-5000F5 units. Tthe proposed CT generators will either be General Electric GE7FA.05 or Siemens SGT6-5000F5 units. The facilitywide pollutant emissions listed are based on the GE F7FA.05 Combusion Turbines & HRSGs with DBs on. PM=PM-10. Emissions for PM-2.5 = 98.1 T/Yr. Emissions for the Siemens SGT6-5000F5 Combusion Turbines & HRSGs with DBs on: Carbon Monoxide: 143.6 Nitrogen Oxides: 164.9 | Large combustion turbines (&gt;25MW) CCT1 and CCT2 | 15.21 | Natural Gas | 2.23 | MMBTU/H | Throughput and Units above are for the GEF7.05. Siemens SGTF-5000F5: Throughput: 2.260 MMBTU/hr | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Catalytic Oxidizer | 0 |  |  | BACT-PSD |  | U | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Option 1 - Normal Operation | 15.21 | natural gas | 34000 | MMCF/YR | Option 1: Two on one configuration: 3,482 MMBtu/hr combustion turbine with 475 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 1 | PPMVD@ 15% O2 | 3 HR AV/WITHOUT DB | BACT-PSD | NSPS , SIP | U | 0 | N | 1.6 | PPMVD@ 15% O2 | 3 HR AV/WITH DB | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during startup and shutdown. CEMS required.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combusion Turbine - Option 2 - Normal Operation | 15.21 | Natural Gas | 35000 | MMCF/YR | Option 2: Two on one configuration: 3,116 MMBtu/hr combustion turbine with 991 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst & good combustion practice | 1.8 | PPMVD @ 15% O2 | 3 H AV/WITH OR WITHOUT DB | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during tuning, water washing, startup and shutdown. CEMS required.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Tuning &amp; Water Washing | 15.21 | natural gas | 34000 | MMCF/YR | Alternative operating scenario: during periods of tuning and water washing | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 194 | LB/TURBINE/DAY | 24 HR AV | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies during tuning (limited to 18 hours/event) and water washing (limited to 60 minutes/event). Determined by CEMS.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Startup and Shutdown | 15.21 | natural gas | 34000 | MMCF/YR | Startup and Shutdown | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practice | 840 | LB/TURBINE/EVENT | COLD START 60 MIN OR LESS | BACT-PSD | SIP | N | 0 | N | 188 | LB/TURBINE/EVENT | WARM START 50 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 180 lb/turbine/event hot start - 30 minutes or less 100 lb/turbine/event shutdown - 30 minutes or less These limits apply during startup and shutdown. CEMS required.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combustion Turbine - Tuning &amp; Water Washing | 15.21 | Natural Gas | 35000 | MMCF/YR | Alternative operating scenario: during periods of tuning and water washing | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 309 | LB/TURBINE/DAY | 24 HR AV | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies during tuning (limited to 18 hours/event) and water washing (limited to 60 minutes/event). Determined by CEMS.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combustion Turbine - Startup &amp; Shutdown | 15.21 | Natural Gas | 35000 | MMCF/YR | Startup and Shutdown | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 434 | LB/TURBINE/EVENT | COLD START 55 MIN OR LESS | BACT-PSD | SIP | N | 0 | N | 397 | LB/TURBINE/EVENT | WARM START 55 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 36 lb/turbine/event hot start - 50 minutes or less 184 lb/turbine/event shutdown - 38 minutes or less These limits apply during startup and shutdown. CEMS required.
*VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2020-03-18 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/hr natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/hr combustion turbine. Emission limits reflect the operation of each of the three turbines. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Controlled by an oxidation catalyst and good combustion practices (e.g. controlled fuel/air mixing, adequate temperature, and gas residence time). | 1 | PPMVD @ 15% O2 | 3 HR AVG | BACT-PSD | NSPS , SIP | N | 0 | N | 94.3 | TONS/YR | 12 MO ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during startup, shutdown, and tuning. CEMS required.
*VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2020-03-18 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/hr natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems Combustion | 15.21 | natural gas | 35000 | MMCF/YR | Alternative operating scenario: during periods of tuning | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 214 | LB/TURBINE/DAY | 24 HR TOTAL | BACT-PSD | SIP , NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies during tuning (limited to 18 hours/event). Determined by CEMS.
*VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2020-03-18 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/hr natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | Startup and Shutdown | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst and good combustion practices | 444 | LB/TURBINE/EVENT | COLD START 42 MIN OR LESS | BACT-PSD | SIP | N | 0 | N | 396 | LB/TURBINE/EVENT | WARM START 42 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 252 lb/turbine/event hot start - 42 minutes or less 156 lb/turbine/event shutdown - 42 minutes or less These limits apply during startup and shutdown. CEMS required.
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Combined Cycle Turbine/Duct Burner | 15.21 | Natural Gas | 2419.61 | mmBtu/Hr | This entry is for both of two identical units at the facility. Nominal 197 mW General Electric Frame 7FA.04 Turbine w/ Duct Burner - throughput denotes aggregate heat input of turbine and duct burner (HHV). | Carbon Monoxide | Other - CEMS | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst + Combustion Controls | 9.2 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 2 | PPM | @ 15% O2 | 0 | 0 | N |  | CO emissions applicable with and without duct firing.
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2018-06-25 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.02 Turbine | 15.21 | Natural Gas | 3496.2 | mmBtu/hr | Nominal 640 mWe All emission limits steady-state and include 1000 mmBtu/hr Duct Burner in operation Short Term startup and shutdown limits in lb/event given in permit. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst, Good Combustion Practices | 20 | LB/HR | 1-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 124 | TONS/YEAR |  | 2 | PPM |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP01) | 15.21 | Natural Gas | 40 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 4 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD |  | U | 0 | U | 3.7 | LB/H | 30-DAY ROLLING AVERAGE | 32 | T/YR |  | 3307 | 5108 | N | 2011
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP02) | 15.21 | Natural Gas | 40 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 4 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD |  | N | 0 | U | 3.7 | LB/H | 30-DAY ROLLING AVERAGE | 32 | T/YR |  | 3307 | 5108 | N | 2011
ID-0018 | LANGLEY GULCH POWER PLANT | IDAHO POWER COMPANY | PAYETTE | ID |  | USA |  | 2083885820 | TMAHLUM@IDAHOPOWER.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2009.0092 | 4911 | 221112 | UNKNOWN | 06/07/2009 &nbsp;ACT | 06/25/2010 &nbsp;ACT | 2010-08-09 | 2010-10-05 | A |  | ONE-ON-ONE COMBINED CYCLE PLANT CONSISTING OF (1) NATURAL GAS-FIRED COMBUSTION TURBINE (CT) AND (1) STEAM TURBINE. THE CT IS EQUIPPED WITH (1) HEAT RECOVERY STEAM GENERATOR (HRSG) AND DUCT BURNER. ANCILLARY EQUIPMENT INCLUDES (1) DIESEL-FIRED EMERGENCY GENERATOR, (1) DIESEL-FIRED FIRE PUMP, (1) WET COOLING TOWER, AND (6) DRY CHEMICAL STORAGE SILOS. |  | COMBUSTION TURBINE, COMBINED CYCLE W/ DUCT BURNER | 15.21 | NATURAL GAS (ONLY) | 2375.28 | MMBTU/H | SIEMENS SGT6-5000F COMBUSTION TURBINE (NGCT, CCGT) FOR ELECTRICAL GENERATION, NOMINAL 269 MW AND 2.1466 MMSCF/HR | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | CATALYTIC OXIDATION (CATOX), DRY LOW NOX (DLN), GOOD COMBUSTION PRACTICES (GCP) | 2 | PPMVD | 3-HR ROLLING / 15% O2 | BACT-PSD |  | N | 0 |  | 24.5 | PPMVD | 3-HR ROLLING / 15% O2 DURING LL | 2510 | LB/H | 1-HR / 15% O2 DURING SU/SD | 0 | 0 | N |  | LIMITS APPLY TO COMBUSTION TURBINE AND DUCT BURNER COMBINED EMISSIONS. SECONDARY LIMIT APPLIES DURING STARTUP, SHUTDOWN, AND LOW-LOAD EVENTS (SU/SD/LL).
*WV-0032 | BROOKE COUNTY POWER PLANT | ESC BROOKE COUNTY POWER I, LLC | BROOKE | WV | 26035 | USA | ANDREW DORN | 7163121042 | DREW.DORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 Steven.R.Pursley@wv.gov | R14-0035 | 4911 | 221112 | Not Found | 03/30/2018 &nbsp;ACT | 09/18/2018 &nbsp;ACT | 2018-12-20 | 2019-01-02 | A |  | Nominal 925 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.01 Turbine | 15.21 | Natural Gas/Ethane | 2737.7 | mmBtu/hr | Facility has 2 identical units, only 1 entry in RBLC. Nominal 462.5 mWe. All emission limits steady-state and include 424 mmBtu/hr Duct Burner in operation. Short Term startup and shutdown limits in lb/event given in permit. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Oxidation Catalyst, Good Combustion Practices | 14.1 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 2 | PPM |  | 0 | 0 | N
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | Mitsubishi M501-GAC combustion turbine, combined cycle configuration with duct burner. | 15.21 | natural gs | 2988 | MMBTU/H | or ULSD; Duct burner 499 MMBtu/hr, natural gas | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst; Limit the time in startup or shutdown. | 3.3 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON NG | BACT-PSD |  | U | 0 | U | 9 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON ULSD | 0 |  |  | 0 | 0 | N
AK-0073 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION | ANCHORAGE | AK | 99518 | USA | GREGORY ARTHUR | 907 762 4492 |  | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Kwame Agyei, Permit Engineer, kwame.agyei@alaska.gov | AQ0164CPT01 | 4911 | 221112 | 110046491854 | 04/14/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2012-02-22 | 2014-01-08 | D |  | Power plant that contains four combustion turbines, four duct burners, a black start generator, and an auxiliary heater. |  | Fuel Combustion | 15.21 | Natural Gas | 59900 | HP | EU IDs 5-8 Combined Cycle Natural Gas-fired Combustion Turbines rated at 59,900 hp (44.7 MW) | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Turbines EU IDs 5 through 8 shall be equipped with Selective Catalytic Reduction and Dry Low NOx (SCR and DLN) combustors. SCR is a post-combustion gas treatment technique for reduction of nitric oxide (NO) and nitrogen dioxide (NO2) in the turbine exhaust stream to molecular nitrogen, water, and oxygen. This process is accomplished by using ammonia (NH3) as a reducing agent, and is injected into the flue gas upstream of the catalyst bed. By lowering the activation energy of the NOx decomposition removal efficiency of 80 to 90 percent are achievable. DLN combustors utilize multistage premix combustors where the air and fuel is mixed at a lean fuel to air ratio. The excess air in the lean mixture acts as a heat sink, which lowers peak combustion temperatures and also ensures a more homogeneous mixture, both resulting in greatly reduced NOx formation rates. DLN can reduce emissions by about 60% | 5 | PPM | 4-HOUR | BACT-PSD |  | U | 90 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (COLD STARTUP PERIODS) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 52.4 | LB/H | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 96 | LB/H | COLD STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | COLD STARTUP PERIODS SHALL NOT EXCEED 1.8 HR/EVENT OR 50 EVENTS/YR
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (WARM &amp; HOT STARTUP PERIODS) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 30 | LB/H | WARM & HOT STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 40 | LB/EVENT | WARM & HOT STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | WARM & HOT STARTUP PERIODS SHALL NOT EXCEED 1.3 HR/EVENT OR 260 EVENTS/YR
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 114 | LB/H | SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 57 | LB/EVENT | SHUTDOWN PERIODS | 0 |  |  | 0 | 0 | N |  | SHUTDOWN PERIODS SHALL NOT EXCEED 0.5 HR/EVENT OR 310 EVENTS/YR
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (COLD STARTUP PERIODS) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 52.4 | LB/H | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 96 | LB/EVENT | COLD STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | COLD STARTUP PERIODS SHALL NOT EXCEED 1.8 HR/EVENT OR 50 EVENTS/YR
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (WARM &amp; HOT STARTUP PERIODS) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 30 | LB/H | WARM & HOW STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 40 | LB/EVENT | WARM & HOW STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | WARM & HOT STARTUP PERIODS SHALL NOT EXCEED 1.3 HR/EVENT OR 260 EVENTS/YR
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 114 | LB/H | SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 57 | LB/EVENT | SHUTDOWN PERIODS | 0 |  |  | 0 | 0 | N |  | SHUTDOWN PERIODS SHALL NOT EXCEED 0.5 HR/EVENT OR 310 EVENTS/YR
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Nitrogen Oxides (NOx) | Other - EPA Method 7E, or Methods 7E and 19 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR, DRY LOW NOX COMBUSTORS | 2 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 13.55 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Nitrogen Oxides (NOx) | Other - EPA Method 7E, or Methods 7E and 19 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR, DRY LOW NOX COMBUSTORS | 2 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 17.2 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (STARTUP &amp; SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 180 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR, DRY LOW NOX COMBUSTORS | 160 | LB/H | EACH TURBINE & HRSG | BACT-PSD |  | U | 0 | U | 240 | LB/H | BOTH TURBINES & HRSGS | 0 |  |  | 0 | 0 | N |  | 1) STARTUP FOR EACH TURBINE & HRSG NOT TO EXCEED 4.5 HOURS; 2) SHUTDOWN FOR EACH TURBINE & HRSG NOT TO EXCEED 0.5 HOURS; 3) ANNUAL LIMIT FOR BOTH TURBINES NOT TO EXCEED 1248 HRS/YR
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Nitrogen Oxides (NOx) | Other - EPA Method 7E, or Methods 7E and 19 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR, DRY LOW NOX COMBUSTORS | 2 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 13.55 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Nitrogen Oxides (NOx) | Other - EPA Method 7E, or Methods 7E and 19 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR, DRY LOW NOX COMBUSTORS | 2 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 17.2 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (STARTUP &amp; SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 180 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR, DRY LOW NOX COMBUSTORS | 160 | LB/H | EACH TURBINE & HRSG | BACT-PSD |  | U | 0 | U | 240 | LB/H | BOTH TURBINES & HRSGS | 0 |  |  | 0 | 0 | N |  | 1) STARTUP FOR EACH TURBINE & HRSG NOT TO EXCEED 4.5 HOURS; 2) SHUTDOWN FOR EACH TURBINE & HRSG NOT TO EXCEED 0.5 HOURS; 3) ANNUAL LIMIT FOR BOTH TURBINES NOT TO EXCEED 1248 HRS/YR
CA-1209 | HIGH DESERT POWER PROJECT | HIGH DESERT POWER PROJECT LLC | SAN BERNADINO | CA | 92394 | USA | JON BOYER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 98-01 | 4911 | 221112 | 110014461420 | 09/25/2009 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-11 | 2014-01-15 | C | http://www.epa.gov/region09/air/permit/r9-permits-issued.html | 720 MW NATURAL GAS FIRED POWER PLANT | RBLC Management: There were many duplicate pollutant records Editor repeated all emission limits for each of the 3 types of operation, Start-up, Normal, and Shutdown. Record was edited and duplicate records were deleted. Original Note: PSD Permit amended to change the design of the power plant. These changes include a modification in the turbine configuration from 3x3x3 (i.e., three combustion turbines (CT), three heat recovery steam generators (HRSG), and three steam turbine generators (STG)) to a 3x3x1 configuration, reconfiguration of the cooling tower from three towers to one, addition of a diesel firewater pump engine, modification of the stack location, elevation, and diameter, and modification in the physical dimensions of the cooling tower, steam turbine, and HRSG structure. The terms and conditions included in the PSD permit issued February 15, 2001, and the modeling analyses on which the original determinations were based, remain valid and in effect. | COMBUSTION TURBINE GENERATORS (NORMAL OPERATION) | 15.21 | NATURAL GAS | 190 | MW | THREE (3) COMBUSTION TURBINE GENERATORS AT 190 MW EACH AND EQUIPPED WITH A 160 MMBTU/HR DUCT BURNER AND HRSG | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW NOX BURNERS (LNB), SELECTIVE CATALYTIC REDUCTION (SCR) | 2.5 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 18 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N
CA-1209 | HIGH DESERT POWER PROJECT | HIGH DESERT POWER PROJECT LLC | SAN BERNADINO | CA | 92394 | USA | JON BOYER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 98-01 | 4911 | 221112 | 110014461420 | 09/25/2009 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-11 | 2014-01-15 | C | http://www.epa.gov/region09/air/permit/r9-permits-issued.html | 720 MW NATURAL GAS FIRED POWER PLANT | RBLC Management: There were many duplicate pollutant records Editor repeated all emission limits for each of the 3 types of operation, Start-up, Normal, and Shutdown. Record was edited and duplicate records were deleted. Original Note: PSD Permit amended to change the design of the power plant. These changes include a modification in the turbine configuration from 3x3x3 (i.e., three combustion turbines (CT), three heat recovery steam generators (HRSG), and three steam turbine generators (STG)) to a 3x3x1 configuration, reconfiguration of the cooling tower from three towers to one, addition of a diesel firewater pump engine, modification of the stack location, elevation, and diameter, and modification in the physical dimensions of the cooling tower, steam turbine, and HRSG structure. The terms and conditions included in the PSD permit issued February 15, 2001, and the modeling analyses on which the original determinations were based, remain valid and in effect. | COMBUSTION TURBINE GENERATOR (STARTUP PERIODS) | 15.21 | NATURAL GAS | 190 | MW | THREE (3) COMBUSTION TURBINE GENERATORS AT 190 MW EACH AND EQUIPPED WITH A 160 MMBTU/HR DUCT BURNER AND HRSG | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW NOX BURNERS (LNB), SELECTIVE CATALYTIC REDUCTION (SCR) | 3541 | LB/COLD STARTUP | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 3596 | LB/WARM STARTUP | WARM STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | RBLC Management: Limit Moved from Standard Limit Fields: &lsquo;&lsquo;3729.0 LB.Hot Startup, Hot Startup Periods&lsquo;&lsquo; Remember, the Standard Limit fields may be used only when the process and pollutant match the information in Volume 3 of the RBLC User's Manual, Appendix E. The Standard Limit fields should not be used to list a third emission limit. If there are more than 2 emission limits, the additional information must be entered in the pollutant notes field. Original Note: OTHER REQUIREMENTS: 1) COLD STARTUP NOT TO EXCEED 4.5 HRS; 2) WARM STARTUP NOT TO EXCEED 2.6 HRS; 3) HOT STARTUP NOT TO EXCEED 1.9 HRS; 4) SEE PERMIT FOR ALTERNATIVE COLD STARTUP SCENARIO REQUIREMENTS
CA-1209 | HIGH DESERT POWER PROJECT | HIGH DESERT POWER PROJECT LLC | SAN BERNADINO | CA | 92394 | USA | JON BOYER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 98-01 | 4911 | 221112 | 110014461420 | 09/25/2009 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-11 | 2014-01-15 | C | http://www.epa.gov/region09/air/permit/r9-permits-issued.html | 720 MW NATURAL GAS FIRED POWER PLANT | RBLC Management: There were many duplicate pollutant records Editor repeated all emission limits for each of the 3 types of operation, Start-up, Normal, and Shutdown. Record was edited and duplicate records were deleted. Original Note: PSD Permit amended to change the design of the power plant. These changes include a modification in the turbine configuration from 3x3x3 (i.e., three combustion turbines (CT), three heat recovery steam generators (HRSG), and three steam turbine generators (STG)) to a 3x3x1 configuration, reconfiguration of the cooling tower from three towers to one, addition of a diesel firewater pump engine, modification of the stack location, elevation, and diameter, and modification in the physical dimensions of the cooling tower, steam turbine, and HRSG structure. The terms and conditions included in the PSD permit issued February 15, 2001, and the modeling analyses on which the original determinations were based, remain valid and in effect. | COMBUSTION TURBINE GENERATOR (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 190 | MW | THREE (3) COMBUSTION TURBINE GENERATORS AT 190 MW EACH AND EQUIPPED WITH A 160 MMBTU/HR DUCT BURNER AND HRSG | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW NOX BURNERS (LNB), SELECTIVE CATALYTIC REDUCTION (SCR) | 97 | LB/SHUTDOWN | SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | SHUTDOWN NOT TO EXCEED 1 HR
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (WARM STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW NOX BURNERS (LNB), SELECTIVE CATALYTIC REDUCTION (SCR) | 249.9 | LB/H | WARM STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 456.2 | LB/EVENT | WARM STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF WARM STARTUPS NOT TO EXCEED 180 MINUTES; 2) WARM STARTUP MEANS A STARTUP THAT IS NOT A HOT OR COLD STARTUP
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (HOT STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW NOX BURNERS (LNB), SELECTIVE CATALYTIC REDUCTION (SCR) | 152 | LB/H | HOT STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 259.9 | LB/EVENT | HOT STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF HOT STARTUPS NOT TO EXCEED 90 MINUTES; 2) HOT STARTUP MEANS A STARTUP WHEN THE COMBUSTION TURBINE HAS BEEN IN OPERATION DURING THE PRECEDING 8 HOURS
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW NOX BURNERS (LNB), SELECTIVE CATALYTIC REDUCTION (SCR) | 115 | LB/H | TURBINE SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 115 | LB/EVENT | TURBINE SHUTDOWN PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF SHUTDOWN NOT TO EXCEED 30 MINUTES; 2) SHUTDOWN MEANS THE PERIOD BEGINNING WITH THE LOWERING OF EQUIPMENT FROM BASE LOAD AND LASTING UNTIL FUEL FLOW IS COMPLETELY OFF AND COMBUSTION HAS CEASED
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Nitrogen Oxides (NOx) | Other - EPA METHOD 7E, OR METHODS 7E AND 19 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW NOX BURNERS (LNB), SELECTIVE CATALYTIC REDUCTION (SCR) | 2 | PPMVD | @15% O2, 1-HR ROLLING AVG | BACT-PSD |  | U | 0 | U | 19.6 | LB/H | 1-HR ROLLING AVG | 0 |  |  | 0 | 0 | N
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (COLD STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW NOX BURNERS (LNB), SELECTIVE CATALYTIC REDUCTION (SCR) | 333.3 | LB/H | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 779.1 | LB/EVENT | COLD STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF COLD STARTUPS NOT TO EXCEED 270 MINUTES; 2) COLD STARTUP MEANS STARTUP WHEN THE COMBUSTION TURBINE HAS NOT BEEN IN OPERATION DURING THE PRECEDING 72 HOURS
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Nitrogen Oxides (NOx) | Other - EPA METHOD 7E, OR METHOD 7E & 19 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW NOX (DLN) COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR) | 2 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (STARTUP PERIODS) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW NOX (DLN) COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR) | 96 | LB/EVENT | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 40 | LB/EVENT | WARM & HOT STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | DURING STARTUP OR SHUTDOWN, EMISSIONS OF CO FROM BOTH CTGS COMBINED SHALL NOT EXCEED 790 LB/HR; DURATION OF COLD STARTUP NOT TO EXCEED 110 MIN; DURATION OF WARM & HOT STARTUP NOT TO EXCEED 80 MIN
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 110 | MMBTU/H | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW NOX (DLN) COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR) | 57 | LB/EVENT | SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | DURING STARTUP OR SHUTDOWN, EMISSIONS OF CO FROM BOTH CTGS COMBINED SHALL NOT EXCEED 790 LB/HR; SHUTDOWN NOT TO EXCEED 30 MIN
CA-1251 | PALMDALE ENERGY PROJECT | PALMDALE ENERGY, LLC | LOS ANGELES | CA | 93551 | USA | TOM CAMERON |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov | Staff Contact: Lisa Beckham beckham.lisa@epa.gov (415) 972-3811 | SE 17-01 | 4911 | 221122 | Not Found | 08/16/2017 &nbsp;ACT | 04/25/2018 &nbsp;ACT | 2018-10-25 | 2020-01-31 | A | https://www.epa.gov/caa-permitting/palmdale-energy-project-prevention-significant-deterioration-psd-permit | 645 MW (nominal) Natural Gas-fired Combined Cycle Power Plant, 2 x 1 configuration, auxiliary boiler for faster startup | See also docket: https://www.regulations.gov/docket?D=EPA-R09-OAR-2017-0473. Permit decision was appealed to EPA's Environmental Appeals Board. Board denied review on October 23, 2018. Information available through www.epa.gov/eab and https://yosemite.epa.gov/oa/EAB_Web_Docket.nsf/f22b4b245fab46c6852570e6004df1bd/ad735c0b822500258525829d004217eb!OpenDocument. 1/31/20 -- SYS MGR -- Link to permit is <https://www.regulations.gov/document?D=EPA-R09-OAR-2017-0473-0028> | Combustion Turbines (GEN1 and GEN2) | 15.21 | Natural Gas | 2217 | MMBTU/H | Each combustion turbine rated at 214 MW, with a maximum heat input rate of 2,217 MMBtu/H (HHV, at ISO conditions); natural gas-fired Siemens SGT6-5000F; each vents to dedicated Heat Recovery Steam Generator and a shared 276 MW Steam Turbine Generator; 160-ft stack height; 22-ft stack diameter | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction, Dry Low NOx Burners | 2 | PPM @ 15% O2 | 1-HOUR | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Mass Emission Limits During Normal Operation: 18.5 lb/hr with duct burner (1-hr average) 17.1 lb/hr without duct burner (1-hr average) Startup and Shutdown Limits: Cold Start: 51.5 lb/event, 39 minutes Warm Start: 46.8 lb/event, 35 minutes Hot Start: 43.2 lb/event, 30 minutes Shutdown: 33.0 lb/event, 25 minutes Startup/Shutdown: 53.6 lb/hr (1-hr average) (used in modeling analysis)
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055426409 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Four combined cycle combution turbines | 15.21 | natural gas | 373 | MMBTU/H | Three GE, LMS6000 PF, natural gas-fired, combined cycle CTG, rated at 373 MMBtu per hour each, based on HHV and one (1) HRSG each with no Duct Burners | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry Low NOx (DLN) Combustor and Selective Catalytic Reduction (SCR) | 3 | PPMVD AT 15% O2 | 1-HR AVE | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 0 | U | 4.1 | LB/H | 30-DAY ROLLING AVE | 0 |  |  | 0 | 0 | N |  | startup limit: 30.0 lb per event shutdown limit: 5.0 lb per event compliance is monitored with continuous emissions monitors
CO-0076 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110058377830 | 06/16/2014 &nbsp;ACT | 12/11/2014 &nbsp;ACT | 2014-12-31 | 2016-02-19 | C |  | Electric generation | Permit modification to convert startup and shutdown BACT limits to an hourly basis (from event based). | Four combined cycle combution turbines | 15.21 | natural gas | 373 | MMBTU/H each | GE, LM6000 PF, natural gas fired, combined cycle combustion turbines, with HRSG and no duct burners. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR and dry low NOx burners | 8 | LB/H | 4-HR ROLLING AVE / STARTUP AND SHUTDOWN | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The NOx limit was converted to an equivalent hourly based limit (the original permit included an event based limit) for periods of startup and shutdown.
FL-0337 | POLK POWER STATION | TAMPA ELECTRIC COMPANY | POLK | FL | 33860 | USA | PAUL CARPINONE | 813-228-4528 | PLCARPINONE@TECOENERGY.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Leigh Ann Pell, Project Engineer Phone; 850-717-9033 | 1050233-034-AC | 4911 | 221112 | 110000365113 | 05/15/2013 &nbsp;ACT | 10/14/2012 &nbsp;ACT | 2013-08-06 | 2014-11-07 | D | http://appprod.dep.state.fl.us/air/emission/apds/listpermits.asp | The Polk Power Station consists of: a nominal 250 MW (net) solid fuel-based integrated gasification and combined cycle (Unit 1) including a sulfuric acid plant and an auxiliary boiler; four natural gas-fueled nominal 165 MW simple cycle combustion turbine-electrical generators (CTGs) designated as Units 2, 3, 4 and 5; and ancillary equipment. Units 2 and 3 are equipped with backup fuel oil-firing capability. | GHG(e) emissions: 4,307,862 | Combine cycle power block (4 on 1) | 15.21 | natural gas | 1160 | MW | Basis for the emission standard is either NSPS Subpart KKKK or Department BACT determinations. The BACT emission standards for NOX while operating in combined cycle are more stringent than the corresponding Subpart KKKK emissions standards of 15 and 42 ppmvd @15% O2 on a 30-day rolling average for natural gas and fuel oil, respectively. | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR/DLN | 2 | PPMVD @15% O2 | 24-HR BLOCK (GAS) CEMS | BACT-PSD | NSPS | U | 0 | U | 8 | PPMVD @15% O2 | 24-HR BLOCK (OIL) CEMS | 0 |  |  | 0 | 0 | N |  | Basis for the emission standard is either NSPS Subpart KKKK or Department BACT determinations. The BACT emission standards for NOX while operating in combined cycle are more stringent than the corresponding Subpart KKKK emissions standards of 15 and 42 ppmvd @15% O2 on a 30-day rolling average for natural gas and fuel oil, respectively. Limits: 2.0 ppmvd @15% O2 All CTs CC mode PNG 8.0 ppmvd @15% O2 All CTs CC mode ULSD
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective catalytic reduction; dry low-NOx; and wet injection | 2 | PPMVD@15% O2 | GAS, 24-HR BLOCK, EXCLUDING SSM | BACT-PSD | NSPS | U | 0 | U | 8 | PPMVD@15% O2 | ULSD, 24-HR BLOCK, EXCLUDING SSM | 0 |  |  | 0 | 0 | N |  | NSPS Subpart KKKK is applicable. This subpart is adopted as &lsquo;&lsquo;Secondary BACT&lsquo;&lsquo; during startup/shutdown/malfunction periods. Compliance by NOx CEMS.
*FL-0367 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 36410 | USA | ROY BELDEN | (203) 357-6820 | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-001-AC | 4911 | 221112 | 110012581820 | 02/16/2018 &nbsp;ACT | 07/27/2018 &nbsp;ACT | 2019-03-19 | 2019-03-19 | B | https://arm-permit2k.dep.state.fl.us/nontv/1010524.001.AC.F.ZIP | A 573-megawatt (MW) (winter) 1-on-1 combined cycle plant which includes a heat recovery steam generator with duct firing, along with supporting equipment. Natural gas is the only permitted fuel for the combined cycle unit. | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/1010524.001.AC.R.ZIP | 1-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural Gas | 3266.9 | MMBtu/hour | One nominal 385 MW GE 7HA.02 CTG and one HRSG with duct firing [approximately 210 MMBtu/hour], and one nominal 210 MW steam turbine generator (STG) | Nitrogen Oxides (NOx) | Other - Continous Emissions Monitoring System | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry low-NOX combustors and Selective Catalytic Reduction (SCR) | 2 | PPMVD AT 15% O2 | 24-HOUR BLOCK AVERAGE BASIS (BACT) | BACT-PSD | NSPS , SIP , OTHER | U | 0 | U | 15 | PPMVD AT 15% O2 | 30-OPERATING-DAY ROLLING AVG. (NSPS) | 0 |  |  | 0 | 0 | N |  | 2nd Limit of 15 ppmvd @ 15% O2 (for turbine loads â‰¥ 75%), 30-operating-day rolling avg. (NSPS Subpart KKKK) 3rd Limit: 96 ppmvd @15% O2 (for turbine loads < 75%), 30-operating-day rolling avg. (NSPS Subpart KKKK)
GA-0138 | LIVE OAKS POWER PLANT | LIVE OAKS COMPANY, LLC | GLYNN | GA | 31525 | USA | BURT WALLACE | 478 943-2331 | BURT_1@BELLSOUTH.NET | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-127-0075-P-02-0 | 4911 | 221122 | UNKNOWN | 11/19/2008 &nbsp;ACT | 04/08/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | A |  | LIVE OAKS POWER PLANT PROPOSED FACILITY WILL OPERATE AS A FULLY DISPATCHABLE ELECTRIC GENERATING FACILITY. THE COMBINED CYCLE SYSTEM WILL UTILIZE TWO COMBUSTION TURBINES AND ONE STEAM TURBINE, CONFIGURED IN A TWO-ON-ONE ARRANGEMENT. THE HEAT CONTENT OF THE EXHAUST GASSES WIL BE RECOVERED BY A HEAT RECOVERY STEAM GENERATOR (HRSG), AND USED TO DRIVE A STEAM TURBINE. DURING PEAK LOADS A DUCT BURNER IN THE HRSG CAN BE FIRED TO AD ADDITIONAL HEAT ENERGY TO THE GAS TURBINE EXHAUST, INCREASING THE PRODUCTION OF STEAM SENT TO THE STEAM TURBINE. THE COMBUSTION TURBINES (CTs) SELECTED ARE SIEMENS MODEL SGT6-5000F. EACH COMBUSTION TURBINE WILL GENERATE 200 MW OF ELECTRIC POWER. THE GROSS ELECTRICAL CAPACITY OF THE COMBINED CYCLE FACILITY FIRING NATURAL GAS WILL THEN BE 600 MW. | PM10 74.3(+) EMISSIONS (T/YR) | COMBINED CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.21 | NATURAL GAS | 600 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DRY LOW NOx BURNERS, SELECTIVE CATALYTIC REDUCTION | 2.5 | PPM@15%02 | 3 HOUR AVERAGE/CONDITION 2.11 | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 87 | T/YR | 12 CONSECUTIVE MONTH AVERAGE/CONDITION 2 | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #1 - combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr | two identical Siemens SGT6-5000F combined cycle turbines without duct firing, each at 2258 mmBtu/hr generating approx. 300 MW each. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low-NOx burners and SCR | 2 | PPM | 30-DAY ROLLING AVG. @15% O2 | BACT-PSD | NSPS | N | 95 | N | 114.5 | TON/YR | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #2 -combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR, Low-NOx burner | 2 | PPM | 30-DAY ROLLING AVERAGE | BACT-PSD | NSPS | U | 95 | U | 114.5 | TON/YR | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N
IL-0112 | NELSON ENERGY CENTER | INVENERGY NELSON, LLC | LEE | IL | 61071-9722 | USA | JOEL SCHROEDER | 312-224-1417 | JSCHROEDER@INVENERGYLLC.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Manish Patel, Permit Analyst Manish.Patel@illinois.gov 217-785-1722 | 98080039 | 4911 | 221112 | 110007399644 | 11/19/2010 &nbsp;ACT | 12/28/2010 &nbsp;ACT | 2013-02-21 | 2020-04-16 | A |  | Natural gas-fired electic power generation facility with two &quot;combined cycle&quot; turbines followed by heat recovery steam generators (HRSG) and the capability for supplemental fuel firing in the HRSG for each turbine using duct burners. NOx emissions will be controlled by SCR and low NOx combustors. | LSP-Nelson Energy started construction pursuant to a permit issued in year 2000 for a facility that was not completed due to financial difficulties, which eventually resulted in LSP-Nelson entering bankruptcy. Substantial construction of foundations and infrastructure for all units and physical installation of one turbine were completed, including construction of HRSGs. | Electric Generation Facility | 15.21 | Natural Gas | 220 | MW each | Two combined cycle combustion turbines followed by HRSGs with capability for supplemental fuel firing in HRSG for each combustion turbine using duct burners. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR and Low-NOx Combustors | 4.5 | PPMVD @ 15% O2 | HOURLY AVG EXCEPT DURING SSM OR TUNING | BACT-PSD | NSPS | U | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | USEPA Method 20 or 7e
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SELECTIVE CATALYTIC REDUCTION AND DRY LOW NOX BURNERS | 2 | PPMVD | 3 HOURS | BACT-PSD |  |  | 90 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LIMIT ONE IS USED WITH 15 % O2 WITH THE USE OF DUCT BURNERS.
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES - START UP/SHUTDOWN CYCLE | 15.21 | NATURAL GAS | 2300 | MMBTU/H | A STARTUP/SHUTDOWN CYCLE IS A PAIR OF SUBSEQUENT SHUTDOWN AND STARTUP EVENTS (I.E., ONE STARTUP FOLLOWED BY ONE SHUTDOWN REPRESENTS ONE STARTUP/SHUTDOWN CYCLE). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 443 | LB | EVENT* | BACT-PSD |  |  | 0 |  | 81.6 | TONS | 12 CONSECUTIVE MONTH PERIOD | 0 |  |  | 0 | 0 | N |  | LIMIT ONE USES THE COLD START EMISSION TOTALS PER CCCT AS A SHORT-TERM LIMIT DURING STARTUP/SHUTDOWN EVENTS. LIMIT TWO IS COMBINED EMISSIONS FROM CCCT1 THROUGH CCCT4 FOR THE DURATION FO THE COMBINED STARTUP/SHUTDOWN EVENTS. *EVENT = ONE STARTUP OR ONE SHUTDOWN
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Combined Cycle Refrigeration Compressor Turbines (8) | 15.21 | natural gas | 286 | MMBTU/H | GE LM2500+G4 | Nitrogen Oxides (NOx) | EPA/OAR Mthd 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | water injection | 22.94 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 20 | PPMV | AT 15% O2 | 0 | 0 | N
LA-0308 | MORGAN CITY POWER PLANT | LOUISIANA ENERGY AND POWER AUTHORITY (LEPA) | ST. MARY | LA | 70380 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-767 | 4911 | 221112 | Not Found | 09/24/2012 &nbsp;ACT | 09/26/2013 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  |  |  | Combustion Turbine with SCR/HRSG | 15.21 | Natural Gas | 607.1 | MMBTU/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction (SCR) and Water/Steam Injection | 11.89 | LB/H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 52.07 | T/YR | ANNUAL MAXIMUM | 5 | PPM@15% O2 | 12 MONTH AVERAGE | 0 | 0 | N |  | BACT Limit: NOx = 0.00022 lb/MMBTU (12 month average)
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1A | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Selective Catalytic Reduction (SCR) with Dry Low NOx Burners (DLNB) during normal operations; Good Combustion Practices during Startup/Shutdown operations. | 26.91 | LB/H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 109.51 | T/YR | ANNUAL MAXIMUM | 15 | PPM@15% O2 | 4-HOUR AVERAGE | 0 | 0 | N |  | BACT Limit = 2.0 PPM@15% O2 (24-hour rolling average)
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1B | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Selective Catalytic Reduction (SCR) with Dry Low NOx Burners (DLNB) during normal operations, and good combustion practices during startup/shutdown operations. | 26.91 | LB/H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 109.51 | T/YR | ANNUAL MAXIMUM | 15 | PPM@15% O2 | 4-HOUR AVERAGE | 0 | 0 | N |  | BACT Limit = 2.0 PPM@15% O2 (24-hour rolling average)
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx Burners, SCR, and Good Combustion Practices | 2.5 | PPMV | 30 DAY ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Units are in ppmv @ 15% O2; Averaging time is 30 Day Rolling Average during Normal Operations.
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES - COLD STARTUP | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | GOOD COMBUSTION PRACTICES, DRY LOW-NOX COMBUSTOR DESIGN AND SELECTIVE CATALYTIC REDUCTION (SCR) | 153 | LB/EVENT | COLD STARTUP | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST. HEAT RATE LIMITED TO 6,793 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR MATTAWOMAN TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS MATTAWOMAN PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | GOOD COMBUSTION PRACTICES, DRY LOW-NOX COMBUSTOR DESIGN AND SELECTIVE CATALYTIC REDUCTION (SCR) | 2 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE (EXCLUDING SU/SD) | BACT-PSD | NSPS |  | 0 |  | 42 | PPM @ 15% O2 | 3-HOUR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | WITH AND WITHOUT DUCT FIRING
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES - WARM STARTUP | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | GOOD COMBUSTION PRACTICES, DRY LOW-NOX COMBUSTOR DESIGN AND SELECTIVE CATALYTIC REDUCTION (SCR) | 132 | LB/EVENT | WARM STARTUP | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES - HOT STARTUP | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | GOOD COMBUSTION PRACTICES, DRY LOW-NOX COMBUSTOR DESIGN AND SELECTIVE CATALYTIC REDUCTION (SCR) | 105 | LB/EVENT | HOT STARTUP | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES - SHUTDOWN | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW-NOX COMBUSTOR DESIGN, GOOD COMBUSTION PRACTICES AND SELECTIVE CATALYTIC REDUCTION (SCR) | 23 | LB/EVENT | SHUT DOWN | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS. HEAT INPUT LIMITED TO 6,802 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR KEYS TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS KEYS PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | GOOD COMBUSTION PRACTICES, DRY LOW-NOX COMBUSTOR DESIGN AND SELECTIVE CATALYTIC REDUCTION | 2 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE, EXCLUDING SU/SD | BACT-PSD | NSPS |  | 0 |  | 42 | PPM @ 15% O2 | 3-HOUR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | WITH AND WITHOUT DUCT FIRING, EXCEPT DURING PERIODS OF STARTUP/SHUTDOWN
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES - COLD STARTUP | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | GOOD COMBUSTION PRACTICES, DRY LOW-NOX COMBUSTOR DESIGN AND SELECTIVE CATALYTIC REDUCTION (SCR) | 245.2 | LB/EVENT | COLD STARTUP | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KEYS IS PROHIBITED FROM OPERATING BOTH CTS IN A CONCURRENT STARTUP MODE AS DEFINED IN CONDITION B-II-4. ADDITIONALLY, THE START-UP OF A SECOND CT SHALL NOT COMMENCE UNTIL THE START-UP OF THE FIRST CT IS COMPLETE.
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES - WARM STARTUP | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | GOOD COMBUSTION PRACTICES, DRY LOW-NOX COMBUSTOR DESIGN AND SELECTIVE CATALYTIC REDUCTION (SCR) | 82.9 | LB/EVENT | WARM STARTUP | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KEYS IS PROHIBITED FROM OPERATING BOTH CTS IN A CONCURRENT STARTUP MODE AS DEFINED IN CONDITION B-II-4. ADDITIONALLY, THE START-UP OF A SECOND CT SHALL NOT COMMENCE UNTIL THE START-UP OF THE FIRST CT IS COMPLETE.
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES - HOT STARTUP | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS.KEYS IS PROHIBITED FROM OPERATING BOTH CTS IN A CONCURRENT STARTUP MODE. ADDITIONALLY, THE START-UP OF A SECOND CT SHALL NOT COMMENCE UNTIL THE START-UP OF THE FIRST CT IS COMPLETE. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | GOOD COMBUSTION PRACTICES, DRY LOW-NOX COMBUSTOR DESIGN AND SELECTIVE CATALYTIC REDUCTION | 71.4 | LB/EVENT | HOT STARTUP | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KEYS IS PROHIBITED FROM OPERATING BOTH CTS IN A CONCURRENT STARTUP MODE AS DEFINED IN CONDITION B-II-4. ADDITIONALLY, THE START-UP OF A SECOND CT SHALL NOT COMMENCE UNTIL THE START-UP OF THE FIRST CT IS COMPLETE.
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES - SHUTDOWN | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW-NOX COMBUSTOR DESIGN, GOOD COMBUSTION PRACTICES AND SELECTIVE CATALYTIC REDUCTION | 60 | LB/EVENT | SHUTDOWN | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0402 | SUMPTER POWER PLANT | WOLVERINE POWER SUPPLY COOPERATIVE INC. | WAYNE | MI | 48111 | USA | BRIAN WARNER | 231-775-5700 | BWARNER@WPSCI.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Julie Brunner at 517-373-7088 or brunnerj1@michigan.gov for questions related to this permit. Thank you. | 81-11 | 4911 | 221112 | 2616305315 | 05/27/2011 &nbsp;ACT | 11/17/2011 &nbsp;ACT | 2012-11-30 | 2016-05-04 | D |  | Utility--Natural gas fired combustion turbine | Other Facility Wide Pollutants not listed below: PM10 = 14.8 tpy PM2.5 = 14.8 tpy CO2e = 232,639 tpy | Combined cycle combustion turbine w/ HRSG | 15.21 | Natural gas | 130 | MW electrical output | This is a combined-cycle combustion turbine with a non-fired heat recovery steam generator (HRSG). Natural gas-fired combustion turbine conversion to combined-cycle. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx burners | 9 | PPM | 24-HR ROLLING AVERAGE | BACT-PSD | NSPS , OTHER | N | 90 | Y | 36.9 | LB/H | 24-HR ROLLING AVERAGE | 0 |  |  | 13733 | 0 | N | 2011 | 2nd ranking option Emission limit 1 above is 9 ppmv dry at 15% oxygen Estimated efficiency (above) is a range of 60%-90%. 'Other' applicable requirement above is NAAQS.
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low NOx (DLN) burner and selective catalytic reduction (SCR) system. | 2 | PPM | EACH CTG; 24-H ROLLING AVG. | BACT-PSD | NSPS , SIP | N | 90 | N | 16.2 | LB/H | EACH CTG; 24-H ROLLING AVG. | 0 |  |  | 0 | 0 | N |  | Emission limit 1 is 2.0 ppmv dry at 15% oxygen for each CTG based on a 24-hour rolling average as determined each hour the turbine operates; except startup/shutdown. Emission limit 2 is 16.2 lb/hr for each CTG based on a 24-hour rolling average as determined each hour the turbine operates; except during startup/shutdown.
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low NOx (DLN) burners and selective catalytic reduction (SCR) system. | 2 | PPM | 24-H ROLLING AVG | BACT-PSD | NSPS , SIP | N | 90 | N | 18 | LB/H | 24-H ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Emission limit 1 is 2.0 ppmv dry at 15% oxygen for each CTG/DB based on a 24-hour rolling average as determined each hour the turbine operates. Emission limit 2 is 18.0 LB/H for each CTG/DB based on a 24-hour rolling average as determined each hour the turbine operates.
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG--Startup/Shutdown | 15.21 | Natural gas | 2237 | MMBTU/H each | Two (2) natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. This entry is for the startup/shutdown operations. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low NOx (DLN) burner and selective catalytic reduction (SCR) | 185.7 | LB/H | HOURLY DURING STARTUP | BACT-PSD | NSPS , SIP | N | 90 | N | 134 | LB/H | HOURLY DURING SHUTDOWN | 0 |  |  | 0 | 0 | N
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry Low NOx burners (DLN) and Selective Catalytic Reduction (SCR) system. | 2 | PPMVOL | 3-H ROLL AVG., EXCEPT STARTUP/SHUTDOWN | BACT-PSD | NSPS , SIP | N | 90 | N | 18.6 | PPH | 24-H ROLL AVG., EXCEPT STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | Emission limit 1 is 2.0 ppmv dry at 15% oxygen. Based upon a 3-hour rolling average as determined each hour the turbine operates; except during startup and shutdown. Emission limit 2 is 18.6 lb/hr based upoon a 24-hour rolling average as determined each hour the turbine operates, except during startup and shutdown.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low NOx burner (DLN) and selective catalytic reduction system (SCR). | 2 | PPMVOL | 3-H ROLL AVG., EXCEPT STARTUP/SHUTDOWN | BACT-PSD | SIP , NSPS | N | 90 | N | 23.7 | PPH | 24-H ROLL AVG., EXCEPT STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | These limits are for the CTGs that operate without the duct burner (DB) on the HRSG. Emission limit 1 is 2.0 ppmv dry at 15% oxygen based upon a 3-hour rolling average as determined each hour the turbine operates except during startup and shutdown. Emission limit 2 is 23.7 lb/hour based upon a 24-hour rolling average as determined each hour the turbine operates.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Startup/Shutdown | 15.21 | Natural gas | 2147 | MMBTU/H | Four natural gas-fired CTGs operating in startup/shutdown mode. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low NOx burners (DLN) and selective catalytic reduction (SCR) system. | 176.9 | PPH | EACH CTG W/O DB; HR LIMIT DURING STARTUP | BACT-PSD | SIP | N | 90 | N | 147.3 | PPH | EACH CTG W/ODB; HR LIMIT DURING SHUTDOWN | 0 |  |  | 0 | 0 | N |  | Emission limit 1 is 176.9 lb/hr; hourly during startup. Emission limit 2 is 147.3 lb/hr; hourly during shutdown.
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners and selective catalytic reduction. | 3 | PPMV | 24-H ROLLING AVERAGE | BACT-PSD | NSPS | N | 0 | N | 760 | LB/H | 1-H AVERAGE | 0 |  |  | 0 | 0 | N |  | *The limits apply to each CTG/HRSG unless otherwise noted. *There are 3 emission limits; 2 are listed here, the 3rd limit (TPY) will be listed in another entry. *The averaging time for the first emission limit listed (3 ppmv) is based on a 24-hour rolling average as determined each hour the turbine operates;/dry at 15% O2; except during startup and shutdown. *The 3 ppmv limit meets NSPS KKKK for each turbine 40 CFR 60.4320(a). *The averaging time for the second emission limit listed (760 LB/H) is based on a 1-hour average. It is applied on a per block basis (each CTG/HRSG pair combined). *LNB + SCR selected based on outlet concentration, not % control efficiency. SCR not functional at low temperatures during startup/shutdown. CEMS monitoring.
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB: 4 nat gas fired CTG with DB for HRSG: Startup/shutdown events | 15.21 | natural gas | 2587 | MMBTU/H design heat input, each | *There are 4 total natural gas fired CTG with DB for HRSG. *They are identified in the permit as either flexible group FGCCA or FGCCB. *Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. *Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners and selective catalytic reduction. | 78.4 | T/YR | 12-MO ROLL TIME PERIOD FOR STARTUP/SHUTD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is 78.4 T/Y based on a 12-month rolling time period FOR startup and shutdown events. It is applied on a per block basis (each CTG/HRSG pair combined). LNB + SCR selected based on outlet concentration, not % control efficiency. SCR not functional at low temperatures during startup/shutdown.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (selective catalytic reduction with dry low NOx burners). | 3 | PPM | 24-H ROLL.AVG. NOT STARTUP/SHUTDOWN | BACT-PSD | SIP , NSPS | N | 95 | N | 8.18 | LB/H | 24-H ROLL.AVG. NOT STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | The emission limits above apply to each CTGHRSG. Emission limit 1 is 3 ppmdv at 15% O2 for each CTGHRSG based on a 24-hour rolling average as determined each operating hour except startup and shutdown. Emission limit 2 is 8.18 lb/hour for each CTGHRSG based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. Startup is defined as the period of time from synchronization to the grid (generator breaker closed) until the unit reaches steady state operation (loads greater than 50 percent of design capacity). Shutdown is defined as that period of time from the initial lowering of the turbine output below 50 percent of full operating load, with the intent to shut down, until the point at which the generator breaker opens.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: Startup &amp; Shutdown | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified seperately for the startup and shutdown periods associated with the process equipment included in FG-CTGHRSG. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (selective catalytic reduction with dry low NOx burners). | 43.7 | LB/H | OPERATING HOUR DURING STARTUP | BACT-PSD | SIP | N | 95 | N | 43.1 | LB/H | OPERATING HOUR DURING SHUTDOWN | 0 |  |  | 0 | 0 | N |  | The limits above apply to each CTGHRSG during startup and shutdown periods. Startup is defined as the period of time from synchronization to the grid (generator breaker closed) until the unit reaches steady state operation (loads greater than 50 percent of design capacity). Shutdown is defined as that period of time from the initial lowering of the turbine output below 50 percent of full operating load, with the intent to shut down, until the point at which the generator breaker opens.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (selective catalytic reduction with dry low NOx burners) | 38.1 | LB/H | 24-H ROLLING AVERAGE | BACT-PSD | NSPS , SIP | N | 80 | N | 286 | LB/H | OPERATING HR DURING STARTUP OR SHUTDOWN | 0 |  |  | 0 | 0 | N |  | There are 4 emission limits (2 in the table above) with are for EACH CTGHRSG. They are as follows: Emission Limit 1 = 3 ppmvd at 15%O2 based on a 24-H rolling avg as determined each operating hour except during startup and shutdown. Emission Limit 2 = 15 ppmvd at 15%O2 based on a 30-day rolling avg as determined each operating day. (NSPS KKKK). Emission Limit 3 = 38.1 LB/H based on a 24-H rolling avg as determined during each operating hour except during startup and shutdown. Emission Limit 4 = 286 LB/H based on an operating hour during startup or shutdown. Startup and shutdown operations are limited to 500 hours per 12-month rolling time period for each CTGHRSG train. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the startup and shutdown emission minimization plan. The efficiency range is 80-90 percent.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective catalytic reduction with dry low NOx burners (SCR with DLNB). | 3 | PPM AT 15% O2 | 24-H ROLLING AVG; EACH EU | BACT-PSD | SIP , NSPS | N | 95 | N | 8.18 | LB/H | 24-H ROLLING AVG; EACH EU | 0 |  |  | 0 | 0 | N |  | The emission limits above are for each emission unit as follows: 1) 3 ppmvd at 15% O2 based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. 2) 8.18 LB/H based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. Startup is defined as the period of time from synchronization to the grid (generator breaker closed) until the unit reaches steady state operation (loads greater than 50 percent of design capacity). Shutdown is defined as that period of time from the initial lowering of the turbine output below 50 percent of full operating load, with the intent to shutdown, until the point at which the generator breaker opens. The efficiency range is 80-99 percent.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG--Startup/Shutdown (2 combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H; EACH | Two combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. This process group is to identify emission limits during startup and shutdown. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective catalytic reduction with dry low NOx burners (SCR with DLNB). | 43.7 | LB/H | OPERATING HOUR DURING STARTUP; EACH EU | BACT-PSD | SIP | N | 95 | N | 43.1 | LB/H | OPERATING HOUR DURING SHUTDOWN; EACH EU | 0 |  |  | 0 | 0 | N |  | The emission limits above are for each emission unit during startup/shutdown. Startup is defined as the period of time from synchronization to the grid (generator breaker closed) until the unit reaches steady state operation (loads greater than 50 percent of design capacity). Shutdown is defined as that period of time from the initial lowering of the turbine output below 50 percent of full operating load, with the intent to shutdown, until the point at which the generator breaker opens. The efficiency range is 80-99 percent.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective catalytic reduction with dry low NOx burners). | 3 | PPM | 24-H ROLL.AVG., EXCEPT STARTUP/SHUTDOWN | BACT-PSD | NSPS , SIP | N | 0 | N | 21.4 | LB/H | 24-H ROLL.AVG., EXCEPT STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | There are 3 separate NOx emission limits which do not include startup/shutdown events. Those will be entered as a separate 'Process' in the RBLC determination. Emission limit 1 above is 3 ppmvd at 15% O2 based on a 24-hour rolling average as determined each operating hour and does not include startup/shutdown. Emission Limit 2 above is 21.4 LB/H based on a 24-hour rolling average as determined each operating hour, except startup/shutdown. There is a third emission limit, which is not above, and is 15 ppm at 15% O2 and is based on a 30-day rolling average as determined each operating day. Table 1 of 40 CFR Part 60 Subpart KKKK allows 96 ppm at 15 percent 02 when the turbines are operating at less than 75 percent of peak load or at temperatures less than 0 deg. F.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Startup/Shutdown) | 15.21 | Natural gas | 1934.7 | MMBTU/H | This emission unit is being entered as a separate process to account for the emission limits associated with startup/shutdown events, which could not be included within the previous EUCCT original process name. A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective catalytic reduction with dry low NOx burners). | 32 | POUNDS | PER EVENT | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 32 pounds per event and applies at each startup or shutdown event. Startup is defined as the period of time from initiation of the combustion process (flame-on) and continues until the unit reaches 50% load. Shutdown is defined as that period of time from the lowering of the turbine output below 50% load, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated.
MI-0431 | INDECK NILES LLC | INDECK NILES LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer Melissa Byrnes at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 75-16A | 4911 | 221112 | Not Found | 06/07/2018 &nbsp;ACT | 06/26/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | A |  | Natural gas combined cycle power plant | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. Also, the permit revises the concentration-based NOx emission limit applied to the two combined-cycle natural gas-fired combustion turbines with heat recovery steam generators (identifed as EUCTGHRSG1 and EUCTGHRSG2) in the original permit 75-16. | FGCTGHRSG (2 Combined Cycle CTG with HRSGs) | 15.21 | Natural gas | 3421 | MMBTU/H | 3421 MMBTU/H for each turbine and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. Two combined-cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSG) (EUCTGHRSG1 & EUCTGHRSG2). The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective Catalytic Reduction with Dry Low NOx Burners) | 2 | PPM | AT 15%O2; 24-HR ROLL AVG | BACT-PSD | NSPS , SIP | N | 80 | N | 38.1 | LB/H | 24-HR ROLL AVG. | 0 |  |  | 0 | 0 | N |  | The concentration-based NOx emission limit above is the only BACT limit changed in PTI 75-16A. All other BACT limits remain as in PTI 75-16 (RBLC ID MI 0423). Emission Limit 1 above is 2 ppmvd at 15% O2 based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. The limit is for EACH CTGHRSG. Emission Limit 2 above is 38.1 lb/hour and is based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. The limit is for EACH CTGHRSG. The permit contains two additional NOx emission limits that apply to EACH CTGHRSG-- 1. 15 ppmvd at 15%O2 based on a 30-day rolling average as determined each operating day. This is per NSPS KKKK. 2. 286 lb/hour for each operating hour during startup or shutdown. This is also a BACT emission limit. Startup and shutdown operations are limited to 500 hours per 12-month rolling time period for each CTGHRSG train. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the startup and shutdown emission minimization plan. The efficiency range is 80-90 percent.
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Good combustion practices, DLN burners and SCR. | 2 | PPMVD | AT 15%O2; EACH INDIV. CT/HRSG TRAIN | BACT-PSD | NSPS , SIP | N | 0 | N | 22.4 | LB/H | EACH INDIV. CT/HRSG TRAIN; 24-H ROLL AVG | 0 |  |  | 0 | 0 | N |  | Each emission limit is per each individual CT/HRSG train in FG-TURB/DB1-3. The emission limits above DO NOT include startup/shutdown. There are 4 NOx emission limits, including an NSPS limit. They are all as follows: Em. Limit 1 = 2.0 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour. Em. Limit 2 = 22.4 lb/h based on a 24-hour rolling average as determined each operating hour. Em Limit 3 = 15 ppmvd at 15%O2 based on a 30-day rolling average as determined each operating day. This limit is per NSPS KKKK. Em Limit 4 = 116 ton/yr based on a 12-month rolling time period as determined at the end of each calendar month.
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3--Startup/Shutdown Operations | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBTU/Hr heat input capacity and a dry low NOx burner. This scenario identifies the emission limits applicable during startup and shutdown operations. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Good combustion practices, DLN burners and SCR. | 249 | LB/H | EACH CT/HRSG TRAIN;STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above is 249 lb/h for each operating hour during startup or shutdown for each individual CT/HRSG train in the flexible group. Startup is defined as the period of time from detection of a flame signal until the unit reaches steady state operation (i.e. loads greater than 50 percent). Shutdown is defined as beginning when the turbine output is lowered to the point that steady state operation can no longer be assured (i.e. loads less than 50 percent), and ending when a flame-off signal is detected.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective catalytic reduction with dry low NOx burners). | 2 | PPMV | AT 15%O2; 24-HR ROLL AVG NOT S.S. | BACT-PSD | NSPS , SIP | N | 80 | N | 29.7 | LB/H | 24-H ROLL AVG NOT S.S. | 0 |  |  | 0 | 0 | N |  | The estimated efficiency of SCR with DLNB is a range of 80-90%. There are 4 NOx emission limits in the permit, as follows: Emission Limit 1 = 2 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour except during startup and shutdown (S.S.). Emission limit 2 - 15 ppmvd at 15%O2 based on a 30-day rolling average as determined each operating day (not including startup and shutdown) per NSPS KKKK. Emission limit 3 = 29.7 LB/H based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. Emission limit 4 = 126.5 LB/H based on each operating hour during startup or shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective catalytic reduction with Dry Low NOx burners). | 2 | PPMVD | AT 15%O2; 24-H ROLL AVG; NOT S.S. | BACT-PSD | NSPS , SIP | N | 80 | N | 29.7 | LB/H | 24-H ROLL AVG; NOT STARTUP/SHUTDOWN (SS) | 0 |  |  | 0 | 0 | N |  | There are 4 NOx emission limits for EUCTGHRSG as follows: Emission limit 1 = 2 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. Emission Limit 2 = 29.7 lb/h based on a 24-hour rolling average as determined each operating hour except during startup and shutdown. Emission Limit 3 = 15 ppmvd at 15%O2 based on a 30-day rolling average as determined each operating day. This limit is from NSPS KKKK. Emission limit 4 = 126.5 lb/h each operating hour during startup or shutdown. Estimated efficiency of SCR with DLNB is a range of 80-90% Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level shall be described in the plan required by Special Condition III.2. Startup and shutdown hours are limited to 300 hours per 12-month rolling time period.
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective catalytic reduction with dry low NOx burners). | 2 | PPMVD | AT 15%O2; 24-H ROLL AVG; EACH UNIT; | BACT-PSD | NSPS , SIP | N | 80 | N | 28.9 | LB/H | 24-H ROLL AVG; EACH UNIT; NOT S.S. | 0 |  |  | 0 | 0 | N |  | There are 4 NOx emission limits in the permit, described below: Emission limit 1 = 2 ppmvd at 15% O2 based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown (S.S.). The limit applies to each unit. Emission limit 2 = 28.90 LB/H based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown (S.S.). The limit applies to each unit. Emission limit 3 = 15 ppmvd at 15% O2 based on a 30-day rolling average as determined each operating day. The limit applies to each unit and is from NSPS KKKK. Emission limit 4 = 262.4 LB/H each operating hour during startup or shutdown (S.S.). The limit applies to each unit. The estimated efficiency of SCR with DLNB is a range of 80-90%. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit.
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2)--Startup &amp; Shutdown | 15.21 | Natural gas | 0 |  | This section is the startup and shutdown emission limits for FGCTGHRSG. Two 3,658 MMBTU/H natural gas-fired combustion turbine generators (CTGs) coupled with heat recovery steam generators (HRSGs). The HRSGs are equipped with natural gas-fired duct burners rated at 800 MMBTU/H to provide heat for additional steam production. The HRSGs are not capable of operating independently from the CTGs. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective catalytic reduction with dry low NOx burners). | 262.4 | LB/H | EACH UNIT; OPERATING HOUR DURING S.S. | BACT-PSD | SIP | N | 80 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is 262.4 LB/H for each unit and is per operating hour during startup or shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit.
MI-0439 | JACKSON GENERATING STATION | CONSUMERS ENERGY COMPANY | JACKSON | MI | 49203-2174 | USA | BRIAN LABBY | 989-667-5008 | BRIAN.LABBY@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, at 517-284-6790 or at byrnesm@michigan.gov, for technical questions regarding this permit. Thank you. | 118-18 | 4911 | 221112 | 110015804511 | 11/29/2018 &nbsp;ACT | 04/02/2019 &nbsp;ACT | 2019-05-20 | 2019-06-19 | C |  | Natural gas combined-cycle power plant |  | FGLMDB1-6 (6 combined cycle natural gas fired CTG each equipped with a HRSG) | 15.21 | natural gas | 420 | MW | FGLMDB1-6 is 6 combined cycle natural gas fired combustion turbine generators (CTG) each equipped with a heat recovery steam generator (HRSG). Nominal rating 420 MW. Each combustion turbine (CT) is a GE LM6000 with a rating of 440 MMBTU/HR (HHV) and a duct burner rating of 222 MMBTU/HR (HHV). A combined cycle natural gas fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 420 MW electricity production. The HRSG is not capable of operating independently from the CTG. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Steam injection, good combustion practices and only combust natural gas. | 25 | PPM | AT 15% O2; 30 DAY ROLLING AVG; EACH UNIT | BACT-PSD | NSPS | N | 0 | U | 22 | PPM | AT 15%O2; 12-MO ROLL AVG; ALL UNITS COMB | 0 |  |  | 0 | 0 | N |  | There are 3 NOx emission limits, two of which are listed in the table above. For clarity, all 3 limits are listed here: Emission limit 1 = 25 ppmv at 15% O2 on a dry gas basis for each unit during periods with no duct firing on a 30-day rolling average as determined at the end of each calendar day. This limit is from NSPS GG and NSPS Db. The limit does not apply during startup and shutdown. Emission limit 2 = 22 ppmv at 15% O2 on a dry gas basis excluding periods for each turbine when it operates in conjunction with its respective duct burner on a 12-month rolling average as determined at the end of each calendar month. This limit is for all units combined and does not apply during periods of startup and shutdown. Emission limit 3 = 54.0 lb/hr (equates to approximately 0.09 lb/MMBTU) when the turbine operates alone and when the turbine operates in conjunction with its respective duct burner on a 30-day rolling average as determined at the end of each calendar day. These limits apply during periods of startup and shutdown. Physical constraints came into BACT decision due to modification to an existing facility.
*MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2019-10-22 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2--A 667 MMBTU/H natural gas fired CTG with a HRSG. | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2 is a nominally rated 667 MMBTU/H natural gas fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas fired duct burner rated at 204 MMBTU/h to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR and oxidation catalyst. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry low NOx burners and selective catalytic reduction for NOx control. | 3 | PPM | PPMVD@15%O2; 24-H AVG; SEE NOTES | BACT-PSD | SIP | N | 0 | U | 25 | PPM | PPMVD@15%O2; 4-H AVG; SEE NOTES | 0 |  |  | 15924 | 0 | N | 2018 | There are 4 NOx emission limits in the permit for this emission unit. Emission limit 1 is 3.0 ppmvd at 15% O2 based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. This limit is when the unit is in combined cycle mode. Emission limit 2 is 25 ppmvd at 15% O2 based on a 4-hour rolling average, except during operation less than 75% peak load. This limit is when the unit is in HRSG bypass mode. Emission limit 3 is 60.0 lb/h when the unit is in combined cycle mode. It is hourly including startup or shutdown. Emission limit 4 is 60.0 lb/h when the unit is in HRSG bypass mode. It is based on a 24-hour rolling average as determined each operating hour. The use of SCR with DLNB is the highest ranked control system and was selected as BACT; therefore, an economic analysis was not performed.
*MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2019-10-22 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1--A 667 MMBTU/H NG fired combustion turbine generator coupled with a heat recovery steam generator (HRSG) | 15.21 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR) and oxidation catalyst. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low NOx burners and selective catalytic reduction for NOx control. | 3 | PPM | PPMVD@15%O2; 24-H ROLL AVG; SEE NOTES | BACT-PSD | SIP | N | 0 | U | 25 | PPM | PPMVD@15%O2; 4-HR ROLL AVG; SEE NOTES | 0 |  |  | 15924 | 0 | N | 2018 | NOx emission limit 1 is 3.0 ppmvd at 15%O2 based on a 24-hour rolling average as determined each operating hour, except during startup and shutdown. The limit applies when the unit is in combined cycle mode. NOx emission limit 2 is 25 ppmvd at 15%O2 based on a 4-hour rolling average, except during operation less than 75% of peak load. The limit applies to the unit in HRSG bypass mode. **There are two additional NOx limits in the permit**************** NOx emission limit 3 is 60.0 lb/h when the unit is in combined cycle mode. The limit is hourly including startup or shutdown. NOx emission limit 4 is 60.0 lb/h when the unit is in HRSG bypass mode. The limit is based on a 24-hour rolling average as determined each operating hour. The use of SCR with the DLNB is the highest ranked control system and was selected as BACT; therefore, an economic analysis was not performed.
*MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2019-12-19 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Good combustion practices, dry low NOx burners and selective catalytic reduction (SCR). | 2 | PPM | EACH; 24-HR ROLL.AVG EXCEPT START/SHUT | BACT-PSD | NSPS | N | 0 | U | 190 | LB/H | EACH; HOURLY INCLUDING STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | There are 3 emission limits within the permit and each limit applies to each unit. Emission Limit 1 = 2 ppmvd based on a 24-hour rolling average as determined each hour, except during startup and shutdown. Table 1 of 40 CFR Part 60 Subpart KKKK allows 96 ppmvd NOx at 15 percent O2 when the turbines are operating at less than 75 percent of peak load, or at temperatures less than 0 deg. F. Emission Limit 2 = 190 lb/hour and applies hourly, including startup or shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the combustion process ends at flame-off. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in special condition (SC) III.2 of the permit. Emission Limit 3 = 15 ppmvd, each unit and is based on a 30-day rolling average, except during operation less than 75 percent of peak load. Does not include startup and shutdown. Table 1 of 40 CFR Part 60 Subpart KKKK allows 96 ppmvd NOx at 15 percent O2 when the turbines are operating at less than 75 percent of peak load, or at temperatures less than 0 deg F. Thomas Township Energy does not consider wet controls, SNCR, XONON, EMxGT or NSCR to be technically feasible for the proposed equipment. Dry Low NOx Combustor Design (DLN) with SCR (80-99% NOx reduction).
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Siemens, without duct burners | 15.21 | Natural Gas | 515600 | MMSCF/rolling 12-months | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process without duct burners. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | selective catalytic reduction (SCR); dry low NOx combustors; lean fuel technology | 22 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 92 | T/YR | PER ROLLING 12-MONTHS | 2 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | testing must be in compliance with 40 CFR 60.4400. BACT: 2.0 ppmvd at 15% O2. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Siemens, with duct burners | 15.21 | Natural Gas | 51560 | MMSCF/rolling 12-MO | Two Siemens 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process with duct burners. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | selective catalytic reduction (SCR); dry low NOx combustors; lean fuel technology | 21 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 92 | T/YR | PER ROLLING 12-MONTHS | 2 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | Testing must be in compliance with 40 CFR 60.4400. BACT: 2.0 ppmvd at 15% O2. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Mitsubishi, without duct burners | 15.21 | Natural Gas | 47917 | MMSCF/rolling 12-MO | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process without duct burners. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | selective catalytic reduction (SCR); dry low NOx combustors; lean fuel technology | 22.6 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 94.8 | T/YR | PER ROLLING 12-MONTHS | 2 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | Testing must be in compliance with 40 CFR 60.4400. BACT: 2.0 ppmvd at 15% O2. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Mitsubishi, with duct burners | 15.21 | Natural Gas | 47917 | MMSCF/rolling 12-MO | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process with duct burners. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | selective catalytic reduction (SCR); dry low NOx combustors; lean fuel technology | 20.8 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 94.8 | T/YR | PER ROLLING 12-MONTHS | 2 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | Testing must be in compliance with 40 CFR 60.4400. BACT: 2.0 ppmvd at 15% O2. T/YR limit is for 2 turbines.
OH-0356 | DUKE ENERGY HANGING ROCK ENERGY | DUKE ENERGY HANGING ROCK, LLC | LAWRENCE | OH | 28207 | USA | ANDREW ROEBEL | 513-287-2356 | ANDREW.ROEBEL@DUKE-ENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110487 | 4911 | 221112 | 110012567203 | 07/17/2012 &nbsp;ACT | 12/18/2012 &nbsp;ACT | 2013-10-01 | 2016-05-04 | C |  | Four Natural Gas Fired Combustion Turbines, with Duct Burners; Combined Cycle, each 172 MW | This is a modification of RBLC OH-0252 to remove operating hour restrictions on duct burners, with changes to hourly limits without increasing the annual emission limitations. Original PTI # was 07-00503 | Turbines (4) (model GE 7FA) Duct Burners Off | 15.21 | NATURAL GAS | 172 | MW | Four GE 7FA combined cycle turbines, dry low NOx burners and selective catalytic reduction. These limits are for each of the 4 turbines individually, while operating with the duct burners off. This permit is a modification to RBLC OH-0252 to remove hourly restrictions on duct burners. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx burners and Selective Catalytic Reduction | 21.1 | LB/H |  | BACT-PSD | NSPS , SIP | U | 0 | Y | 120.9 | T/YR | PER ROLLING 12 MONTHS | 3 | PPM | PPMVD AT 15% O2 ON 3-H BLOCK AVERAGE | 0 | 0 | N |  | Limits are for each individual turbine. Subject to Part 60 Subparts Da and GG. CEMS for NOx and O2.
OH-0356 | DUKE ENERGY HANGING ROCK ENERGY | DUKE ENERGY HANGING ROCK, LLC | LAWRENCE | OH | 28207 | USA | ANDREW ROEBEL | 513-287-2356 | ANDREW.ROEBEL@DUKE-ENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110487 | 4911 | 221112 | 110012567203 | 07/17/2012 &nbsp;ACT | 12/18/2012 &nbsp;ACT | 2013-10-01 | 2016-05-04 | C |  | Four Natural Gas Fired Combustion Turbines, with Duct Burners; Combined Cycle, each 172 MW | This is a modification of RBLC OH-0252 to remove operating hour restrictions on duct burners, with changes to hourly limits without increasing the annual emission limitations. Original PTI # was 07-00503 | Turbines (4) (model GE 7FA) Duct Burners On | 15.21 | NATURAL GAS | 172 | MW | Four GE 7FA combined cycle turbines, dry low NOx burners and selective catalytic reduction. These limits are for each of the 4 turbines individually, while operating with the duct burners on. This permit is a modification to RBLC OH-0252 to remove hourly restrictions on duct burners. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx burners and Selective Catalytic Reduction | 27.6 | LB/H |  | BACT-PSD | NSPS , SIP | U | 0 | Y | 120.9 | T/YR | PER ROLLING 12 MONTHS | 3 | PPM | PPMVD AT 15% O2 ON 3-H BLOCK AVERAGE | 0 | 0 | N |  | Limits are for each individual turbine. Subject to Part 60 Subparts Da and GG. CEMS for NOx and O2.
OH-0360 | CARROLL COUNTY ENERGY | CARROLL COUNTY ENERGY | CARROLL | OH | 44615 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0113762 | 4911 | 221112 | 110064671127 | 04/11/2013 &nbsp;ACT | 11/05/2013 &nbsp;ACT | 2015-12-30 | 2019-04-01 | A |  | Natural gas fired combined cycle gas turbine electric generating station of nominal capacity of 742 MW | Installation of a natural gas-fired combined cycle combustion turbine electric utility power plant, nominally rated at 742 MW. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural Gas | 2045 | MMBTU/H | Two identical General Electric 7FA combined cycle combustion turbine (each at 2,045 mmBtu/hr heat input turbine at ISO conditions and 566 mmBtu/hr heat input duct burner, HHV) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. All throughputs and emission limits are for each turbine. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | selective catalytic reduction (SCR) and dry low NOx combustors | 20.5 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 103.2 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME AT 15% O2 | 0 | 0 | N |  | Limits are for each turbine. 20.5 lb/h with ductburner and 16.3 lb/h turbine only (except startup and shutdown). 103.2 t/yr per rolling 12 month period including startup and shutdown. 116.6 lb/h for cold startup, 124.1 lb/h for hot startup, 115.3 lb/h for warm startup and 76.8 lb/h for shutdown. Pound per hour emissions rates as presented are averaged over the duration of the event where (for the lead/lag turbine) the duration of a cold start is 245/220 minutes, the duration of a warm start is 140/115 minutes, the duration of a hot start is 83/58 minutes, and the duration of a shutdown is less than 1 hour. Emissions reflect the higher of the lead or lag turbine, on a pollutant-specific basis.
OH-0363 | NTE OHIO, LLC |  | BUTLER | OH | 45044 | USA | MICHAEL SCHUSTER | (904)436-6896 | MSCHUSTER@NTEENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0116610 | 4911 | 221112 | 110070379584 | 04/07/2014 &nbsp;ACT | 11/05/2014 &nbsp;ACT | 2019-02-22 | 2019-04-01 | A |  | Combined-cycle, natural gas-fired power plant | Initial installation of either one (1) Mitsubishi Hitachi Power Systems Americas M501JAC or one (1) Mitsubishi Hitachi Power Systems Americas M501GAC single power block in a 1x1 combined-cycle multi-shaft configuration, including a combustion turbine and heat recovery steam generator with duct burners and a steam turbine to be known as the Middletown Energy Center. | Turbine generator with HRSG and duct burners (P001) | 15.21 | Natural gas | 3278.5 | MMBTU/H | Combined-cycle combustion turbine generator (CTG) with heat recovery steam generator (HRSG), natural gas-fired, including duct burners (DB). Permit was for either Mitsubishi Hitachi Power Systems America M501GAC or M501JAC. The M501GAC was installed. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Use of natural gas, low NOx burner, and selective catalytic reduction (SCR). | 27.7 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 88.4 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen. 27.7 lb/h with duct burner, except startup and shutdown. 21.8 lb/h turbine only, except startup and shutdown. 88.4 tons per rolling 12 month period for all operating modes, including startup. 58.3 lb/h during cold startup, 32.0 lb/h during hot startup, 46.2 lb/h during warm startup, and 28.0 lb/h during shutdown. Pound per hour emissions rates as presented are averaged over the duration of the event where the duration of a cold start is 142.5 minutes, the duration of a warm start is 103 minutes, and it has been assumed that the CTs are at their respective maximum potential emission rates (100% load) for the balance of the averaging period that they are not in start-up or shutdown mode. The duration of a hot start is 22.8 minutes, and the duration of a shutdown is 12.5 minutes.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 1 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2022 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry-low NOx (DLN) burner and selective catalytic reduction (SCR) | 14.7 | LB/H | WITHOUT DUCT BURNERS. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 435.3 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | Limits are for single turbine except as noted. 2.0 ppm by volume, dry basis (ppmvd) at 15% oxygen, 3-hour average, with and without duct burners. 14.7 lb/h, 3-hour average, turbine only without duct burners. 18.68 3.1 lb/h, 3-hour average, turbine with duct burners. 324 lb/cold startup, 192 lb/hot startup, 257 lb/warm startup and 82 lb/shutdown. 635.30 t/yr per rolling 12 month period total for all 4 turbines.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 2 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2144 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry-low NOx (DLN) burner and selective catalytic reduction (SCR) | 15.6 | LB/H | WITHOUT DUCT BURNERS. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 449.31 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | Limits are for single turbine except as noted. 2.0 ppm by volume, dry basis (ppmvd) at 15% oxygen, 3-hour average, with and without duct burners. 15.6 lb/h, 3-hour average, turbine only without duct burners. 19.60 3.1 lb/h, 3-hour average, turbine with duct burners. 324 lb/cold startup, 192 lb/hot startup, 257 lb/warm startup and 82 lb/shutdown. 449.31 t/yr per rolling 12 month period total for all 4 turbines.
OH-0366 | CLEAN ENERGY FUTURE - LORDSTOWN, LLC | CLEAN ENERGY FUTURE - LORDSTOWN, LLC | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0117655 | 4911 | 221112 | 110070396317 | 09/17/2014 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2019-02-27 | 2019-06-19 | A |  | 962 MW (gross winter output) combined cycle gas turbine (CCGT) facility | Initial installation permit for the construction of the Lordstown Energy Center - a nominal 940 MW combined cycle gas turbine (CCGT) facility. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 2725 | MMBTU/H | Combined cycle combustion turbine (2,725 MMBtu/hr heat input turbine at ISO conditions and 179 MMBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Limits and throughputs are for single turbine. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry low NOx combustors, selective catalytic reduction (SCR) | 23.5 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 107.2 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen. 23.5 lb/h with duct burner (except startup and shutdown). 22.3 lb/h without duct burner (except startup and shutdown). 107.2 t/yr per rolling 12 month period for all operating modes, including startup. 162.1 lb/h during cold startup, 78.7 lb/h during hot startup, 112.8 lb/h during warm startup, and 57.3 lb/h during shutdown.
OH-0367 | SOUTH FIELD ENERGY LLC | SOUTH FIELD ENERGY LLC | COLUMBIANA | OH | 43968 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0119495 | 4911 | 221112 | Not Found | 09/14/2015 &nbsp;ACT | 09/23/2016 &nbsp;ACT | 2019-02-28 | 2019-06-19 | A |  | 1150 MW combined-cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the South Field Energy facility, a nominal 1,150 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in Wellsville, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3131 | MMBTU/H | Two identical combined cycle combustion turbine (3,131 MMBtu/hr heat input turbine at ISO conditions, natural gas firing with evaporative cooler on and 800 MMBtu/hr maximum heat input natural gas-fired duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), catalytic oxidizer, and wet injection for ULSD firing. Heat input for ULSD firing at ISO conditions, with evaporative cooler on is 3,173 MMBtu/hr. Throughputs and limits are for single turbine except as noted. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry low NOx (DLN) burners for natural gas firing, wet injection when firing ultra low sulfur diesel, and selective catalytic reduction (SCR) for both natural gas and ultra low sulfur diesel. | 30.51 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 151.3 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen, hourly average, natural gas, with and without duct burner. 5.0 ppm by volume dry basis (ppmvd) at 15% oxygen, hourly average, ultra low sulfur diesel. 30.51 lb/h with duct burner (except startup and shutdown). 24.92 lb/h without duct burner (except startup and shutdown). 66.32 lb/h for ultra low sulfur diesel (except startup and shutdown). 151.3 t/yr per rolling 12 month period for all operating modes, including startup and shutdown. When firing natural gas, 231.4 lb/h during startup and 26.5 lb/h during shutdown. When firing ultra low sulfur diesel, 181.3 lb/h during startup and 85.4 lb/h during shutdown.
OH-0370 | TRUMBULL ENERGY CENTER | TRUMBULL ENERGY CENTER | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122331 | 4911 | 221112 | Not Found | 03/23/2017 &nbsp;ACT | 09/07/2017 &nbsp;ACT | 2019-03-05 | 2019-06-19 | A |  | 940 MW combined cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the Trumbull Energy Center, a nominal 940 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in the Village of Lordstown, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3025 | MMBTU/H | Two identical combined cycle combustion turbine (3,025 mmBtu/hr heat input turbine at ISO conditions and 237 mmBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Throughputs and limits are for single turbine except as noted. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | dry low NOx combustors (DLN) and selective catalytic reduction (SCR) | 25.3 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 117.6 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen, 25.3 lb/h with duct burner, 23.8 lb/h without duct burner (each limit except startup and shutdown). 117.6 t/yr per rolling 12 month period for all operating modes, including startup and shutdown. 162.0 lb/h during cold startup, 78.7 lb/h during hot startup, 113.0 lb/h during warm startup, and 72.7 lb/h during shutdown.
OH-0372 | OREGON ENERGY CENTER | OREGON ENERGY CENTER | LUCAS | OH | 43616 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0121049 | 4911 | 221112 | Not Found | 06/27/2016 &nbsp;ACT | 09/27/2017 &nbsp;ACT | 2019-03-06 | 2019-06-19 | A |  | Combined cycle gas turbine (CCGT) facility | Installation of natural gas-fired combined cycle combustion turbine power plant. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3055 | MMBTU/H | Combined cycle combustion turbine (3,055 mmBtu/hr heat input turbine at ISO conditions and 221.3 mmBtu/hr heat input duct burner) with dry low NOX combustors, selective catalytic reduction (SCR), and catalytic oxidation. All heat values are on a HHV basis. Throughputs and limits are for single turbine except as noted. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry low NOX combustors and selective catalytic reduction (SCR) | 25.3 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 118.02 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen. 25.3 lb/h with duct burner (except startup and shutdown). 23.8 lb/h without duct burner (except startup and shutdown). 118.02 t/yr per rolling 12 month period for all operating modes, including startup. 162 lb/h during cold startup, 78.7 lb/h during hot startup, 113 lb/h during warm startup, and 57.3 lb/h during shutdown.
OH-0374 | GUERNSEY POWER STATION LLC | GUERNSEY POWER STATION LLC | GUERNSEY | OH | 43723 | USA | MARY KING | (317)447-4513 | MARY@APEXPOWERGROUP.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122594 | 4911 | 221112 | 110070379546 | 04/14/2017 &nbsp;ACT | 10/23/2017 &nbsp;ACT | 2019-03-08 | 2019-06-19 | A |  | 1,650 MW combined cycle combustion turbine electrical generating facility | Installation PTI for a new 1,650 MW combined cycle natural-gas fired turbine plant and associated auxiliary boiler, firewater pumps, emergency generators and fuel gas heaters | Combined Cycle Combustion Turbines (3, identical) (P001 to P003) | 15.21 | Natural gas | 3516 | MMBTU/H | Three identical Combustion Turbines; GE 7HA.02 natural gas-fired lean pre-mix combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,516 MMBtu/hr HHV at 100% load and -18Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 997 MMBtu/hr HHV controlled with catalytic oxidation and selective catalytic reduction (SCR) and cooled with an air-cooled condenser (ACC) used to generate electricity. Throughputs and limits are for a single turbine except as noted. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry low NOx burners and SCR | 33.85 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 26.37 | LB/H | WITHOUT DUCT BURNERS. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | Limits are for single turbine except as noted. 2.0 ppm by volume, dry basis (ppmvd) at 15% oxygen turbine with duct burners and turbine only, both excluding startup and shutdown. 26.37 lb/h without duct burners. 33.85 lb/h with duct burners. Both excluding startup and shutdown 266.7 lb/cold startup, 140.7 lb/hot startup, 88.4 lb/warm startup and 32.7 lb/shutdown. 422.19 t/yr per rolling 12 month period total for all 3 turbines.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | General Electric Combustion Turbine (P004) | 15.21 | Natural gas | 3544 | MMBTU/H | General Electric model 7HA.02 natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,544 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry low NOx burners and an SCR system | 26.1 | LB/H | EXCEPT STARTUP AND SHUTDOWN. SEE NOTES | BACT-PSD | NSPS | U | 0 | U | 125.8 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppmvd at 15% oxygen (O2) and 26.1 pounds per hour, excluding periods of startup and shutdown. 125.8 tons of NOx per rolling, 12-month period, including start-up and shutdown emissions. 164.5 lb/h during cold startup, 109.7 lb/h during hot startup, 87.4 lb/h during warm startup, and 27.9 lb/h during shutdown.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Mitsubishi Combustion Turbine (P005) | 15.21 | Natural gas | 3320 | MMBTU/H | Mitsubishi Model 501JAC natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,320 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 108 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry low NOx burners and an SCR system | 25.1 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 119.4 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen. 25.10 lb/h with duct burner (except startup and shutdown). 26.4 lb/h without duct burner (except startup and shutdown). 119.4 t/yr per rolling 12 month period for all operating modes, including startup. 68.1 lb/h during cold startup, 55.4 lb/h during warm startup, 34.6 lb/h during hot startup, and 37.9 lb/h during shutdown.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Siemens Combustion Turbine (P006) | 15.21 | Natural gas | 3602 | MMBTU/H | Siemens Model SCC6-8000H natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,602 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 667 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry low NOx burners and an SCR system | 27.1 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 128.8 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen. 27.10 lb/h with duct burner (except startup and shutdown). 22.4 lb/h without duct burner (except startup and shutdown). 128.8 t/yr per rolling 12 month period for all operating modes, including startup. 72.7 lb/h during cold startup, 87.1 lb/h during warm startup, 77.7 lb/h during hot startup, and 44.8 lb/h during shutdown.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry low NOx burners and an SCR system | 29.5 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 139 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen on a 24-hr block averaging period. 29.5 lb/h with duct burner, except startup and shutdown. 25.1 lb/h without duct burner, except startup and shutdown. 139 tons per rolling 12 month period for all operating modes, including startup and shutdown. 12.99 tons per rolling 12 month period for startup and shutdown periods.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry low NOx burners and an SCR system | 28 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 124 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen on a 24-hr block averaging period. 28 lb/h with duct burner, except startup and shutdown. 26.7 lb/h without duct burner, except startup and shutdown. 124.0 tons per rolling 12 month period for all operating modes, including startup and shutdown. 3.22 tons per rolling 12 month period for startup and shutdown periods.
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | Combustion Turbine | 15.21 | Natural Gas | 360 | MW | This process represents the GE option for the project - One GE 7FA.05 natural gas-fired combustion turbine generator with an 820.5 MMBTUH duct burner. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low-NOx burners with SCR. | 2 | PPMVD@15% O2 | ONE-HR | BACT-PSD | NSPS | U | 0 | U | 23 | LB/HR | ONE-HR | 0 |  |  | 0 | 0 | N
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | COMBUSTION TURBINE | 15.21 | NATURAL GAS | 360 | MW | This process represents the Siemens option for the project - One Siemens SGT6-5000F5 natural gas-fired combustion turbine generator with an 820.3 MMBTUH duct burner. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW-NOx BURNER WITH SCR. | 2 | PPMVD@15% O2 | ONE-HR | BACT-PSD | NSPS | U | 0 | U | 23.8 | LB/HR | ONE-HR | 0 |  |  | 0 | 0 | N
OR-0048 | CARTY PLANT | PORTLAND GENERAL ELECTRIC | MORROW | OR |  | USA |  | 5034648519 | RAY.HENDRICKS@PGN.COM | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us |  | 25-0016-ST-02 | 4911 | 221112 | N/A | 12/24/2009 &nbsp;ACT | 12/29/2010 &nbsp;ACT | 2011-04-15 | 2011-08-30 | A |  | COMBINED CYCLE NATURAL GAS-FIRED ELECTRIC GENERATING UNIT PSD PERMIT | PSD PERMIT | COMBINED CYCLE NATURAL GAS-FIRED ELECTRIC GENERATING UNIT | 15.21 | NATURAL GAS | 2866 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SELECTIVE CATALYTIC REDUCTION (SCR) | 2 | PPM@15%O2 | 3-HOUR ROLLING | BACT-PSD | NSPS |  | 98 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
PA-0278 | MOXIE LIBERTY LLC/ASYLUM POWER PL T | MOXIE ENERGY LLC | BRADFORD COUNTY | PA |  | USA | KENT J MORTON | (571) 594 - 0150 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MUHAMMAD Q. ZAMAN, ENVIRONMENTAL PROGRAM MANAGER, NORTHCENTRAL REGION | 08Â·00045A | 491 | 221112 | 45-2015223-1 | 09/26/2011 &nbsp;ACT | 10/10/2012 &nbsp;ACT | 2012-12-03 | 2015-04-03 | A |  |  | The project consists of two identical 1 x 1 power blocks, and each block includes a combustion gas turbine and a steam turbine. Each combined-cycle process will also include a heat recovery steam generator and supplemental duct burners. Additionally, one diesel-fired emergency generator, one diesel-fired fire water pump, two diesel fuel storage tanks, two lube oil storage tanks, and one aqueous ammonia storage tank were proposed to be constructed and operated. Each combined-cycle process will be rated at 468 MW or less. | Combined-cycle Turbines (2) - Natural gas fired | 15.21 | Natural Gas | 3277 | MMBTU/H | Two combine cycle Turbines, each with a combustion turbine and heat recovery steam generator with duct burner. Each combined-cycle process will be rated at 468 MW or less. The heat input rating of each combustion gas turbine is 2890 MMBtu/hr (HHV) or less, and the heat input rating of each supplemental duct burner is equal to 387 MMBtu/hr (HHV) or less. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low-NOx (DLN) combustor and selective catalytic reduction (SCR) | 2 | PPMVD |  | BACT-PSD |  | U | 90 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Moxi LIberty will install CEMS to demonstrate compliance.
PA-0286 | MOXIE ENERGY LLC/PATRIOT GENERATION PLT | MOXIE ENERGY LLC | LYCOMING COUNTY | PA |  | USA | KENT MORTON | (571) 594 - 0150 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MUHAMMAD Q. ZAMAN, ENVIRONMENTAL PROGRAM MANAGER NORTHCENTRAL REGION 208 West Third St, Suite 101 Williamsport, PA 17701 570-327-3648 | 41-00084A | 4911 | 221112 | 110057116124 | 07/18/2012 &nbsp;ACT | 01/31/2013 &nbsp;ACT | 2013-03-27 | 2020-03-02 | A |  | This plan approval is for the construction of two natural-gas-fired combined cycle powerblocks where each powerblock consists of a combustion turbine and heat recovery steam generator with duct burner. The two powerblocks constructed pursuant to this plan approval will be either the two powerblocks rated 472 megawatts (MW) (P101 and P102) or the powerblocks rated 458 MW (P103 and P104). Additionally, this plan approval is for the construction of a 1464 bhp diesel-fired emergency generator, 460 bhp dieselfired fire pump, 1600 gallon diesel tank, 300 gallon diesel tank, two 15,000 gallon (each) lube oil tanks and ancillary electrical equipment. |  | Combined Cycle Power Blocks 472 MW - (2) | 15.21 | Natural Gas | 0 |  | Two natural-gas-fired combined cycle powerblocks where each powerblock consists of a combustion turbine and heat recovery steam generator with duct burner. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 2 | PPMDV |  | BACT-PSD | OTHER | U | 0 | U | 111.2 | T/YR | EACH UNIT | 0 |  |  | 0 | 0 | N
PA-0296 | BERKS HOLLOW ENERGY ASSOC LLC/ONTELAUNEE | BERKS HOLLOW ENERGY ASSOC LLC | BERKS | PA | 19605 | USA | BRADLEY J COOLEY | 636-534-3268 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | WILLIAM R. WEAVER, SOUTHCENTRAL REGION AIR PROGRAM MANAGER 909 Elmerton Ave, Harrisburg, PA 17701 717-705-4868 | 06-05150A | 4931 | 221112 | 110056155342 | 05/08/2012 &nbsp;ACT | 12/17/2013 &nbsp;ACT | 2014-04-17 | 2020-03-02 | A |  | This application is for the construction of a natural gas-fired combined-cycle electric generation facility that is designed to generate up to 855 MW nominal, using 2 combustion turbine generators and 2 heat recovery steam generators that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. | This application is for the construction of a natural gas-fired combined-cycle electric generation facility that is designed to generate up to 855 MW nominal, using 2 combustion turbine generators and 2 heat recovery steam generators that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. | Turbine, Combined Cycle, #1 and #2 | 15.21 | Natural Gas | 3046 | MMBTU/H | Equipped with SCR and Oxidation Catalyst | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 131.6 | TPY | 12-MONTH ROLLING TOTAL | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0298 | FUTURE POWER PA/GOOD SPRINGS NGCC FACILITY | FUTURE POWER PA INC | SCHUYLKILL | PA | 17980 | USA | JAMES PALUMBO | 570-342-5200 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MARK J. WEJKSZNER NORTHEAST REGION AIR PROGRAM MANAGER 2 Public Square Wilkes-Barre, PA 18711 570-826-2357 | 54-00082A | 4911 | 221112 | 110062854870 | 05/03/2013 &nbsp;ACT | 03/04/2014 &nbsp;ACT | 2014-04-17 | 2020-02-19 | A |  | Natural gas-fired combined-cycle electric generation facility that is designed to generate up to 346 MW nominal, using a combustion turbine generator and a heat recovery steam generator that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. The Turbine is rated at 2,267 MMBTU/hr HHV (2,042 MMBTU/hr LHV). The Duct burner is rated at 134.3 MMBTU/hr HHV (120 MMBTU/hr LHV). The proposed project will also include a diesel engine-driven emergency generator; a diesel engine-driven firewater pump; a multi-cell evaporative cooling tower; and associated emission control systems, tanks, and other plant equipment. |  | Turbine, COMBINED CYCLE UNIT (Siemens 5000) | 15.21 | Natural Gas | 2267 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 2 | PPMVD | @ 15% OXYGEN | BACT-PSD | NSPS | U | 0 | U | 19.6 | LB/H | WITH DUCT BURNER | 79.9 | TPY | BASED ON A 12-MONTH ROLLING TOTAL | 0 | 0 | N
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Natural Gas-Fired Combustion Turbine with HRSG | 15.21 | Natural Gas | 1339 | MMBtu/hr | Turbine throughput is 1019.7 MMBtu/hr when burning natural gas and 1083.7 MMBtu/hr when burning No. 2 oil. Duct burner throughput is 319.3 MMBtu/hr. Duct burner firing will occur during natural gas combustion only. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Good combustion design and practices, selective catalytic reduction (SCR) | 2 | PPMVD @ 15% O2 | 30 UNIT-OPERATING-DAY MOVING AVERAGE | BACT-PSD | NSPS | N | 90 | U | 8 | PPMVD @ 15% O2 | 15 UNIT-OPERATING-DAY MOVING AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission limit #1 is for natural gas combustion, emission limit #2 is for No. 2 oil combustion.
*TN-0164 | TVA - JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134 | USA | JACK BYARS | (423) 751-2666 | JGBYARS@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov |  | 972969 | 4911 | 221112 | 110070502905 | 09/26/2017 &nbsp;ACT | 02/01/2018 &nbsp;ACT | 2019-03-21 | 2019-03-21 | D |  | Combustion turbines and combined cycle plant | Permit 972969 adds startup and shutdown limits to the requirements established in PSD permit 970816F. | Dual-fuel CT and HRSG with duct burner | 15.21 | Natural Gas | 1020 | MMBtu/hr | Rated input capacity is 1020 MMBtu/hr (CT) and 319 MMBtu/hr (duct burner) when burning natural gas and 1084 MMBtu/hr when burning #2 oil. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR, good combustion design & practices | 2 | PPMVD @ 15% O2 | 30-DAY AVG WHEN BURNING NATURAL GAS | BACT-PSD | NSPS | N | 0 | U | 8 | PPMVD @ 15% O2 | 30-DAY AVG WHEN BURNING #2 OIL | 0 |  |  | 0 | 0 | N |  | BACT limits exclude startup and shutdown. NSPS KKKK limits apply to NOX emissions during startup and shutdown
TX-0600 | THOMAS C. FERGUSON POWER PLANT | LOWER COLORADO RIVER AUTHORITY | LLANO | TX | 7657 | USA | JOE BENTLEY | 512-473-3272 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tan Nguyen 512-239-3445 tan.nguyen@tceq.texas.gov | PSDTX1244 & 93938 | 4911 | 221112 | 110035336222 | 07/27/2011 &nbsp;ACT | 09/01/2011 &nbsp;ACT | 2011-09-02 | 2020-02-03 | B |  | Power Plant. Two natural gas-fired combined cycle turbine generators (GE 7FA) with unfired HRSG | 93938 | Natural gas-fired turbines | 15.21 | natural gas | 390 | MW | (2) GE7FA at 195 MW each, (1) steam turbine at 200 MW. Each turbine is equipped with an unfired heat recovery steam generator (HRSG), which provides steam for the steam turbine. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low NOx burners and Selective Catalytic Reduction | 2 | PPMVD | ROLLING 24-HR AT 15% OXYGEN | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0620 | ES JOSLIN POWER PLANT | CALHOUN PORT AUTHORITY | CALHOUN | TX |  | USA | CHARLES HAUSMANN | 361-987-2813 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1256, 96336 | 4911 | 221112 | 110001866641 | 05/31/2012 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2012-11-14 | 2020-02-03 | B |  | Three gas-fired combined cycle turbine generators, including a steam turbine generator, to replace the existing steam boiler/turbine generator. | 96336 | Combined cycle gas turbine | 15.21 | natural gas | 195 | MW | The three combustion turbine generators (CTG) will be the General Electric 7FA, each with a maximum base-load electric power output of approximately 195 megawatts (MW). The steam turbine is rated at approximately 235 MW. This project also includes the installation of two emergency generators, one fire water pump, and auxiliary equipment. No duct burners. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective catalytic reduction | 2 | PPMVD | @15% O2, 24-HR ROLLING AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 | 221122 | Not Found | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2019-03-06 | A |  | Combinec Cycle Electric Generating Plant | 103839 | combined cycle turbine | 15.21 | natural gas | 700 | MW | The generating equipment consists of two natural gas-fired combustion turbines (CTs), each exhausting to a fired heat recovery steam generator (HRSG) to produce steam to drive a shared steam turbine generator. The steam turbine is rated at 271 MW of electric output. Three models of combustion turbines are being considered for this site: the General Electric 7FA.05, the Siemens SGT6-5000F(4), and the Siemens SGT6-5000F(5). The final selection of the combustion turbine will not be made until after the permit is issued. Plant output will range between 637 and 735 MW, depending on the model turbine selected. Duct Burners are rated at 750 MMBtu/hr each. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | selective catalytic reduction | 2 | PPMVD | 24-HR ROLLING AVG, 15% OXYGEN | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0660 | FGE TEXAS POWER I AND FGE TEXAS POWER II | FGE POWER LLC | MITCHELL | TX | 79565 | USA | EMERSON FARRELL | 281-362-2830 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX1364 & 110025 | 3511 | 221112 | NOT FOUND | 10/23/2013 &nbsp;ACT | 03/24/2014 &nbsp;ACT | 2014-06-13 | 2020-03-05 | U |  | Electric Generating Utility | TCEQ Permit No. 110025 | Alstom Turbine | 15.21 | Natural Gas | 230.7 | MW | Four (4) Alstom GT24 CTGs, each with a HRSG and DBs, max design capacity 409 MMBtu/hr | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective catalytic reduction | 2 | PPMVD | CORRECTED TO 15% O2, ROLLING 24 HR AVE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057188626 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.21 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (6) GE LM2500+ DLE turbines that drive the ethylene section compressors with waste heat recovery for amine solution regeneration. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low emission combustors | 25 | PPMVD | @15% O2, 4 HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Combustion Turbine | 15.21 | natural gas | 87 | MW | The exhaust heat from the turbine will be used to heat a heating medium which is used to regenerate rich amine from the acid gas removal system. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 2 | PPMVD | 15@ O2, 3 HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The turbine is fuelad by what is technically natural gas but contains enough nitrogen to affect the Wobbe Index of the turbine fuel gas compared to typical pipeline gas.
TX-0689 | CEDAR BAYOU ELECTRIC GENERATION STATION | NRG TEXAS POWER | CHAMBERS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 105810, PSDTX1308 | 4911 | 221112 | 110015743301 | 09/12/2012 &nbsp;ACT | 08/29/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power gereration station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the combined cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The new units will produce between 215-263 MW each. |  | Combined cycle natural gas turbines | 15.21 | Natural Gas | 225 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DLN, SCR | 2 | PPM | 24HR ROLLING AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0698 | BAYPORT COMPLEX | AIR LIQUIDE LARGE INDUSTRIES U.S., L.P. | HARRIS | TX |  | USA | JASON MILLER | (281) 474-8243 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 | 9346 PSDTX612M2 | 4931 | 325120 | 110000462758 | 07/27/2012 &nbsp;ACT | 09/05/2013 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | Air Liquid currently operates a cogeneration facility in Pasadena, Texas (Bayou Cogeneration Plant). The permit amendment submitted by Air Liquide will authorize a redevelopment project of its cogeneration plant. The proposed project will involve the replacement of four existing gas-fired turbines (GE 7EA) with similar gas-fired turbines (GE 7EA), the addition of three new gas-fired boilers rated at 550 MMBtu/hr and the removal of three existing gas-fired boilers rated at 443 MMBtu/hr. |  | (4) cogeneration turbines | 15.21 | natural gas | 90 | MW | (4) GE 7EA turbines providing power and process steam | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN and Closed Loop Emissions Controls (CLEC) | 5 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | (2) combined cycle turbines | 15.21 | natural gas | 650 | MW | The specific equipment includes two combustion turbines (CTs) connected to electric generators, producing between 183 and 232 MW of electricity, depending on ambient temperature and the selected CT. The two HRSGs use duct burners rated at 750 MMBtu/hr each to supplement the heat energy from the CTs. The steam from the two HRSGs is combined and routed to a single steam turbine driving a third electric generator with an electricity output capacity of 271 MW. Depending on the selected CT, total plant output at 59Â°F is between 637 MW and 735 MW. The applicant is considering three models of CT; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) Siemens SGT6-5000F(4); or (3) Siemens SGT6-5000F(5). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 2 | PPMVD | @15% O2, 24-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0709 | SAND HILL ENERGY CENTER | CITY OF AUSTIN | TRAVIS | TX |  | USA | JOSEPH RAVI | (512) 322-6284 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez (512) 239-5220 Ruth.alvirez@tceq.texas.gov | 48106, PSDTX1012M2 | 4911 | 221112 | 110008975804 | 03/20/2015 &nbsp;ACT | 09/13/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | GE 7FA Natural Gas-fired Combined Cycle Turbine with DB fired HRSG |  | Natural gas-fired combined cycle turbines | 15.21 | Natural Gas | 173.9 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 2 | PPM | 24HR ROLLING AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0710 | VICTORIA POWER STATION | VICTORIA WLE L.P. | VICTORIA | TX |  | USA | GARY CLARK | (361) 947-9934 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | 108258 PSDTX1348 | 4911 | 221112 | 110000501154 | 02/14/2013 &nbsp;ACT | 12/01/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | The facility is currently authorized under Standard Permit No. 80878 and several Permits by Rule (PBR), including Â§106.263 for maintenance, startup, and shutdown (MSS) (PBR Registration No. 94387) and Title V Permit No. O-35. Victoria proposes to install an additional natural gas-fired turbine (GT) and HRSG with duct burners at the Victoria Station. The resulting new facility will be a combined cycle generating facility in a 2x2x1 configuration (two combustion turbines, two HRSGs with duct burners, and one steam turbine). |  | combined cycle turbine | 15.21 | natural gas | 197 | MW | General Electric 7FA.04 at 197 MW nominal ouput. The duct burners will be capable of a maximum natural gas firing rate of up to 483 MMBtu/hr (HHV). The duct burners may be fired additional hours; however, total annual firing will not exceed the equivalent of 4,375 hours at maximum capacity per duct burner. The available capacity of the existing steam turbine will be increased from 125 MW in its existing 1x1x1 configuration to approximately 185 MW in the 2x2x1 configuration. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 2 | PPMVD | @15% O2, 24-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 3.5 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | 0 |  |  | 0 | 0 | N
TX-0712 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER COMPANY | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | (205) 257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tzvi Shalem 512-239-1310 tzvi.shalem@tceq.texas.gov | 111393 PSDTX1368 | 4911 | 221112 | 110007199735 | 06/27/2013 &nbsp;ACT | 11/20/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | Southern Power Company (SPC) is proposing to construct an electric generating facility near Trinidad, Henderson County, Texas. The Trinidad Generating Facility (TGF) will include a natural gas-fired combined cycle combustion turbine generator (CTG) equipped with heat recovery steam generator (HRSG) and duct burners (DB). |  | combined cycle turbine | 15.21 | natural gas | 497 | MW | The facility will consist of a Mitsubishi Heavy Industries (MHI) J model gas fired combustion turbine nominally rated at 497 megawatts (MW) equipped with a HRSG and DB with a maximum design capacity of 402 million British thermal units per hour (MMBtu/hr). The gross nominal output of the CTG with HRSG and DB is 530 MW. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 2 | PPMVD | @15% O2, 24-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 7 ppm ammonia slip limit
TX-0713 | TENASKA BROWNSVILLE GENERATING STATION | TENASKA BROWNSVILLE PARTNERS, LLC | CAMERON | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 108411 PSDTX1350 | 4911 | 221112 | unknown | 02/21/2013 &nbsp;ACT | 04/29/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | Tenaska proposes a new electric power plant, using combined cycle gas turbine (CCGT) technology and fueled by pipeline quality natural gas. The proposed permit authorizes two CTs (2x1 CCGT), although the final design selected by Tenaska may only consist of one CT (1x1 CCGT). |  | (2) combined cycle turbines | 15.21 | natural gas | 274 | MW | Each CTG is site-rated at 274 MW gross electric output at 62Â°F ambient temperature. At this condition, two HRSGs with full duct burner firing produce enough steam to generate an additional 336 MW, for a total of 884 MW gross, or with about 5% losses, about 840 MW net electric output. Under summertime conditions, the net output is approximately 800 MW with the 2x1 CCGT configuration or about 400 MW with the 1x1 CCGT configuration. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 2 | PPMVD | @15% O2, 24-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0714 | S R BERTRON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | HARRIS | TX |  | USA | CRAIG ECKBERG | (713) 537-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | 102731 PSDTX1294 | 4911 | 221112 | 110034988413 | 05/10/2012 &nbsp;ACT | 12/19/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | NRG Texas is proposing to construct an additional electric power generation station at the Bertron Power Project which will generate electric power for sale on the wholesale electric market. The Bertron Power Project will include two power blocks that can be operated in combined cycle mode. |  | (2) combined cycle turbines | 15.21 | natural gas | 240 | MW | The gas turbines will be one of three options: (1) Two Siemens Model F5 (SF5) CTGs each rated at nominal capability of 225 megawatts (MW). Each CTG will have a duct fired HRSG with a maximum heat input of 688 million British thermal units per hour (MMBtu/hr). (2) Two General Electric Model 7FA (GE7FA) CTGs each rated at nominal capability of 215 MW. Each CTG will have a duct fired HRSG with a maximum heat input of 523 MMBtu/hr. (3) Two Mitsubishi Heavy Industry G Frame (MHI501G) CTGs each rated at a nominal electric output of 263 MW. Each CTG will have a duct fired HRSG with a maximum heat input of 686 MMBtu/hr. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 2 | PPMVD | @15% O2, 24-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 7 ppm ammonia slip limit
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041470431 | 02/24/2015 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2020-01-31 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR and oxidation catalyst | 2 | PPMVD @ 15% O2 | 24-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0767 | LON C. HILL POWER STATION | LON C. HILL, L.P. | NUECES | TX |  | USA | MATTHEW LINDSEY | 713-358-9734 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem, 512-239-1310, Tzvi.Shalem@tceq.texas.gov | 114911 AND PSDTX1380 | 4911 | 221122 | 110000501127 | 07/15/2015 &nbsp;ACT | 10/02/2015 &nbsp;ACT | 2015-09-23 | 2016-07-06 | A |  | The Lon C. Hill Power Station (LCHP) will include two natural gas-fired combined cycle combustion turbines (CTGs) equipped with dry low NOx burners (DLNs), heat recovery steam generators (HRSG), and natural gas-fired duct burners (DBs). Ancillary equipment includes evaporative coolers or inlet chillers, a single steam turbine (ST), auxiliary boiler, emergency generator, firewater pump, two cooling towers, oil water separator, degreaser, two diesel storage tanks, gasoline storage tank, selective catalytic reduction (SCR) and ammonia (NH3) handling systems including an NH3 storage tank, and two water tanks. The LCHP will be a 2x1 combined cycle power plant consisting of two CTGs, two HRSGs and one ST. The CTGs and ST will be one of two options: two Siemens SCC6-5000 CTGs and a SST6-5000 ST, or two General Electric 7FA CTGs and a D-11 ST. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 195 | MW | Two power configuration options authorized Siemens â€“ 240 MW + 250 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 195 MW + 670 MMBtu/hr duct burner | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 2 | PPM | ROLLING 24-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0773 | FGE EAGLE PINES PROJECT | FGE EAGLE PINES, LLC | CHEROKEE | TX |  | USA | EMERSON FARRELL | 281-407-7749 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, 512-239-1095, Erik.Hendrickson@tceq.texas.gov | 131316, PSDTX1454, AND GHGPSDT | 4911 | 221112 | UNKNOWN | 09/10/2015 &nbsp;ACT | 11/04/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | The FGEEP Project will include three natural gas-fired combined cycle (NGCC) power blocks, each block comprised of two gas-fired combustion turbines, two supplemental fired duct burners (DBs) heat recovery steam generators (HRSGs), and one steam turbine. FGEEP selected Alstom GT36 combustion turbines (CTs), each nominally rated at 321 megawatts (MW). Each HRSG is equipped with DBs that will have a maximum design heat input capacity of 799 million British thermal units per hour (MMBtu/hr). The CTs and DBs are fueled with pipeline quality natural gas. Each power block will also have a steam turbine generator designed to produce approximately 502 MW with the additional duct firing. Each of the three blocks will include the following ancillary equipment: one multi-cell condenser/cooling tower, one emergency generator, one firewater pump, two diesel storage tanks, and pressurized aqueous ammonia storage tanks. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 321 | MW | Alstom GT36 combustion turbines (321 MW)+ 799 million British thermal units per hour (MMBtu/hr) duct burner | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 2 | PPM | 24-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 2 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK AND TTTT
TX-0789 | DECORDOVA STEAM ELECTRIC STATION | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas.gov | 107569 AND PSDTX1432 | 4911 | 221112 | 110008149217 | 12/23/2015 &nbsp;ACT | 03/08/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | The DeCordova Station will consist of two combustion turbine generators (CTGs) operating in simple cycle or combined cycle modes. The gas turbines will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE). Simple cycle operations limited to 2,500 hr/yr. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 2 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.21 | natural gas | 10 | M TONNES/YR | Four GE Frame 7E gas turbines for refrigeration and compression at the site | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low NOx burners and good combustion practices | 9 | PPM | ROLLING 24-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKKK
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Simple Cycle Electrical Generation Gas Turbines 15.210 | 15.21 | natural gas | 34 | MW | Nine GE PGT25+G4 gas turbines for electrical generation at the site at 34 MW/turbine | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SELECTIVE CATALYTIC REDUCTION | 5 | PPM | ROLLING 24-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Combined Cycle Turbine with Heat Recovery Steam Generator, fired Duct Burners, and Steam Turbine Generator | 15.21 | NATURAL GAS | 426 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines with HRSGs and Steam Turbine Generators | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Selective Catalytic Reduction (SCR) and Dry Low NOx burners | 2 | PPMVD | 15% O2 3-H AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0315 | WARREN COUNTY POWER PLANT - DOMINION | VIRGINIA ELECTRIC AND POWER COMPANY | WARREN | VA | 22630 | USA | ROBERT BISHA | 804-273-3010 | ROBERT.M.BISHA@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Manager, Mr. Janardan Pandey, by phone at (540) 574-7817 or by e-mail: Janardan.Pandey@deq.virginia.gov | 81391-007 | 4911 | 221112 | 110040513110 | 09/03/2010 &nbsp;ACT | 12/17/2010 &nbsp;ACT | 2012-09-28 | 2015-03-30 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Virginia Electric and Power Company (Dominion) has proposed to construct and operate a combined-cycle electric power generating facility in Warren County with a nominal generating capacity of 1280 megawatts (MW) at ISO (International Organization for Standardization) conditions. | Equipment to be constructed at ths facility consists of: 3 Mitsubishi Model M501 GAC natural gas-fired combined-cylce turbines, each rated at 299,600 kW (2,996 MMBtu/hr. Each equipped with a heat recovery steam generator (HRSG) having a duct burner with a design rating of 500 MMBtu/hr. This permit supersedes the previous permit issued on 7/30/2004 to CPV Warren LLC. | COMBINED CYCLE TURBINE &amp; DUCT BURNER, 3 | 15.21 | Natural Gas | 2996 | MMBTU/H | Emissions are for one of three units (Mitsubishi natural gas-fired combustion turbine (CT) generator,Model M501 GAC). | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Two-stage, lean pre-mix dry low-NOx combustor and a selective catalytic reduction (SCR) control system using ammonia injection. | 2 | PPMVD@15%O2 | ONE HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 25.3 | LB/H | ONE HOUR AVERAGE | 0 |  |  | 0 | 0 | N
VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404 | 4911 | 221112 | 110055066440 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2019-06-19 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | COMBUSTION TURBINE GENERATORS, (3) | 15.21 | Natural Gas | 3442 | MMBTU/H | Three (3) Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners (natural gas-fired). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective catalytic reduction and ultra low NOx burners. | 2 | PPMVD @ 15% O2 | 1 H AVG | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Option 1 - Normal Operation | 15.21 | natural gas | 34000 | MMCF/YR | Option 1: Two on one configuration: 3,482 MMBtu/hr combustion turbine with 475 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry, low NOx burners and selective catalytic reduction | 2 | PPMVD @ 15% O2 | 1 H AV | BACT-PSD | NSPS , SIP | N | 0 | N | 141.3 | T/YR | 12 MO ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during tuning, water washing, startup and shutdown. CEMS required.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combusion Turbine - Option 2 - Normal Operation | 15.21 | Natural Gas | 35000 | MMCF/YR | Option 2: Two on one configuration: 3,116 MMBtu/hr combustion turbine with 991 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Nitrogen Oxides (NOx) | Other - 40 CFR 60, METHODS 7E OR 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DRY, LOW NOx BURNERS & SCR | 2 | PPMVD @ 15% O2 | 1 H AV | BACT-PSD | NSPS , SIP | N | 0 | N | 141.4 | T/YR | 12 MO ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during tuning, water washing, startup and shutdown. CEMS required.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Tuning &amp; Water Washing | 15.21 | natural gas | 34000 | MMCF/YR | Alternative operating scenario: during periods of tuning and water washing | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry, low NOx burners and SCR | 638 | LB/TURBINE/CAL DAY | 24 HR AV | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies during tuning (limited to 18 hours/event) and water washing (limited to 60 minutes/event). Determined by CEMS.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Startup and Shutdown | 15.21 | natural gas | 34000 | MMCF/YR | Startup and Shutdown | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry, low NOx burners and SCR | 273 | LB/TURBINE/EVENT | COLD START 60 MIN OR LESS | BACT-PSD | NSPS , SIP | N | 0 | N | 163 | LB/TURBINE/EVENT | WARM START 50 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 105 lb/turbine/event hot start - 30 minutes or less 18 lb/turbine/event shut down - 30 minutes or less These limits apply during startup and shutdown, which are defined in the permit. Determined by CEMS.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combustion Turbine - Tuning &amp; Water Washing | 15.21 | Natural Gas | 35000 | MMCF/YR | Alternative operating scenario: during periods of tuning and water washing | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry, low NOx burners and SCR | 564 | LB/TURBINE CAL DAY | 24 HR AV | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies during tuning (limited to 18 hours/event) and water washing (limited to 60 minutes/event). Determined by CEMS.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combustion Turbine - Startup &amp; Shutdown | 15.21 | Natural Gas | 35000 | MMCF/YR | Startup and Shutdown | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry, low NOx burners and SCR | 95 | LB/TURBINE/EVENT | COLD START 55 MIN OR LESS | BACT-PSD | NSPS , SIP | N | 0 | N | 117 | LB/TURBINE/EVENT | WARM START 55 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 8 lb/turbine/event hot start - 50 minutes or less 51 lb/turbine/event shut down - 38 minutes or less These limits apply during startup and shutdown, which are defined in the permit. Compliance based on CEMS.
*VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2020-03-18 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/hr natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/hr combustion turbine. Emission limits reflect the operation of each of the three turbines. | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Controlled by dry, low NOx burners and selective catalytic reduction (SCR). | 2 | PPMVD 15% O2 | 1 HR AVG | BACT-PSD | NSPS , SIP | N | 0 | N | 128.4 | TONS/YR | 12-MO ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Alternative short-term emission limits apply during tuning, startup and shutdown. CEMS required.
*VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2020-03-18 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/hr natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems Combustion | 15.21 | natural gas | 35000 | MMCF/YR | Alternative operating scenario: during periods of tuning | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry, low NOx burners and selective catalytic reduction | 703 | LB/TURBINE/CAL. DAY | 24 HR TOTAL | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies during tuning (limited to 18 hours/event). Determined by CEMS.
*VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2020-03-18 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/hr natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | Startup and Shutdown | Nitrogen Oxides (NOx) | Other - 40 CFR 60, Methods 7E or 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | dry, low NOx burners and selective catalytic reduction | 60 | LB/TURBINE/EVENT | COLD START-42 MINUTES OR LESS | BACT-PSD | SIP , NSPS | N | 0 | N | 0 | LB/TURBINE/EVENT | COLD START-42 MINUTES OR LESS | 0 |  |  | 0 | 0 | N |  | 42 lb/turbine/event hot start - 42 minutes or less 20 lb/turbine/event shut down - 15 minutes or less These limits apply during startup and shutdown, which are defined in the permit. Determined by CEMS.
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Combined Cycle Turbine/Duct Burner | 15.21 | Natural Gas | 2419.61 | mmBtu/Hr | This entry is for both of two identical units at the facility. Nominal 197 mW General Electric Frame 7FA.04 Turbine w/ Duct Burner - throughput denotes aggregate heat input of turbine and duct burner (HHV). | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR & Dry Low-NOx Burners | 15.2 | LB/H |  | BACT-PSD | NSPS | U | 80 | U | 0 |  |  | 2 | PPM | @ 15% O2 | 0 | 0 | N |  | NOx emissions are applicable with and without duct firing.
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2018-06-25 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.02 Turbine | 15.21 | Natural Gas | 3496.2 | mmBtu/hr | Nominal 640 mWe All emission limits steady-state and include 1000 mmBtu/hr Duct Burner in operation Short Term startup and shutdown limits in lb/event given in permit. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry-Low NOx Burners, SCR | 32.9 | LB/HR | 1-HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 156.2 | TONS/YEAR |  | 2 | PPM |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP01) | 15.21 | Natural Gas | 40 | MW |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 3 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD | NSPS | N | 0 | U | 4.6 | LB/H | 30-DAY ROLLING AVERAGE | 25.5 | T/YR |  | 8149 | 6554 | N | 2011
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP02) | 15.21 | Natural Gas | 40 | MW |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 3 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD | NSPS | N | 0 | U | 4.6 | LB/H | 30-DAY ROLLING AVERAGE | 25.5 | T/YR |  | 8149 | 6554 | N | 2011
ID-0018 | LANGLEY GULCH POWER PLANT | IDAHO POWER COMPANY | PAYETTE | ID |  | USA |  | 2083885820 | TMAHLUM@IDAHOPOWER.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2009.0092 | 4911 | 221112 | UNKNOWN | 06/07/2009 &nbsp;ACT | 06/25/2010 &nbsp;ACT | 2010-08-09 | 2010-10-05 | A |  | ONE-ON-ONE COMBINED CYCLE PLANT CONSISTING OF (1) NATURAL GAS-FIRED COMBUSTION TURBINE (CT) AND (1) STEAM TURBINE. THE CT IS EQUIPPED WITH (1) HEAT RECOVERY STEAM GENERATOR (HRSG) AND DUCT BURNER. ANCILLARY EQUIPMENT INCLUDES (1) DIESEL-FIRED EMERGENCY GENERATOR, (1) DIESEL-FIRED FIRE PUMP, (1) WET COOLING TOWER, AND (6) DRY CHEMICAL STORAGE SILOS. |  | COMBUSTION TURBINE, COMBINED CYCLE W/ DUCT BURNER | 15.21 | NATURAL GAS (ONLY) | 2375.28 | MMBTU/H | SIEMENS SGT6-5000F COMBUSTION TURBINE (NGCT, CCGT) FOR ELECTRICAL GENERATION, NOMINAL 269 MW AND 2.1466 MMSCF/HR | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SELECTIVE CATALYTIC REDUCTION (SCR), DRY LOW NOX (DLN), GOOD COMBUSTION PRACTICES (GCP) | 2 | PPMVD | 3-HR ROLLING / 15% O2 | BACT-PSD | NSPS | N | 0 |  | 96 | PPMVD | 3-HR ROLLING / 15% O2 DURING SU/SD/LL | 0 |  |  | 0 | 0 | N |  | LIMITS APPLY TO COMBUSTION TURBINE AND DUCT BURNER COMBINED EMISSIONS. SECONDARY LIMIT APPLIES DURING STARTUP, SHUTDOWN, AND LOW-LOAD EVENTS (SU/SD/LL).
*WV-0032 | BROOKE COUNTY POWER PLANT | ESC BROOKE COUNTY POWER I, LLC | BROOKE | WV | 26035 | USA | ANDREW DORN | 7163121042 | DREW.DORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 Steven.R.Pursley@wv.gov | R14-0035 | 4911 | 221112 | Not Found | 03/30/2018 &nbsp;ACT | 09/18/2018 &nbsp;ACT | 2018-12-20 | 2019-01-02 | A |  | Nominal 925 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.01 Turbine | 15.21 | Natural Gas/Ethane | 2737.7 | mmBtu/hr | Facility has 2 identical units, only 1 entry in RBLC. Nominal 462.5 mWe. All emission limits steady-state and include 424 mmBtu/hr Duct Burner in operation. Short Term startup and shutdown limits in lb/event given in permit. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry-Low NOx Burners, SCR | 23.2 | LB/HR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 2 | PPM |  | 0 | 0 | N
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | Mitsubishi M501-GAC combustion turbine, combined cycle configuration with duct burner. | 15.21 | natural gs | 2988 | MMBTU/H | or ULSD; Duct burner 499 MMBtu/hr, natural gas | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Utilize dry low-NOx burners when combusting natural gas; Utilize water injection when combusting ULSD; Utilize selective catalytic reduction (SCR) with aqueous ammonia injection at all times except during startup and shutdown; Limit the time in startup or shutdown. | 2 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON NG | BACT-PSD |  | U | 0 | U | 5.5 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON ULSD | 0 |  |  | 0 | 0 | N
AK-0073 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION | ANCHORAGE | AK | 99518 | USA | GREGORY ARTHUR | 907 762 4492 |  | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Kwame Agyei, Permit Engineer, kwame.agyei@alaska.gov | AQ0164CPT01 | 4911 | 221112 | 110046491854 | 04/14/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2012-02-22 | 2014-01-08 | D |  | Power plant that contains four combustion turbines, four duct burners, a black start generator, and an auxiliary heater. |  | Fuel Combustion | 15.21 | Natural Gas | 59900 | HP | EU IDs 5-8 Combined Cycle Natural Gas-fired Combustion Turbines rated at 59,900 hp (44.7 MW) | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion Turbines EU IDs 5-8 use good combustion practices involve increasing the residence time and excess oxygen to ensure complete combustion which in turn minimize particulates without an add-on control technology. | 0.0066 | LB/MMBTU | 3-HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0337 | POLK POWER STATION | TAMPA ELECTRIC COMPANY | POLK | FL | 33860 | USA | PAUL CARPINONE | 813-228-4528 | PLCARPINONE@TECOENERGY.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Leigh Ann Pell, Project Engineer Phone; 850-717-9033 | 1050233-034-AC | 4911 | 221112 | 110000365113 | 05/15/2013 &nbsp;ACT | 10/14/2012 &nbsp;ACT | 2013-08-06 | 2014-11-07 | D | http://appprod.dep.state.fl.us/air/emission/apds/listpermits.asp | The Polk Power Station consists of: a nominal 250 MW (net) solid fuel-based integrated gasification and combined cycle (Unit 1) including a sulfuric acid plant and an auxiliary boiler; four natural gas-fueled nominal 165 MW simple cycle combustion turbine-electrical generators (CTGs) designated as Units 2, 3, 4 and 5; and ancillary equipment. Units 2 and 3 are equipped with backup fuel oil-firing capability. | GHG(e) emissions: 4,307,862 | Combine cycle power block (4 on 1) | 15.21 | natural gas | 1160 | MW | Basis for the emission standard is either NSPS Subpart KKKK or Department BACT determinations. The BACT emission standards for NOX while operating in combined cycle are more stringent than the corresponding Subpart KKKK emissions standards of 15 and 42 ppmvd @15% O2 on a 30-day rolling average for natural gas and fuel oil, respectively. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Other - fuel specifications | (Particulate Matter (PM)) | PM | P | work practices | 2 | GR S/100 SCF OF GAS |  | BACT-PSD |  | U | 0 | U | 0.0015 | S FUEL OIL |  | 0 |  |  | 0 | 0 | N |  | Visible emissions shall not exceed 10% opacity for each 6-minute block average, as measured by EPA Method 9. Ammonia emissions shall not exceed 5 ppmvd @15% O2 as measured by initial and annual stack tests. The listed work practices and limits on surrogates and precursors limit potential PM/PM10/PM2.5 (filterable and condensable). Pollutant: PM/PM10/PM2.5
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD CUMBUSTION PRACTICE AND FUEL SPECIFICATION | 18 | LB/H | 3 HOURS | BACT-PSD |  |  | 0 |  | 0.0078 | LB/MMBTU | 3 HOURS | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: 15 LBS/HR FOURTH LIMIT: 0.0092 LBS/MMBTU LIMITS ONE AND TWO ARE USED WITH DUCT FIRING. LIMITIS THREE AND FOUR ARE USED WITHOUT DUCT FIRING.
LA-0308 | MORGAN CITY POWER PLANT | LOUISIANA ENERGY AND POWER AUTHORITY (LEPA) | ST. MARY | LA | 70380 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-767 | 4911 | 221112 | Not Found | 09/24/2012 &nbsp;ACT | 09/26/2013 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  |  |  | Combustion Turbine with SCR/HRSG | 15.21 | Natural Gas | 607.1 | MMBTU/hr |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean burning fuels (natural gas) | 12.03 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 52.68 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit: PM10 = 0.0197 lb/MMBTU (12 month average)
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1A | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean burning fuels (natural gas) | 17.52 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 73.35 | T/YR |  | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.008 LB/MMBTU (3-Hour Average)
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1B | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean burning fuels (natural gas) | 17.52 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 73.35 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.0082 LB/MMBTU (3-hour average)
NJ-0080 | HESS NEWARK ENERGY CENTER | HESS NEWARK ENERGY CENTER, LLC | ESSEX | NJ | 7105 | USA | PETER HAID | (774) 750-7088 | PHAID@HESS.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Supervisor: Yogesh Doshi - yogesh.doshi@dep.state.nj.us Phone: 609-633-7249 Permit Evaluator: Michael Hogan - michael.hogan@dep.state.nj.us. Phone: (609)-633-1124 | 08857/BOP110001 | 4911 | 221112 | 110044839903 | 12/10/2011 &nbsp;ACT | 11/01/2012 &nbsp;ACT | 2013-04-04 | 2018-04-17 | A |  | Combined Cycle Electric Generating Facility HESS Newark Energy Center (Hess-NEC), proposed at City of Newark (Essex County), New Jersey, would be a new, highly efficient, 655 MW combined-cycle power generating facility. Hess-NEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,320 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, a 12-cell mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Facility-wide Greenhouse Gas (GHG) emissions as CO2e emissions = 2,003,654 tpy | Combined cylce turbine with duct burner | 15.21 | natural gas | 39463 | mmcubic ft/year* | * Annual throughput is for 2 turbines, 2 duct burners and 1 auxiliary boiler | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Other - EPA/OAR method 201A and 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 13.2 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0080 | HESS NEWARK ENERGY CENTER | HESS NEWARK ENERGY CENTER, LLC | ESSEX | NJ | 7105 | USA | PETER HAID | (774) 750-7088 | PHAID@HESS.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Supervisor: Yogesh Doshi - yogesh.doshi@dep.state.nj.us Phone: 609-633-7249 Permit Evaluator: Michael Hogan - michael.hogan@dep.state.nj.us. Phone: (609)-633-1124 | 08857/BOP110001 | 4911 | 221112 | 110044839903 | 12/10/2011 &nbsp;ACT | 11/01/2012 &nbsp;ACT | 2013-04-04 | 2018-04-17 | A |  | Combined Cycle Electric Generating Facility HESS Newark Energy Center (Hess-NEC), proposed at City of Newark (Essex County), New Jersey, would be a new, highly efficient, 655 MW combined-cycle power generating facility. Hess-NEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,320 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, a 12-cell mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Facility-wide Greenhouse Gas (GHG) emissions as CO2e emissions = 2,003,654 tpy | Combined Cycle Combustion Turbine | 15.21 | natural gas | 39463 | MMCubic ft/yr | Fuel: Annual throughput is for 2 turbines, 2 duct burners and 1 auxiliary boiler CO2e = 2,000,268 t/yr for the facility (2 turbines, 2 duct burners and 1 auxiliary boiler, 1 emergency generator and 1 fire pump) | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Other - EPA/OAR Method 201A and 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 11 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OR-0048 | CARTY PLANT | PORTLAND GENERAL ELECTRIC | MORROW | OR |  | USA |  | 5034648519 | RAY.HENDRICKS@PGN.COM | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us |  | 25-0016-ST-02 | 4911 | 221112 | N/A | 12/24/2009 &nbsp;ACT | 12/29/2010 &nbsp;ACT | 2011-04-15 | 2011-08-30 | A |  | COMBINED CYCLE NATURAL GAS-FIRED ELECTRIC GENERATING UNIT PSD PERMIT | PSD PERMIT | COMBINED CYCLE NATURAL GAS-FIRED ELECTRIC GENERATING UNIT | 15.21 | NATURAL GAS | 2866 | MMBTU/H |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Other - METHOD 5 WITH METHOD 202 | (Particulate Matter (PM)) | PM | P | CLEAN FUEL | 2.5 | LB/MMCF |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | METHOD 5 WITH METHOD 202 good combustion practices using natural gas fuel
PA-0296 | BERKS HOLLOW ENERGY ASSOC LLC/ONTELAUNEE | BERKS HOLLOW ENERGY ASSOC LLC | BERKS | PA | 19605 | USA | BRADLEY J COOLEY | 636-534-3268 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | WILLIAM R. WEAVER, SOUTHCENTRAL REGION AIR PROGRAM MANAGER 909 Elmerton Ave, Harrisburg, PA 17701 717-705-4868 | 06-05150A | 4931 | 221112 | 110056155342 | 05/08/2012 &nbsp;ACT | 12/17/2013 &nbsp;ACT | 2014-04-17 | 2020-03-02 | A |  | This application is for the construction of a natural gas-fired combined-cycle electric generation facility that is designed to generate up to 855 MW nominal, using 2 combustion turbine generators and 2 heat recovery steam generators that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. | This application is for the construction of a natural gas-fired combined-cycle electric generation facility that is designed to generate up to 855 MW nominal, using 2 combustion turbine generators and 2 heat recovery steam generators that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. | Turbine, Combined Cycle, #1 and #2 | 15.21 | Natural Gas | 3046 | MMBTU/H | Equipped with SCR and Oxidation Catalyst | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 48.56 | TPY | 12-MONTH ROLLING TOTAL | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0817 | CHOCOLATE BAYOU STEAM GENERATING (CBSG) STATION | INEOS USALLC | BRAZORIA | TX |  | USA | THERESA VITEK | 281-581-3498 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | 123117, PSDTX1460, GHGPSDTX135 | 4911 | 221112 | Not Found | 12/22/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-28 | 2017-11-16 | A |  | support facility providing steam and electricity |  | Combined Cycle Cogeneration | 15.21 | NATURAL GAS | 50 | MW | 2 UNITS EACH 50 MW GE LM6000 | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 6.98 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
ID-0018 | LANGLEY GULCH POWER PLANT | IDAHO POWER COMPANY | PAYETTE | ID |  | USA |  | 2083885820 | TMAHLUM@IDAHOPOWER.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2009.0092 | 4911 | 221112 | UNKNOWN | 06/07/2009 &nbsp;ACT | 06/25/2010 &nbsp;ACT | 2010-08-09 | 2010-10-05 | A |  | ONE-ON-ONE COMBINED CYCLE PLANT CONSISTING OF (1) NATURAL GAS-FIRED COMBUSTION TURBINE (CT) AND (1) STEAM TURBINE. THE CT IS EQUIPPED WITH (1) HEAT RECOVERY STEAM GENERATOR (HRSG) AND DUCT BURNER. ANCILLARY EQUIPMENT INCLUDES (1) DIESEL-FIRED EMERGENCY GENERATOR, (1) DIESEL-FIRED FIRE PUMP, (1) WET COOLING TOWER, AND (6) DRY CHEMICAL STORAGE SILOS. |  | COMBUSTION TURBINE, COMBINED CYCLE W/ DUCT BURNER | 15.21 | NATURAL GAS (ONLY) | 2375.28 | MMBTU/H | SIEMENS SGT6-5000F COMBUSTION TURBINE (NGCT, CCGT) FOR ELECTRICAL GENERATION, NOMINAL 269 MW AND 2.1466 MMSCF/HR | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES (GCP) | 0 |  | SEE NOTE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICE AND FUEL SPECIFICATION | 18 | LB/H | 3 HOURS | BACT-PSD |  |  | 0 |  | 0.0078 | LB/MMBTU | 3 HOURS | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: 15 LBS/HR FOURTH LIMIT: 0.0092 LBS/MMBTU LIMITS ONE AND TWO ARE USED WITH DUCT FIRING. LIMITS THREE AND FOUR ARE USED WITHOUT DUCT FIRING.
LA-0308 | MORGAN CITY POWER PLANT | LOUISIANA ENERGY AND POWER AUTHORITY (LEPA) | ST. MARY | LA | 70380 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-767 | 4911 | 221112 | Not Found | 09/24/2012 &nbsp;ACT | 09/26/2013 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  |  |  | Combustion Turbine with SCR/HRSG | 15.21 | Natural Gas | 607.1 | MMBTU/hr |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean burning fuel (natural gas) | 12.03 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 52.68 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit: PM2.5 = 0.0197 lb/MMBTU (12 month average)
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1A | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean burning fuels (natural gas) | 17.52 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 73.35 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.008 LB/MMBTU (3-Hour Average)
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1B | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean burning fuel (natural gas) | 17.52 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 73.35 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.008 LB/MMBTU (3-hour average)
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITH DUCT BURNER - GENERAL ELECTRIC | 15.21 | Natural gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each General Electric combustion each turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 MMBtu/hr duct burner | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Other - NJ Test Method | (Particulate Matter (PM)) | PM | P | Use of Natural Gas a clean burning fuel | 9.8 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | BACT-PSD | OPERATING PERMIT | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0689 | CEDAR BAYOU ELECTRIC GENERATION STATION | NRG TEXAS POWER | CHAMBERS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 105810, PSDTX1308 | 4911 | 221112 | 110015743301 | 09/12/2012 &nbsp;ACT | 08/29/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power gereration station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the combined cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The new units will produce between 215-263 MW each. |  | Combined cycle natural gas turbines | 15.21 | Natural Gas | 225 | MW |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, natural gas | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Includes PM and PM10
TX-0817 | CHOCOLATE BAYOU STEAM GENERATING (CBSG) STATION | INEOS USALLC | BRAZORIA | TX |  | USA | THERESA VITEK | 281-581-3498 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | 123117, PSDTX1460, GHGPSDTX135 | 4911 | 221112 | Not Found | 12/22/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-28 | 2017-11-16 | A |  | support facility providing steam and electricity |  | Combined Cycle Cogeneration | 15.21 | NATURAL GAS | 50 | MW | 2 UNITS EACH 50 MW GE LM6000 | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 6.98 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 13.5 | LB/H | STACK TEST | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (COLD STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 12 | LB/H | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 48.8 | LB/EVENT | COLD START UP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF COLD STARTUPS NOT TO EXCEED 270 MINUTES; 2) COLD STARTUP MEANS STARTUP WHEN THE COMBUSTION TURBINE HAS NOT BEEN IN OPERATION DURING THE PRECEDING 72 HOURS
CA-1251 | PALMDALE ENERGY PROJECT | PALMDALE ENERGY, LLC | LOS ANGELES | CA | 93551 | USA | TOM CAMERON |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov | Staff Contact: Lisa Beckham beckham.lisa@epa.gov (415) 972-3811 | SE 17-01 | 4911 | 221122 | Not Found | 08/16/2017 &nbsp;ACT | 04/25/2018 &nbsp;ACT | 2018-10-25 | 2020-01-31 | A | https://www.epa.gov/caa-permitting/palmdale-energy-project-prevention-significant-deterioration-psd-permit | 645 MW (nominal) Natural Gas-fired Combined Cycle Power Plant, 2 x 1 configuration, auxiliary boiler for faster startup | See also docket: https://www.regulations.gov/docket?D=EPA-R09-OAR-2017-0473. Permit decision was appealed to EPA's Environmental Appeals Board. Board denied review on October 23, 2018. Information available through www.epa.gov/eab and https://yosemite.epa.gov/oa/EAB_Web_Docket.nsf/f22b4b245fab46c6852570e6004df1bd/ad735c0b822500258525829d004217eb!OpenDocument. 1/31/20 -- SYS MGR -- Link to permit is <https://www.regulations.gov/document?D=EPA-R09-OAR-2017-0473-0028> | Combustion Turbines (GEN1 and GEN2) | 15.21 | Natural Gas | 2217 | MMBTU/H | Each combustion turbine rated at 214 MW, with a maximum heat input rate of 2,217 MMBtu/H (HHV, at ISO conditions); natural gas-fired Siemens SGT6-5000F; each vents to dedicated Heat Recovery Steam Generator and a shared 276 MW Steam Turbine Generator; 160-ft stack height; 22-ft stack diameter | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | Clean fuel and good combustion practices | 0.0048 | LB/MMBTU | TEST AVERAGE | BACT-PSD |  | U | 0 | U | 11.8 | LB/H | TEST AVERAGE | 0 |  |  | 0 | 0 | N |  | The sulfur content of the gas shall not exceed 0.20 grains per 100 dry standard cubic feet (dscf), based on a 12-month rolling average, and shall not exceed 1.0 grains per 100 dscf at any time.
*FL-0363 | DANIA BEACH ENERGY CENTER | FLORIDA POWER AND LIGHT COMPANY | BROWARD | FL | 33314 | USA | JOHN HAMPP | 561-691-2894 | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-017-AC | 4911 | 221112 | 110002044065 | 07/27/2017 &nbsp;ACT | 12/04/2017 &nbsp;ACT | 2018-04-03 | 2018-04-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.F.ZIP | 1200 megawatt 2-on-1 combined cycle facility, natural gas-fired, with limited ULSD use. GE 7HA turbines | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.D.ZIP | 2-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural gas | 4000 | MMBtu/hr | Two nominal 430 MW combustion turbines, coupled to a steam turbine generator | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean fuels | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limits on sulfur content of fuels limit PM emissions. Gas limited to 2.0 grains per 100 scf, and oil limited to 0.0015% sulfur. Also subject to 10% opacity limit.
*FL-0367 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 36410 | USA | ROY BELDEN | (203) 357-6820 | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-001-AC | 4911 | 221112 | 110012581820 | 02/16/2018 &nbsp;ACT | 07/27/2018 &nbsp;ACT | 2019-03-19 | 2019-03-19 | B | https://arm-permit2k.dep.state.fl.us/nontv/1010524.001.AC.F.ZIP | A 573-megawatt (MW) (winter) 1-on-1 combined cycle plant which includes a heat recovery steam generator with duct firing, along with supporting equipment. Natural gas is the only permitted fuel for the combined cycle unit. | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/1010524.001.AC.R.ZIP | 1-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural Gas | 3266.9 | MMBtu/hour | One nominal 385 MW GE 7HA.02 CTG and one HRSG with duct firing [approximately 210 MMBtu/hour], and one nominal 210 MW steam turbine generator (STG) | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean fuels | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limits on sulfur content of fuel limit PM emissions. Natural Gas limited to 2.0 grains per 100 scf. Also subject to 10% opacity limit.
IL-0129 | CPV THREE RIVERS ENERGY CENTER | CPV THREE RIVERS, LLC | GRUNDY | IL | 60450 | USA | MIKE BRUNO | 781-817-8972 | MBRUNO@CPV.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Illinois EPA, Bureau of Air Permit Section | 16060032 | 4911 | 221112 | Not Found | 06/10/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2019-01-02 | 2019-02-19 | A |  | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, each with a combustion turbine and associated heat recovery steam generator (HRSG). The turbines would burn natural gas and ultra-low sulfur diesel (ULSD) as a backup fuel. Other units include an auxiliary boiler, fuel heater, engines, natural gas piping and components, circuit breakers and roadways. |  | Combined Cycle Combustion Turbines | 15.21 | Natural Gas | 3474 | mmBtu/hr | Throughput of ultra-low sulfur diesel (ULSD) is 3798 mmBtu/hr. Combined cycle combustion turbines w/ heat recovery steam generator (HRSG). Turbine inlets will have inlet evaporative cooling systems to cool inlet air during warm weather to increase power output. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0037 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0.0167 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 is for natural gas. Emission limit 2 is for ULSD. Permit limits are as follows. Averaging time for all permit limits are 3-hour block average. For natural gas: Without duct burner: 8.6 lb/hr With duct burner: 14.4 lb/hr For ULSD: 34.3 lb/hr
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD CUMBUSTION PRACTICE AND FUEL SPECIFICATION | 18 | LB/H | 3 HOURS | BACT-PSD |  |  | 0 |  | 0.0078 | LB/MMBTU | 3 HOURS | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: 15 LBS/HR FOURTH LIMIT: 0.0092 LBS/MMBTU LIMITS ONE AND TWO ARE USED WITH DUCT FIRING. LIMITS THREE AND FOUR ARE USED WITHOUT DUCT FIRING.
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 725 | MEGAWATT | TWO GENERAL ELECTRIC (GE) F-CLASS ADVANCED COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 725 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE-QUALITY NATURAL GAS EXCLUSIVELY AND GOOD COMBUSTION PRACTICE | 0.005 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0.004 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | EMISSION #1 IS WITHOUT DUCT FIRING (FILTERABLE ONLY) EMISSION #2 IS WITH DUCT FIRING (FILTERABLE ONLY)
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITH DUCT FIRING | 15.21 | NATURAL GAS | 1000 | MW | TWO MITSUBISHI &lsquo;&lsquo;G&lsquo;&lsquo; MODEL COMBUSTION TURBINE GENERATORS (CTS) WITH A NOMINAL GENERATING CAPACITY OF 270 MW CAPACITY EACH, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR), OXIDATION CATALYST | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND EFFICIENT TURBINE DESIGN | 22.8 | LB/H | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITHOUT DUCT FIRING | 15.21 | NATURAL GAS | 270 | MW |  | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND EFFICIENT TURBINE DESIGN | 15 | LB/H | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST. HEAT RATE LIMITED TO 6,793 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR MATTAWOMAN TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS MATTAWOMAN PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE-QUALITY NATURAL GAS EXCLUSIVELY AND GOOD COMBUSTION PRACTICE | 8.9 | LB/H | 3-HOUR BLOCK AVERAGE (W/OUT DUCT FIRING) | BACT-PSD |  |  | 0 |  | 13.9 | LB/H | 3-HOUR BLOCK AVERAGE (WITH DUCT FIRING) | 0 |  |  | 0 | 0 | N
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS. HEAT INPUT LIMITED TO 6,802 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR KEYS TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS KEYS PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE-QUALITY NATURAL GAS EXCLUSIVELY AND GOOD COMBUSTION PRACTICE | 8.8 | LB/H | 3-HOUR BLOCK AVERAGE, W/OUT DUCT FIRING | BACT-PSD |  |  | 0 |  | 12.2 | LB/H | WITH DUCT FIRING | 0 |  |  | 0 | 0 | N
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0042 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0073 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion air filters; efficient combustion control; low sulfur natural gas fuel. | 0.0033 | LB/MMBTU | TEST PROTOCOL; (3 1-H TESTS IF POSSIBLE) | BACT-PSD | OTHER | N | 90 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit applies to each CTG/HRSG. Limit applies at all times and includes duct burner operation. Other applicable requirement: state rule
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 0.007 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 0.007 lb/MMBTU for each CTGHRSG. Test protocol will specify averaging time. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2013. Pulse Jet Fabric Filter Baghouse: minimum of $62,842 per ton. Mechanical Shaker Fabric Filter Baghouse: minimum of $53,684 per ton. Reverse-Air Fabric Filter Bathouse: minimum of $77,328 per ton. Dry ESP (Wire-Plate Type): minimum of $44,525 per ton. Dry ESP (Wire-Pipe Type): minimum of $66,472 per ton. Wet ESP (Wire-Plate Type): minimum of $77,761 per ton. Wet ESP (Wire-Pipe Type): minimum of $110,364 per ton. Venturi Scrubber: minimum of $52,773 per ton.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 9.9 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit in the table above is for EACH CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. Pulse jet fabric filter baghouse: minimum of $364,528 per ton. Mechanical shaker fabric filter baghouse: minimum of $404,724 per ton. Reverse-air fabric filter baghouse: minimum of $476,689 per ton. Dry ESP (Wire-plate type): minimum of $478,806 Dry ESP (Wire-pipe type): minimum of $303,809 per ton. Wet ESP (Wire-plate type): minimum of $576,763 per ton. Wet ESP (Wire-pipe type): minimum of $440,047 per ton. Venturi Scrubber: minimum of $1,445,564 per ton.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 0.007 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. Pulse jet fabric filter baghouse: minimum of $64,473 per ton. Mechanical shaker fabric filter baghouse: minimum of $55,077 per ton. Reverse-air fabric filter baghouse: minimum of $79,336 per ton. Dry ESP (Wire-plate type): minimum of $45,681 per ton. Dry ESP (Wire-pipe type): minimum of $68,197 per ton. Wet ESP (Wire-plate type): minimum of $79,780 per ton. West ESP (Wire-pipe type): minimum of $113,229 per ton. Venturi scrubber: minimum of $54,143 per ton.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas, combustion inlet air filter. | 0.0025 | LB/MMBTU |  | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Fabric filter control: over $260,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5). Electrostatic Precipitator (ESP): over $188,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5). Wet ESP: over $165,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5). Venturi Scrubber: over $112,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5).
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 5.8 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | 5.8 pph is equivalent to 0.002 lb/MMBTU, which is about 30 percent of PM10 and PM2.5. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse Jet Fabric Filter Baghouse: average of $334,000 per ton Mechanical Shaker Fabric Filter Baghouse: average of $370,500 per ton Reverse-Air Fabric Filter Baghouse: average of $437,000 per ton Dry ESP (Wire-Plate Type): average of $438,500 per ton Dry ESP (Wire-Pipe Type): average of $278,500 per ton Wet ESP (Wire-Plate Type): average of $528,500 per ton Wet ESP (Wire-Pipe Type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 5.8 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | (5.8 lb/hr is equivalent to 0.002 lb/MMBTU which is about 30 percent of PM10 and PM2.5) The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10 which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse jet fabric filter baghouse: average of $334,000 per ton. Mechanical shaker fabric filter baghouse: average of $370,500 per ton Reverse-Air fabric filter baghouse: average of $437,000 per ton Dry ESP (Wire-plate type): average of $438,500 per ton Dry ESP (Wire-pipe type): average of $278,500 per ton Wet ESP (Wire-plate type): average of $528,500 per ton Wet ESP (Wire-pipe type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton.
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 16 | LB/H | HOURLY; EACH UNIT | BACT-PSD | SIP | N | 0 | N | 12.2 | LB/H | HOURLY; EACH UNIT W/O DUCT BURNER FIRING | 0 |  |  | 0 | 0 | N |  | The cost analysis was for the best scenario: 100 percent capture of PM2.5, where PM and PM10 calculations equaled PM2.5. Pulse Jet Fabric Filter Baghouse: minimum of $174,206 per ton Mechanical Shaker Fabric Filter Baghouse: minimum of $145,172 per ton Reverse-Air Fabric Filter Baghouse: minimum of $232,274 per ton Dry ESP (Wire-Plate Type): minimum of $116,721 per ton Dry ESP (Wire-Pipe Type): minimum of $261,309 per ton Wet ESP (Wire-Plate Type): minimum of $263,153 per ton Wet ESP (Wire-Pipe Type): minimum of $348,412 per ton Venturi Scrubber: minimum of $167,000 per ton
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | Combined Cycle Combustion Turbine -Siemens turbine without Duct Burner | 15.21 | Natural gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each Siemens combustion turbine will be 2,356 MMBtu/hr(HHV) | Particulate matter, filterable (FPM) | Other - NJ Test Method | (Particulate Matter (PM)) | PM | P | Use of Natural Gas as a clean burning fuel | 10.5 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITH DUCT BURNER - SIEMENS | 15.21 | Natural Gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two Siemens turbines and two associated duct burners) The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). | Particulate matter, filterable (FPM) | Other - NJ Test Method | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 10.6 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | BACT-PSD | OPERATING PERMIT | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITHOUT DUCT BURNER - GENERAL ELECTRIC | 15.21 | Natural Gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each General Electric combustion turbine will be 2,312 MMBtu/hr(HHV) | Particulate matter, filterable (FPM) | Other - NJ Test Method | (Particulate Matter (PM)) | PM | P | Use of Natural Gas as a clean burning fuel | 8.7 | LB/H | AVERAGE OF THREE ONE-HOUR TESTS | BACT-PSD | OPERATING PERMIT | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine without Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burner. | Particulate matter, filterable (FPM) | Other - NJ Test Method | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 6 | LB/H | AVERAGE OF THREE ONE HOUR STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burners. | Particulate matter, filterable (FPM) | Other - NJ TEST METHOD | (Particulate Matter (PM)) | PM | P | Use of Natural gas a clean burning fuel | 15.1 | LB/H | AVERAGE OF THREE STACK TEST RUNS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0.0048 | LB/MMBTU | AVERAGE OF THREE STACK TEST RUNS | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas with Duct Burner | 15.21 | natural gas | 4000 | h/yr |  | Particulate matter, filterable (FPM) | Other - NJ TEST METHOD | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 10.4 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY STACK TESTING
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas without Duct Burner | 15.21 | Natural Gas | 8040 | H/YR |  | Particulate matter, filterable (FPM) | Other - NJ TEST METHOD | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 4.4 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY STACK TESTING
NY-0104 | CPV VALLEY ENERGY CENTER | CPV VALLEY LLC | ORANGE | NY | 10940 | USA |  |  |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-335600136/00001 | 4911 | 221112 | 110043332471 | 08/01/2013 &nbsp;ACT | 08/01/2013 &nbsp;ACT | 2017-08-25 | 2017-09-28 | A |  | CPV Valley Energy Center is a 680 MW combined cycle electric generating facility located in Middletown, NY. The combustion turbines are rated at 2,234 MMBTU/H firing natural gas and 2,145 MMBTU/H firing diesel fuel. The duct burners are rated for 500 MMBTU/H firing natural gas. In addition to the turbines their emission limits for the auxiliary boiler (73.5 MMBTU/H), emergency generator, fire pump, and gas heater. | State Facility Permit | Turbines and duct burners - NG | 15.21 | natural gas | 0 |  | Combined cycle units heat rate 7,605 BTU/KW-H (HHV) or less without duct burner firing to achieve design thermal efficiency of 57.4% (LHV). | Particulate matter, filterable (FPM) | Other - Methods 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Natural gas | 0.0073 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Also PM-10
OH-0363 | NTE OHIO, LLC |  | BUTLER | OH | 45044 | USA | MICHAEL SCHUSTER | (904)436-6896 | MSCHUSTER@NTEENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0116610 | 4911 | 221112 | 110070379584 | 04/07/2014 &nbsp;ACT | 11/05/2014 &nbsp;ACT | 2019-02-22 | 2019-04-01 | A |  | Combined-cycle, natural gas-fired power plant | Initial installation of either one (1) Mitsubishi Hitachi Power Systems Americas M501JAC or one (1) Mitsubishi Hitachi Power Systems Americas M501GAC single power block in a 1x1 combined-cycle multi-shaft configuration, including a combustion turbine and heat recovery steam generator with duct burners and a steam turbine to be known as the Middletown Energy Center. | Turbine generator with HRSG and duct burners (P001) | 15.21 | Natural gas | 3278.5 | MMBTU/H | Combined-cycle combustion turbine generator (CTG) with heat recovery steam generator (HRSG), natural gas-fired, including duct burners (DB). Permit was for either Mitsubishi Hitachi Power Systems America M501GAC or M501JAC. The M501GAC was installed. | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | B | Exclusive use of natural gas, high efficiency inlet air filters and low NOx burner. | 20 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 59.4 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  |  | 0 | 0 | N |  | 20.0 lb/h and 5.70x10-3 lb/mmbtu with duct burner, except startup and shutdown. 10.8 lb/h and 3.80x10-3 lb/mmbtu turbine only, except startup and shutdown. 59.4 tons per rolling 12 month period for all operating modes, including startup.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | General Electric Combustion Turbine (P004) | 15.21 | Natural gas | 3544 | MMBTU/H | General Electric model 7HA.02 natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,544 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | natural gas or a natural gas and ethane mixture only | 0.0036 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 12.1 | LB/H |  | 0 |  | SEE NOTES | 0 | 0 | N |  | 53.0 t/yr per rolling, 12-month period, including start-up and shutdown emissions.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Mitsubishi Combustion Turbine (P005) | 15.21 | Natural gas | 3320 | MMBTU/H | Mitsubishi Model 501JAC natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,320 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 108 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | natural gas or a natural gas and ethane mixture only | 0.004 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 12.6 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.004 lb/mmbtu and 12.60 lb/h with duct burner (except startup and shutdown). 0.0037 lb/mmbtu and 12.3 lb/h without duct burner (except startup and shutdown). 55.2 t/yr per rolling 12 month period for all operating modes, including startup.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Siemens Combustion Turbine (P006) | 15.21 | Natural gas | 3602 | MMBTU/H | Siemens Model SCC6-8000H natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,602 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 667 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | natural gas or a natural gas and ethane mixture only | 0.0057 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 19.8 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.0057 lb/mmbtu and 19.8 lb/h with duct burner (except startup and shutdown). 0.006 lb/mmbtu and 13 lb/h without duct burner (except startup and shutdown). 86.7 t/yr per rolling 12 month period for all operating modes, including startup.
*PA-0298 | FUTURE POWER PA/GOOD SPRINGS NGCC FACILITY | FUTURE POWER PA INC | SCHUYLKILL | PA | 17980 | USA | JAMES PALUMBO | 570-342-5200 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MARK J. WEJKSZNER NORTHEAST REGION AIR PROGRAM MANAGER 2 Public Square Wilkes-Barre, PA 18711 570-826-2357 | 54-00082A | 4911 | 221112 | 110062854870 | 05/03/2013 &nbsp;ACT | 03/04/2014 &nbsp;ACT | 2014-04-17 | 2020-02-19 | A |  | Natural gas-fired combined-cycle electric generation facility that is designed to generate up to 346 MW nominal, using a combustion turbine generator and a heat recovery steam generator that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. The Turbine is rated at 2,267 MMBTU/hr HHV (2,042 MMBTU/hr LHV). The Duct burner is rated at 134.3 MMBTU/hr HHV (120 MMBTU/hr LHV). The proposed project will also include a diesel engine-driven emergency generator; a diesel engine-driven firewater pump; a multi-cell evaporative cooling tower; and associated emission control systems, tanks, and other plant equipment. |  | Turbine, COMBINED CYCLE UNIT (Siemens 5000) | 15.21 | Natural Gas | 2267 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 10.4 | LB/H | WITH DUCT BURNER | BACT-PSD | NSPS | U | 0 | U | 38.95 | T/YR | BASED ON A 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N
PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Combustion turbine with duct burner | 15.21 | Natural gas | 3304.3 | MMBtu/hr | Limits are for each CCCT and yearly limits are for cumulative turbine and duct burner. Duct burner throughput is 637.9 MMBtu/hr. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive natural gas, high-efficiency inlet air filters and DLN | 0.003 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 24.1 | TONS | YEAR | 0 |  |  | 0 | 0 | N
*TN-0164 | TVA - JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134 | USA | JACK BYARS | (423) 751-2666 | JGBYARS@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov |  | 972969 | 4911 | 221112 | 110070502905 | 09/26/2017 &nbsp;ACT | 02/01/2018 &nbsp;ACT | 2019-03-21 | 2019-03-21 | D |  | Combustion turbines and combined cycle plant | Permit 972969 adds startup and shutdown limits to the requirements established in PSD permit 970816F. | Dual-fuel CT and HRSG with duct burner | 15.21 | Natural Gas | 1020 | MMBtu/hr | Rated input capacity is 1020 MMBtu/hr (CT) and 319 MMBtu/hr (duct burner) when burning natural gas and 1084 MMBtu/hr when burning #2 oil. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion design & practice | 0.005 | LB/MMBTU | WHEN BURNING NATURAL GAS | BACT-PSD |  | U | 0 | U | 0.015 | LB/MMBTU | WHEN BURNING #2 OIL | 0 |  |  | 0 | 0 | N
*VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2020-03-18 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/hr natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/hr combustion turbine. Emission limits reflect the operation of each of the three turbines. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Controlled by good combustion practices (e.g. controlled fuel/air mixing, adequate temperature, and gas residence time) and the use of pipeline-quality natural gas with a maximum sulfur content of 0.4 grains per 100 scf, on a 12-month rolling average. | 0.0052 | LB/MMBTU | AVG. OF 3 TEST RUNS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 8.91 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 11.78 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 8.91 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 11.78 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (WARM STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 12 | LB/H | WARM STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 30.8 | LB/EVENT | WARM STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF WARM STARTUPS NOT TO EXCEED 180 MINUTES; 2) WARM STARTUP MEANS A STARTUP THAT IS NOT A HOT OR COLD STARTUP
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (HOT STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 12 | LB/H | HOT STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 12.8 | LB/EVENT | HOT STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF HOT STARTUPS NOT TO EXCEED 90 MINUTES; 2) HOT STARTUP MEANS A STARTUP WHEN THE COMBUSTION TURBINE HAS BEEN IN OPERATION DURING THE PRECEDING 8 HOURS
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 6 | LB/H | TURBINE SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 6 | LB/EVENT | TURBINE SHUTDOWN PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF SHUTDOWN NOT TO EXCEED 30 MINUTES; 2) SHUTDOWN MEANS THE PERIOD BEGINNING WITH THE LOWERING OF EQUIPMENT FROM BASE LOAD AND LASTING UNTIL FUEL FLOW IS COMPLETELY OFF AND COMBUSTION HAS CEASED
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - SEE POLLUTANT NOTES | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 13.5 | LB/H | STACK TEST | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | PM10 TEST METHOD: USE EPA METHODS 5 & 202, OR CTM-039 OR CTM-040 IN LIEU OF METHOD 202
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (COLD STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 12 | LB/H | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 48 | LB/EVENT | COLD STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF COLD STARTUPS NOT TO EXCEED 270 MINUTES; 2) COLD STARTUP MEANS STARTUP WHEN THE COMBUSTION TURBINE HAS NOT BEEN IN OPERATION DURING THE PRECEDING 72 HOURS
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA METHODS 5 & 202, OR METHODS 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 0.0048 | LB/MMBTU | 9-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0.0049 | LB/MMBTU | 9-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1251 | PALMDALE ENERGY PROJECT | PALMDALE ENERGY, LLC | LOS ANGELES | CA | 93551 | USA | TOM CAMERON |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov | Staff Contact: Lisa Beckham beckham.lisa@epa.gov (415) 972-3811 | SE 17-01 | 4911 | 221122 | Not Found | 08/16/2017 &nbsp;ACT | 04/25/2018 &nbsp;ACT | 2018-10-25 | 2020-01-31 | A | https://www.epa.gov/caa-permitting/palmdale-energy-project-prevention-significant-deterioration-psd-permit | 645 MW (nominal) Natural Gas-fired Combined Cycle Power Plant, 2 x 1 configuration, auxiliary boiler for faster startup | See also docket: https://www.regulations.gov/docket?D=EPA-R09-OAR-2017-0473. Permit decision was appealed to EPA's Environmental Appeals Board. Board denied review on October 23, 2018. Information available through www.epa.gov/eab and https://yosemite.epa.gov/oa/EAB_Web_Docket.nsf/f22b4b245fab46c6852570e6004df1bd/ad735c0b822500258525829d004217eb!OpenDocument. 1/31/20 -- SYS MGR -- Link to permit is <https://www.regulations.gov/document?D=EPA-R09-OAR-2017-0473-0028> | Combustion Turbines (GEN1 and GEN2) | 15.21 | Natural Gas | 2217 | MMBTU/H | Each combustion turbine rated at 214 MW, with a maximum heat input rate of 2,217 MMBtu/H (HHV, at ISO conditions); natural gas-fired Siemens SGT6-5000F; each vents to dedicated Heat Recovery Steam Generator and a shared 276 MW Steam Turbine Generator; 160-ft stack height; 22-ft stack diameter | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Clean fuel and good combustion practices | 0.0048 | LB/MMBTU | TEST AVERAGE | BACT-PSD |  | N | 0 | U | 11.8 | LB/H | TEST AVERAGE | 0 |  |  | 0 | 0 | N |  | The sulfur content of the gas shall not exceed 0.20 grains per 100 dry standard cubic feet (dscf), based on a 12-month rolling average, and shall not exceed 1.0 grains per 100 dscf at any time.
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055426409 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Four combined cycle combution turbines | 15.21 | natural gas | 373 | MMBTU/H | Three GE, LMS6000 PF, natural gas-fired, combined cycle CTG, rated at 373 MMBtu per hour each, based on HHV and one (1) HRSG each with no Duct Burners | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustor design | 4.3 | LB/H | AVE OVER STACK TEST LENGTH | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/o Duct Firing | 15.21 | Natural Gas | 2969 | MMBtu/hr | Throughput is for turbine only | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and OTM 28 | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.044 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/Duct Firing | 15.21 | Natural Gas | 2639 | MMBtu/hr | Duct burner MRC is 946 MMbtu/hr | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.005 | LB/MMBTU |  | BACT-PSD | OPERATING PERMIT , SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - No tests required | (Particulate Matter (PM)) | PM | P | Use of clean fuels | 2 | GR. S/100 SCF GAS | FOR NATURAL GAS | BACT-PSD |  | U | 0 | U | 0.0015 | % S IN ULSD | FOR ULSD | 0 |  |  | 0 | 0 | N |  | Clean fuels prevent PM formation
*FL-0363 | DANIA BEACH ENERGY CENTER | FLORIDA POWER AND LIGHT COMPANY | BROWARD | FL | 33314 | USA | JOHN HAMPP | 561-691-2894 | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-017-AC | 4911 | 221112 | 110002044065 | 07/27/2017 &nbsp;ACT | 12/04/2017 &nbsp;ACT | 2018-04-03 | 2018-04-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.F.ZIP | 1200 megawatt 2-on-1 combined cycle facility, natural gas-fired, with limited ULSD use. GE 7HA turbines | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.D.ZIP | 2-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural gas | 4000 | MMBtu/hr | Two nominal 430 MW combustion turbines, coupled to a steam turbine generator | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean fuels | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limits on sulfur content of fuels limit PM emissions. Gas limited to 2.0 grains per 100 scf, and oil limited to 0.0015% sulfur. Also subject to 10% opacity limit.
*FL-0367 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 36410 | USA | ROY BELDEN | (203) 357-6820 | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-001-AC | 4911 | 221112 | 110012581820 | 02/16/2018 &nbsp;ACT | 07/27/2018 &nbsp;ACT | 2019-03-19 | 2019-03-19 | B | https://arm-permit2k.dep.state.fl.us/nontv/1010524.001.AC.F.ZIP | A 573-megawatt (MW) (winter) 1-on-1 combined cycle plant which includes a heat recovery steam generator with duct firing, along with supporting equipment. Natural gas is the only permitted fuel for the combined cycle unit. | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/1010524.001.AC.R.ZIP | 1-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural Gas | 3266.9 | MMBtu/hour | One nominal 385 MW GE 7HA.02 CTG and one HRSG with duct firing [approximately 210 MMBtu/hour], and one nominal 210 MW steam turbine generator (STG) | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean fuels | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limits on sulfur content of fuel limit PM emissions. Natural Gas limited to 2.0 grains per 100 scf. Also subject to 10% opacity limit.
IL-0112 | NELSON ENERGY CENTER | INVENERGY NELSON, LLC | LEE | IL | 61071-9722 | USA | JOEL SCHROEDER | 312-224-1417 | JSCHROEDER@INVENERGYLLC.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Manish Patel, Permit Analyst Manish.Patel@illinois.gov 217-785-1722 | 98080039 | 4911 | 221112 | 110007399644 | 11/19/2010 &nbsp;ACT | 12/28/2010 &nbsp;ACT | 2013-02-21 | 2020-04-16 | A |  | Natural gas-fired electic power generation facility with two &quot;combined cycle&quot; turbines followed by heat recovery steam generators (HRSG) and the capability for supplemental fuel firing in the HRSG for each turbine using duct burners. NOx emissions will be controlled by SCR and low NOx combustors. | LSP-Nelson Energy started construction pursuant to a permit issued in year 2000 for a facility that was not completed due to financial difficulties, which eventually resulted in LSP-Nelson entering bankruptcy. Substantial construction of foundations and infrastructure for all units and physical installation of one turbine were completed, including construction of HRSGs. | Electric Generation Facility | 15.21 | Natural Gas | 220 | MW each | Two combined cycle combustion turbines followed by HRSGs with capability for supplemental fuel firing in HRSG for each combustion turbine using duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 0.012 | LB/MMBTU | HOURLY AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0129 | CPV THREE RIVERS ENERGY CENTER | CPV THREE RIVERS, LLC | GRUNDY | IL | 60450 | USA | MIKE BRUNO | 781-817-8972 | MBRUNO@CPV.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Illinois EPA, Bureau of Air Permit Section | 16060032 | 4911 | 221112 | Not Found | 06/10/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2019-01-02 | 2019-02-19 | A |  | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, each with a combustion turbine and associated heat recovery steam generator (HRSG). The turbines would burn natural gas and ultra-low sulfur diesel (ULSD) as a backup fuel. Other units include an auxiliary boiler, fuel heater, engines, natural gas piping and components, circuit breakers and roadways. |  | Combined Cycle Combustion Turbines | 15.21 | Natural Gas | 3474 | mmBtu/hr | Throughput of ultra-low sulfur diesel (ULSD) is 3798 mmBtu/hr. Combined cycle combustion turbines w/ heat recovery steam generator (HRSG). Turbine inlets will have inlet evaporative cooling systems to cool inlet air during warm weather to increase power output. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practice | 0.0069 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0.032 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 is for natural gas. Emission Limit 2 is for ULSD. Emission Limits 1 and 2 and permit limits address PM10 and PM2.5 together as PM10/PM2.5. Permit limits are as follows. For natural gas: With duct burner: 18.9 lb/hr Without duct burner: 11.5 lb/hr For ULSD: 65.1 lb/hr
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Combined cycle combustion turbine | 15.21 | Natural gas | 250 | MW | Combined cycle combustion unit; this unit includes a heat recovery steam generator (HRSG) with supplemental natural gas duct firing (duct burners) and a condensing steam turbine generator with SCR and CO catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | dry low NOx burners heat recovery steam generator (HRSG) | 30.2 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002049328 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | COMBINED CYCLE TURBINE GENERATORS (UNITS 6A &amp; 6B) | 15.21 | NATURAL GAS | 7146 | MMBTU/H | TURBINES ALSO PERMITTED TO BURN NO. 2 FUEL OIL AND ULTRA LOW SULFUR DIESEL. FUEL OIL USE IS LIMITED TO 1000 HOURS PER YEAR. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | WHILE FIRING NATURAL GAS: USE OF PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES WHILE FIRING FUEL OIL: USE OF ULTRA LOW SULFUR FUEL OIL AND GOOD COMBUSTION PRACTICES | 26.23 | LB/H | HOURLY AVERAGE W/O DUCT BURNER | BACT-PSD | OPERATING PERMIT | U | 0 | U | 33.16 | LB/H | HOURLY AVERAGE W/ DUCT BURNER | 0 |  |  | 0 | 0 | N |  | WHILE FIRING FUEL OIL, THE BACT LIMIT FOR PM10 IS 36.37 LB/HR (HOURLY AVERAGE) BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE).
LA-0256 | COGENERATION PLANT | WESTLAKE VINYLS COMPANY LP | ASCENSION | LA | 70734 | USA | KAREN KHONSARI | (225) 673-0647 | KKHONSARI@WESTLAKE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: DAN NGUYEN, 225-219-3417 | PSD-LA-754 | 4939 | 221112 | 110000746328 | 01/12/2011 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2011-12-21 | 2012-04-03 | B |  | COGENERATION PLANT AT SYNTHETIC ORGANIC CHEMICAL MANUFACTURING FACILITY | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS &lsquo;&lsquo;FWE&lsquo;&lsquo; REPRESENT POTENTIAL EMISSIONS ASSOCIATED WITH THE COGENERATION PLANT. NOX &lsquo;&lsquo;NETTED OUT&lsquo;&lsquo; OF PSD/NNSR. | COGENERATION TRAINS 1-3 (1-10, 2-10, 3-10) | 15.21 | NATURAL GAS | 475 | MMBTU/H | EACH COGEN TRAIN CONSISTS OF A 50 MW GE LM6000 PF SPRINT TURBINE AND A HEAT RECOVERY STEAM GENERATOR EQUIPPED WITH A 70 MM BTU/HR DUCT BURNER. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS AS FUEL AND GOOD COMBUSTION PRACTICES | 3.72 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | IN ADDITION, AN ANNUAL LIMIT OF 16.31 TPY WAS ESTABLISHED BY THE ACCOMPANYING TITLE V PERMIT (3090-V0).
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive Combustion of Fuel Gas and Good Combustion Practices. | 9.53 | LB/H | 3 HOUR AVERAGE | BACT-PSD | OPERATING PERMIT , NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Averaging time 3-hour Average during duct burner and turbine operations.
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000310459 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 2449 | MMBTU/H | two 315 MW (nominal) GE Energy 7F Series 5 Rapid Response Combined Cycle Combustion Turbines with Duct Burners and 31 MW (estimated) steam turbine generators | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0062 | LB/MMBTU | 1 HR AVG/DO NOT APPLY DURING SS | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 13 | LB/H | 1 HR AVG/DO NOT APPLY DURING SS | 0 |  |  | 0 | 0 | N |  | PM10(no duct firing): â‰¤0.0071lb/MMBtu, â‰¤8.8 lb/hr during start-ups(â‰¤ 45 minutes): PM/PM10/PM2.5 â‰¤ 6.60 lb per event during shutdowns (â‰¤ 27 minutes): PM/PM10/PM2.5 â‰¤ 3.96 lb per event
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 725 | MEGAWATT | TWO GENERAL ELECTRIC (GE) F-CLASS ADVANCED COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 725 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE-QUALITY NATURAL GAS EXCLUSIVELY AND GOOD COMBUSTION PRACTICE | 0.008 | LB/MMBTU | AVERAGE OF THREE STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.006 | LB/MMBTU | AVERAGE OF THREE STACK TEST RUNS | 0 |  |  | 0 | 0 | N |  | EMISSIONS #1 IS WITHOUT DUCT FIRING EMISSIONS #2 IS WITH DUCT FIRING
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITH DUCT FIRING | 15.21 | NATURAL GAS | 1000 | MW | TWO MITSUBISHI &lsquo;&lsquo;G&lsquo;&lsquo; MODEL COMBUSTION TURBINE GENERATORS (CTS) WITH A NOMINAL GENERATING CAPACITY OF 270 MW CAPACITY EACH, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR), OXIDATION CATALYST | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND EFFICIENT TURBINE DESIGN | 38 | LB/H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITHOUT DUCT FIRING | 15.21 | NATURAL GAS | 270 | MW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND EFFICIENT TURBINE DESIGN | 25.1 | LB/H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST. HEAT RATE LIMITED TO 6,793 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR MATTAWOMAN TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS MATTAWOMAN PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE QUALITY NATURAL GAS EXCLUSIVELY AND GOOD COMBUSTION PRACTICES | 17.9 | LB/H | W/OUT DUCT FIRING, AVG. OF 3 STACK TESTS | BACT-PSD |  |  | 0 |  | 27.7 | LB/H | WITH DUCT FIRING, AVG. OF 3 STACK TESTS | 0 |  |  | 0 | 0 | N |  | AT ALL TIMES
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS. HEAT INPUT LIMITED TO 6,802 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR KEYS TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS KEYS PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE-QUALITY NATURAL GAS EXCLUSIVELY AND GOOD COMBUSTION PRACTICES. | 11 | LB/H | W/OUT DUCT FIRING, AVG. OF 3 STACK TESTS | BACT-PSD |  |  | 0 |  | 15 | LB/H | WITH DUCT FIRING, AVG. OF 3 STACK TESTS | 0 |  |  | 0 | 0 | N |  | AT ALL TIMES
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.006 | LB/MMBTU | EACH CTG; TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0.012 | LB/MMBTU | EACH CTG; TEST PROTOCOL | 0 |  |  | 0 | 0 | N | 2012 | No additional costs were calculated for PM10 or PM2.5 since additional costs to remove condensable particulate would only inflate the costs calculated for PM. Therefore, the costs for PM were considered to be conservative. Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton West ESP = $42,780/ton West Scrubber = $16,663/ton
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.008 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 19.9 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N | 2012 | Cost effectiveness information: No additional costs were calculated for PM10 or PM2.5 since additional costs to remove condensable particulate would only inflate the costs calculated for PM. Therefore, the costs for PM were considered to be conservative. Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet scrubber = $16,663/ton
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0042 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 9 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Emission limit 1 & 2 are for each unit operating without the DB.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0073 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 15.6 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Emission limit 1 & 2 are for each unit operating with the DB.
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion air filters; efficient combustion control; low sulfur natural gas fuel. | 0.0066 | LB/MMBTU | TEST PROTOCOL (3 1-H TESTS IF POSSIBLE) | BACT-PSD |  | N | 90 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit applies to each CTG/HRSG. Limit applies at all times and includes duct burner operation.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 0.014 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 0.014 lb/MMBTU and applies to each CTGHRSG. Test protocol will specify the averaging time. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM10 emissions were assumed the same as PM2.5, so the cost analysis is equivalent. The dollar value year used was 2013. Pulse Jet Fabric Filter Baghouse: minimum of $62,842 per ton. Mechanical Shaker Fabric Filter Baghouse: minimum of $53,684 per ton. Reverse-Air Fabric Filter Bathouse: minimum of $77,328 per ton. Dry ESP (Wire-Plate Type): minimum of $44,525 per ton. Dry ESP (Wire-Pipe Type): minimum of $66,472 per ton. Wet ESP (Wire-Plate Type): minimum of $77,761 per ton. Wet ESP (Wire-Pipe Type): minimum of $110,364 per ton. Venturi Scrubber: minimum of $52,773 per ton.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.8 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit in the table above applies to EACH CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10 which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. Pulse Jet Fabric Filter Baghouse: minimum of $364,528 per ton Mechanical Shaker Fabric Filter Baghouse: minimum of $404,724 per ton Reverse-Air Fabric Filter Baghouse: minimum of $476,689 per ton Dry ESP (Wire-Plate Type): minimum of $478,806 per ton Dry ESP (Wire-Pipe Type): minimum of $303,809 per ton Wet ESP (Wire-Plate Type): minimum of $576,763 per ton Wet ESP (Wire-Pipe Type): minimum of $440,047 per ton Venturi Scrubber: minimum of $1,445,564 per ton
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 0.014 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is for each CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. â€¢ Pulse Jet Fabric Filter Baghouse: minimum of $64,473 per ton â€¢ Mechanical Shaker Fabric Filter Baghouse: minimum of $55,077 per ton â€¢ Reverse-Air Fabric Filter Baghouse: minimum of $79,336 per ton â€¢ Dry ESP (Wire-Plate Type): minimum of $45,681 per ton â€¢ Dry ESP (Wire-Pipe Type): minimum of $68,197 per ton â€¢ Wet ESP (Wire-Plate Type): minimum of $79,780 per ton â€¢ Wet ESP (Wire-Pipe Type): minimum of $113,229 per ton â€¢ Venturi Scrubber: minimum of $54,143 per ton
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas, combustion inlet air filter. | 0.0066 | LB/MMBTU |  | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Fabric Filter Control: over $260,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5). Electrostatic Precipitator (ESP): over $188,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5). Wet ESP: over $165,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5). Venturi Scrubber: over $112,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5).
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Use clean fuel (natural gas) and good combustion practices. | 10.7 | LB/H | HOURLY; EACH CT/HRSG TRAIN | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning and the use of pipeline quality natural gas. | 19.1 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | 19.1 pph is equivalent to 0.005 lb/MMBTU, which includes startup and shutdown The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse Jet Fabric Filter Baghouse: average of $334,000 per ton Mechanical Shaker Fabric Filter Baghouse: average of $370,500 per ton Reverse-Air Fabric Filter Baghouse: average of $437,000 per ton Dry ESP (Wire-Plate Type): average of $438,500 per ton Dry ESP (Wire-Pipe Type): average of $278,500 per ton Wet ESP (Wire-Plate Type): average of $528,500 per ton Wet ESP (Wire-Pipe Type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.1 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | (19.1 lb/h is equivalent to 0.005 lb/MMBTU which includes startup and shutdown). The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10 which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulset jet fabric filter baghouse: average of $334,000 per ton. Mechanical shaker fabric filter baghouse: average of $370,500 per ton. Reverse-air fabric filter baghouse: average of $437,000 per ton. Dry ESP (Wire-plate type): average of $438,500 per ton Dry ESP (Wire-pipe type): average of $278,500 per ton Wet ESP (Wire-plate type): average of $528,500 per ton Wet ESP (Wire-pipe type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton.
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 16 | LB/H | HOURLY; EACH UNIT | BACT-PSD | SIP | N | 0 | N | 12.2 | LB/H | HOURLY; EACH UNIT W/O DUCT BURNER FIRING | 0 |  |  | 0 | 0 | N |  | The cost analysis was for the best scenario: 100 percent capture of PM2.5, where PM and PM10 calculations equaled PM2.5. Pulse Jet Fabric Filter Baghouse: minimum of $174,206 per ton Mechanical Shaker Fabric Filter Baghouse: minimum of $145,172 per ton Reverse-Air Fabric Filter Baghouse: minimum of $232,274 per ton Dry ESP (Wire-Plate Type): minimum of $116,721 per ton Dry ESP (Wire-Pipe Type): minimum of $261,309 per ton Wet ESP (Wire-Plate Type): minimum of $263,153 per ton Wet ESP (Wire-Pipe Type): minimum of $348,412 per ton Venturi Scrubber: minimum of $167,000 per ton
MI-0439 | JACKSON GENERATING STATION | CONSUMERS ENERGY COMPANY | JACKSON | MI | 49203-2174 | USA | BRIAN LABBY | 989-667-5008 | BRIAN.LABBY@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, at 517-284-6790 or at byrnesm@michigan.gov, for technical questions regarding this permit. Thank you. | 118-18 | 4911 | 221112 | 110015804511 | 11/29/2018 &nbsp;ACT | 04/02/2019 &nbsp;ACT | 2019-05-20 | 2019-06-19 | C |  | Natural gas combined-cycle power plant |  | FGLMDB1-6 (6 combined cycle natural gas fired CTG each equipped with a HRSG) | 15.21 | natural gas | 420 | MW | FGLMDB1-6 is 6 combined cycle natural gas fired combustion turbine generators (CTG) each equipped with a heat recovery steam generator (HRSG). Nominal rating 420 MW. Each combustion turbine (CT) is a GE LM6000 with a rating of 440 MMBTU/HR (HHV) and a duct burner rating of 222 MMBTU/HR (HHV). A combined cycle natural gas fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 420 MW electricity production. The HRSG is not capable of operating independently from the CTG. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion inlet air filters, good combustion practices and only combust natural gas. | 4.9 | LB/H | 24-HR AVG, EACH HR UNIT OPERATES, EACH | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 4.9 lb/hr on a 24-hr rolling average determined each hour the unit operates and applies to each unit. The limit is also per stack during periods when the turbine operates alone and when the turbine operates in conjunction with its respective duct burner. The limits do not apply during startup and shutdown. This limit equates to approximately 0.0078 lb/MMBTU.
*MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2019-10-22 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2--A 667 MMBTU/H natural gas fired CTG with a HRSG. | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2 is a nominally rated 667 MMBTU/H natural gas fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas fired duct burner rated at 204 MMBTU/h to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR and oxidation catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning, and good combustion practices. | 6.02 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 of 6.02 lb/h applies during all operating modes. Add-on control technology was not technically feasible; however, options were evaluated and it was determined they were not economically feasible.
*MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2019-10-22 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1--A 667 MMBTU/H NG fired combustion turbine generator coupled with a heat recovery steam generator (HRSG) | 15.21 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR) and oxidation catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning, and good combustion practices. | 6.02 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is during all operating modes. Add-on control technology was not technically feasible; however, options were evaluated and it was determined they were not economically feasible.
*MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2019-12-19 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur fuel and good combustion practices. | 0.006 | LB/MMBTU | HOURLY; EACH UNIT | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The lowest cost (for a fabric filter) was greater than $87,000/ton of total PM controlled. Therefore, add-on controls were not considered economically feasible for particulate control.
NJ-0079 | WOODBRIDGE ENERGY CENTER | CPV SHORE, LLC | MIDDLESEX | NJ | 7095 | USA | MARK TURNER | (415)293-1463 | MTURNER@CPV.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Mr. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS, yogesh.doshi@dep.state.nj.us; phone 609-633-7249 | 18940 - BOP110003 | 4911 | 221112 | 110055590953 | 10/12/2011 &nbsp;ACT | 07/25/2012 &nbsp;ACT | 2012-11-27 | 2018-04-17 | A |  | Woodbridge Energy Center (WEC), proposed at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, would be a new, highly efficient, 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,307 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, one small dew point fuel gas heater (fuel gas heater), a mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Other Permitting Information: Facility-Wide Greenhouse Gas (GHG) emissions as CO2e emissions= 2,073,645 tons per year | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural gas | 40297.6 | mmcubic ft/year | Woodbridge Energy Center (WEC), located at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, will be a new 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) each with a maximum rated heat input of 2,307 million British thermal units per hour (MMBtu/hr), that will utilize pipeline natural gas only, with 2 HRSGs, 2 Duct Burners (each 500 MMbtu/hr). | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Good Combustion Practices and use of Natural gas,a clean burning fuel. | 19.1 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD |  | U | 0 | Y | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Compliance Verified by Stack test in 2016, TPM10 Emission limit 1 was 5.47 LB/H
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | Combined Cycle Combustion Turbine -Siemens turbine without Duct Burner | 15.21 | Natural gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each Siemens combustion turbine will be 2,356 MMBtu/hr(HHV) | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 13 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITH DUCT BURNER - SIEMENS | 15.21 | Natural Gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two Siemens turbines and two associated duct burners) The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 14 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITH DUCT BURNER - GENERAL ELECTRIC | 15.21 | Natural gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each General Electric combustion each turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 MMBtu/hr duct burner | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas only as a clean burning fuel | 14.6 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | BACT-PSD | OPERATING PERMIT | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This project not subject to BACT for PM<2.5 microns.
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITHOUT DUCT BURNER - GENERAL ELECTRIC | 15.21 | Natural Gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each General Electric combustion turbine will be 2,312 MMBtu/hr(HHV) | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of Natural Gas as a clean burning fuel | 12.7 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | BACT-PSD | OPERATING PERMIT | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine without Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burner. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 10 | LB/H | AVERAGE OF THREE ONE HOUR STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Use of Natural gas a clean burning fuel | 21.55 | LB/H | AVERAGE OF THREE STACK TEST RUNS | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0.0069 | LB/MMBTU | AVERAGE OF THREE STACK TEST RUNS | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas with Duct Burner | 15.21 | natural gas | 4000 | h/yr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | COMPLIANCE BY STACK TESTING | 18.3 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY STACK TESTING
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas without Duct Burner | 15.21 | Natural Gas | 8040 | H/YR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 11.7 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY STACK TESTING
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Siemens, without duct burners | 15.21 | Natural Gas | 515600 | MMSCF/rolling 12-months | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process without duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | clean burning fuel, only natural gas | 13.3 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 61.3 | T/YR | PER ROLLING 12-MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for both PM10 and PM2.5 together. Additional limit: 0.0047 lb PM10/PM2.5 per MMBtu of heat input. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Siemens, with duct burners | 15.21 | Natural Gas | 51560 | MMSCF/rolling 12-MO | Two Siemens 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process with duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | clean burning fuel, only natural gas | 14 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 61.3 | T/YR | PER ROLLING 12-MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for both PM10 and PM2.5 together. Additional limit: 0.0055 lb PM10/PM2.5 per MMBtu of heat input. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Mitsubishi, without duct burners | 15.21 | Natural Gas | 47917 | MMSCF/rolling 12-MO | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process without duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | clean burning fuel, only natural gas | 11.3 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 44.2 | T/YR | PER ROLLING 12-MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for both PM10 and PM2.5 together. Additional limit: 0.00384 LB PM/PM2.5 per MMBtu of heat input. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Mitsubishi, with duct burners | 15.21 | Natural Gas | 47917 | MMSCF/rolling 12-MO | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process with duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | clean burning fuel, only natural gas | 10.1 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 44.2 | T/YR | PER ROLLING 12-MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for both PM10 and PM2.5 together. Additional limit: 0.00373 LB PM10/PM2.5 per MMBtu of heat input. T/YR limit is for 2 turbines.
OH-0356 | DUKE ENERGY HANGING ROCK ENERGY | DUKE ENERGY HANGING ROCK, LLC | LAWRENCE | OH | 28207 | USA | ANDREW ROEBEL | 513-287-2356 | ANDREW.ROEBEL@DUKE-ENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110487 | 4911 | 221112 | 110012567203 | 07/17/2012 &nbsp;ACT | 12/18/2012 &nbsp;ACT | 2013-10-01 | 2016-05-04 | C |  | Four Natural Gas Fired Combustion Turbines, with Duct Burners; Combined Cycle, each 172 MW | This is a modification of RBLC OH-0252 to remove operating hour restrictions on duct burners, with changes to hourly limits without increasing the annual emission limitations. Original PTI # was 07-00503 | Turbines (4) (model GE 7FA) Duct Burners Off | 15.21 | NATURAL GAS | 172 | MW | Four GE 7FA combined cycle turbines, dry low NOx burners and selective catalytic reduction. These limits are for each of the 4 turbines individually, while operating with the duct burners off. This permit is a modification to RBLC OH-0252 to remove hourly restrictions on duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Burning natural gas in an efficient combustion turbine | 15 | LB/H |  | BACT-PSD | NSPS , SIP | U | 0 | N | 87.2 | T/YR | PER ROLLING 12 MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for each individual turbine. Subject to Part 60 Subparts Da. If required test Methods 1 through 5 and Method 202.
OH-0356 | DUKE ENERGY HANGING ROCK ENERGY | DUKE ENERGY HANGING ROCK, LLC | LAWRENCE | OH | 28207 | USA | ANDREW ROEBEL | 513-287-2356 | ANDREW.ROEBEL@DUKE-ENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110487 | 4911 | 221112 | 110012567203 | 07/17/2012 &nbsp;ACT | 12/18/2012 &nbsp;ACT | 2013-10-01 | 2016-05-04 | C |  | Four Natural Gas Fired Combustion Turbines, with Duct Burners; Combined Cycle, each 172 MW | This is a modification of RBLC OH-0252 to remove operating hour restrictions on duct burners, with changes to hourly limits without increasing the annual emission limitations. Original PTI # was 07-00503 | Turbines (4) (model GE 7FA) Duct Burners On | 15.21 | NATURAL GAS | 172 | MW | Four GE 7FA combined cycle turbines, dry low NOx burners and selective catalytic reduction. These limits are for each of the 4 turbines individually, while operating with the duct burners on. This permit is a modification to RBLC OH-0252 to remove hourly restrictions on duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Burning natural gas in an efficient combustion turbine | 19.9 | LB/H |  | BACT-PSD | NSPS , SIP | U | 0 | N | 87.2 | T/YR | PER ROLLING 12 MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for each turbine individually. Subject to Part 60 Subparts Da. If required test Methods 1 through 5 and Method 202.
OH-0360 | CARROLL COUNTY ENERGY | CARROLL COUNTY ENERGY | CARROLL | OH | 44615 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0113762 | 4911 | 221112 | 110064671127 | 04/11/2013 &nbsp;ACT | 11/05/2013 &nbsp;ACT | 2015-12-30 | 2019-04-01 | A |  | Natural gas fired combined cycle gas turbine electric generating station of nominal capacity of 742 MW | Installation of a natural gas-fired combined cycle combustion turbine electric utility power plant, nominally rated at 742 MW. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural Gas | 2045 | MMBTU/H | Two identical General Electric 7FA combined cycle combustion turbine (each at 2,045 mmBtu/hr heat input turbine at ISO conditions and 566 mmBtu/hr heat input duct burner, HHV) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. All throughputs and emission limits are for each turbine. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | natural gas only | 19.8 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 85.7 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | Limits are for each turbine. 0.0078 lb/mmbtu and 19.8 lb/h for turbine and duct burner, except startup and shutdown. 0.0108 lb/mmbtu and 12.4 lb/h for turbine only, except startup and shutdown. 85.7 t/yr per rolling 12 month period including startup and shutdown.
OH-0363 | NTE OHIO, LLC |  | BUTLER | OH | 45044 | USA | MICHAEL SCHUSTER | (904)436-6896 | MSCHUSTER@NTEENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0116610 | 4911 | 221112 | 110070379584 | 04/07/2014 &nbsp;ACT | 11/05/2014 &nbsp;ACT | 2019-02-22 | 2019-04-01 | A |  | Combined-cycle, natural gas-fired power plant | Initial installation of either one (1) Mitsubishi Hitachi Power Systems Americas M501JAC or one (1) Mitsubishi Hitachi Power Systems Americas M501GAC single power block in a 1x1 combined-cycle multi-shaft configuration, including a combustion turbine and heat recovery steam generator with duct burners and a steam turbine to be known as the Middletown Energy Center. | Turbine generator with HRSG and duct burners (P001) | 15.21 | Natural gas | 3278.5 | MMBTU/H | Combined-cycle combustion turbine generator (CTG) with heat recovery steam generator (HRSG), natural gas-fired, including duct burners (DB). Permit was for either Mitsubishi Hitachi Power Systems America M501GAC or M501JAC. The M501GAC was installed. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | Exclusive use of natural gas, high efficiency inlet air filters and low NOx burner. | 20 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 59.4 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  |  | 0 | 0 | N |  | 20.0 lb/h and 5.70x10-3 lb/mmbtu with duct burner, except startup and shutdown. 10.8 lb/h and 3.80x10-3 lb/mmbtu turbine only, except startup and shutdown. 59.4 tons per rolling 12 month period for all operating modes, including startup.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 1 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2022 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices along with clean fuels | 0.0068 | LB/MMBTU | HHV, 3 HR AVG. SEE NOTES. | BACT-PSD |  | U | 0 | U | 58.62 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  |  | 0 | 0 | N |  | Limits are for single turbine except as noted. 0.0068 lb/mmbtu HHV, 3 hour average with duct burners. 9.5 lb/h, 3 hour average without duct burners. 15.8 lb/h, 3 hour average with duct burners. 58.62 t/yr per rolling 12 month period.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 2 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2144 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices along with clean fuels | 0.0085 | LB/MMBTU | HHV, 3 HR AVG. SEE NOTES. | BACT-PSD |  | U | 0 | U | 86.7 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  |  | 0 | 0 | N |  | Limits are for single turbine except as noted. 0.0085 lb/mmbtu HHV, 3 hour average with and without duct burners. 15.9 lb/h, 3 hour average without duct burners. 22.2 lb/h, 3 hour average with duct burners. 86.7 t/yr per rolling 12 month period.
OH-0366 | CLEAN ENERGY FUTURE - LORDSTOWN, LLC | CLEAN ENERGY FUTURE - LORDSTOWN, LLC | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0117655 | 4911 | 221112 | 110070396317 | 09/17/2014 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2019-02-27 | 2019-06-19 | A |  | 962 MW (gross winter output) combined cycle gas turbine (CCGT) facility | Initial installation permit for the construction of the Lordstown Energy Center - a nominal 940 MW combined cycle gas turbine (CCGT) facility. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 2725 | MMBTU/H | Combined cycle combustion turbine (2,725 MMBtu/hr heat input turbine at ISO conditions and 179 MMBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Limits and throughputs are for single turbine. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuel | 14.9 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 62.6 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 14.9 lb/h and 4.9x10-3 lb/mmbtu with duct burner, except startup and shutdown. 13.1 lb/h and 6.8x10-3 lb/mmbtu turbine only, except startup and shutdown. 62.6 tons per rolling 12 month period for all operating modes, including startup.
OH-0367 | SOUTH FIELD ENERGY LLC | SOUTH FIELD ENERGY LLC | COLUMBIANA | OH | 43968 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0119495 | 4911 | 221112 | Not Found | 09/14/2015 &nbsp;ACT | 09/23/2016 &nbsp;ACT | 2019-02-28 | 2019-06-19 | A |  | 1150 MW combined-cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the South Field Energy facility, a nominal 1,150 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in Wellsville, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3131 | MMBTU/H | Two identical combined cycle combustion turbine (3,131 MMBtu/hr heat input turbine at ISO conditions, natural gas firing with evaporative cooler on and 800 MMBtu/hr maximum heat input natural gas-fired duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), catalytic oxidizer, and wet injection for ULSD firing. Heat input for ULSD firing at ISO conditions, with evaporative cooler on is 3,173 MMBtu/hr. Throughputs and limits are for single turbine except as noted. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Good combustion controls | 25 | LB/H | NAT GAS, WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 128.9 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  |  | 0 | 0 | N |  | 6.9x10-3 lb/mmbtu, hourly average, natural gas, with duct burner. 7.7x10-3 lb/mmbtu, hourly average, natural gas, turbine only. 1.9x10-2 lb/mmbtu, hourly average, ultra low sulfur diesel. 25.0 lb/h with duct burner (including startup and shutdown). 16.16 lb/h without duct burner (including startup and shutdown). 55.4 lb/h for ultra low sulfur diesel (except startup and shutdown). 128.9 t/yr per rolling 12 month period for all operating modes, including startup and shutdown. When firing ultra low sulfur diesel, 77.4 lb/h during startup and shutdown.
OH-0370 | TRUMBULL ENERGY CENTER | TRUMBULL ENERGY CENTER | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122331 | 4911 | 221112 | Not Found | 03/23/2017 &nbsp;ACT | 09/07/2017 &nbsp;ACT | 2019-03-05 | 2019-06-19 | A |  | 940 MW combined cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the Trumbull Energy Center, a nominal 940 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in the Village of Lordstown, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3025 | MMBTU/H | Two identical combined cycle combustion turbine (3,025 mmBtu/hr heat input turbine at ISO conditions and 237 mmBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Throughputs and limits are for single turbine except as noted. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Good combustion controls and low sulfur fuel | 15.2 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 64.4 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 4.6x10-3 lb/mmbtu with duct burners, 6.0x10-3 lb/mmbtu without duct burners, 15.2 lb/h with duct burner, 12.9 lb/h without duct burner (each limit except startup and shutdown). 64.4 t/yr per rolling 12 month period for all operating modes, including startup and shutdown.
OH-0372 | OREGON ENERGY CENTER | OREGON ENERGY CENTER | LUCAS | OH | 43616 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0121049 | 4911 | 221112 | Not Found | 06/27/2016 &nbsp;ACT | 09/27/2017 &nbsp;ACT | 2019-03-06 | 2019-06-19 | A |  | Combined cycle gas turbine (CCGT) facility | Installation of natural gas-fired combined cycle combustion turbine power plant. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3055 | MMBTU/H | Combined cycle combustion turbine (3,055 mmBtu/hr heat input turbine at ISO conditions and 221.3 mmBtu/hr heat input duct burner) with dry low NOX combustors, selective catalytic reduction (SCR), and catalytic oxidation. All heat values are on a HHV basis. Throughputs and limits are for single turbine except as noted. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices and pipeline quality natural gas | 15.4 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 65.26 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 4.6x10-3 lb/mmbtu with duct burners. 6.0x10-3 lb/mmbtu without duct burners. 15.4 lb/h with duct burner (except startup and shutdown). 14.0 lb/h without duct burner (except startup and shutdown). 65.26 t/yr per rolling 12 month period for all operating modes, including startup.
OH-0374 | GUERNSEY POWER STATION LLC | GUERNSEY POWER STATION LLC | GUERNSEY | OH | 43723 | USA | MARY KING | (317)447-4513 | MARY@APEXPOWERGROUP.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122594 | 4911 | 221112 | 110070379546 | 04/14/2017 &nbsp;ACT | 10/23/2017 &nbsp;ACT | 2019-03-08 | 2019-06-19 | A |  | 1,650 MW combined cycle combustion turbine electrical generating facility | Installation PTI for a new 1,650 MW combined cycle natural-gas fired turbine plant and associated auxiliary boiler, firewater pumps, emergency generators and fuel gas heaters | Combined Cycle Combustion Turbines (3, identical) (P001 to P003) | 15.21 | Natural gas | 3516 | MMBTU/H | Three identical Combustion Turbines; GE 7HA.02 natural gas-fired lean pre-mix combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,516 MMBtu/hr HHV at 100% load and -18Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 997 MMBtu/hr HHV controlled with catalytic oxidation and selective catalytic reduction (SCR) and cooled with an air-cooled condenser (ACC) used to generate electricity. Throughputs and limits are for a single turbine except as noted. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | pipeline quality natural gas | 0.0073 | LB/MMBTU | SEE NOTES. | BACT-PSD |  | U | 0 | U | 23.3 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | Limits are for single turbine except as noted. 0.0073 lb/mmbtu with duct burners and without duct burners. Both excluding startup and shutdown. 12.30 lb/h without duct burners. 23.30 lb/h with duct burners. Both excluding startup and shutdown. 290.39 t/yr per rolling 12 month period total for all 3 turbines.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | General Electric Combustion Turbine (P004) | 15.21 | Natural gas | 3544 | MMBTU/H | General Electric model 7HA.02 natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,544 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | natural gas or a natural gas and ethane mixture only | 0.0036 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 12.1 | LB/H |  | 0 |  | SEE NOTES | 0 | 0 | N |  | 53.0 t/yr per rolling, 12-month period, including start-up and shutdown emissions.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Mitsubishi Combustion Turbine (P005) | 15.21 | Natural gas | 3320 | MMBTU/H | Mitsubishi Model 501JAC natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,320 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 108 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | natural gas or a natural gas and ethane mixture only | 0.004 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 12.6 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.004 lb/mmbtu and 12.60 lb/h with duct burner (except startup and shutdown). 0.0037 lb/mmbtu and 12.3 lb/h without duct burner (except startup and shutdown). 55.2 t/yr per rolling 12 month period for all operating modes, including startup.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Siemens Combustion Turbine (P006) | 15.21 | Natural gas | 3602 | MMBTU/H | Siemens Model SCC6-8000H natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,602 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 667 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | natural gas or a natural gas and ethane mixture only | 0.0057 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 19.8 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.0057 lb/mmbtu and 19.8 lb/h with duct burner (except startup and shutdown). 0.006 lb/mmbtu and 13 lb/h without duct burner (except startup and shutdown). 86.7 t/yr per rolling 12 month period for all operating modes, including startup.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and pipeline quality natural gas | 0.0052 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 18.4 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.00522 lb/mmbtu and 18.4 lb/h with duct burner. 0.00735 lb/mmbtu and 12.0 lb/h without duct burner. 80.2 tons per rolling 12 month period for all operating modes.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and pipeline quality natural gas | 0.005 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 17.7 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.005 lb/mmbtu and 17.7 lb/h with duct burner. 0.00444 lb/mmbtu and 14.10 lb/h without duct burner. 77.5 tons per rolling 12 month period for all operating modes.
*PA-0298 | FUTURE POWER PA/GOOD SPRINGS NGCC FACILITY | FUTURE POWER PA INC | SCHUYLKILL | PA | 17980 | USA | JAMES PALUMBO | 570-342-5200 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MARK J. WEJKSZNER NORTHEAST REGION AIR PROGRAM MANAGER 2 Public Square Wilkes-Barre, PA 18711 570-826-2357 | 54-00082A | 4911 | 221112 | 110062854870 | 05/03/2013 &nbsp;ACT | 03/04/2014 &nbsp;ACT | 2014-04-17 | 2020-02-19 | A |  | Natural gas-fired combined-cycle electric generation facility that is designed to generate up to 346 MW nominal, using a combustion turbine generator and a heat recovery steam generator that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. The Turbine is rated at 2,267 MMBTU/hr HHV (2,042 MMBTU/hr LHV). The Duct burner is rated at 134.3 MMBTU/hr HHV (120 MMBTU/hr LHV). The proposed project will also include a diesel engine-driven emergency generator; a diesel engine-driven firewater pump; a multi-cell evaporative cooling tower; and associated emission control systems, tanks, and other plant equipment. |  | Turbine, COMBINED CYCLE UNIT (Siemens 5000) | 15.21 | Natural Gas | 2267 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 15.6 | LB/H | WITH DUCT BURNER | BACT-PSD | NSPS | U | 0 | U | 58.7 | T/YR | BASED ON A 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N
PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2018-12-21 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large combustion turbine | 15.21 | Natural Gas | 0 |  | This process entry is for operations with the duct burner. Limits entered are for each turbine. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices with the use of low ash/sulfer fuels | 0.0039 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 11.8 | LB/HR |  | 0 |  |  | 0 | 0 | N
PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2018-12-21 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two combined cycle turbines with out duct burner | 15.21 | Natural Gas | 2291.64 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode, the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. (Operational limits are for each CCCT NG-fired without duct burner) | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA/OAR 201 or 201A, and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.0068 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative Emissions from both CCCT in any 12-month period
PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2018-12-21 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two Combine Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 3001.57 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. . (Operational limits are for each CCCT NG-fired with duct burner) | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA/OAR 201 or 201A, and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.0066 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 159.1 | TONS | ANY 12-MONTH PERIOD | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative emissions from both CCCT in any 12-month period
PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Combustion turbine with duct burner | 15.21 | Natural gas | 3304.3 | MMBtu/hr | Limits are for each CCCT and yearly limits are for cumulative turbine and duct burner. Duct burner throughput is 637.9 MMBtu/hr. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive natural gas, high-efficiency inlet air filters and DLN | 0.0059 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 48.2 | TONS | YEAR | 0 |  |  | 0 | 0 | N
PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG with duct burner NG only | 15.21 | Natural Gas | 3338 | MMBtu/hr | Emission limits are for each turbine operating with duct burner and do not include startup/shutdown emissions. Tons per year limits is a cumulative value for all three CCCT. CEMS for NOx, CO, and O2. Each CCCT and duct burner have 5 operational scenarios: 1 CCCT with duct burner fired - fueled by NG only 2 CCCT with duct burner fired - fueled by NG blend with ethane 3 CCCT without duct burner fired - fueled by NG only 4 CCCT without duct burner fired - fueled by NG blend with ethane 5 CCCT without duct burner fired - fueled by ULSD (Limited to emergency use only) | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuel, good combustion practices | 0.005 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 131.5 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N |  | lb/MMBtu limit is for each turbine and duct burner, TPY is a cumulative total
PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG without duct burner NG only | 15.21 | Natural gas | 0 |  | Emission limits are for each turbine fueled by NG and operating without duct burner being fired and do not include startup/shutdown emissions. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuels and good combustion practices | 0.0068 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit is for each turbine and HRSG with the duct burner not fired.
PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064098541 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2018-12-21 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine With Duct Burner | 15.21 | Natural Gas | 3727 | MMBtu/hr | DLN burner, SCR, Oxidation Catalyst and shall maintain and operate the sources and associated air cleaning devices in accordance with good engineering practice. shall install, certify, maintain and operate continuous emission monitoring systems (CEMS) for nitrogen oxides, carbon monoxide, carbon dioxide, and ammonia emissions on the exhaust of each combined-cycle powerblock. Emissions limits are for each combustion turbine/duct burner block. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 0.0063 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 13.9 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 58 tpy 12-month rolling basis
*PA-0315 | HILLTOP ENERGY CENTER, LLC | HILLTOP ENERGY CENTER, LLC | GREENE | PA | 15351 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 30-00233B | 4911 | 221112 | 110066828222 | &nbsp; | 04/12/2017 &nbsp;ACT | 2018-12-21 | 2019-03-26 | U |  | The project consists of a single power block in a one-on-one (1x1), combined cycle, single shaft configuration, including a combustion turbine (CT) and heat recovery steam generator (HRSG) with a steam turbine (ST). â€¢ One (1) 3,509 MMBtu/hr General Electric International, Inc. (GE) model no. GE 7HA.02 natural gas-fired combined cycle combustion turbine equipped with a heat recovery steam generator (HRSG) with supplemental 981.4 MMBtu/hr natural gas fired duct burners; controlled by selective catalytic reduction and oxidation catalyst. â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. â€¢ One (1) 500 gallon firewater pump diesel storage tank. â€¢ One (1) 35,000 gallon 19% aqueous ammonia storage tank. â€¢ Lubricating oil storage tanks. â€¢ Miscellaneous components in natural gas service, and SF6 containing circuit breakers; controlled by leak detection and repair (LDAR). â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. | The project consists of a single power block in a one-on-one (1x1), combined cycle, single shaft configuration, including a combustion turbine (CT) and heat recovery steam generator (HRSG) with a steam turbine (ST). â€¢ One (1) 3,509 MMBtu/hr General Electric International, Inc. (GE) model no. GE 7HA.02 natural gas-fired combined cycle combustion turbine equipped with a heat recovery steam generator (HRSG) with supplemental 981.4 MMBtu/hr natural gas fired duct burners; controlled by selective catalytic reduction and oxidation catalyst. â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. â€¢ One (1) 500 gallon firewater pump diesel storage tank. â€¢ One (1) 35,000 gallon 19% aqueous ammonia storage tank. â€¢ Lubricating oil storage tanks. â€¢ Miscellaneous components in natural gas service, and SF6 containing circuit breakers; controlled by leak detection and repair (LDAR). â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. | Combustion Turbine without Duct Burner | 15.21 | Natural Gas | 3509 | MMBtu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0072 | LB | MMBTU | BACT-PSD |  | U | 0 | U | 105.28 | TPY |  | 0 |  |  | 0 | 0 | N
*PA-0319 | RENAISSANCE ENERGY CENTER | APV RENAISSANCE PARTNERS | GREENE | PA | 15320 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 30-00235A | 4911 | 221112 | Not Found | 03/17/2017 &nbsp;ACT | 08/27/2018 &nbsp;ACT | 2019-03-26 | 2019-10-11 | U |  | This Plan Approval is to allow the construction and temporary operation of a natural gas-fired combined cycle power plant to be located in Monongahela Township, Greene County. with Two (2) Siemens, SGT6-8000H (or equivalent), natural gas-fired combustion turbines 3,580 MMBtu/hr heat input rating (LHV) each (controlled with low NOx burners), including natural gas-fired duct burners, 914.1 MMBtu/hr heat input rating each; controlled by Ultra-low NOx combustors, SCR, and oxidation catalysts; 1,127 MW total net generating capacity. One (1) natural gas-fired auxiliary boiler, 90 MMBtu/hr heat input rating. One (1) Cummins model #CFP15E-F20 (or equivalent), diesel-fired fire pump engine, 411 bhp rating; including One (1) diesel fuel storage tank, 2,175 gallons One (1) Caterpillar 3516 (or equivalent), diesel-fired emergency generator engine rated at 2000 kW. Miscellaneous components in natural gas service, and circuit breakers; controlled by leak detection and repair (â€œLDARâ€). One (1) aqueous ammonia (19%) storage vessel rated at 19,000 gallons (or as determined during final design). |  | COMBUSTION TURBINE UNIT w/o DUCT BURNERS UNIT | 15.21 | Natural Gas | 2665.9 | MMBtu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0043 | LB/MMBTU | HR | BACT-PSD |  | U | 0 | U | 121.72 | TPY |  | 0 |  |  | 0 | 0 | N
TX-0590 | KING POWER STATION | PONDERA CAPITAL MANAGEMENT GP INC | HARRIS | TX | 77044 | USA | MARK CHRISOS | (781) 993-3036 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Katherine Stinchcomb (512) 239-1583 katherine.stinchcomb@tceq.texas.gov | PSDTX1125 AND N75, 84289 | 4911 | 221119 | 110040440902 | 04/05/2010 &nbsp;ACT | 08/05/2010 &nbsp;ACT | 2011-08-26 | 2020-02-03 | A |  | Four combined-cycle natural gas-fired combustion turbines | State permit number 84289 Nonattainment permit number N75 | Turbine | 15.21 | natural gas | 1350 | MW | The plant will be designed to generate 1,350 nominal megawatts of power. There are two configuration scenarios: either four Siemens SGT6-5000F CTGs in combined-cycle mode (Scenario A) or four GE Frame 7FA CTGs in combined cycle mode (Scenario B). Scenario B also includes one or two auxiliary boilers. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | use of low ash fuel (natural gas or low sulfur diesel as a backup) | 11.1 | LB/H |  | BACT-PSD |  | U | 0 | U | 19.8 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 represents Scenario A (Siemens turbines) and Emission Limit 2 represents Scenario B (GE turbines).
TX-0618 | CHANNEL ENERGY CENTER LLC | CHANNEL ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX955M1, N021M1, 42179 | 4911 | 221112 | 110034690564 | 09/04/2012 &nbsp;ACT | 10/15/2012 &nbsp;ACT | 2012-10-24 | 2020-02-03 | B |  | Combustion turbine (Siemens 501F)/duct burners (475 MMBtu/hr) with heat recovery steam generator | 42179 and N021M1 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | The turbine is a Siemens 501F rated at a nominal 180 MW and the duct burner will have a maximum design heat input of 475 MMBtu/hr. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion and the use of gaseous fuel | 27 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0619 | DEER PARK ENERGY CENTER | DEER PARK ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX979M2, N036M2, 45642 | 4911 | 221112 | 110017743254 | 08/13/2012 &nbsp;ACT | 09/26/2012 &nbsp;ACT | 2012-10-25 | 2020-02-03 | B |  | The Deer Park Energy Center is a combined cycle cogeneration facility consisting of five Siemens/Westinghouse 501F combustion turbine generators, each with a 725 MMBtu/hr duct burner and heat recovery steam generator. | 45642 and N036M2 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | natural gas-fired combined cycle turbine generator with a heat recovery steam generator equipped with a duct burner. The turbine is a Siemens 501F rated at a nominal 180 megawatts and the DB will have a maximum design rate capability of 725 million British thermal units per hour | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion and the use of natural gas | 27 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0620 | ES JOSLIN POWER PLANT | CALHOUN PORT AUTHORITY | CALHOUN | TX |  | USA | CHARLES HAUSMANN | 361-987-2813 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1256, 96336 | 4911 | 221112 | 110001866641 | 05/31/2012 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2012-11-14 | 2020-02-03 | B |  | Three gas-fired combined cycle turbine generators, including a steam turbine generator, to replace the existing steam boiler/turbine generator. | 96336 | Combined cycle gas turbine | 15.21 | natural gas | 195 | MW | The three combustion turbine generators (CTG) will be the General Electric 7FA, each with a maximum base-load electric power output of approximately 195 megawatts (MW). The steam turbine is rated at approximately 235 MW. This project also includes the installation of two emergency generators, one fire water pump, and auxiliary equipment. No duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion and natural gas as fuel | 18 | LB/H | PER TURBINE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041470431 | 02/24/2015 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2020-01-31 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | efficient combustion, natural gas fuel | 43 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0751 | EAGLE MOUNTAIN STEAM ELECTRIC STATION | EAGLE MOUNTAIN POWER COMPANY LLC | TARRANT | TX |  | USA | PAUL COON | 214-875-8647 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.Alvirez@tceq.texas.com | 117026, PSDTX1390, N194 | 4911 | 221122 | 110005028638 | 03/26/2015 &nbsp;ACT | 06/18/2015 &nbsp;ACT | 2015-06-22 | 2016-07-06 | B |  | Eagle is proposing to construct two new combined cycle combustion turbines (CTG) which will generate electric power for sale on the wholesale electric market. The ancillary equipment includes an auxiliary boiler, a firewater pump, an emergency generator, a steam turbine, and various support facilities. |  | Combined Cycle Turbines (&gt;25 MW) â€“ natural gas | 15.21 | natural gas | 210 | MW | Two power configuration options authorized Siemens â€“ 231 MW + 500 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 210 MW + 349.2 MMBtu/hr duct burner | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 35.47 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 81.88 | T/YR |  | 0 |  |  | 0 | 0 | N |  | Good combustion practices, low sulfur fuel
TX-0767 | LON C. HILL POWER STATION | LON C. HILL, L.P. | NUECES | TX |  | USA | MATTHEW LINDSEY | 713-358-9734 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem, 512-239-1310, Tzvi.Shalem@tceq.texas.gov | 114911 AND PSDTX1380 | 4911 | 221122 | 110000501127 | 07/15/2015 &nbsp;ACT | 10/02/2015 &nbsp;ACT | 2015-09-23 | 2016-07-06 | A |  | The Lon C. Hill Power Station (LCHP) will include two natural gas-fired combined cycle combustion turbines (CTGs) equipped with dry low NOx burners (DLNs), heat recovery steam generators (HRSG), and natural gas-fired duct burners (DBs). Ancillary equipment includes evaporative coolers or inlet chillers, a single steam turbine (ST), auxiliary boiler, emergency generator, firewater pump, two cooling towers, oil water separator, degreaser, two diesel storage tanks, gasoline storage tank, selective catalytic reduction (SCR) and ammonia (NH3) handling systems including an NH3 storage tank, and two water tanks. The LCHP will be a 2x1 combined cycle power plant consisting of two CTGs, two HRSGs and one ST. The CTGs and ST will be one of two options: two Siemens SCC6-5000 CTGs and a SST6-5000 ST, or two General Electric 7FA CTGs and a D-11 ST. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 195 | MW | Two power configuration options authorized Siemens â€“ 240 MW + 250 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 195 MW + 670 MMBtu/hr duct burner | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and use of pipeline quality natural gas | 16 | LB/HR |  | BACT-PSD | NSPS | N | 0 | U | 109.5 | TPY |  | 0 |  |  | 0 | 0 | N |  | Lbs/hr limit based on one stack and TPY is based on both turbines
TX-0773 | FGE EAGLE PINES PROJECT | FGE EAGLE PINES, LLC | CHEROKEE | TX |  | USA | EMERSON FARRELL | 281-407-7749 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, 512-239-1095, Erik.Hendrickson@tceq.texas.gov | 131316, PSDTX1454, AND GHGPSDT | 4911 | 221112 | UNKNOWN | 09/10/2015 &nbsp;ACT | 11/04/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | The FGEEP Project will include three natural gas-fired combined cycle (NGCC) power blocks, each block comprised of two gas-fired combustion turbines, two supplemental fired duct burners (DBs) heat recovery steam generators (HRSGs), and one steam turbine. FGEEP selected Alstom GT36 combustion turbines (CTs), each nominally rated at 321 megawatts (MW). Each HRSG is equipped with DBs that will have a maximum design heat input capacity of 799 million British thermal units per hour (MMBtu/hr). The CTs and DBs are fueled with pipeline quality natural gas. Each power block will also have a steam turbine generator designed to produce approximately 502 MW with the additional duct firing. Each of the three blocks will include the following ancillary equipment: one multi-cell condenser/cooling tower, one emergency generator, one firewater pump, two diesel storage tanks, and pressurized aqueous ammonia storage tanks. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 321 | MW | Alstom GT36 combustion turbines (321 MW)+ 799 million British thermal units per hour (MMBtu/hr) duct burner | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 21.4 | LB/H |  | BACT-PSD |  | U | 0 | U | 93.7 | T/YR |  | 0 |  |  | 0 | 0 | N
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES, LOW SULFUR FUEL | 19.35 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0789 | DECORDOVA STEAM ELECTRIC STATION | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas.gov | 107569 AND PSDTX1432 | 4911 | 221112 | 110008149217 | 12/23/2015 &nbsp;ACT | 03/08/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | The DeCordova Station will consist of two combustion turbine generators (CTGs) operating in simple cycle or combined cycle modes. The gas turbines will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE). Simple cycle operations limited to 2,500 hr/yr. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND LOW SULFUR FUEL | 35.47 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.21 | natural gas | 10 | M TONNES/YR | Four GE Frame 7E gas turbines for refrigeration and compression at the site | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 11.07 | LB/H |  | BACT-PSD |  | N | 0 | U | 42.15 | T/YR |  | 0 |  |  | 0 | 0 | N |  | Dry low NOx burners, good combustion practices, pipeline quality sweet natural gas fuel
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Simple Cycle Electrical Generation Gas Turbines 15.210 | 15.21 | natural gas | 34 | MW | Nine GE PGT25+G4 gas turbines for electrical generation at the site at 34 MW/turbine | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Equipment specifications & work practices - Good combustion practices and use of low carbon, low sulfur fuel | 2.32 | LB/H |  | BACT-PSD |  | N | 0 | U | 8.84 | T/YR |  | 0 |  |  | 0 | 0 | N
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Combined Cycle Turbine with Heat Recovery Steam Generator, fired Duct Burners, and Steam Turbine Generator | 15.21 | NATURAL GAS | 426 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines with HRSGs and Steam Turbine Generators | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; good combustion practices | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | PIPELINE NATURAL GAS, GOOD COMBUSTION | 125.7 | TON/YR |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
VA-0315 | WARREN COUNTY POWER PLANT - DOMINION | VIRGINIA ELECTRIC AND POWER COMPANY | WARREN | VA | 22630 | USA | ROBERT BISHA | 804-273-3010 | ROBERT.M.BISHA@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Manager, Mr. Janardan Pandey, by phone at (540) 574-7817 or by e-mail: Janardan.Pandey@deq.virginia.gov | 81391-007 | 4911 | 221112 | 110040513110 | 09/03/2010 &nbsp;ACT | 12/17/2010 &nbsp;ACT | 2012-09-28 | 2015-03-30 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Virginia Electric and Power Company (Dominion) has proposed to construct and operate a combined-cycle electric power generating facility in Warren County with a nominal generating capacity of 1280 megawatts (MW) at ISO (International Organization for Standardization) conditions. | Equipment to be constructed at ths facility consists of: 3 Mitsubishi Model M501 GAC natural gas-fired combined-cylce turbines, each rated at 299,600 kW (2,996 MMBtu/hr. Each equipped with a heat recovery steam generator (HRSG) having a duct burner with a design rating of 500 MMBtu/hr. This permit supersedes the previous permit issued on 7/30/2004 to CPV Warren LLC. | COMBINED CYCLE TURBINE &amp; DUCT BURNER, 3 | 15.21 | Natural Gas | 2996 | MMBTU/H | Emissions are for one of three units (Mitsubishi natural gas-fired combustion turbine (CT) generator,Model M501 GAC). | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Natural Gas only, fuel has maximum sulfur content of 0.0003% by weight. | 8 | LB/H | 3 HR AVG. (WITHOUT DUCT BURNER FIRING) | BACT-PSD |  | U | 0 | U | 14 | LB/H | 3 HR. AVG. (WITH DUCT BURNER FIRING) | 0 |  |  | 0 | 0 | N |  | PM-10 includes condensable PM. Emissions are for one of three units.
VA-0319 | GATEWAY COGENERATION 1, LLC - SMART WATER PROJECT | GATEWAY GREEN ENERGY | PRINCE GEORGE | VA | 23875-3000 | USA | T. EDWARD MCDANIEL | 972-638-8798 | EMCDANIEL@GGEHLLC.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52375-002 | 4911 | 221112 | 110045446718 | 01/11/2012 &nbsp;ACT | 08/27/2012 &nbsp;ACT | 2013-01-16 | 2015-05-29 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Combined cycle electrical power generating facility (160 MW), consisting of two combusion turbines (Rolls Royce Trent 60 WLE) with associated HRSG and no duct burning. |  | COMBUSTION TURBINES, (2) | 15.21 | Natural Gas | 593 | MMBTU/H | Burns primarily natural gas but has the capacity to burn up to 500 hours of ultra low sulfur diesel fuel (ULSD) as backup. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean-burning fuels and good combustion practices. | 5 | LB/H | 3 H AVG | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Stack testing and visible emission evaluation.
VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404 | 4911 | 221112 | 110055066440 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2019-06-19 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | COMBUSTION TURBINE GENERATORS, (3) | 15.21 | Natural Gas | 3442 | MMBTU/H | Three (3) Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners (natural gas-fired). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur/carbon fuel and good combustion practices. | 0.0033 | LB/MMBTU | 3 H AVG/WITHOUT DUCT BURNING | BACT-PSD | NSPS | U | 0 | U | 9.7 | LB/H | 3 H AVG/WITHOUT DUCT BURNING | 0 |  |  | 0 | 0 | N
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Option 1 - Normal Operation | 15.21 | natural gas | 34000 | MMCF/YR | Option 1: Two on one configuration: 3,482 MMBtu/hr combustion turbine with 475 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and the use of pipeline quality natural gas with a maximum sulfur content of 0.4 gr/100 scf on a 12-month rolling average. | 0.0069 | LB/MMBTU WITHOUT DUC | AV OF 3 TEST RUNS | BACT-PSD | SIP | N | 0 | N | 0.0049 | LB/MMBTU WITH DUC | AV OF 3 TEST RUNS | 0 |  |  | 0 | 0 | N |  | Additional limits: 12.2 lb/hr without duct burning; 17.3 lb/hr with duct burning. These short term limits apply at all times.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combusion Turbine - Option 2 - Normal Operation | 15.21 | Natural Gas | 35000 | MMCF/YR | Option 2: Two on one configuration: 3,116 MMBtu/hr combustion turbine with 991 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and the use of pipeline quality natural gas with a maximum sulfur content of 0.4 gr/100 scf on a 12 mo rolling av. | 0.0065 | LB/MMBTU | AV OF 3 TEST RUNS/WITHOUT DUCT BURNING | BACT-PSD | SIP | N | 0 | N | 0.0065 | LB/MMBTU | AV OF 3 TEST RUNS/WITH DUCT BURNING | 0 |  |  | 0 | 0 | N |  | Additional limits: 13.7 lb/hr without duct burning; 24.2 lb/hr with duct burning. These short term limits apply at all times.
*VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2020-03-18 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/hr natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/hr combustion turbine. Emission limits reflect the operation of each of the three turbines. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Controlled by good combustion practices (e.g. controlled fuel/air mixing, adequate temperature, and gas residence time) and the use of pipeline-quality natural gas with a maximum sulfur content of 0.4 grains per 100 scf, on a 12-month rolling average. | 0.0052 | LB/MMBTU | AVG OF 3 TEST RUNS | BACT-PSD | NSPS , SIP | N | 0 | N | 12.3 | LB/HR | AVG OF 3 TEST RUNS | 0 |  |  | 0 | 0 | N |  | Short term limits apply at all times. Additional limit: 53.9 tons/year
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | Mitsubishi M501-GAC combustion turbine, combined cycle configuration with duct burner. | 15.21 | natural gs | 2988 | MMBTU/H | or ULSD; Duct burner 499 MMBtu/hr, natural gas | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Utilize only natural gas or ULSD fuel; Limit the time in startup or shutdown. | 23.6 | LB/H TOTAL PM | 6-HR AVERAGE ON NG | BACT-PSD |  | U | 0 | U | 42.3 | LB/H TOTAL PM | 6-HR AVERAGE ON ULSD | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA Method 5 and 202, or CTM 039 or CTM 040 | (Particulate Matter (PM)) | PM | P | PUC QUALITY NATURAL GAS | 12 | LB/H | PUC QUALITY NATURAL GAS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA Method 5 and 202, or CTM 039 or CTM 040 | (Particulate Matter (PM)) | PM | P | PUC QUALITY NATURAL GAS | 18 | LB/H | 12-MONTH ROLLING AVG (W/ DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | Natural Gas | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA Method 5 and 202, or CTM 039 or CTM 040 | (Particulate Matter (PM)) | PM | P | PUC QUALITY NATURAL GAS | 12 | LB/H | 12-MONTH ROLLING AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA Method 5 and 202, or CTM 039 or CTM 040 | (Particulate Matter (PM)) | PM | P | PUC QUALITY NATURAL GAS | 18 | LB/H | 12-MONTH ROLLING AVG (W/ DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA METHODS 5 & 202, OR METHODS 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 0.0048 | LB/MMBTU | 9-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0.0049 | LB/MMBTU | 9-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1251 | PALMDALE ENERGY PROJECT | PALMDALE ENERGY, LLC | LOS ANGELES | CA | 93551 | USA | TOM CAMERON |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov | Staff Contact: Lisa Beckham beckham.lisa@epa.gov (415) 972-3811 | SE 17-01 | 4911 | 221122 | Not Found | 08/16/2017 &nbsp;ACT | 04/25/2018 &nbsp;ACT | 2018-10-25 | 2020-01-31 | A | https://www.epa.gov/caa-permitting/palmdale-energy-project-prevention-significant-deterioration-psd-permit | 645 MW (nominal) Natural Gas-fired Combined Cycle Power Plant, 2 x 1 configuration, auxiliary boiler for faster startup | See also docket: https://www.regulations.gov/docket?D=EPA-R09-OAR-2017-0473. Permit decision was appealed to EPA's Environmental Appeals Board. Board denied review on October 23, 2018. Information available through www.epa.gov/eab and https://yosemite.epa.gov/oa/EAB_Web_Docket.nsf/f22b4b245fab46c6852570e6004df1bd/ad735c0b822500258525829d004217eb!OpenDocument. 1/31/20 -- SYS MGR -- Link to permit is <https://www.regulations.gov/document?D=EPA-R09-OAR-2017-0473-0028> | Combustion Turbines (GEN1 and GEN2) | 15.21 | Natural Gas | 2217 | MMBTU/H | Each combustion turbine rated at 214 MW, with a maximum heat input rate of 2,217 MMBtu/H (HHV, at ISO conditions); natural gas-fired Siemens SGT6-5000F; each vents to dedicated Heat Recovery Steam Generator and a shared 276 MW Steam Turbine Generator; 160-ft stack height; 22-ft stack diameter | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Methods 201A and 202 | (Particulate Matter (PM)) | PM | P | Clean fuel and good combustion practices | 0.0048 | LB/MMBTU | TEST AVERAGE | BACT-PSD |  | N | 0 | U | 11.8 | LB/H | TEST AVERAGE | 0 |  |  | 0 | 0 | N |  | The sulfur content of the gas shall not exceed 0.20 grains per 100 dry standard cubic feet (dscf), based on a 12-month rolling average, and shall not exceed 1.0 grains per 100 dscf at any time.
CT-0157 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo james.grillo@ct.cov 860-424-3570 | 144-0023 | 4911 | 221112 | 110040589672 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-03 | 2016-02-19 | A |  | 805 MW Combined Cycle Power Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/12 months |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 9.73 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 20.4 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
CT-0158 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo; james.grillo@ct.gov; 860-424-3570 | 144-0024 | 4911 | 221112 | 110040589672 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-04 | 2016-02-19 | A |  | 805 MW Combined Cycle Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/yr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 9.73 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 20.4 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/o Duct Firing | 15.21 | Natural Gas | 2969 | MMBtu/hr | Throughput is for turbine only | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.0044 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/Duct Firing | 15.21 | Natural Gas | 2639 | MMBtu/hr | Duct burner MRC is 946 MMbtu/hr | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.005 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - No tests required | (Particulate Matter (PM)) | PM | P | Use of clean fuels | 2 | GR. S/100 SCF GAS | FOR NATURAL GAS | BACT-PSD |  | U | 0 | U | 0.0015 | % S IN ULSD | FOR ULSD | 0 |  |  | 0 | 0 | N |  | Use of clean fuels prevents PM formation
*FL-0363 | DANIA BEACH ENERGY CENTER | FLORIDA POWER AND LIGHT COMPANY | BROWARD | FL | 33314 | USA | JOHN HAMPP | 561-691-2894 | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-017-AC | 4911 | 221112 | 110002044065 | 07/27/2017 &nbsp;ACT | 12/04/2017 &nbsp;ACT | 2018-04-03 | 2018-04-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.F.ZIP | 1200 megawatt 2-on-1 combined cycle facility, natural gas-fired, with limited ULSD use. GE 7HA turbines | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.D.ZIP | 2-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural gas | 4000 | MMBtu/hr | Two nominal 430 MW combustion turbines, coupled to a steam turbine generator | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean fuels | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limits on sulfur content of fuels limit PM emissions. Gas limited to 2.0 grains per 100 scf, and oil limited to 0.0015% sulfur. Also subject to 10% opacity limit.
*FL-0367 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 36410 | USA | ROY BELDEN | (203) 357-6820 | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-001-AC | 4911 | 221112 | 110012581820 | 02/16/2018 &nbsp;ACT | 07/27/2018 &nbsp;ACT | 2019-03-19 | 2019-03-19 | B | https://arm-permit2k.dep.state.fl.us/nontv/1010524.001.AC.F.ZIP | A 573-megawatt (MW) (winter) 1-on-1 combined cycle plant which includes a heat recovery steam generator with duct firing, along with supporting equipment. Natural gas is the only permitted fuel for the combined cycle unit. | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/1010524.001.AC.R.ZIP | 1-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural Gas | 3266.9 | MMBtu/hour | One nominal 385 MW GE 7HA.02 CTG and one HRSG with duct firing [approximately 210 MMBtu/hour], and one nominal 210 MW steam turbine generator (STG) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean fuels | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limits on sulfur content of fuel limit PM emissions. Natural Gas limited to 2.0 grains per 100 scf. Also subject to 10% opacity limit.
IL-0112 | NELSON ENERGY CENTER | INVENERGY NELSON, LLC | LEE | IL | 61071-9722 | USA | JOEL SCHROEDER | 312-224-1417 | JSCHROEDER@INVENERGYLLC.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Manish Patel, Permit Analyst Manish.Patel@illinois.gov 217-785-1722 | 98080039 | 4911 | 221112 | 110007399644 | 11/19/2010 &nbsp;ACT | 12/28/2010 &nbsp;ACT | 2013-02-21 | 2020-04-16 | A |  | Natural gas-fired electic power generation facility with two &quot;combined cycle&quot; turbines followed by heat recovery steam generators (HRSG) and the capability for supplemental fuel firing in the HRSG for each turbine using duct burners. NOx emissions will be controlled by SCR and low NOx combustors. | LSP-Nelson Energy started construction pursuant to a permit issued in year 2000 for a facility that was not completed due to financial difficulties, which eventually resulted in LSP-Nelson entering bankruptcy. Substantial construction of foundations and infrastructure for all units and physical installation of one turbine were completed, including construction of HRSGs. | Electric Generation Facility | 15.21 | Natural Gas | 220 | MW each | Two combined cycle combustion turbines followed by HRSGs with capability for supplemental fuel firing in HRSG for each combustion turbine using duct burners. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | N |  | 0.006 | LB/MMBTU | HOURLY AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002049328 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | COMBINED CYCLE TURBINE GENERATORS (UNITS 6A &amp; 6B) | 15.21 | NATURAL GAS | 7146 | MMBTU/H | TURBINES ALSO PERMITTED TO BURN NO. 2 FUEL OIL AND ULTRA LOW SULFUR DIESEL. FUEL OIL USE IS LIMITED TO 1000 HOURS PER YEAR. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - METHOD 201A | (Particulate Matter (PM)) | PM | P | WHILE FIRING NATURAL GAS: USE OF PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES WHILE FIRING FUEL OIL: USE OF ULTRA LOW SULFUR FUEL OIL AND GOOD COMBUSTION PRACTICES | 26.23 | LB/H | HOURLY AVERAGE W/O DUCT BURNER | BACT-PSD | OPERATING PERMIT | U | 0 | U | 33.16 | LB/H | HOURLY AVERAGE W/ DUCT BURNER | 0 |  |  | 0 | 0 | N |  | WHILE FIRING FUEL OIL, THE BACT LIMIT FOR PM2.5 IS 36.37 LB/HR (HOURLY AVERAGE) BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE).
LA-0256 | COGENERATION PLANT | WESTLAKE VINYLS COMPANY LP | ASCENSION | LA | 70734 | USA | KAREN KHONSARI | (225) 673-0647 | KKHONSARI@WESTLAKE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: DAN NGUYEN, 225-219-3417 | PSD-LA-754 | 4939 | 221112 | 110000746328 | 01/12/2011 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2011-12-21 | 2012-04-03 | B |  | COGENERATION PLANT AT SYNTHETIC ORGANIC CHEMICAL MANUFACTURING FACILITY | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS &lsquo;&lsquo;FWE&lsquo;&lsquo; REPRESENT POTENTIAL EMISSIONS ASSOCIATED WITH THE COGENERATION PLANT. NOX &lsquo;&lsquo;NETTED OUT&lsquo;&lsquo; OF PSD/NNSR. | COGENERATION TRAINS 1-3 (1-10, 2-10, 3-10) | 15.21 | NATURAL GAS | 475 | MMBTU/H | EACH COGEN TRAIN CONSISTS OF A 50 MW GE LM6000 PF SPRINT TURBINE AND A HEAT RECOVERY STEAM GENERATOR EQUIPPED WITH A 70 MM BTU/HR DUCT BURNER. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS AS FUEL AND GOOD COMBUSTION PRACTICES | 3.72 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | IN ADDITION, AN ANNUAL LIMIT OF 16.31 TPY WAS ESTABLISHED BY THE ACCOMPANYING TITLE V PERMIT (3090-V0).
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive Combustion of Fuel Gas and Good Combustion Practices. | 9.53 | LB/H | 3 HOUR AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Averaging time 3-hour Average during duct burner and turbine operations.
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000310459 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 2449 | MMBTU/H | two 315 MW (nominal) GE Energy 7F Series 5 Rapid Response Combined Cycle Combustion Turbines with Duct Burners and 31 MW (estimated) steam turbine generators | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0062 | LB/MMBTU | 1 HR AVG/DO NOT APPLY DURING SS | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 13 | LB/H | 1 HR AVG/DO NOT APPLY DURING SS | 0 |  |  | 0 | 0 | N |  | PM 2.5 (no duct firing): â‰¤0.0071lb/MMBtu, â‰¤8.8 lb/hr during start-ups (â‰¤ 45 minutes): PM/PM10/PM2.5 â‰¤ 6.60 lb per event during shutdowns (â‰¤ 27 minutes): PM/PM10/PM2.5 â‰¤ 3.96 lb per event
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITH DUCT FIRING | 15.21 | NATURAL GAS | 1000 | MW | TWO MITSUBISHI &lsquo;&lsquo;G&lsquo;&lsquo; MODEL COMBUSTION TURBINE GENERATORS (CTS) WITH A NOMINAL GENERATING CAPACITY OF 270 MW CAPACITY EACH, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR), OXIDATION CATALYST | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND EFFICIENT TURBINE DESIGN | 38 | LB/H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITHOUT DUCT FIRING | 15.21 | NATURAL GAS | 270 | MW |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND EFFICIENT TURBINE DESIGN | 25.1 | LB/H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST. HEAT RATE LIMITED TO 6,793 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR MATTAWOMAN TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS MATTAWOMAN PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE QUALITY NATURAL GAS EXCLUSIVELY AND GOOD COMBUSTION PRACTICES. | 17.9 | LB/H | W/OUT DUCT FIRING, AVG. OF 3 STACK TESTS | BACT-PSD |  |  | 0 |  | 27.7 | LB/H | WITH DUCT FIRING, AVG. OF 3 STACK TESTS | 0 |  |  | 0 | 0 | N |  | AT ALL TIMES
MI-0402 | SUMPTER POWER PLANT | WOLVERINE POWER SUPPLY COOPERATIVE INC. | WAYNE | MI | 48111 | USA | BRIAN WARNER | 231-775-5700 | BWARNER@WPSCI.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Julie Brunner at 517-373-7088 or brunnerj1@michigan.gov for questions related to this permit. Thank you. | 81-11 | 4911 | 221112 | 2616305315 | 05/27/2011 &nbsp;ACT | 11/17/2011 &nbsp;ACT | 2012-11-30 | 2016-05-04 | D |  | Utility--Natural gas fired combustion turbine | Other Facility Wide Pollutants not listed below: PM10 = 14.8 tpy PM2.5 = 14.8 tpy CO2e = 232,639 tpy | Combined cycle combustion turbine w/ HRSG | 15.21 | Natural gas | 130 | MW electrical output | This is a combined-cycle combustion turbine with a non-fired heat recovery steam generator (HRSG). Natural gas-fired combustion turbine conversion to combined-cycle. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0066 | LB/MMBTU | TEST | BACT-PSD | OTHER | N | 0 | N | 7.4 | LB/H | TEST | 0 |  |  | 0 | 0 | N |  | Top ranking option 'Other' is due to NAAQS.
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.006 | LB/MMBTU | EACH CTG; TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0.012 | LB/MMBTU | EACH CTG; TEST PROTOCOL | 0 |  |  | 0 | 0 | N | 2012 | Cost Effectiveness Information: No additional costs were calculated for PM10 or PM2.5 since additional costs to remove condensable particulate would only inflate the costs calculated for PM. Therefore, the costs for PM were considered to be conservative. Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet Scrubber = $16,663/ton
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.008 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 19.9 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N | 2012 | Cost Effectiveness Information: No additonal costs were calculated for PM10 or PM2.5 since additional costs to remove condensable particulate would only inflate the costs calculated for PM. Therefore, the costs for PM were considered to be conservative. Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet scrubber = $16,663/ton
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0042 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 9 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Emission limit 1 & 2 are for each unit operating without the DB.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0073 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 15.6 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Emission limit 1 & 2 are for each unit operating with the DB.
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion air filters, efficient combustion control, low sulfur natural gas fuel. | 0.0066 | LB/MMBTU | TEST PROTOCOL (3 1-H TESTS IF POSSIBLE) | BACT-PSD |  | N | 90 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit applies to each CTG/HRSG. Limit applies at all times and includes duct burner operation.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 0.014 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 0.014 lb/MMBTU for each CTGHRSG. Test protocol will specify averaging time. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10 which are higher emitting than PM. PM10 emissions were assumed the same as PM2.5, so the cost analysis is equivalent. The dollar value year used was 2013. Pulse Jet Fabric Filter Baghouse: minimum of $62,842 per ton. Mechanical Shaker Fabric Filter Baghouse: minimum of $53,684 per ton. Reverse-Air Fabric Filter Bathouse: minimum of $77,328 per ton. Dry ESP (Wire-Plate Type): minimum of $44,525 per ton. Dry ESP (Wire-Pipe Type): minimum of $66,472 per ton. Wet ESP (Wire-Plate Type): minimum of $77,761 per ton. Wet ESP (Wire-Pipe Type): minimum of $110,364 per ton. Venturi Scrubber: minimum of $52,773 per ton.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.8 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit in the table above is for EACH CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. Pulse Jet Fabric Filter Baghouse: minimum of $364,528 per ton Mechanical Shaker Fabric Filter Baghouse: minimum of $404,724 per ton Reverse-Air Fabric Filter Baghouse: minimum of $476,689 per ton Dry ESP (Wire-Plate Type): minimum of $478,806 per ton Dry ESP (Wire-Pipe Type): minimum of $303,809 per ton Wet ESP (Wire-Plate Type): minimum of $576,763 per ton Wet ESP (Wire-Pipe Type): minimum of $440,047 per ton Venturi Scrubber: minimum of $1,445,564 per ton
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 0.014 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is for each CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. â€¢ Pulse Jet Fabric Filter Baghouse: minimum of $64,473 per ton â€¢ Mechanical Shaker Fabric Filter Baghouse: minimum of $55,077 per ton â€¢ Reverse-Air Fabric Filter Baghouse: minimum of $79,336 per ton â€¢ Dry ESP (Wire-Plate Type): minimum of $45,681 per ton â€¢ Dry ESP (Wire-Pipe Type): minimum of $68,197 per ton â€¢ Wet ESP (Wire-Plate Type): minimum of $79,780 per ton â€¢ Wet ESP (Wire-Pipe Type): minimum of $113,229 per ton â€¢ Venturi Scrubber: minimum of $54,143 per ton
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas, combustion inlet air filter. | 0.0066 | LB/MMBTU |  | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Fabric filter control: over $260,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5). Electrostatic precipitator (ESP): OVER $188,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5). Wet ESP: over $165,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5). Venturi Scrubber: over $112,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5).
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Use clean fuel (natural gas) and good combustion practices. | 10.7 | LB/H | HOURLY; EACH CT/HRSG TRAIN | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.1 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | 19.1 pph is equivalent to 0.005 lb/MMBTU, which includes startup and shutdown The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse Jet Fabric Filter Baghouse: average of $334,000 per ton Mechanical Shaker Fabric Filter Baghouse: average of $370,500 per ton Reverse-Air Fabric Filter Baghouse: average of $437,000 per ton Dry ESP (Wire-Plate Type): average of $438,500 per ton Dry ESP (Wire-Pipe Type): average of $278,500 per ton Wet ESP (Wire-Plate Type): average of $528,500 per ton Wet ESP (Wire-Pipe Type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.1 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2017 | (19.1 pph is equivalent to 0.005 lb/MMBTU, which includes startup and shutdown). The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. Pulse Jet Fabric Filter Baghouse: average of $334,000 per ton Mechanical Shaker Fabric Filter Baghouse: average of $370,500 per ton Reverse-Air Fabric Filter Baghouse: average of $437,000 per ton Dry ESP (Wire-Plate Type): average of $438,500 per ton Dry ESP (Wire-Pipe Type): average of $278,500 per ton Wet ESP (Wire-Plate Type): average of $528,500 per ton Wet ESP (Wire-Pipe Type): average of $403,000 per ton Venturi Scrubber: average of $1,321,000 per ton
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning and the use of pipeline quality natural gas. | 16 | LB/H | HOURLY; EACH UNIT | BACT-PSD | SIP | N | 0 | N | 12.2 | LB/H | HOURLY; EACH UNIT W/O DUCT BURNER FIRING | 0 |  |  | 0 | 0 | N |  | The cost analysis was for the best scenario: 100 percent capture of PM2.5, where PM and PM10 calculations equaled PM2.5. Pulse Jet Fabric Filter Baghouse: minimum of $174,206 per ton Mechanical Shaker Fabric Filter Baghouse: minimum of $145,172 per ton Reverse-Air Fabric Filter Baghouse: minimum of $232,274 per ton Dry ESP (Wire-Plate Type): minimum of $116,721 per ton Dry ESP (Wire-Pipe Type): minimum of $261,309 per ton Wet ESP (Wire-Plate Type): minimum of $263,153 per ton Wet ESP (Wire-Pipe Type): minimum of $348,412 per ton Venturi Scrubber: minimum of $167,000 per ton
MI-0439 | JACKSON GENERATING STATION | CONSUMERS ENERGY COMPANY | JACKSON | MI | 49203-2174 | USA | BRIAN LABBY | 989-667-5008 | BRIAN.LABBY@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, at 517-284-6790 or at byrnesm@michigan.gov, for technical questions regarding this permit. Thank you. | 118-18 | 4911 | 221112 | 110015804511 | 11/29/2018 &nbsp;ACT | 04/02/2019 &nbsp;ACT | 2019-05-20 | 2019-06-19 | C |  | Natural gas combined-cycle power plant |  | FGLMDB1-6 (6 combined cycle natural gas fired CTG each equipped with a HRSG) | 15.21 | natural gas | 420 | MW | FGLMDB1-6 is 6 combined cycle natural gas fired combustion turbine generators (CTG) each equipped with a heat recovery steam generator (HRSG). Nominal rating 420 MW. Each combustion turbine (CT) is a GE LM6000 with a rating of 440 MMBTU/HR (HHV) and a duct burner rating of 222 MMBTU/HR (HHV). A combined cycle natural gas fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 420 MW electricity production. The HRSG is not capable of operating independently from the CTG. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion inlet air filters, good combustion practices and only combust natural gas. | 4.9 | LB/HR | 24 HR AVG DET.EACH OPERATING HR; EACH | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is 4.9 lb/hr on a 24-hour rolling average determined each hour the unit operates and applies to each unit. The limit is also per stack during periods when the turbine operates alone and when the turbine operates in conjunction with its respective duct burner. The limits do not apply during startup and shutdown. This limit equates to approximately 0.0078 lb/MMBTU.
*MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2019-10-22 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2--A 667 MMBTU/H natural gas fired CTG with a HRSG. | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2 is a nominally rated 667 MMBTU/H natural gas fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas fired duct burner rated at 204 MMBTU/h to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR and oxidation catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning, and good combustion practices. | 6.02 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 of 6.02 lb/h applies during all operating modes. Add-on control technology was not technically feasible; however options were evaluated, and it was determined they were not economically feasible.
*MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2019-10-22 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1--A 667 MMBTU/H NG fired combustion turbine generator coupled with a heat recovery steam generator (HRSG) | 15.21 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR) and oxidation catalyst. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas, inlet air conditioning and good combustion practices. | 6.02 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is during all operating modes. Add-on control technology was not technically feasible; however, options were evaluated and it was determined they were not economically feasible.
*MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2019-12-19 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur fuel and good combustion practices. | 0.006 | LB/MMBTU | HOURLY; EACH UNIT | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The lowest cost (for a fabric filter) was greater than $87,000/ton of total PM controlled. Therefore, add-on controls were not considered economically feasible for particulate control.
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine without Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burner. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 10 | LB/H | AVERAGE OF THREE ONE HOUR STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burners. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of Natural Gas a clean burning fuel | 21.55 | LB/H | AVERAGE OF THREE STACK TEST RUNS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0.0069 | LB/MMBTU | AVERAGE OF THREE STACK TEST RUNS | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas with Duct Burner | 15.21 | natural gas | 4000 | h/yr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | COMPLIANCE BY STACK TESTING | 18.3 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY STACK TESTING
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas without Duct Burner | 15.21 | Natural Gas | 8040 | H/YR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 11.7 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY STACK TESTING
OH-0360 | CARROLL COUNTY ENERGY | CARROLL COUNTY ENERGY | CARROLL | OH | 44615 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0113762 | 4911 | 221112 | 110064671127 | 04/11/2013 &nbsp;ACT | 11/05/2013 &nbsp;ACT | 2015-12-30 | 2019-04-01 | A |  | Natural gas fired combined cycle gas turbine electric generating station of nominal capacity of 742 MW | Installation of a natural gas-fired combined cycle combustion turbine electric utility power plant, nominally rated at 742 MW. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural Gas | 2045 | MMBTU/H | Two identical General Electric 7FA combined cycle combustion turbine (each at 2,045 mmBtu/hr heat input turbine at ISO conditions and 566 mmBtu/hr heat input duct burner, HHV) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. All throughputs and emission limits are for each turbine. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Natural gas only | 19.8 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 85.7 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | Limits are for each turbine. 0.0078 lb/mmbtu and 19.8 lb/h for turbine and duct burner, except startup and shutdown. 0.0108 lb/mmbtu and 12.4 lb/h for turbine only, except startup and shutdown. 85.7 t/yr per rolling 12 month period including startup and shutdown.
OH-0363 | NTE OHIO, LLC |  | BUTLER | OH | 45044 | USA | MICHAEL SCHUSTER | (904)436-6896 | MSCHUSTER@NTEENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0116610 | 4911 | 221112 | 110070379584 | 04/07/2014 &nbsp;ACT | 11/05/2014 &nbsp;ACT | 2019-02-22 | 2019-04-01 | A |  | Combined-cycle, natural gas-fired power plant | Initial installation of either one (1) Mitsubishi Hitachi Power Systems Americas M501JAC or one (1) Mitsubishi Hitachi Power Systems Americas M501GAC single power block in a 1x1 combined-cycle multi-shaft configuration, including a combustion turbine and heat recovery steam generator with duct burners and a steam turbine to be known as the Middletown Energy Center. | Turbine generator with HRSG and duct burners (P001) | 15.21 | Natural gas | 3278.5 | MMBTU/H | Combined-cycle combustion turbine generator (CTG) with heat recovery steam generator (HRSG), natural gas-fired, including duct burners (DB). Permit was for either Mitsubishi Hitachi Power Systems America M501GAC or M501JAC. The M501GAC was installed. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Methods 201A and 202 | (Particulate Matter (PM)) | PM | B | Exclusive use of natural gas, high efficiency inlet air filters and low NOx burner. | 20 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 59.4 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  |  | 0 | 0 | N |  | 20.0 lb/h and 5.70x10-3 lb/mmbtu with duct burner, except startup and shutdown. 10.8 lb/h and 3.80x10-3 lb/mmbtu turbine only, except startup and shutdown. 59.4 tons per rolling 12 month period for all operating modes, including startup.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 1 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2022 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Method 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices along with clean fuels | 0.0068 | LB/MMBTU | HHV, 3 HR AVG. SEE NOTES. | BACT-PSD |  | U | 0 | U | 58.62 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  |  | 0 | 0 | N |  | Limits are for single turbine except as noted. 0.0068 lb/mmbtu HHV, 3 hour average with duct burners. 9.5 lb/h, 3 hour average without duct burners. 15.8 lb/h, 3 hour average with duct burners. 58.62 t/yr per rolling 12 month period.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 2 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2144 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Method 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices along with clean fuels | 0.0085 | LB/MMBTU | HHV, 3 HR AVG. SEE NOTES. | BACT-PSD |  | U | 0 | U | 86.7 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  |  | 0 | 0 | N |  | Limits are for single turbine except as noted. 0.0085 lb/mmbtu HHV, 3 hour average with and without duct burners. 15.9 lb/h, 3 hour average without duct burners. 22.2 lb/h, 3 hour average with duct burners. 86.7 t/yr per rolling 12 month period.
OH-0366 | CLEAN ENERGY FUTURE - LORDSTOWN, LLC | CLEAN ENERGY FUTURE - LORDSTOWN, LLC | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0117655 | 4911 | 221112 | 110070396317 | 09/17/2014 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2019-02-27 | 2019-06-19 | A |  | 962 MW (gross winter output) combined cycle gas turbine (CCGT) facility | Initial installation permit for the construction of the Lordstown Energy Center - a nominal 940 MW combined cycle gas turbine (CCGT) facility. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 2725 | MMBTU/H | Combined cycle combustion turbine (2,725 MMBtu/hr heat input turbine at ISO conditions and 179 MMBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Limits and throughputs are for single turbine. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Method 201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuel | 14.9 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 62.6 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 14.9 lb/h and 4.9x10-3 lb/mmbtu with duct burner, except startup and shutdown. 13.1 lb/h and 6.8x10-3 lb/mmbtu turbine only, except startup and shutdown. 62.6 tons per rolling 12 month period for all operating modes, including startup.
OH-0367 | SOUTH FIELD ENERGY LLC | SOUTH FIELD ENERGY LLC | COLUMBIANA | OH | 43968 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0119495 | 4911 | 221112 | Not Found | 09/14/2015 &nbsp;ACT | 09/23/2016 &nbsp;ACT | 2019-02-28 | 2019-06-19 | A |  | 1150 MW combined-cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the South Field Energy facility, a nominal 1,150 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in Wellsville, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3131 | MMBTU/H | Two identical combined cycle combustion turbine (3,131 MMBtu/hr heat input turbine at ISO conditions, natural gas firing with evaporative cooler on and 800 MMBtu/hr maximum heat input natural gas-fired duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), catalytic oxidizer, and wet injection for ULSD firing. Heat input for ULSD firing at ISO conditions, with evaporative cooler on is 3,173 MMBtu/hr. Throughputs and limits are for single turbine except as noted. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Methods 201A and 202 | (Particulate Matter (PM)) | PM | P | Good combustion controls | 25 | LB/H | NAT GAS, WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 128.9 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  |  | 0 | 0 | N |  | 6.9x10-3 lb/mmbtu, hourly average, natural gas, with duct burner. 7.7x10-3 lb/mmbtu, hourly average, natural gas, turbine only. 1.9x10-2 lb/mmbtu, hourly average, ultra low sulfur diesel. 25.0 lb/h with duct burner (including startup and shutdown). 16.16 lb/h without duct burner (including startup and shutdown). 55.4 lb/h for ultra low sulfur diesel (except startup and shutdown). 128.9 t/yr per rolling 12 month period for all operating modes, including startup and shutdown. When firing ultra low sulfur diesel, 77.4 lb/h during startup and shutdown.
OH-0370 | TRUMBULL ENERGY CENTER | TRUMBULL ENERGY CENTER | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122331 | 4911 | 221112 | Not Found | 03/23/2017 &nbsp;ACT | 09/07/2017 &nbsp;ACT | 2019-03-05 | 2019-06-19 | A |  | 940 MW combined cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the Trumbull Energy Center, a nominal 940 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in the Village of Lordstown, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3025 | MMBTU/H | Two identical combined cycle combustion turbine (3,025 mmBtu/hr heat input turbine at ISO conditions and 237 mmBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Throughputs and limits are for single turbine except as noted. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Methods 201A and 202 | (Particulate Matter (PM)) | PM | P | Good combustion controls and low sulfur fuel | 15.2 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 64.4 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 4.6x10-3 lb/mmbtu with duct burners, 6.0x10-3 lb/mmbtu without duct burners, 15.2 lb/h with duct burner, 12.9 lb/h without duct burner (each limit except startup and shutdown). 64.4 t/yr per rolling 12 month period for all operating modes, including startup and shutdown.
OH-0372 | OREGON ENERGY CENTER | OREGON ENERGY CENTER | LUCAS | OH | 43616 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0121049 | 4911 | 221112 | Not Found | 06/27/2016 &nbsp;ACT | 09/27/2017 &nbsp;ACT | 2019-03-06 | 2019-06-19 | A |  | Combined cycle gas turbine (CCGT) facility | Installation of natural gas-fired combined cycle combustion turbine power plant. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3055 | MMBTU/H | Combined cycle combustion turbine (3,055 mmBtu/hr heat input turbine at ISO conditions and 221.3 mmBtu/hr heat input duct burner) with dry low NOX combustors, selective catalytic reduction (SCR), and catalytic oxidation. All heat values are on a HHV basis. Throughputs and limits are for single turbine except as noted. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Methods 201A and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices and pipeline quality natural gas | 15.4 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 65.26 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 4.6x10-3 lb/mmbtu with duct burners. 6.0x10-3 lb/mmbtu without duct burners. 15.4 lb/h with duct burner (except startup and shutdown). 14.0 lb/h without duct burner (except startup and shutdown). 65.26 t/yr per rolling 12 month period for all operating modes, including startup.
OH-0374 | GUERNSEY POWER STATION LLC | GUERNSEY POWER STATION LLC | GUERNSEY | OH | 43723 | USA | MARY KING | (317)447-4513 | MARY@APEXPOWERGROUP.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122594 | 4911 | 221112 | 110070379546 | 04/14/2017 &nbsp;ACT | 10/23/2017 &nbsp;ACT | 2019-03-08 | 2019-06-19 | A |  | 1,650 MW combined cycle combustion turbine electrical generating facility | Installation PTI for a new 1,650 MW combined cycle natural-gas fired turbine plant and associated auxiliary boiler, firewater pumps, emergency generators and fuel gas heaters | Combined Cycle Combustion Turbines (3, identical) (P001 to P003) | 15.21 | Natural gas | 3516 | MMBTU/H | Three identical Combustion Turbines; GE 7HA.02 natural gas-fired lean pre-mix combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,516 MMBtu/hr HHV at 100% load and -18Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 997 MMBtu/hr HHV controlled with catalytic oxidation and selective catalytic reduction (SCR) and cooled with an air-cooled condenser (ACC) used to generate electricity. Throughputs and limits are for a single turbine except as noted. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Methods 201A and 202 | (Particulate Matter (PM)) | PM | P | pipeline quality natural gas | 0.0073 | LB/MMBTU | SEE NOTES. | BACT-PSD |  | U | 0 | U | 23.3 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | Limits are for single turbine except as noted. 0.0073 lb/mmbtu with duct burners and without duct burners. Both excluding startup and shutdown. 12.30 lb/h without duct burners. 23.30 lb/h with duct burners. Both excluding startup and shutdown. 290.39 t/yr per rolling 12 month period total for all 3 turbines.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | General Electric Combustion Turbine (P004) | 15.21 | Natural gas | 3544 | MMBTU/H | General Electric model 7HA.02 natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,544 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Methods 201A and 202 | (Particulate Matter (PM)) | PM | P | natural gas or a natural gas and ethane mixture only | 0.0036 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 12.1 | LB/H |  | 0 |  | SEE NOTES | 0 | 0 | N |  | 53.0 t/yr per rolling, 12-month period, including start-up and shutdown emissions.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Mitsubishi Combustion Turbine (P005) | 15.21 | Natural gas | 3320 | MMBTU/H | Mitsubishi Model 501JAC natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,320 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 108 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Methods 201A and 202 | (Particulate Matter (PM)) | PM | P | natural gas or a natural gas and ethane mixture only | 0.004 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 12.6 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.004 lb/mmbtu and 12.60 lb/h with duct burner (except startup and shutdown). 0.0037 lb/mmbtu and 12.3 lb/h without duct burner (except startup and shutdown). 55.2 t/yr per rolling 12 month period for all operating modes, including startup.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Siemens Combustion Turbine (P006) | 15.21 | Natural gas | 3602 | MMBTU/H | Siemens Model SCC6-8000H natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,602 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 667 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Methods 201A and 202 | (Particulate Matter (PM)) | PM | P | natural gas or a natural gas and ethane mixture only | 0.0057 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 19.8 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.0057 lb/mmbtu and 19.8 lb/h with duct burner (except startup and shutdown). 0.006 lb/mmbtu and 13 lb/h without duct burner (except startup and shutdown). 86.7 t/yr per rolling 12 month period for all operating modes, including startup.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Methods 201A and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and pipeline quality natural gas | 0.0052 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 18.4 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.00522 lb/mmbtu and 18.4 lb/h with duct burner. 0.00735 lb/mmbtu and 12.0 lb/h without duct burner. 80.2 tons per rolling 12 month period for all operating modes.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Methods 201A and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and pipeline quality natural gas | 0.005 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 17.7 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.005 lb/mmbtu and 17.7 lb/h with duct burner. 0.00444 lb/mmbtu and 14.10 lb/h without duct burner. 77.5 tons per rolling 12 month period for all operating modes.
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | Combustion Turbine | 15.21 | Natural Gas | 360 | MW | This process represents the GE option for the project - One GE 7FA.05 natural gas-fired combustion turbine generator with an 820.5 MMBTUH duct burner. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | LOW ASH FUEL AND COMBUSTION CONTROL. | 22.1 | LB/HR | >50% LOAD W/O DUCT FIRING | BACT-PSD | N/A | U | 0 | U | 31.8 | LB/HR | >50% LOAD WITH DUCT FIRING | 0 |  |  | 0 | 0 | N
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | COMBUSTION TURBINE | 15.21 | NATURAL GAS | 360 | MW | This process represents the Siemens option for the project - One Siemens SGT6-5000F5 natural gas-fired combustion turbine generator with an 820.3 MMBTUH duct burner. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | LOW ASH FUEL AND COMBUSTION CONTROL. | 22.2 | LB/HR | >50% LOAD W/O DUCT FIRING | BACT-PSD | N/A | U | 0 | U | 31.6 | LB/HR | >50% LOAD WITH DUCT FIRING | 0 |  |  | 0 | 0 | N
PA-0296 | BERKS HOLLOW ENERGY ASSOC LLC/ONTELAUNEE | BERKS HOLLOW ENERGY ASSOC LLC | BERKS | PA | 19605 | USA | BRADLEY J COOLEY | 636-534-3268 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | WILLIAM R. WEAVER, SOUTHCENTRAL REGION AIR PROGRAM MANAGER 909 Elmerton Ave, Harrisburg, PA 17701 717-705-4868 | 06-05150A | 4931 | 221112 | 110056155342 | 05/08/2012 &nbsp;ACT | 12/17/2013 &nbsp;ACT | 2014-04-17 | 2020-03-02 | A |  | This application is for the construction of a natural gas-fired combined-cycle electric generation facility that is designed to generate up to 855 MW nominal, using 2 combustion turbine generators and 2 heat recovery steam generators that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. | This application is for the construction of a natural gas-fired combined-cycle electric generation facility that is designed to generate up to 855 MW nominal, using 2 combustion turbine generators and 2 heat recovery steam generators that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. | Turbine, Combined Cycle, #1 and #2 | 15.21 | Natural Gas | 3046 | MMBTU/H | Equipped with SCR and Oxidation Catalyst | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 48.56 | TPY | 12-MONTH ROLLING TOTAL | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2018-12-21 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large combustion turbine | 15.21 | Natural Gas | 0 |  | This process entry is for operations with the duct burner. Limits entered are for each turbine. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0039 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 11.8 | LB/HR |  | 0 |  |  | 0 | 0 | N
PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2018-12-21 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two combined cycle turbines with out duct burner | 15.21 | Natural Gas | 2291.64 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode, the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. (Operational limits are for each CCCT NG-fired without duct burner) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA/OAR 201A, and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.0068 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative Emissions from both CCCT in any 12-month period
PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2018-12-21 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two Combine Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 3001.57 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. . (Operational limits are for each CCCT NG-fired with duct burner) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - 201or 201 A, and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.0066 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 159.1 | TONS | ANY 12-MONTH PERIOD | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative emissions from both CCCT in any 12-month period
PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Combustion turbine with duct burner | 15.21 | Natural gas | 3304.3 | MMBtu/hr | Limits are for each CCCT and yearly limits are for cumulative turbine and duct burner. Duct burner throughput is 637.9 MMBtu/hr. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive natural gas, high-efficiency inlet air filters and DLN | 0.0059 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 48.2 | TONS | YEAR | 0 |  |  | 0 | 0 | N
PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG with duct burner NG only | 15.21 | Natural Gas | 3338 | MMBtu/hr | Emission limits are for each turbine operating with duct burner and do not include startup/shutdown emissions. Tons per year limits is a cumulative value for all three CCCT. CEMS for NOx, CO, and O2. Each CCCT and duct burner have 5 operational scenarios: 1 CCCT with duct burner fired - fueled by NG only 2 CCCT with duct burner fired - fueled by NG blend with ethane 3 CCCT without duct burner fired - fueled by NG only 4 CCCT without duct burner fired - fueled by NG blend with ethane 5 CCCT without duct burner fired - fueled by ULSD (Limited to emergency use only) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuel, good combustion practices | 0.005 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 131.5 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N |  | lb/MMBtu limit is for each turbine and duct burner, TPY is a cumulative total
PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG without duct burner NG only | 15.21 | Natural gas | 0 |  | Emission limits are for each turbine fueled by NG and operating without duct burner being fired and do not include startup/shutdown emissions. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuels and good combustion practices | 0.0068 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit is for each turbine and HRSG with the duct burner not fired.
PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064098541 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2018-12-21 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine With Duct Burner | 15.21 | Natural Gas | 3727 | MMBtu/hr | DLN burner, SCR, Oxidation Catalyst and shall maintain and operate the sources and associated air cleaning devices in accordance with good engineering practice. shall install, certify, maintain and operate continuous emission monitoring systems (CEMS) for nitrogen oxides, carbon monoxide, carbon dioxide, and ammonia emissions on the exhaust of each combined-cycle powerblock. Emissions limits are for each combustion turbine/duct burner block. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA/OAR Method 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 0.0063 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 13.9 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 13.9 tpy 12-month rolling basis
*PA-0315 | HILLTOP ENERGY CENTER, LLC | HILLTOP ENERGY CENTER, LLC | GREENE | PA | 15351 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 30-00233B | 4911 | 221112 | 110066828222 | &nbsp; | 04/12/2017 &nbsp;ACT | 2018-12-21 | 2019-03-26 | U |  | The project consists of a single power block in a one-on-one (1x1), combined cycle, single shaft configuration, including a combustion turbine (CT) and heat recovery steam generator (HRSG) with a steam turbine (ST). â€¢ One (1) 3,509 MMBtu/hr General Electric International, Inc. (GE) model no. GE 7HA.02 natural gas-fired combined cycle combustion turbine equipped with a heat recovery steam generator (HRSG) with supplemental 981.4 MMBtu/hr natural gas fired duct burners; controlled by selective catalytic reduction and oxidation catalyst. â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. â€¢ One (1) 500 gallon firewater pump diesel storage tank. â€¢ One (1) 35,000 gallon 19% aqueous ammonia storage tank. â€¢ Lubricating oil storage tanks. â€¢ Miscellaneous components in natural gas service, and SF6 containing circuit breakers; controlled by leak detection and repair (LDAR). â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. | The project consists of a single power block in a one-on-one (1x1), combined cycle, single shaft configuration, including a combustion turbine (CT) and heat recovery steam generator (HRSG) with a steam turbine (ST). â€¢ One (1) 3,509 MMBtu/hr General Electric International, Inc. (GE) model no. GE 7HA.02 natural gas-fired combined cycle combustion turbine equipped with a heat recovery steam generator (HRSG) with supplemental 981.4 MMBtu/hr natural gas fired duct burners; controlled by selective catalytic reduction and oxidation catalyst. â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. â€¢ One (1) 500 gallon firewater pump diesel storage tank. â€¢ One (1) 35,000 gallon 19% aqueous ammonia storage tank. â€¢ Lubricating oil storage tanks. â€¢ Miscellaneous components in natural gas service, and SF6 containing circuit breakers; controlled by leak detection and repair (LDAR). â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. | Combustion Turbine without Duct Burner | 15.21 | Natural Gas | 3509 | MMBtu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0072 | LB | MMBTU | BACT-PSD |  | U | 0 | U | 105.28 | TPY |  | 0 |  |  | 0 | 0 | N
*PA-0319 | RENAISSANCE ENERGY CENTER | APV RENAISSANCE PARTNERS | GREENE | PA | 15320 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 30-00235A | 4911 | 221112 | Not Found | 03/17/2017 &nbsp;ACT | 08/27/2018 &nbsp;ACT | 2019-03-26 | 2019-10-11 | U |  | This Plan Approval is to allow the construction and temporary operation of a natural gas-fired combined cycle power plant to be located in Monongahela Township, Greene County. with Two (2) Siemens, SGT6-8000H (or equivalent), natural gas-fired combustion turbines 3,580 MMBtu/hr heat input rating (LHV) each (controlled with low NOx burners), including natural gas-fired duct burners, 914.1 MMBtu/hr heat input rating each; controlled by Ultra-low NOx combustors, SCR, and oxidation catalysts; 1,127 MW total net generating capacity. One (1) natural gas-fired auxiliary boiler, 90 MMBtu/hr heat input rating. One (1) Cummins model #CFP15E-F20 (or equivalent), diesel-fired fire pump engine, 411 bhp rating; including One (1) diesel fuel storage tank, 2,175 gallons One (1) Caterpillar 3516 (or equivalent), diesel-fired emergency generator engine rated at 2000 kW. Miscellaneous components in natural gas service, and circuit breakers; controlled by leak detection and repair (â€œLDARâ€). One (1) aqueous ammonia (19%) storage vessel rated at 19,000 gallons (or as determined during final design). |  | COMBUSTION TURBINE UNIT w/o DUCT BURNERS UNIT | 15.21 | Natural Gas | 2665.9 | MMBtu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0043 | LB/MMBTU | HR | BACT-PSD |  | U | 0 | U | 121.72 | TPY |  | 0 |  |  | 0 | 0 | N
TX-0590 | KING POWER STATION | PONDERA CAPITAL MANAGEMENT GP INC | HARRIS | TX | 77044 | USA | MARK CHRISOS | (781) 993-3036 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Katherine Stinchcomb (512) 239-1583 katherine.stinchcomb@tceq.texas.gov | PSDTX1125 AND N75, 84289 | 4911 | 221119 | 110040440902 | 04/05/2010 &nbsp;ACT | 08/05/2010 &nbsp;ACT | 2011-08-26 | 2020-02-03 | A |  | Four combined-cycle natural gas-fired combustion turbines | State permit number 84289 Nonattainment permit number N75 | Turbine | 15.21 | natural gas | 1350 | MW | The plant will be designed to generate 1,350 nominal megawatts of power. There are two configuration scenarios: either four Siemens SGT6-5000F CTGs in combined-cycle mode (Scenario A) or four GE Frame 7FA CTGs in combined cycle mode (Scenario B). Scenario B also includes one or two auxiliary boilers. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | use of low ash fuel (natural gas or low sulfur diesel as a backup) | 11.1 | LB/H |  | BACT-PSD |  | U | 0 | U | 19.8 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 represents Scenario A (Siemens turbines) and Emission Limit 2 represents Scenario B (GE turbines).
TX-0600 | THOMAS C. FERGUSON POWER PLANT | LOWER COLORADO RIVER AUTHORITY | LLANO | TX | 7657 | USA | JOE BENTLEY | 512-473-3272 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tan Nguyen 512-239-3445 tan.nguyen@tceq.texas.gov | PSDTX1244 & 93938 | 4911 | 221112 | 110035336222 | 07/27/2011 &nbsp;ACT | 09/01/2011 &nbsp;ACT | 2011-09-02 | 2020-02-03 | B |  | Power Plant. Two natural gas-fired combined cycle turbine generators (GE 7FA) with unfired HRSG | 93938 | Natural gas-fired turbines | 15.21 | natural gas | 390 | MW | (2) GE7FA at 195 MW each, (1) steam turbine at 200 MW. Each turbine is equipped with an unfired heat recovery steam generator (HRSG), which provides steam for the steam turbine. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | pipeline quality natural gas | 33.43 | LB/H | 1-H | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies to total PM and PM10 also
TX-0618 | CHANNEL ENERGY CENTER LLC | CHANNEL ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX955M1, N021M1, 42179 | 4911 | 221112 | 110034690564 | 09/04/2012 &nbsp;ACT | 10/15/2012 &nbsp;ACT | 2012-10-24 | 2020-02-03 | B |  | Combustion turbine (Siemens 501F)/duct burners (475 MMBtu/hr) with heat recovery steam generator | 42179 and N021M1 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | The turbine is a Siemens 501F rated at a nominal 180 MW and the duct burner will have a maximum design heat input of 475 MMBtu/hr. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion and the use of gaseous fuel | 27 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0619 | DEER PARK ENERGY CENTER | DEER PARK ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX979M2, N036M2, 45642 | 4911 | 221112 | 110017743254 | 08/13/2012 &nbsp;ACT | 09/26/2012 &nbsp;ACT | 2012-10-25 | 2020-02-03 | B |  | The Deer Park Energy Center is a combined cycle cogeneration facility consisting of five Siemens/Westinghouse 501F combustion turbine generators, each with a 725 MMBtu/hr duct burner and heat recovery steam generator. | 45642 and N036M2 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | natural gas-fired combined cycle turbine generator with a heat recovery steam generator equipped with a duct burner. The turbine is a Siemens 501F rated at a nominal 180 megawatts and the DB will have a maximum design rate capability of 725 million British thermal units per hour | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 27 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0620 | ES JOSLIN POWER PLANT | CALHOUN PORT AUTHORITY | CALHOUN | TX |  | USA | CHARLES HAUSMANN | 361-987-2813 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1256, 96336 | 4911 | 221112 | 110001866641 | 05/31/2012 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2012-11-14 | 2020-02-03 | B |  | Three gas-fired combined cycle turbine generators, including a steam turbine generator, to replace the existing steam boiler/turbine generator. | 96336 | Combined cycle gas turbine | 15.21 | natural gas | 195 | MW | The three combustion turbine generators (CTG) will be the General Electric 7FA, each with a maximum base-load electric power output of approximately 195 megawatts (MW). The steam turbine is rated at approximately 235 MW. This project also includes the installation of two emergency generators, one fire water pump, and auxiliary equipment. No duct burners. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 18 | LB/H | PER TURBINE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 | 221122 | Not Found | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2019-03-06 | A |  | Combinec Cycle Electric Generating Plant | 103839 | combined cycle turbine | 15.21 | natural gas | 700 | MW | The generating equipment consists of two natural gas-fired combustion turbines (CTs), each exhausting to a fired heat recovery steam generator (HRSG) to produce steam to drive a shared steam turbine generator. The steam turbine is rated at 271 MW of electric output. Three models of combustion turbines are being considered for this site: the General Electric 7FA.05, the Siemens SGT6-5000F(4), and the Siemens SGT6-5000F(5). The final selection of the combustion turbine will not be made until after the permit is issued. Plant output will range between 637 and 735 MW, depending on the model turbine selected. Duct Burners are rated at 750 MMBtu/hr each. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | pipeline quality natural gas and good combustion practices | 26.2 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Turbine models ranged from 25.5-26.2 lb/hr
*TX-0660 | FGE TEXAS POWER I AND FGE TEXAS POWER II | FGE POWER LLC | MITCHELL | TX | 79565 | USA | EMERSON FARRELL | 281-362-2830 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX1364 & 110025 | 3511 | 221112 | NOT FOUND | 10/23/2013 &nbsp;ACT | 03/24/2014 &nbsp;ACT | 2014-06-13 | 2020-03-05 | U |  | Electric Generating Utility | TCEQ Permit No. 110025 | Alstom Turbine | 15.21 | Natural Gas | 230.7 | MW | Four (4) Alstom GT24 CTGs, each with a HRSG and DBs, max design capacity 409 MMBtu/hr | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur fuel, good combustion practices | 2 | PPMVD |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057188626 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.21 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (6) GE LM2500+ DLE turbines that drive the ethylene section compressors with waste heat recovery for amine solution regeneration. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.72 | LB/H | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Natural gas is the fuel. PM and PM10 are equal to PM2.5.
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Combustion Turbine | 15.21 | natural gas | 87 | MW | The exhaust heat from the turbine will be used to heat a heating medium which is used to regenerate rich amine from the acid gas removal system. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 15.22 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0698 | BAYPORT COMPLEX | AIR LIQUIDE LARGE INDUSTRIES U.S., L.P. | HARRIS | TX |  | USA | JASON MILLER | (281) 474-8243 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 | 9346 PSDTX612M2 | 4931 | 325120 | 110000462758 | 07/27/2012 &nbsp;ACT | 09/05/2013 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | Air Liquid currently operates a cogeneration facility in Pasadena, Texas (Bayou Cogeneration Plant). The permit amendment submitted by Air Liquide will authorize a redevelopment project of its cogeneration plant. The proposed project will involve the replacement of four existing gas-fired turbines (GE 7EA) with similar gas-fired turbines (GE 7EA), the addition of three new gas-fired boilers rated at 550 MMBtu/hr and the removal of three existing gas-fired boilers rated at 443 MMBtu/hr. |  | (4) cogeneration turbines | 15.21 | natural gas | 90 | MW | (4) GE 7EA turbines providing power and process steam | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas as fuel, includes PM and PM10
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | (2) combined cycle turbines | 15.21 | natural gas | 650 | MW | The specific equipment includes two combustion turbines (CTs) connected to electric generators, producing between 183 and 232 MW of electricity, depending on ambient temperature and the selected CT. The two HRSGs use duct burners rated at 750 MMBtu/hr each to supplement the heat energy from the CTs. The steam from the two HRSGs is combined and routed to a single steam turbine driving a third electric generator with an electricity output capacity of 271 MW. Depending on the selected CT, total plant output at 59Â°F is between 637 MW and 735 MW. The applicant is considering three models of CT; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) Siemens SGT6-5000F(4); or (3) Siemens SGT6-5000F(5). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas as fuel, includes PM and PM10
TX-0709 | SAND HILL ENERGY CENTER | CITY OF AUSTIN | TRAVIS | TX |  | USA | JOSEPH RAVI | (512) 322-6284 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez (512) 239-5220 Ruth.alvirez@tceq.texas.gov | 48106, PSDTX1012M2 | 4911 | 221112 | 110008975804 | 03/20/2015 &nbsp;ACT | 09/13/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | GE 7FA Natural Gas-fired Combined Cycle Turbine with DB fired HRSG |  | Natural gas-fired combined cycle turbines | 15.21 | Natural Gas | 173.9 | MW |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Natural Gas fired.
TX-0710 | VICTORIA POWER STATION | VICTORIA WLE L.P. | VICTORIA | TX |  | USA | GARY CLARK | (361) 947-9934 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | 108258 PSDTX1348 | 4911 | 221112 | 110000501154 | 02/14/2013 &nbsp;ACT | 12/01/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | The facility is currently authorized under Standard Permit No. 80878 and several Permits by Rule (PBR), including Â§106.263 for maintenance, startup, and shutdown (MSS) (PBR Registration No. 94387) and Title V Permit No. O-35. Victoria proposes to install an additional natural gas-fired turbine (GT) and HRSG with duct burners at the Victoria Station. The resulting new facility will be a combined cycle generating facility in a 2x2x1 configuration (two combustion turbines, two HRSGs with duct burners, and one steam turbine). |  | combined cycle turbine | 15.21 | natural gas | 197 | MW | General Electric 7FA.04 at 197 MW nominal ouput. The duct burners will be capable of a maximum natural gas firing rate of up to 483 MMBtu/hr (HHV). The duct burners may be fired additional hours; however, total annual firing will not exceed the equivalent of 4,375 hours at maximum capacity per duct burner. The available capacity of the existing steam turbine will be increased from 125 MW in its existing 1x1x1 configuration to approximately 185 MW in the 2x2x1 configuration. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas as fuel, includes PM and PM10
TX-0712 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER COMPANY | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | (205) 257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tzvi Shalem 512-239-1310 tzvi.shalem@tceq.texas.gov | 111393 PSDTX1368 | 4911 | 221112 | 110007199735 | 06/27/2013 &nbsp;ACT | 11/20/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | Southern Power Company (SPC) is proposing to construct an electric generating facility near Trinidad, Henderson County, Texas. The Trinidad Generating Facility (TGF) will include a natural gas-fired combined cycle combustion turbine generator (CTG) equipped with heat recovery steam generator (HRSG) and duct burners (DB). |  | combined cycle turbine | 15.21 | natural gas | 497 | MW | The facility will consist of a Mitsubishi Heavy Industries (MHI) J model gas fired combustion turbine nominally rated at 497 megawatts (MW) equipped with a HRSG and DB with a maximum design capacity of 402 million British thermal units per hour (MMBtu/hr). The gross nominal output of the CTG with HRSG and DB is 530 MW. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas as fuel
TX-0713 | TENASKA BROWNSVILLE GENERATING STATION | TENASKA BROWNSVILLE PARTNERS, LLC | CAMERON | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 108411 PSDTX1350 | 4911 | 221112 | unknown | 02/21/2013 &nbsp;ACT | 04/29/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | Tenaska proposes a new electric power plant, using combined cycle gas turbine (CCGT) technology and fueled by pipeline quality natural gas. The proposed permit authorizes two CTs (2x1 CCGT), although the final design selected by Tenaska may only consist of one CT (1x1 CCGT). |  | (2) combined cycle turbines | 15.21 | natural gas | 274 | MW | Each CTG is site-rated at 274 MW gross electric output at 62Â°F ambient temperature. At this condition, two HRSGs with full duct burner firing produce enough steam to generate an additional 336 MW, for a total of 884 MW gross, or with about 5% losses, about 840 MW net electric output. Under summertime conditions, the net output is approximately 800 MW with the 2x1 CCGT configuration or about 400 MW with the 1x1 CCGT configuration. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas as fuel, includes PM and PM10
TX-0714 | S R BERTRON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | HARRIS | TX |  | USA | CRAIG ECKBERG | (713) 537-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | 102731 PSDTX1294 | 4911 | 221112 | 110034988413 | 05/10/2012 &nbsp;ACT | 12/19/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | NRG Texas is proposing to construct an additional electric power generation station at the Bertron Power Project which will generate electric power for sale on the wholesale electric market. The Bertron Power Project will include two power blocks that can be operated in combined cycle mode. |  | (2) combined cycle turbines | 15.21 | natural gas | 240 | MW | The gas turbines will be one of three options: (1) Two Siemens Model F5 (SF5) CTGs each rated at nominal capability of 225 megawatts (MW). Each CTG will have a duct fired HRSG with a maximum heat input of 688 million British thermal units per hour (MMBtu/hr). (2) Two General Electric Model 7FA (GE7FA) CTGs each rated at nominal capability of 215 MW. Each CTG will have a duct fired HRSG with a maximum heat input of 523 MMBtu/hr. (3) Two Mitsubishi Heavy Industry G Frame (MHI501G) CTGs each rated at a nominal electric output of 263 MW. Each CTG will have a duct fired HRSG with a maximum heat input of 686 MMBtu/hr. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas as fuel, includes PM and PM10
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041470431 | 02/24/2015 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2020-01-31 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | efficient combustion, natural gas fuel | 43 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0751 | EAGLE MOUNTAIN STEAM ELECTRIC STATION | EAGLE MOUNTAIN POWER COMPANY LLC | TARRANT | TX |  | USA | PAUL COON | 214-875-8647 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.Alvirez@tceq.texas.com | 117026, PSDTX1390, N194 | 4911 | 221122 | 110005028638 | 03/26/2015 &nbsp;ACT | 06/18/2015 &nbsp;ACT | 2015-06-22 | 2016-07-06 | B |  | Eagle is proposing to construct two new combined cycle combustion turbines (CTG) which will generate electric power for sale on the wholesale electric market. The ancillary equipment includes an auxiliary boiler, a firewater pump, an emergency generator, a steam turbine, and various support facilities. |  | Combined Cycle Turbines (&gt;25 MW) â€“ natural gas | 15.21 | natural gas | 210 | MW | Two power configuration options authorized Siemens â€“ 231 MW + 500 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 210 MW + 349.2 MMBtu/hr duct burner | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 35.47 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 81.88 | T/YR |  | 0 |  |  | 0 | 0 | N |  | Good combustion practices, low sulfur fuel
TX-0767 | LON C. HILL POWER STATION | LON C. HILL, L.P. | NUECES | TX |  | USA | MATTHEW LINDSEY | 713-358-9734 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem, 512-239-1310, Tzvi.Shalem@tceq.texas.gov | 114911 AND PSDTX1380 | 4911 | 221122 | 110000501127 | 07/15/2015 &nbsp;ACT | 10/02/2015 &nbsp;ACT | 2015-09-23 | 2016-07-06 | A |  | The Lon C. Hill Power Station (LCHP) will include two natural gas-fired combined cycle combustion turbines (CTGs) equipped with dry low NOx burners (DLNs), heat recovery steam generators (HRSG), and natural gas-fired duct burners (DBs). Ancillary equipment includes evaporative coolers or inlet chillers, a single steam turbine (ST), auxiliary boiler, emergency generator, firewater pump, two cooling towers, oil water separator, degreaser, two diesel storage tanks, gasoline storage tank, selective catalytic reduction (SCR) and ammonia (NH3) handling systems including an NH3 storage tank, and two water tanks. The LCHP will be a 2x1 combined cycle power plant consisting of two CTGs, two HRSGs and one ST. The CTGs and ST will be one of two options: two Siemens SCC6-5000 CTGs and a SST6-5000 ST, or two General Electric 7FA CTGs and a D-11 ST. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 195 | MW | Two power configuration options authorized Siemens â€“ 240 MW + 250 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 195 MW + 670 MMBtu/hr duct burner | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and use of pipeline quality natural gas | 16 | LB/HR |  | BACT-PSD | NSPS | N | 0 | U | 109.5 | TPY |  | 0 |  |  | 0 | 0 | N
TX-0773 | FGE EAGLE PINES PROJECT | FGE EAGLE PINES, LLC | CHEROKEE | TX |  | USA | EMERSON FARRELL | 281-407-7749 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, 512-239-1095, Erik.Hendrickson@tceq.texas.gov | 131316, PSDTX1454, AND GHGPSDT | 4911 | 221112 | UNKNOWN | 09/10/2015 &nbsp;ACT | 11/04/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | The FGEEP Project will include three natural gas-fired combined cycle (NGCC) power blocks, each block comprised of two gas-fired combustion turbines, two supplemental fired duct burners (DBs) heat recovery steam generators (HRSGs), and one steam turbine. FGEEP selected Alstom GT36 combustion turbines (CTs), each nominally rated at 321 megawatts (MW). Each HRSG is equipped with DBs that will have a maximum design heat input capacity of 799 million British thermal units per hour (MMBtu/hr). The CTs and DBs are fueled with pipeline quality natural gas. Each power block will also have a steam turbine generator designed to produce approximately 502 MW with the additional duct firing. Each of the three blocks will include the following ancillary equipment: one multi-cell condenser/cooling tower, one emergency generator, one firewater pump, two diesel storage tanks, and pressurized aqueous ammonia storage tanks. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 321 | MW | Alstom GT36 combustion turbines (321 MW)+ 799 million British thermal units per hour (MMBtu/hr) duct burner | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 21.4 | LB/H |  | BACT-PSD |  | N | 0 | U | 93.7 | T/YR |  | 0 |  |  | 0 | 0 | N
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND LOW SULFUR FUEL | 19.35 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0789 | DECORDOVA STEAM ELECTRIC STATION | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas.gov | 107569 AND PSDTX1432 | 4911 | 221112 | 110008149217 | 12/23/2015 &nbsp;ACT | 03/08/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | The DeCordova Station will consist of two combustion turbine generators (CTGs) operating in simple cycle or combined cycle modes. The gas turbines will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE). Simple cycle operations limited to 2,500 hr/yr. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND LOW SULFUR FUEL | 35.47 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.21 | natural gas | 10 | M TONNES/YR | Four GE Frame 7E gas turbines for refrigeration and compression at the site | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 11.07 | LB/H |  | BACT-PSD |  | N | 0 | U | 42.15 | T/YR |  | 0 |  |  | 0 | 0 | N |  | Dry low NOx burners, good combustion practices, pipeline quality sweet natural gas fuel
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Simple Cycle Electrical Generation Gas Turbines 15.210 | 15.21 | natural gas | 34 | MW | Nine GE PGT25+G4 gas turbines for electrical generation at the site at 34 MW/turbine | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Equipment specifications & work practices - Good combustion practices and use of low carbon, low sulfur fuel | 2.32 | LB/H |  | BACT-PSD |  | N | 0 | U | 8.84 | T/YR |  | 0 |  |  | 0 | 0 | N
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Combined Cycle Turbine with Heat Recovery Steam Generator, fired Duct Burners, and Steam Turbine Generator | 15.21 | NATURAL GAS | 426 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines with HRSGs and Steam Turbine Generators | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; good combustion practices | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | PIPELINE NATURAL GAS, GOOD COMBUSTION | 125.7 | TON/YR |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
VA-0315 | WARREN COUNTY POWER PLANT - DOMINION | VIRGINIA ELECTRIC AND POWER COMPANY | WARREN | VA | 22630 | USA | ROBERT BISHA | 804-273-3010 | ROBERT.M.BISHA@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Manager, Mr. Janardan Pandey, by phone at (540) 574-7817 or by e-mail: Janardan.Pandey@deq.virginia.gov | 81391-007 | 4911 | 221112 | 110040513110 | 09/03/2010 &nbsp;ACT | 12/17/2010 &nbsp;ACT | 2012-09-28 | 2015-03-30 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Virginia Electric and Power Company (Dominion) has proposed to construct and operate a combined-cycle electric power generating facility in Warren County with a nominal generating capacity of 1280 megawatts (MW) at ISO (International Organization for Standardization) conditions. | Equipment to be constructed at ths facility consists of: 3 Mitsubishi Model M501 GAC natural gas-fired combined-cylce turbines, each rated at 299,600 kW (2,996 MMBtu/hr. Each equipped with a heat recovery steam generator (HRSG) having a duct burner with a design rating of 500 MMBtu/hr. This permit supersedes the previous permit issued on 7/30/2004 to CPV Warren LLC. | COMBINED CYCLE TURBINE &amp; DUCT BURNER, 3 | 15.21 | Natural Gas | 2996 | MMBTU/H | Emissions are for one of three units (Mitsubishi natural gas-fired combustion turbine (CT) generator,Model M501 GAC). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Natural Gas only, fuel has maximum sulfur content of 0.0003% by weight. | 8 | LB/H | 3 HR AVG. (WITHOUT DUCT BURNER FIRING) | BACT-PSD |  | U | 0 | U | 14 | LB/H | 3 HR. AVG. (WITH DUCT BURNER FIRING) | 0 |  |  | 0 | 0 | N
VA-0319 | GATEWAY COGENERATION 1, LLC - SMART WATER PROJECT | GATEWAY GREEN ENERGY | PRINCE GEORGE | VA | 23875-3000 | USA | T. EDWARD MCDANIEL | 972-638-8798 | EMCDANIEL@GGEHLLC.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52375-002 | 4911 | 221112 | 110045446718 | 01/11/2012 &nbsp;ACT | 08/27/2012 &nbsp;ACT | 2013-01-16 | 2015-05-29 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Combined cycle electrical power generating facility (160 MW), consisting of two combusion turbines (Rolls Royce Trent 60 WLE) with associated HRSG and no duct burning. |  | COMBUSTION TURBINES, (2) | 15.21 | Natural Gas | 593 | MMBTU/H | Burns primarily natural gas but has the capacity to burn up to 500 hours of ultra low sulfur diesel fuel (ULSD) as backup. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean burning fuels and good combustion practices. | 5 | LB/H | 3 H AVG | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Stack testing and visible emission evaluation.
VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404 | 4911 | 221112 | 110055066440 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2019-06-19 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | COMBUSTION TURBINE GENERATORS, (3) | 15.21 | Natural Gas | 3442 | MMBTU/H | Three (3) Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners (natural gas-fired). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur/carbon fuel and good combustion practices. | 0.0033 | LB/MMBTU | 3 H AVG/WITHOUT DUCT BURNING | BACT-PSD | NSPS | U | 0 | U | 9.7 | LB/H | 3 H AVG/WITHOUT DUCT BURNING | 0 |  |  | 0 | 0 | N
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Option 1 - Normal Operation | 15.21 | natural gas | 34000 | MMCF/YR | Option 1: Two on one configuration: 3,482 MMBtu/hr combustion turbine with 475 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and the use of pipeline quality natural gas with a maximum sulfur content of 0.4 gr/100 scf on a 12-month rolling average. | 0.0069 | LB/MMBTU WITHOUT DUC | AV OF 3 TEST RUNS | BACT-PSD | SIP | N | 0 | N | 0.0049 | LB/MMBTU WITH DUC | AV OF 3 TEST RUNS | 0 |  |  | 0 | 0 | N |  | Additional limits: 12.2 lb/hr without duct burning; 17.3 lb/hr with duct burning. These short term limits apply at all times.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combusion Turbine - Option 2 - Normal Operation | 15.21 | Natural Gas | 35000 | MMCF/YR | Option 2: Two on one configuration: 3,116 MMBtu/hr combustion turbine with 991 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and the use of pipeline quality natural gas with a maximum sulfur content of 0.4 gr/100 scf on a 12-month rolling average. | 0.0065 | LB/MMBTU | AV OF 3 TEST RUNS/WITHOUT DUCT BURNING | BACT-PSD | SIP | N | 0 | N | 0.0065 | LB/MMBTU | AV OF 3 TEST RUNS/WITH DUCT BURNING | 0 |  |  | 0 | 0 | N |  | Additional limits: 13.7 lb/hr without duct burning; 24.2 lb/hr with duct burning. These short term limits apply at all times.
*VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2020-03-18 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/hr natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/hr combustion turbine. Emission limits reflect the operation of each of the three turbines. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Controlled by good combustion practices (e.g. controlled fuel/air mixing, adequate temperature, and gas residence time) and the use of pipeline-quality natural gas with a maximum sulfur content of 0.4 grains per 100 scf, on a 12-month rolling average. | 0.0052 | LB/MMBTU | AVG OF 3 TEST RUNS | BACT-PSD | NSPS , SIP | N | 0 | N | 12.3 | LB/HR | AVG OF 3 TEST RUNS | 0 |  |  | 0 | 0 | N |  | Short term limits apply at all times. Additional limit: 53.9 tons/year
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Combined Cycle Turbine/Duct Burner | 15.21 | Natural Gas | 2419.61 | mmBtu/Hr | This entry is for both of two identical units at the facility. Nominal 197 mW General Electric Frame 7FA.04 Turbine w/ Duct Burner - throughput denotes aggregate heat input of turbine and duct burner (HHV). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Good Combustion Practices, Inlet Air Filtration, & use of Natural Gas | 8.9 | LB/H |  | BACT-PSD |  | U | 0 | U | 0.0037 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N |  | Assume all PM is PM2.5 or less. PM2.5 limit is applicable with and without duct firing.
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | PUC QUALITY NATURAL GAS | 12 | LB/H | 12-MONTH ROLLING AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | PUC QUALITY NATURAL GAS | 18 | LB/H | 12-MONTH ROLLING AVG (W/ DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | Natural Gas | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | PUC QUALITY NATURAL GAS | 12 | LB/H | 12-MONTH ROLLING AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 18 | LB/H | 12-MONTH ROLLING AVG (W/ DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total (TPM) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 8.91 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total (TPM) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 11.78 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total (TPM) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 8.91 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total (TPM) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 11.78 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (WARM STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 12 | LB/H | WARM STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 30.8 | LB/EVENT | WARM STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF WARM STARTUPS NOT TO EXCEED 180 MINUTES; 2) WARM STARTUP MEANS A STARTUP THAT IS NOT A HOT OR COLD STARTUP
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (HOT STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 12 | LB/H | HOT STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 12.8 | LB/EVENT | HOT STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF HOT STARTUPS NOT TO EXCEED 90 MINUTES; 2) HOT STARTUP MEANS A STARTUP WHEN THE COMBUSTION TURBINE HAS BEEN IN OPERATION DURING THE PRECEDING 8 HOURS
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 6 | LB/H | TURBINE SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 6 | LB/EVENT | TURBINE SHUTDOWN PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF SHUTDOWN NOT TO EXCEED 30 MINUTES; 2) SHUTDOWN MEANS THE PERIOD BEGINNING WITH THE LOWERING OF EQUIPMENT FROM BASE LOAD AND LASTING UNTIL FUEL FLOW IS COMPLETELY OFF AND COMBUSTION HAS CEASED
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Particulate matter, total (TPM) | Other - EPA METHODS 5 & 202, OR METHODS 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 0.0048 | LB/MMBTU | 9-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0.0049 | LB/MMBTU | 9-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055426409 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Four combined cycle combution turbines | 15.21 | natural gas | 373 | MMBTU/H | Three GE, LMS6000 PF, natural gas-fired, combined cycle CTG, rated at 373 MMBtu per hour each, based on HHV and one (1) HRSG each with no Duct Burners | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustor design | 4.3 | LB/H | AVE OVER STACK TEST LENGTH | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
DE-0024 | GARRISON ENERGY CENTER | GARRISON ENERGY CENTER, LLC/ CALPINE CORPORATION | KENT COUNTY | DE | 19901 | USA | STUART WIDOM | 302-468-5324 | STUART.WIDOM@CALPINE.COM | 3 | DE001 | DELAWARE DEPT OF NATURAL RES & ENV CTRL | MR. PAUL FOSTER | (302)323-4542 | PAUL.FOSTER@STATE.DE.US |  | APC-2012/0098 | 4911 | 221112 | 110043806931 | 04/04/2012 &nbsp;ACT | 01/30/2013 &nbsp;ACT | 2013-05-13 | 2014-01-28 | A |  | one (1) 309 MW GE Combined Cycle Combustion Turbine Generating system fired principally on Natural Gas, one (1) 86,000 GPM Cooling Tower, one (1) 1,400,000 ULSD Storage Tank |  | Unit 1 | 15.21 | Natural Gas | 2260 | million BTUs |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N | Fuel Usage Restriction to natural gas and low sulfur distillate oil | 120.4 | TONS | 12 MONTH ROLLING AVERAGE | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Particulate matter, total (TPM) | Other - No test required | (Particulate Matter (PM)) | PM | P | Use of clean fuels | 2 | GRAIN S/100 SCF GAS | FOR NATURAL GAS | BACT-PSD |  | U | 0 | U | 0.0015 | % S IN ULSD | FOR ULSD | 0 |  |  | 0 | 0 | N |  | Use of low-sulfur fuels prevents PM formation. Also, subject to 10% opacity limit with annual Method 9 test.
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #1 - combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr | two identical Siemens SGT6-5000F combined cycle turbines without duct firing, each at 2258 mmBtu/hr generating approx. 300 MW each. | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | N |  | 0.01 | LB/MMBTU | AVG. OF 3 ONE HOUR TEST RUNS | BACT-PSD |  | U | 0 | U | 77.1 | TON/YR | 12-MONTH ROLLING | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #2 -combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | N |  | 0.01 | LB/MMBTU | AVERAGE OF 3 ONE-HOUR TEST RUNS | BACT-PSD |  | U | 0 | U | 77.1 | TON/YR | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | 0.01 lb/mmBtu at steady state operation 77.1 tpy includes startup, shutdown and malfunction
IL-0130 | JACKSON ENERGY CENTER | JACKSON GENERATION, LLC | WILL | IL | 60421 | USA | JAMES KIEFER | 847-908-2833 | JKEIFER@POWERUSA.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov |  | 17040013 | 4911 | 221112 | Not Found | 04/04/2017 &nbsp;ACT | 12/31/2018 &nbsp;ACT | 2019-07-23 | 2020-04-16 | A |  | The proposed facility is designed to generate baseload power. It will consist of two combined-cycle generating units, each with a combustion turbine and associated heat recovery steam generator (HRSG). The turbines would only burn natural gas. Other units include an auxiliary boiler, fuel heater, emergency engines, natural gas piping and components, circuit breakers and roadways | Additional pollutants: Sulfuric Acid Mist: 48 tons/year; GHG as CO2e: 4,752,085 tons/year | Combined-Cycle Combustion Turbine | 15.21 | Natural Gas | 3864 | mmBtu/hr | Combined-cycle combustion turbines with heat recovery steam generator (HRSG). Turbines will have inlet evaporative cooling systems to cool inlet air during warm weather to increase power output. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0026 | LB/MMBTU | 3-HR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0.0042 | LB/MMBTU | 3-HR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 is applicable to PM. Emission Limit 2 is applicable to PM10/PM2.5. For PM, pounds/hour emission limits for startup/shutdown/commissioning are 11.5 (without duct burner) and 12.3 (with duct burner). For PM10/PM2.5, pounds/hour emission limits for startup/shutdown/commissioning are 12.4 (without duct burner) and 19.8 (with duct burner)
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Combined cycle combustion turbine | 15.21 | Natural gas | 250 | MW | Combined cycle combustion unit; this unit includes a heat recovery steam generator (HRSG) with supplemental natural gas duct firing (duct burners) and a condensing steam turbine generator with SCR and CO catalyst. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | dry low NOx burners heat recovery steam generator (HRSG) | 30.2 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Combined Cycle Refrigeration Compressor Turbines (8) | 15.21 | natural gas | 286 | MMBTU/H | GE LM2500+G4 | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and fueled by natural gas | 2.08 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | also for PM10 and PM2.5
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.006 | LB/MMBTU | EACH CTG; TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 11432 | 0 | N | 2012 | Cost effectiveness information: Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet scrubber = $16,663/ton
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.004 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2012 | Cost effectiveness information: Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet scrubber = $16,663/ton
*MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2019-12-19 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur fuel and good combustion practices. | 0.0034 | LB/MMBTU | HOURLY; EACH UNIT | BACT-PSD |  | N | 0 | U | 123 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | Emission limit 2 is 123 tons/year based upon a 12-month rolling time period as determined at the end of each calendar month. Limit applies to the entire flexible group. The lowest cost (for a fabric filter) was greater than $87,000/ton of total PM controlled. Therefore, add-on controls were not considered economically feasible for particulate control.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 1 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2022 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices along with clean fuels | 0.0068 | LB/MMBTU | HHV, 3 HR AVG. SEE NOTES. | BACT-PSD |  | U | 0 | U | 58.62 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  |  | 0 | 0 | N |  | Limits are for single turbine except as noted. 0.0068 lb/mmbtu HHV, 3 hour average with duct burners. 9.5 lb/h, 3 hour average without duct burners. 15.8 lb/h, 3 hour average with duct burners. 58.62 t/yr per rolling 12 month period.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 2 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2144 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices along with clean fuels | 0.0085 | LB/MMBTU | HHV, 3 HR AVG. SEE NOTES. | BACT-PSD |  | U | 0 | U | 86.7 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  |  | 0 | 0 | N |  | Limits are for single turbine except as noted. 0.0085 lb/mmbtu HHV, 3 hour average with and without duct burners. 15.9 lb/h, 3 hour average without duct burners. 22.2 lb/h, 3 hour average with duct burners. 86.7 t/yr per rolling 12 month period.
OH-0374 | GUERNSEY POWER STATION LLC | GUERNSEY POWER STATION LLC | GUERNSEY | OH | 43723 | USA | MARY KING | (317)447-4513 | MARY@APEXPOWERGROUP.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122594 | 4911 | 221112 | 110070379546 | 04/14/2017 &nbsp;ACT | 10/23/2017 &nbsp;ACT | 2019-03-08 | 2019-06-19 | A |  | 1,650 MW combined cycle combustion turbine electrical generating facility | Installation PTI for a new 1,650 MW combined cycle natural-gas fired turbine plant and associated auxiliary boiler, firewater pumps, emergency generators and fuel gas heaters | Combined Cycle Combustion Turbines (3, identical) (P001 to P003) | 15.21 | Natural gas | 3516 | MMBTU/H | Three identical Combustion Turbines; GE 7HA.02 natural gas-fired lean pre-mix combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,516 MMBtu/hr HHV at 100% load and -18Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 997 MMBtu/hr HHV controlled with catalytic oxidation and selective catalytic reduction (SCR) and cooled with an air-cooled condenser (ACC) used to generate electricity. Throughputs and limits are for a single turbine except as noted. | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | pipeline quality natural gas | 0.0073 | LB/MMBTU | SEE NOTES. | BACT-PSD |  | U | 0 | U | 23.3 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | Limits are for single turbine except as noted. 0.0073 lb/mmbtu with duct burners and without duct burners. Both excluding startup and shutdown. 12.30 lb/h without duct burners. 23.30 lb/h with duct burners. Both excluding startup and shutdown. 290.39 t/yr per rolling 12 month period total for all 3 turbines.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and pipeline quality natural gas | 0.0052 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 18.4 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.00522 lb/mmbtu and 18.4 lb/h with duct burner. 0.00735 lb/mmbtu and 12.0 lb/h without duct burner. 80.2 tons per rolling 12 month period for all operating modes.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and pipeline quality natural gas | 0.005 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 17.7 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.005 lb/mmbtu and 17.7 lb/h with duct burner. 0.00444 lb/mmbtu and 14.10 lb/h without duct burner. 77.5 tons per rolling 12 month period for all operating modes.
PA-0278 | MOXIE LIBERTY LLC/ASYLUM POWER PL T | MOXIE ENERGY LLC | BRADFORD COUNTY | PA |  | USA | KENT J MORTON | (571) 594 - 0150 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MUHAMMAD Q. ZAMAN, ENVIRONMENTAL PROGRAM MANAGER, NORTHCENTRAL REGION | 08Â·00045A | 491 | 221112 | 45-2015223-1 | 09/26/2011 &nbsp;ACT | 10/10/2012 &nbsp;ACT | 2012-12-03 | 2015-04-03 | A |  |  | The project consists of two identical 1 x 1 power blocks, and each block includes a combustion gas turbine and a steam turbine. Each combined-cycle process will also include a heat recovery steam generator and supplemental duct burners. Additionally, one diesel-fired emergency generator, one diesel-fired fire water pump, two diesel fuel storage tanks, two lube oil storage tanks, and one aqueous ammonia storage tank were proposed to be constructed and operated. Each combined-cycle process will be rated at 468 MW or less. | Combined-cycle Turbines (2) - Natural gas fired | 15.21 | Natural Gas | 3277 | MMBTU/H | Two combine cycle Turbines, each with a combustion turbine and heat recovery steam generator with duct burner. Each combined-cycle process will be rated at 468 MW or less. The heat input rating of each combustion gas turbine is 2890 MMBtu/hr (HHV) or less, and the heat input rating of each supplemental duct burner is equal to 387 MMBtu/hr (HHV) or less. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Using fuel with little or no ash and sulfur content. | 0.004 | LB/MMBTU | FOR 468 MW POWERBLOCK | BACT-PSD |  | U | 0 | U | 0.0057 | LB/MMBTU | FOR 454 MW POWERBLOCK | 0 |  |  | 0 | 0 | N |  | FUel sulfur content of 0.4 grain/100scf
PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2018-12-21 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large combustion turbine | 15.21 | Natural Gas | 0 |  | This process entry is for operations with the duct burner. Limits entered are for each turbine. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices with the use of low ash/sulfer fuels | 0.0039 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 11.8 | LB/HR |  | 0 |  |  | 0 | 0 | N
PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2018-12-21 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two combined cycle turbines with out duct burner | 15.21 | Natural Gas | 2291.64 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode, the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. (Operational limits are for each CCCT NG-fired without duct burner) | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.0068 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative Emissions from both CCCT in any 12-month period
PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2018-12-21 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two Combine Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 3001.57 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. . (Operational limits are for each CCCT NG-fired with duct burner) | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.0066 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 159.1 | TONS | ANY 12-MONTH PERIOD | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative emissions from both CCCT in any 12-month period
PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG with duct burner NG only | 15.21 | Natural Gas | 3338 | MMBtu/hr | Emission limits are for each turbine operating with duct burner and do not include startup/shutdown emissions. Tons per year limits is a cumulative value for all three CCCT. CEMS for NOx, CO, and O2. Each CCCT and duct burner have 5 operational scenarios: 1 CCCT with duct burner fired - fueled by NG only 2 CCCT with duct burner fired - fueled by NG blend with ethane 3 CCCT without duct burner fired - fueled by NG only 4 CCCT without duct burner fired - fueled by NG blend with ethane 5 CCCT without duct burner fired - fueled by ULSD (Limited to emergency use only) | Particulate matter, total (TPM) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuel, good combustion practicies | 0.005 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 131.5 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N |  | lb/MMBtu limit is for each turbine and duct burner, TPY is a cumulative total
PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG without duct burner NG only | 15.21 | Natural gas | 0 |  | Emission limits are for each turbine fueled by NG and operating without duct burner being fired and do not include startup/shutdown emissions. | Particulate matter, total (TPM) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuels and good combustion practices | 0.0068 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit is for each turbine and HRSG with the duct burner not fired.
PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064098541 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2018-12-21 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine With Duct Burner | 15.21 | Natural Gas | 3727 | MMBtu/hr | DLN burner, SCR, Oxidation Catalyst and shall maintain and operate the sources and associated air cleaning devices in accordance with good engineering practice. shall install, certify, maintain and operate continuous emission monitoring systems (CEMS) for nitrogen oxides, carbon monoxide, carbon dioxide, and ammonia emissions on the exhaust of each combined-cycle powerblock. Emissions limits are for each combustion turbine/duct burner block. | Particulate matter, total (TPM) | Other - EPA/OAR Method 5 | (Particulate Matter (PM)) | PM | N |  | 0.0063 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 13.9 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 58.0 tpy 12-month rolling basis
*PA-0315 | HILLTOP ENERGY CENTER, LLC | HILLTOP ENERGY CENTER, LLC | GREENE | PA | 15351 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 30-00233B | 4911 | 221112 | 110066828222 | &nbsp; | 04/12/2017 &nbsp;ACT | 2018-12-21 | 2019-03-26 | U |  | The project consists of a single power block in a one-on-one (1x1), combined cycle, single shaft configuration, including a combustion turbine (CT) and heat recovery steam generator (HRSG) with a steam turbine (ST). â€¢ One (1) 3,509 MMBtu/hr General Electric International, Inc. (GE) model no. GE 7HA.02 natural gas-fired combined cycle combustion turbine equipped with a heat recovery steam generator (HRSG) with supplemental 981.4 MMBtu/hr natural gas fired duct burners; controlled by selective catalytic reduction and oxidation catalyst. â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. â€¢ One (1) 500 gallon firewater pump diesel storage tank. â€¢ One (1) 35,000 gallon 19% aqueous ammonia storage tank. â€¢ Lubricating oil storage tanks. â€¢ Miscellaneous components in natural gas service, and SF6 containing circuit breakers; controlled by leak detection and repair (LDAR). â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. | The project consists of a single power block in a one-on-one (1x1), combined cycle, single shaft configuration, including a combustion turbine (CT) and heat recovery steam generator (HRSG) with a steam turbine (ST). â€¢ One (1) 3,509 MMBtu/hr General Electric International, Inc. (GE) model no. GE 7HA.02 natural gas-fired combined cycle combustion turbine equipped with a heat recovery steam generator (HRSG) with supplemental 981.4 MMBtu/hr natural gas fired duct burners; controlled by selective catalytic reduction and oxidation catalyst. â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. â€¢ One (1) 500 gallon firewater pump diesel storage tank. â€¢ One (1) 35,000 gallon 19% aqueous ammonia storage tank. â€¢ Lubricating oil storage tanks. â€¢ Miscellaneous components in natural gas service, and SF6 containing circuit breakers; controlled by leak detection and repair (LDAR). â€¢ One (1) 42 MMBtu/hr natural gas-fired auxiliary boiler. â€¢ One (1) 6.4 MMBtu/hr natural gas-fired fuel gas heater. â€¢ One (1) 2.95 MMBtu/hr, 422 hp diesel-fired emergency firewater pump engine. â€¢ One (1) 18.77 MMBtu/hr, 2,682 hp diesel-fired emergency generator engine. â€¢ Eight-cell, mechanical draft, evaporative cooling tower controlled by drift eliminators. â€¢ One (1) 3,000 gallon emergency generator diesel storage tank. | Combustion Turbine without Duct Burner | 15.21 | Natural Gas | 3509 | MMBtu/hr |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0072 | LB | MMBTU | BACT-PSD |  | U | 0 | U | 105.28 | TPY |  | 0 |  |  | 0 | 0 | N
*PA-0319 | RENAISSANCE ENERGY CENTER | APV RENAISSANCE PARTNERS | GREENE | PA | 15320 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 30-00235A | 4911 | 221112 | Not Found | 03/17/2017 &nbsp;ACT | 08/27/2018 &nbsp;ACT | 2019-03-26 | 2019-10-11 | U |  | This Plan Approval is to allow the construction and temporary operation of a natural gas-fired combined cycle power plant to be located in Monongahela Township, Greene County. with Two (2) Siemens, SGT6-8000H (or equivalent), natural gas-fired combustion turbines 3,580 MMBtu/hr heat input rating (LHV) each (controlled with low NOx burners), including natural gas-fired duct burners, 914.1 MMBtu/hr heat input rating each; controlled by Ultra-low NOx combustors, SCR, and oxidation catalysts; 1,127 MW total net generating capacity. One (1) natural gas-fired auxiliary boiler, 90 MMBtu/hr heat input rating. One (1) Cummins model #CFP15E-F20 (or equivalent), diesel-fired fire pump engine, 411 bhp rating; including One (1) diesel fuel storage tank, 2,175 gallons One (1) Caterpillar 3516 (or equivalent), diesel-fired emergency generator engine rated at 2000 kW. Miscellaneous components in natural gas service, and circuit breakers; controlled by leak detection and repair (â€œLDARâ€). One (1) aqueous ammonia (19%) storage vessel rated at 19,000 gallons (or as determined during final design). |  | COMBUSTION TURBINE UNIT w/o DUCT BURNERS UNIT | 15.21 | Natural Gas | 2665.9 | MMBtu/hr |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0043 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 121.72 |  |  | 0 |  |  | 0 | 0 | N
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | LACEY HARDIN | (615) 532-0545 | Lacey.Hardin@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Natural Gas-Fired Combustion Turbine with HRSG | 15.21 | Natural Gas | 1339 | MMBtu/hr | Turbine throughput is 1019.7 MMBtu/hr when burning natural gas and 1083.7 MMBtu/hr when burning No. 2 oil. Duct burner throughput is 319.3 MMBtu/hr. Duct burner firing will occur during natural gas combustion only. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion design and practices | 0.005 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0.015 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N |  | Limit #1 is for gas combustion, limit #2 is for No. 2 oil combustion
TX-0590 | KING POWER STATION | PONDERA CAPITAL MANAGEMENT GP INC | HARRIS | TX | 77044 | USA | MARK CHRISOS | (781) 993-3036 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Katherine Stinchcomb (512) 239-1583 katherine.stinchcomb@tceq.texas.gov | PSDTX1125 AND N75, 84289 | 4911 | 221119 | 110040440902 | 04/05/2010 &nbsp;ACT | 08/05/2010 &nbsp;ACT | 2011-08-26 | 2020-02-03 | A |  | Four combined-cycle natural gas-fired combustion turbines | State permit number 84289 Nonattainment permit number N75 | Turbine | 15.21 | natural gas | 1350 | MW | The plant will be designed to generate 1,350 nominal megawatts of power. There are two configuration scenarios: either four Siemens SGT6-5000F CTGs in combined-cycle mode (Scenario A) or four GE Frame 7FA CTGs in combined cycle mode (Scenario B). Scenario B also includes one or two auxiliary boilers. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | use low ash fuel (natural gas or low sulfur diesel as a backup) and good combustion practices | 11.1 | LB/H |  | BACT-PSD |  | N | 0 | U | 19.8 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 represents Scenario A (Siemens turbines) and Emission Limit 2 represents Scenario B (GE turbines)
TX-0618 | CHANNEL ENERGY CENTER LLC | CHANNEL ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX955M1, N021M1, 42179 | 4911 | 221112 | 110034690564 | 09/04/2012 &nbsp;ACT | 10/15/2012 &nbsp;ACT | 2012-10-24 | 2020-02-03 | B |  | Combustion turbine (Siemens 501F)/duct burners (475 MMBtu/hr) with heat recovery steam generator | 42179 and N021M1 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | The turbine is a Siemens 501F rated at a nominal 180 MW and the duct burner will have a maximum design heat input of 475 MMBtu/hr. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion and the use of gaseous fuel | 27 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0619 | DEER PARK ENERGY CENTER | DEER PARK ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX979M2, N036M2, 45642 | 4911 | 221112 | 110017743254 | 08/13/2012 &nbsp;ACT | 09/26/2012 &nbsp;ACT | 2012-10-25 | 2020-02-03 | B |  | The Deer Park Energy Center is a combined cycle cogeneration facility consisting of five Siemens/Westinghouse 501F combustion turbine generators, each with a 725 MMBtu/hr duct burner and heat recovery steam generator. | 45642 and N036M2 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | natural gas-fired combined cycle turbine generator with a heat recovery steam generator equipped with a duct burner. The turbine is a Siemens 501F rated at a nominal 180 megawatts and the DB will have a maximum design rate capability of 725 million British thermal units per hour | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion and use of natural gas | 27 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0620 | ES JOSLIN POWER PLANT | CALHOUN PORT AUTHORITY | CALHOUN | TX |  | USA | CHARLES HAUSMANN | 361-987-2813 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1256, 96336 | 4911 | 221112 | 110001866641 | 05/31/2012 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2012-11-14 | 2020-02-03 | B |  | Three gas-fired combined cycle turbine generators, including a steam turbine generator, to replace the existing steam boiler/turbine generator. | 96336 | Combined cycle gas turbine | 15.21 | natural gas | 195 | MW | The three combustion turbine generators (CTG) will be the General Electric 7FA, each with a maximum base-load electric power output of approximately 195 megawatts (MW). The steam turbine is rated at approximately 235 MW. This project also includes the installation of two emergency generators, one fire water pump, and auxiliary equipment. No duct burners. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion and natural gas as fuel | 18 | LB/H | PER TURBINE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041470431 | 02/24/2015 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2020-01-31 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | efficient combustion, natural gas fuel | 43 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0817 | CHOCOLATE BAYOU STEAM GENERATING (CBSG) STATION | INEOS USALLC | BRAZORIA | TX |  | USA | THERESA VITEK | 281-581-3498 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | 123117, PSDTX1460, GHGPSDTX135 | 4911 | 221112 | Not Found | 12/22/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-28 | 2017-11-16 | A |  | support facility providing steam and electricity |  | Combined Cycle Cogeneration | 15.21 | NATURAL GAS | 50 | MW | 2 UNITS EACH 50 MW GE LM6000 | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 6.98 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Combined Cycle Turbine with Heat Recovery Steam Generator, fired Duct Burners, and Steam Turbine Generator | 15.21 | NATURAL GAS | 426 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines with HRSGs and Steam Turbine Generators | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; good combustion practices | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | PIPELINE NATURAL GAS, GOOD COMBUSTION | 125.7 | TON/YR |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2018-06-25 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.02 Turbine | 15.21 | Natural Gas | 3496.2 | mmBtu/hr | Nominal 640 mWe All emission limits steady-state and include 1000 mmBtu/hr Duct Burner in operation Short Term startup and shutdown limits in lb/event given in permit. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Air Filter, Use of Natural Gas, Good Combustion Practices | 18.2 | LB/HR |  | BACT-PSD |  | U | 0 | U | 100.1 | TONS/YEAR |  | 18.2 | LB/HR |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP01) | 15.21 | Natural Gas | 40 | MW |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 4 | LB/H | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 17.5 | TONS | CALENDAR YEAR | 0 |  |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP02) | 15.21 | Natural Gas | 40 | MW |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 4 | LB/H | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 17.5 | TONS | CALENDAR YEAR | 0 |  |  | 0 | 0 | N
*WV-0032 | BROOKE COUNTY POWER PLANT | ESC BROOKE COUNTY POWER I, LLC | BROOKE | WV | 26035 | USA | ANDREW DORN | 7163121042 | DREW.DORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 Steven.R.Pursley@wv.gov | R14-0035 | 4911 | 221112 | Not Found | 03/30/2018 &nbsp;ACT | 09/18/2018 &nbsp;ACT | 2018-12-20 | 2019-01-02 | A |  | Nominal 925 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.01 Turbine | 15.21 | Natural Gas/Ethane | 2737.7 | mmBtu/hr | Facility has 2 identical units, only 1 entry in RBLC. Nominal 462.5 mWe. All emission limits steady-state and include 424 mmBtu/hr Duct Burner in operation. Short Term startup and shutdown limits in lb/event given in permit. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Air Filter, Use of Natural Gas, Good Combustion Practices | 16.9 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0.008 | LB/MMBTU |  | 0 | 0 | N |  | All PM is assumed to be PM2.5 or less.
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (WARM STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.4 | LB/H | WARM STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 0.58 | LB/EVENT | WARM STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF WARM STARTUPS NOT TO EXCEED 180 MINUTES; 2) WARM STARTUP MEANS A STARTUP THAT IS NOT A HOT OR COLD STARTUP
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (HOT STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.4 | LB/H | HOT STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 0.33 | LB/EVENT | HOT STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF HOT STARTUPS NOT TO EXCEED 90 MINUTES; 2) HOT STARTUP MEANS A STARTUP WHEN THE COMBUSTION TURBINE HAS BEEN IN OPERATION DURING THE PRECEDING 8 HOURS
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.2 | LB/H | TURBINE SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 0.2 | LB/EVENT | TURBINE SHUTDOWN PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF SHUTDOWN NOT TO EXCEED 30 MINUTES; 2) SHUTDOWN MEANS THE PERIOD BEGINNING WITH THE LOWERING OF EQUIPMENT FROM BASE LOAD AND LASTING UNTIL FUEL FLOW IS COMPLETELY OFF AND COMBUSTION HAS CEASED
CT-0157 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo james.grillo@ct.cov 860-424-3570 | 144-0023 | 4911 | 221112 | 110040589672 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-03 | 2016-02-19 | A |  | 805 MW Combined Cycle Power Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/12 months |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 4.49 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 6.2 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
CT-0158 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo; james.grillo@ct.gov; 860-424-3570 | 144-0024 | 4911 | 221112 | 110040589672 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-04 | 2016-02-19 | A |  | 805 MW Combined Cycle Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/yr |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Use of inherently low sulfur fuel | 4.49 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 6.2 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
FL-0337 | POLK POWER STATION | TAMPA ELECTRIC COMPANY | POLK | FL | 33860 | USA | PAUL CARPINONE | 813-228-4528 | PLCARPINONE@TECOENERGY.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Leigh Ann Pell, Project Engineer Phone; 850-717-9033 | 1050233-034-AC | 4911 | 221112 | 110000365113 | 05/15/2013 &nbsp;ACT | 10/14/2012 &nbsp;ACT | 2013-08-06 | 2014-11-07 | D | http://appprod.dep.state.fl.us/air/emission/apds/listpermits.asp | The Polk Power Station consists of: a nominal 250 MW (net) solid fuel-based integrated gasification and combined cycle (Unit 1) including a sulfuric acid plant and an auxiliary boiler; four natural gas-fueled nominal 165 MW simple cycle combustion turbine-electrical generators (CTGs) designated as Units 2, 3, 4 and 5; and ancillary equipment. Units 2 and 3 are equipped with backup fuel oil-firing capability. | GHG(e) emissions: 4,307,862 | Combine cycle power block (4 on 1) | 15.21 | natural gas | 1160 | MW | Basis for the emission standard is either NSPS Subpart KKKK or Department BACT determinations. The BACT emission standards for NOX while operating in combined cycle are more stringent than the corresponding Subpart KKKK emissions standards of 15 and 42 ppmvd @15% O2 on a 30-day rolling average for natural gas and fuel oil, respectively. | Sulfur Dioxide (SO2) | Other - Fuel Specifications | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 2 | GR S/100 SCF GAS |  | BACT-PSD | NSPS | U | 0 | U | 0.0015 | % S FUEL OIL |  | 0 |  |  | 0 | 0 | N |  | The applicant requested the stated sulfur fuel limits. These BACT values are more stringent and insure compliance with the corresponding Subpart KKKK SO2 emission standard.
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Sulfur Dioxide (SO2) | Other - No test required | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Use of low-sulfur fuels | 2 | GR. S/100 SCF GAS | FOR NATURAL GAS | BACT-PSD | NSPS | U | 0 | U | 0.0015 | % S IN ULSD | FOR ULSD | 0 |  |  | 0 | 0 | N
*FL-0363 | DANIA BEACH ENERGY CENTER | FLORIDA POWER AND LIGHT COMPANY | BROWARD | FL | 33314 | USA | JOHN HAMPP | 561-691-2894 | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-017-AC | 4911 | 221112 | 110002044065 | 07/27/2017 &nbsp;ACT | 12/04/2017 &nbsp;ACT | 2018-04-03 | 2018-04-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.F.ZIP | 1200 megawatt 2-on-1 combined cycle facility, natural gas-fired, with limited ULSD use. GE 7HA turbines | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.D.ZIP | 2-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural gas | 4000 | MMBtu/hr | Two nominal 430 MW combustion turbines, coupled to a steam turbine generator | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Clean fuels | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limits on sulfur content of fuels limit emissions. Gas limited to 2.0 grains per 100 scf, and oil limited to 0.0015% sulfur.
*FL-0367 | SHADY HILLS COMBINED CYCLE FACILITY | SHADY HILLS ENERGY CENTER, LLC | PASCO | FL | 36410 | USA | ROY BELDEN | (203) 357-6820 | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1010524-001-AC | 4911 | 221112 | 110012581820 | 02/16/2018 &nbsp;ACT | 07/27/2018 &nbsp;ACT | 2019-03-19 | 2019-03-19 | B | https://arm-permit2k.dep.state.fl.us/nontv/1010524.001.AC.F.ZIP | A 573-megawatt (MW) (winter) 1-on-1 combined cycle plant which includes a heat recovery steam generator with duct firing, along with supporting equipment. Natural gas is the only permitted fuel for the combined cycle unit. | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/1010524.001.AC.R.ZIP | 1-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural Gas | 3266.9 | MMBtu/hour | One nominal 385 MW GE 7HA.02 CTG and one HRSG with duct firing [approximately 210 MMBtu/hour], and one nominal 210 MW steam turbine generator (STG) | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Clean Fuels | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limits on sulfur content of fuel limit SO2 emissions. Natural Gas limited to 2.0 grains per 100 scf.
IL-0112 | NELSON ENERGY CENTER | INVENERGY NELSON, LLC | LEE | IL | 61071-9722 | USA | JOEL SCHROEDER | 312-224-1417 | JSCHROEDER@INVENERGYLLC.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Manish Patel, Permit Analyst Manish.Patel@illinois.gov 217-785-1722 | 98080039 | 4911 | 221112 | 110007399644 | 11/19/2010 &nbsp;ACT | 12/28/2010 &nbsp;ACT | 2013-02-21 | 2020-04-16 | A |  | Natural gas-fired electic power generation facility with two &quot;combined cycle&quot; turbines followed by heat recovery steam generators (HRSG) and the capability for supplemental fuel firing in the HRSG for each turbine using duct burners. NOx emissions will be controlled by SCR and low NOx combustors. | LSP-Nelson Energy started construction pursuant to a permit issued in year 2000 for a facility that was not completed due to financial difficulties, which eventually resulted in LSP-Nelson entering bankruptcy. Substantial construction of foundations and infrastructure for all units and physical installation of one turbine were completed, including construction of HRSGs. | Electric Generation Facility | 15.21 | Natural Gas | 220 | MW each | Two combined cycle combustion turbines followed by HRSGs with capability for supplemental fuel firing in HRSG for each combustion turbine using duct burners. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.0062 | LB/MMBTU | HOURLY AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | FUEL SPECIFICATION | 0.75 | GR S/100 SCF FUEL |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Exclusive Combustion of Low Sulfur Fuel and Proper Engineering Practices | 4 | PPMV | ANNUAL AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT limit is 4 PPMV H2S; Annual Average Content in Fuel.
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITH DUCT FIRING | 15.21 | NATURAL GAS | 1000 | MW | TWO MITSUBISHI &lsquo;&lsquo;G&lsquo;&lsquo; MODEL COMBUSTION TURBINE GENERATORS (CTS) WITH A NOMINAL GENERATING CAPACITY OF 270 MW CAPACITY EACH, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR), OXIDATION CATALYST | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6C | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND EFFICIENT TURBINE DESIGN | 8.2 | LB/H | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITHOUT DUCT FIRING | 15.21 | NATURAL GAS | 270 | MW |  | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6C | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS | 6.3 | LB/H | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good Combustion Practices and the use of pipeline quality natural gas. | 11.7 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | NSPS , SIP | N | 0 | N | 0.06 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | 0 |  |  | 0 | 0 | N |  | The emission limits above are for EACH CTGHRSG. There is also a NSPS natural gas material limit of 20 grains of sulfur per 100 scf.
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Use of clean fuel (natural gas) with a fuel sulfur limit of 0.8 grains per 100 standard cubic feet of natural gas. | 0.8 | GR/100 SCF | NAT.GAS BURNED IN FG-TURB/DB1-3 | BACT-PSD | NSPS , SIP | N | 0 | N | 0.06 | LB/MMBTU | HOURLY; EACH CT/HRSG TRAIN; NSPS KKKK | 0 |  |  | 0 | 0 | N |  | Emission limit 2 above is from NSPS KKKK and is 0.060 LB/MMBTU heat input. Emission limit 1 above is a material limit of 0.8 grains/100 scf of natural gas burned in FG-TURB/DB1-3
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and the use of pipeline quality natural gas. | 6.6 | LB/H | HOURLY | BACT-PSD | NSPS , SIP | N | 0 | N | 0.6 | GR S/100 SCF | FUEL SUPPLIER RECORDS | 0 |  |  | 0 | 0 | N |  | There are 3 emission limits and one material limit in the permit as follows: Emission Limit 1 = 6.6 LB/H Emission Limit 2 = 0.6 GR Sulfur/100 scf Emission Limit 3 = 0.060 LB/MMBTU from the NSPS Emission Limit 4 is a NSPS natural gas material limit of 20 grains of sulfur per 100 scf. Even though MEC determined FGD to be technically infeasible due to the low SO2 content in the flue gas, they also provided an economic analysis. The use of pipeline quality natural gas and good combustion practices were used for the emission calculations. All reductions in emissions were with these potential control options already incorporated as baseline conditions. They concluded that with costs of over $200,000 per ton of controlled SO2 and H2SO4 combined, FGD also would not be economically feasible.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and the use of pipeline quality natural gas. | 6.6 | LB/H | HOURLY | BACT-PSD | NSPS , SIP | N | 0 | N | 0.6 | GR S/100 SCF | FUEL SUPPLIER RECORDS | 0 |  |  | 0 | 0 | N |  | There is a 3rd emission limit which is 0.060 lb/MMBTU based on the NSPS. There is also a NSPS natural gas material limit of 20 grains of sulfur per 100 scf. Even though MEC determined FGD to be technically infeasible due to the low SO2 content in the flue gas, they also provided an economic analysis. The use of pipeline quality natural gas and good combustion practices were used for the emission calculations. All reductions in emissions were with these potential control options already incorporated as baseline conditions. They concluded that with costs of over $200,000 per ton of controlled SO2 and H2SO4 combined, FGD also would not be economically feasible.
*MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2019-12-19 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | The use of clean fuel (natural gas), with a fuel sulfur limit of 1 grain per 100 standard cubic feet of natural gas. | 0.003 | LB/MMBTU | HOURLY; EACH UNIT | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Flue gas desulfurization (FGD) and fuel desulfurization were not considered as feasible control alternative for this project.
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine without Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burner. | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6C | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Use of natural gas a clean burning fuel | 4.94 | LB/H | AVERAGE OF THREE ONE HOUR STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063377821 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burners. | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6C | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Use of natural gas a clean burning fuel | 6.56 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0104 | CPV VALLEY ENERGY CENTER | CPV VALLEY LLC | ORANGE | NY | 10940 | USA |  |  |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-335600136/00001 | 4911 | 221112 | 110043332471 | 08/01/2013 &nbsp;ACT | 08/01/2013 &nbsp;ACT | 2017-08-25 | 2017-09-28 | A |  | CPV Valley Energy Center is a 680 MW combined cycle electric generating facility located in Middletown, NY. The combustion turbines are rated at 2,234 MMBTU/H firing natural gas and 2,145 MMBTU/H firing diesel fuel. The duct burners are rated for 500 MMBTU/H firing natural gas. In addition to the turbines their emission limits for the auxiliary boiler (73.5 MMBTU/H), emergency generator, fire pump, and gas heater. | State Facility Permit | Turbines and duct burners - NG | 15.21 | natural gas | 0 |  | Combined cycle units heat rate 7,605 BTU/KW-H (HHV) or less without duct burner firing to achieve design thermal efficiency of 57.4% (LHV). | Sulfur Dioxide (SO2) | Other - EPA approved method | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Natural gas | 0.0022 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0356 | DUKE ENERGY HANGING ROCK ENERGY | DUKE ENERGY HANGING ROCK, LLC | LAWRENCE | OH | 28207 | USA | ANDREW ROEBEL | 513-287-2356 | ANDREW.ROEBEL@DUKE-ENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110487 | 4911 | 221112 | 110012567203 | 07/17/2012 &nbsp;ACT | 12/18/2012 &nbsp;ACT | 2013-10-01 | 2016-05-04 | C |  | Four Natural Gas Fired Combustion Turbines, with Duct Burners; Combined Cycle, each 172 MW | This is a modification of RBLC OH-0252 to remove operating hour restrictions on duct burners, with changes to hourly limits without increasing the annual emission limitations. Original PTI # was 07-00503 | Turbines (4) (model GE 7FA) Duct Burners Off | 15.21 | NATURAL GAS | 172 | MW | Four GE 7FA combined cycle turbines, dry low NOx burners and selective catalytic reduction. These limits are for each of the 4 turbines individually, while operating with the duct burners off. This permit is a modification to RBLC OH-0252 to remove hourly restrictions on duct burners. | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Burning natural gas in an efficient combustion turbine burning low sulfur fuel | 1.2 | LB/H |  | BACT-PSD | NSPS , SIP | U | 0 | N | 6.7 | T/YR | PER ROLLING 12 MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for each individual turbine. Subject to Part 60 Subparts Da and GG. If required Methods 1 through 4 and 6.
OH-0356 | DUKE ENERGY HANGING ROCK ENERGY | DUKE ENERGY HANGING ROCK, LLC | LAWRENCE | OH | 28207 | USA | ANDREW ROEBEL | 513-287-2356 | ANDREW.ROEBEL@DUKE-ENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110487 | 4911 | 221112 | 110012567203 | 07/17/2012 &nbsp;ACT | 12/18/2012 &nbsp;ACT | 2013-10-01 | 2016-05-04 | C |  | Four Natural Gas Fired Combustion Turbines, with Duct Burners; Combined Cycle, each 172 MW | This is a modification of RBLC OH-0252 to remove operating hour restrictions on duct burners, with changes to hourly limits without increasing the annual emission limitations. Original PTI # was 07-00503 | Turbines (4) (model GE 7FA) Duct Burners On | 15.21 | NATURAL GAS | 172 | MW | Four GE 7FA combined cycle turbines, dry low NOx burners and selective catalytic reduction. These limits are for each of the 4 turbines individually, while operating with the duct burners on. This permit is a modification to RBLC OH-0252 to remove hourly restrictions on duct burners. | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Burning natural gas in an efficient combustion turbine burning low sulfur fuel | 1.52 | LB/H |  | BACT-PSD | NSPS , SIP | U | 0 | N | 6.7 | T/YR | PER ROLLING 12 MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for each individual turbine. Subject to Part 60 Subparts Da and GG. If required Methods 1 through 4 and 6.
OH-0367 | SOUTH FIELD ENERGY LLC | SOUTH FIELD ENERGY LLC | COLUMBIANA | OH | 43968 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0119495 | 4911 | 221112 | Not Found | 09/14/2015 &nbsp;ACT | 09/23/2016 &nbsp;ACT | 2019-02-28 | 2019-06-19 | A |  | 1150 MW combined-cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the South Field Energy facility, a nominal 1,150 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in Wellsville, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3131 | MMBTU/H | Two identical combined cycle combustion turbine (3,131 MMBtu/hr heat input turbine at ISO conditions, natural gas firing with evaporative cooler on and 800 MMBtu/hr maximum heat input natural gas-fired duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), catalytic oxidizer, and wet injection for ULSD firing. Heat input for ULSD firing at ISO conditions, with evaporative cooler on is 3,173 MMBtu/hr. Throughputs and limits are for single turbine except as noted. | Sulfur Dioxide (SO2) | Other - 40 CFR 60.4415 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Low sulfur fuels | 5.64 | LB/H | NAT GAS, WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 23.5 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 1.4x10-3 lb/mmbtu, hourly average, natural gas, with and without duct burner. 1.5x10-3 lb/mmbtu, hourly average, ultra low sulfur diesel. 5.64 lb/h with duct burner (except startup and shutdown). 4.61 lb/h without duct burner (except startup and shutdown). 5.19 lb/h for ultra low sulfur diesel (except startup and shutdown). 23.5 t/yr per rolling 12 month period for all operating modes, including startup and shutdown.
OH-0370 | TRUMBULL ENERGY CENTER | TRUMBULL ENERGY CENTER | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122331 | 4911 | 221112 | Not Found | 03/23/2017 &nbsp;ACT | 09/07/2017 &nbsp;ACT | 2019-03-05 | 2019-06-19 | A |  | 940 MW combined cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the Trumbull Energy Center, a nominal 940 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in the Village of Lordstown, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3025 | MMBTU/H | Two identical combined cycle combustion turbine (3,025 mmBtu/hr heat input turbine at ISO conditions and 237 mmBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Throughputs and limits are for single turbine except as noted. | Sulfur Dioxide (SO2) | Other - 40 CFR 60.4415 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Low sulfur fuel | 5.1 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 21 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 1.5x10-3 lb/mmbtu, 5.1 lb/h with duct burner, 4.8 lb/h without duct burner (each limit except startup and shutdown). 21.0 t/yr per rolling 12 month period for all operating modes, including startup and shutdown.
OH-0372 | OREGON ENERGY CENTER | OREGON ENERGY CENTER | LUCAS | OH | 43616 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0121049 | 4911 | 221112 | Not Found | 06/27/2016 &nbsp;ACT | 09/27/2017 &nbsp;ACT | 2019-03-06 | 2019-06-19 | A |  | Combined cycle gas turbine (CCGT) facility | Installation of natural gas-fired combined cycle combustion turbine power plant. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3055 | MMBTU/H | Combined cycle combustion turbine (3,055 mmBtu/hr heat input turbine at ISO conditions and 221.3 mmBtu/hr heat input duct burner) with dry low NOX combustors, selective catalytic reduction (SCR), and catalytic oxidation. All heat values are on a HHV basis. Throughputs and limits are for single turbine except as noted. | Sulfur Dioxide (SO2) | Other - 40 CFR 60.4415 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | low sulfur fuel | 5.1 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 21.46 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 1.5x10-3 lb/mmbtu. 5.1 lb/h with duct burner (except startup and shutdown). 4.8 lb/h without duct burner (except startup and shutdown). 21.46 t/yr per rolling 12 month period for all operating modes, including startup.
OH-0374 | GUERNSEY POWER STATION LLC | GUERNSEY POWER STATION LLC | GUERNSEY | OH | 43723 | USA | MARY KING | (317)447-4513 | MARY@APEXPOWERGROUP.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122594 | 4911 | 221112 | 110070379546 | 04/14/2017 &nbsp;ACT | 10/23/2017 &nbsp;ACT | 2019-03-08 | 2019-06-19 | A |  | 1,650 MW combined cycle combustion turbine electrical generating facility | Installation PTI for a new 1,650 MW combined cycle natural-gas fired turbine plant and associated auxiliary boiler, firewater pumps, emergency generators and fuel gas heaters | Combined Cycle Combustion Turbines (3, identical) (P001 to P003) | 15.21 | Natural gas | 3516 | MMBTU/H | Three identical Combustion Turbines; GE 7HA.02 natural gas-fired lean pre-mix combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,516 MMBtu/hr HHV at 100% load and -18Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 997 MMBtu/hr HHV controlled with catalytic oxidation and selective catalytic reduction (SCR) and cooled with an air-cooled condenser (ACC) used to generate electricity. Throughputs and limits are for a single turbine except as noted. | Sulfur Dioxide (SO2) | Other - 40 CFR 60.4415 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | pipeline quality natural gas with a maximum sulfur content not exceed 0.50 grain/100 scf | 0.0015 | LB/MMBTU | SEE NOTES. | BACT-PSD |  | U | 0 | U | 6.77 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | Limits are for single turbine except as noted. 0.0015 lb/mmbtu with duct burners and without duct burners. Both excluding startup and shutdown. 5.27 lb/h without duct burners. 6.77 lb/h with duct burners. Both excluding startup and shutdown. 88.96 t/yr per rolling 12 month period total for all 3 turbines.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Sulfur Dioxide (SO2) | Other - 40 CFR 60.4415 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and pipeline quality natural gas | 0.0017 | LB/MMBTU | SEE NOTES. | BACT-PSD | NSPS | U | 0 | U | 5.75 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.00174 lb/mmbtu and 4.13 lb/h with duct burner, except startup and shutdown. 0.00174 lb/mmbtu and 5.75 lb/h without duct burner. 28.65 tons per rolling 12 month period for all operating modes, including startup.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Sulfur Dioxide (SO2) | Other - 40 CFR 60.4415 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and pipeline quality natural gas | 0.0021 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 7.22 | LB/H | WITH DUCT BURNERS. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | 0.0021 lb/mmbtu and 7.22 lb/h with duct burner. 0.0021 lb/mmbtu and 6.92 lb/h without duct burner. 29.57 tons per rolling 12 month period.
TX-0600 | THOMAS C. FERGUSON POWER PLANT | LOWER COLORADO RIVER AUTHORITY | LLANO | TX | 7657 | USA | JOE BENTLEY | 512-473-3272 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tan Nguyen 512-239-3445 tan.nguyen@tceq.texas.gov | PSDTX1244 & 93938 | 4911 | 221112 | 110035336222 | 07/27/2011 &nbsp;ACT | 09/01/2011 &nbsp;ACT | 2011-09-02 | 2020-02-03 | B |  | Power Plant. Two natural gas-fired combined cycle turbine generators (GE 7FA) with unfired HRSG | 93938 | Natural gas-fired turbines | 15.21 | natural gas | 390 | MW | (2) GE7FA at 195 MW each, (1) steam turbine at 200 MW. Each turbine is equipped with an unfired heat recovery steam generator (HRSG), which provides steam for the steam turbine. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | pipeline quality natural gas | 27.07 | LB/H | 1-H | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0660 | FGE TEXAS POWER I AND FGE TEXAS POWER II | FGE POWER LLC | MITCHELL | TX | 79565 | USA | EMERSON FARRELL | 281-362-2830 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX1364 & 110025 | 3511 | 221112 | NOT FOUND | 10/23/2013 &nbsp;ACT | 03/24/2014 &nbsp;ACT | 2014-06-13 | 2020-03-05 | U |  | Electric Generating Utility | TCEQ Permit No. 110025 | Alstom Turbine | 15.21 | Natural Gas | 230.7 | MW | Four (4) Alstom GT24 CTGs, each with a HRSG and DBs, max design capacity 409 MMBtu/hr | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Low sulfur fuel, good combustion practices | 1 | GR S / 100 DSCF | HOURLY | BACT-PSD |  | N | 0 | U | 0.25 | GS S / 100 DSCF | ANNUAL | 0 |  |  | 0 | 0 | N
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057188626 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.21 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (6) GE LM2500+ DLE turbines that drive the ethylene section compressors with waste heat recovery for amine solution regeneration. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.31 | LB/H | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Fuel sulfur is very low for natural gas.
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Combustion Turbine | 15.21 | natural gas | 87 | MW | The exhaust heat from the turbine will be used to heat a heating medium which is used to regenerate rich amine from the acid gas removal system. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 3.68 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | low sulfur natural-gas fired
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041470431 | 02/24/2015 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2020-01-31 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | efficient combustion, natural gas fuel | 2 | GR/100 SCF | 1-HOUR | BACT-PSD |  | N | 0 | U | 0.5 | GR/100 SCF | ANNUAL | 0 |  |  | 0 | 0 | N
TX-0751 | EAGLE MOUNTAIN STEAM ELECTRIC STATION | EAGLE MOUNTAIN POWER COMPANY LLC | TARRANT | TX |  | USA | PAUL COON | 214-875-8647 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.Alvirez@tceq.texas.com | 117026, PSDTX1390, N194 | 4911 | 221122 | 110005028638 | 03/26/2015 &nbsp;ACT | 06/18/2015 &nbsp;ACT | 2015-06-22 | 2016-07-06 | B |  | Eagle is proposing to construct two new combined cycle combustion turbines (CTG) which will generate electric power for sale on the wholesale electric market. The ancillary equipment includes an auxiliary boiler, a firewater pump, an emergency generator, a steam turbine, and various support facilities. |  | Combined Cycle Turbines (&gt;25 MW) â€“ natural gas | 15.21 | natural gas | 210 | MW | Two power configuration options authorized Siemens â€“ 231 MW + 500 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 210 MW + 349.2 MMBtu/hr duct burner | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 40.66 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 35.62 | T/YR |  | 0 |  |  | 0 | 0 | N |  | Good combustion practices, low sulfur fuel
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD COMBUSTION PRACTICES, LOW SULFUR FUEL | 1 | GR/100 SCF | HOURLY | BACT-PSD | NSPS | N | 0 | U | 0.25 | GR/100 SCF | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0789 | DECORDOVA STEAM ELECTRIC STATION | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas.gov | 107569 AND PSDTX1432 | 4911 | 221112 | 110008149217 | 12/23/2015 &nbsp;ACT | 03/08/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | The DeCordova Station will consist of two combustion turbine generators (CTGs) operating in simple cycle or combined cycle modes. The gas turbines will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE). Simple cycle operations limited to 2,500 hr/yr. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD COMBUSTION PRACTICES AND LOW SULFUR FUEL | 5 | GR/100 SCF | HOURLY | BACT-PSD | NSPS | N | 0 | U | 1 | GR/100 SCF | ANNUAL | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.21 | natural gas | 10 | M TONNES/YR | Four GE Frame 7E gas turbines for refrigeration and compression at the site | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Dry low NOx burners, good combustion practices, pipeline quality sweet natural gas fuel (low sulfur fuel) | 5 | GR/100 SCF |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Simple Cycle Electrical Generation Gas Turbines 15.210 | 15.21 | natural gas | 34 | MW | Nine GE PGT25+G4 gas turbines for electrical generation at the site at 34 MW/turbine | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Equipment specifications & work practices - Good combustion practices and use of low carbon, low sulfur fuel | 2.96 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 1.88 | T/YR |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Combined Cycle Turbine with Heat Recovery Steam Generator, fired Duct Burners, and Steam Turbine Generator | 15.21 | NATURAL GAS | 426 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines with HRSGs and Steam Turbine Generators | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Pipeline quality natural gas | 1.54 | GR/100 DSCF |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2019-02-19 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | PIPELINE QUALITY NATURAL GAS | 1 | GR/100 DSCF |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404 | 4911 | 221112 | 110055066440 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2019-06-19 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | COMBUSTION TURBINE GENERATORS, (3) | 15.21 | Natural Gas | 3442 | MMBTU/H | Three (3) Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners (natural gas-fired). | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Low sulfur fuel | 0.0011 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2020-03-18 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/hr natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/hr combustion turbine. Emission limits reflect the operation of each of the three turbines. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Controlled by the use of pipeline-quality natural gas with a maximum sulfur content of 0.4 grains per 100 standard cubic feet (scf), on a 12-month rolling average. | 0.0011 | LB/MMBTU | 3 HR AVG | BACT-PSD | NSPS , SIP | N | 0 | N | 20.4 | TONS/YR |  | 0 |  |  | 0 | 0 | N |  | Short term limits apply at all times. Compliance determined by fuel monitoring.
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (WARM STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 27.7 | LB/H | WARM STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 47.4 | LB/EVENT | WARM STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF WARM STARTUPS NOT TO EXCEED 180 MINUTES; 2) WARM STARTUP MEANS A STARTUP THAT IS NOT A HOT OR COLD STARTUP
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (HOT STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 27.7 | LB/H | HOT STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 38 | LB/EVENT | HOT STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF HOT STARTUPS NOT TO EXCEED 90 MINUTES; 2) HOT STARTUP MEANS A STARTUP WHEN THE COMBUSTION TURBINE HAS BEEN IN OPERATION DURING THE PRECEDING 8 HOURS
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 23.9 | LB/H | TURBINE SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 23.9 | LB/EVENT | TURBINE SHUTDOWN PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF SHUTDOWN NOT TO EXCEED 30 MINUTES; 2) SHUTDOWN MEANS THE PERIOD BEGINNING WITH THE LOWERING OF EQUIPMENT FROM BASE LOAD AND LASTING UNTIL FUEL FLOW IS COMPLETELY OFF AND COMBUSTION HAS CEASED
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Volatile Organic Compounds (VOC) | Other - EPA METHOD 25A OR 25B | (Volatile Organic Compounds (VOC)) | VOC | N |  | 2 | PPMVD | @15% O2, 1-HR ROLLING AVG | BACT-PSD |  | U | 0 | U | 11 | LB/H | 1-HR ROLLING AVG | 0 |  |  | 0 | 0 | N
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (COLD STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 27.7 | LB/H | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 106.7 | LB/EVENT | COLD STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF COLD STARTUPS NOT TO EXCEED 270 MINUTES; 2) COLD STARTUP MEANS STARTUP WHEN THE COMBUSTION TURBINE HAS NOT BEEN IN OPERATION DURING THE PRECEDING 72 HOURS
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055426409 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Four combined cycle combution turbines | 15.21 | natural gas | 373 | MMBTU/H | Three GE, LMS6000 PF, natural gas-fired, combined cycle CTG, rated at 373 MMBtu per hour each, based on HHV and one (1) HRSG each with no Duct Burners | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | good combustion control and catalytic oxidation | 4 | PPMVD AT 15% O2 | AVE OVER STACK TEST LENGTH | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CT-0157 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo james.grillo@ct.cov 860-424-3570 | 144-0023 | 4911 | 221112 | 110040589672 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-03 | 2016-02-19 | A |  | 805 MW Combined Cycle Power Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/12 months |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 1 | PPMVD @15% O2 |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 2 | PPMVD @15% O2 |  | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
CT-0158 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo; james.grillo@ct.gov; 860-424-3570 | 144-0024 | 4911 | 221112 | 110040589672 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-04 | 2016-02-19 | A |  | 805 MW Combined Cycle Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/yr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 1 | PPMVD @15% O2 |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 2 | PPMVD @15% O2 |  | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/o Duct Firing | 15.21 | Natural Gas | 2969 | MMBtu/hr | Throughput is for turbine only | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 0.7 | PPMVD @15% O2 |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/Duct Firing | 15.21 | Natural Gas | 2639 | MMBtu/hr | Duct burner MRC is 946 MMbtu/hr | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 1.6 | PPMVD @15% O2 |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0337 | POLK POWER STATION | TAMPA ELECTRIC COMPANY | POLK | FL | 33860 | USA | PAUL CARPINONE | 813-228-4528 | PLCARPINONE@TECOENERGY.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Leigh Ann Pell, Project Engineer Phone; 850-717-9033 | 1050233-034-AC | 4911 | 221112 | 110000365113 | 05/15/2013 &nbsp;ACT | 10/14/2012 &nbsp;ACT | 2013-08-06 | 2014-11-07 | D | http://appprod.dep.state.fl.us/air/emission/apds/listpermits.asp | The Polk Power Station consists of: a nominal 250 MW (net) solid fuel-based integrated gasification and combined cycle (Unit 1) including a sulfuric acid plant and an auxiliary boiler; four natural gas-fueled nominal 165 MW simple cycle combustion turbine-electrical generators (CTGs) designated as Units 2, 3, 4 and 5; and ancillary equipment. Units 2 and 3 are equipped with backup fuel oil-firing capability. | GHG(e) emissions: 4,307,862 | Combine cycle power block (4 on 1) | 15.21 | natural gas | 1160 | MW | Basis for the emission standard is either NSPS Subpart KKKK or Department BACT determinations. The BACT emission standards for NOX while operating in combined cycle are more stringent than the corresponding Subpart KKKK emissions standards of 15 and 42 ppmvd @15% O2 on a 30-day rolling average for natural gas and fuel oil, respectively. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | fuel Sulfur limits | 1.4 | PPMVD @15% O2 |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An initial VOC stack test shall be conducted on each CTG while firing natural gas and operating in combined cycle mode. Separate tests with duct burners are not required. Separate tests while operating in simple cycle are not required. Fuel shall not exceed 2 gr S/100 SCF of gas, 0.0015% S fuel oil.
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | Complete combustion minimizes VOC | 1 | PPMVD@15%O2 | GAS OPERATION | BACT-PSD |  | U | 0 | U | 2 | PPMVD@15%O2 | ULSD OPERATION | 0 |  |  | 0 | 0 | N |  | Method 18 or 25A. Initial test only -- CO used as proxy thereafter.
*FL-0363 | DANIA BEACH ENERGY CENTER | FLORIDA POWER AND LIGHT COMPANY | BROWARD | FL | 33314 | USA | JOHN HAMPP | 561-691-2894 | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-017-AC | 4911 | 221112 | 110002044065 | 07/27/2017 &nbsp;ACT | 12/04/2017 &nbsp;ACT | 2018-04-03 | 2018-04-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.F.ZIP | 1200 megawatt 2-on-1 combined cycle facility, natural gas-fired, with limited ULSD use. GE 7HA turbines | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.D.ZIP | 2-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural gas | 4000 | MMBtu/hr | Two nominal 430 MW combustion turbines, coupled to a steam turbine generator | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | Clean fuels | 1 | PPMVD@15% O2 | FOR NATURAL GAS OPERATION | BACT-PSD |  | U | 0 | U | 2.6 | PPMVD@15% O2 | FOR OIL OPERATION | 0 |  |  | 0 | 0 | N |  | Initial stack test only; CO used as proxy thereafter
FL-0364 | SEMINOLE GENERATING STATION | SEMINOLE ELECTRIC COOPERATIVE, INC. | PUTNAM | FL | 32177 | USA | CHRIS WEBER | 813-739-1359 | CWEBER@SEMINOLE-ELECTRIC.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1070025-028-AC / PSD-FL-443 | 4911 | 221112 | 110041142304 | 12/11/2017 &nbsp;ACT | 03/21/2018 &nbsp;ACT | 2018-04-13 | 2018-05-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/1070025.028.AC.F.ZIP | Existing fossil-fueled power plant. Two coal-fired units each rated at 736 MW. Project entails retirement of one coal-fired unit and construction of a 2-on-1 natural gas combined cycle unit. | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/1070025.028.AC.D.ZIP | 2-on-1 natural gas combined-cycle unit (GE 7HA.02) | 15.21 | Natural gas | 3514 | MMBtu/hr | Two GE 7HA.02 combustion turbines, each rated at 415 MW. Total unit capacity is approximately 1,183 MW (gross) and 1,050 MW (net). Due to netting, triggered PSD only for VOC. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 18 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation catalyst | 1 | PPMVD@15% O2 | WITHOUT DUCT BURNER FIRING | BACT-PSD |  | U | 0 | U | 2 | PPMVD@15% O2 | CT + DUCT BURNER OPERATION | 0 |  |  | 0 | 0 | N |  | Methods 18 and 25A are permitted. Compliance by stack test upon Title V permit renewal. Separate tests with and without duct burner firing are required.
GA-0138 | LIVE OAKS POWER PLANT | LIVE OAKS COMPANY, LLC | GLYNN | GA | 31525 | USA | BURT WALLACE | 478 943-2331 | BURT_1@BELLSOUTH.NET | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-127-0075-P-02-0 | 4911 | 221122 | UNKNOWN | 11/19/2008 &nbsp;ACT | 04/08/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | A |  | LIVE OAKS POWER PLANT PROPOSED FACILITY WILL OPERATE AS A FULLY DISPATCHABLE ELECTRIC GENERATING FACILITY. THE COMBINED CYCLE SYSTEM WILL UTILIZE TWO COMBUSTION TURBINES AND ONE STEAM TURBINE, CONFIGURED IN A TWO-ON-ONE ARRANGEMENT. THE HEAT CONTENT OF THE EXHAUST GASSES WIL BE RECOVERED BY A HEAT RECOVERY STEAM GENERATOR (HRSG), AND USED TO DRIVE A STEAM TURBINE. DURING PEAK LOADS A DUCT BURNER IN THE HRSG CAN BE FIRED TO AD ADDITIONAL HEAT ENERGY TO THE GAS TURBINE EXHAUST, INCREASING THE PRODUCTION OF STEAM SENT TO THE STEAM TURBINE. THE COMBUSTION TURBINES (CTs) SELECTED ARE SIEMENS MODEL SGT6-5000F. EACH COMBUSTION TURBINE WILL GENERATE 200 MW OF ELECTRIC POWER. THE GROSS ELECTRICAL CAPACITY OF THE COMBINED CYCLE FACILITY FIRING NATURAL GAS WILL THEN BE 600 MW. | PM10 74.3(+) EMISSIONS (T/YR) | COMBINED CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.21 | NATURAL GAS | 600 | MW |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | GOOD COMBUSTION PRACTICES, CATALYTIC OXIDATION | 2 | PPM@15%02 | 3-HOUR AVERAGE/CONDITION 2.11 | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #1 - combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr | two identical Siemens SGT6-5000F combined cycle turbines without duct firing, each at 2258 mmBtu/hr generating approx. 300 MW each. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | A | catalytic oxidizer | 1 | PPM | AVG. OF 3 ONE HOUR TEST RUNS | BACT-PSD |  | U | 95 | U | 71.2 | TON/YR | 12-MONTH ROLLING | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #2 -combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | N |  | 1 | PPM | AVERAGE 0F 3 ONE-HOUR TEST RUNS | BACT-PSD |  | N | 0 | U | 71.2 | TON/YR | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | 71.2 ton/yr limit includes startup, shutdown and malfunction
IL-0112 | NELSON ENERGY CENTER | INVENERGY NELSON, LLC | LEE | IL | 61071-9722 | USA | JOEL SCHROEDER | 312-224-1417 | JSCHROEDER@INVENERGYLLC.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Manish Patel, Permit Analyst Manish.Patel@illinois.gov 217-785-1722 | 98080039 | 4911 | 221112 | 110007399644 | 11/19/2010 &nbsp;ACT | 12/28/2010 &nbsp;ACT | 2013-02-21 | 2020-04-16 | A |  | Natural gas-fired electic power generation facility with two &quot;combined cycle&quot; turbines followed by heat recovery steam generators (HRSG) and the capability for supplemental fuel firing in the HRSG for each turbine using duct burners. NOx emissions will be controlled by SCR and low NOx combustors. | LSP-Nelson Energy started construction pursuant to a permit issued in year 2000 for a facility that was not completed due to financial difficulties, which eventually resulted in LSP-Nelson entering bankruptcy. Substantial construction of foundations and infrastructure for all units and physical installation of one turbine were completed, including construction of HRSGs. | Electric Generation Facility | 15.21 | Natural Gas | 220 | MW each | Two combined cycle combustion turbines followed by HRSGs with capability for supplemental fuel firing in HRSG for each combustion turbine using duct burners. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 18 | (Volatile Organic Compounds (VOC)) | VOC | N |  | 4 | PPMVD @ 15% O2 | HOURLY AVG EXCEPT DURING SSM OR TUNING | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | USEPA Method 18 or 25A
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDIZED CATALYST | 1 | PPMVD | 3 HOURS | BACT-PSD |  |  | 40 |  | 2 | PPMVD | 3 HOURS | 0 |  |  | 0 | 0 | N |  | LIMIT ONE IS USED UNDER CONDITIONS OF 15% O2 WITHOUT DUCT BURNERS IN USE. LIMIT TWO IS USED UNDER CONDITIONS OF 15% O2 WITH DUCT BURNERS IN USE.
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES - START UP/SHUTDOWN CYCLE | 15.21 | NATURAL GAS | 2300 | MMBTU/H | A STARTUP/SHUTDOWN CYCLE IS A PAIR OF SUBSEQUENT SHUTDOWN AND STARTUP EVENTS (I.E., ONE STARTUP FOLLOWED BY ONE SHUTDOWN REPRESENTS ONE STARTUP/SHUTDOWN CYCLE). | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 22 | TONS | 12 CONSECUTIVE MONTH PERIOD | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LIMIT TWO IS COMBINED EMISSIONS FROM CCCT1 THROUGH CCCT4 FUR THE DURATION OF THE COMBINED STARTUP/CHUTDOWN EVENTS
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002049328 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | COMBINED CYCLE TURBINE GENERATORS (UNITS 6A &amp; 6B) | 15.21 | NATURAL GAS | 7146 | MMBTU/H | TURBINES ALSO PERMITTED TO BURN NO. 2 FUEL OIL AND ULTRA LOW SULFUR DIESEL. FUEL OIL USE IS LIMITED TO 1000 HOURS PER YEAR. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 1.4 | PPMVD @ 15% O2 | HOURLY AVERAGE W/O DUCT BURNER | BACT-PSD | OPERATING PERMIT | U | 0 | U | 3.8 | PPMVD @ 15% O2 | HOURLY AVERAGE W/ DUCT BURNER | 0 |  |  | 0 | 0 | N |  | WHILE FIRING FUEL OIL, THE BACT LIMIT FOR VOC IS 3.1 PPMVD @ 15% O2 (HOURLY AVERAGE) STARTUP/SHUTDOWN: PROGRESS THROUGH THE SU/SD EVENT AS QUICKLY AS POSSIBLE WHILE FOLLOWING THE MANUFACTURER'S RECOMMENDED PROCEDURES. SU/SD OPERATIONS LIMITED TO 1302 HR/YR. BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE).
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Combined Cycle Refrigeration Compressor Turbines (8) | 15.21 | natural gas | 286 | MMBTU/H | GE LM2500+G4 | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices and fueled by natural gas | 0.66 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1A | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Catalytic oxidation and good combustion practices for normal operations, and good combustion practices for startup/shutdown operations. | 61.27 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 226.16 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 2.0 PPM@15% O2 during normal operations only (not during startup/shutdown conditions) (3-hour average)
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1B | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Catalytic oxidation and good combustion practices during normal operations, and good combustion practices during startup/shutdown operations. | 61.27 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 226.16 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 2.0 PPM@15% O2 during normal operations only (not during startup/shutdown conditions) (3-hour average)
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Catalytic Oxidation, Proper Equipment Design and Good Combustion Practices. | 1.1 | PPMV | 3 HOUR AVERAGE | BACT-PSD | OPERATING PERMIT , NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Units are in ppmv @ 15% O2; Averaging Time 3-Hour Average During Normal Operations.
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 0.0018 | LB/MMBTU | EACH CTG; TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 57386 | 0 | N | 2012 | The cost was estimated for a catalytic oxidation system (COS). VOC = $57,386/TON CO + VOC = $8,948/TON
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 0.004 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 57386 | 0 | N | 2012 | Cost effectiveness information: The cost was estimated for a catalytic oxidation system (COS) VOC = $57,386/TON CO + VOC = $8,948/ton
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Catalytic oxidation system (COS) | 2 | PPMVOL | DRY AT 15% OXYGEN | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Test protocol will specify averaging time.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Catalytic oxidation system (COS) | 2 | PPMVOL | DRY AT 15% OXYGEN | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Test protocol will specify averaging time.
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Efficient combustion control plus catalytic oxidation system. | 0 |  |  | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Both CO and VOC are products of incomplete combustion and are controlled using efficient combustion methods and catalytic oxidation system. The limitation on CO is an appropriate surrogate for VOC emissions.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 4 | PPM | TEST PROTOCOL | BACT-PSD |  | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The VOC emisison limit is 4 ppmdv at 15% O2 and applies to each CTGHRSG. Test protocol will specify averaging time. Startup and shutdown operations are limited to 635 hours per 12-month rolling time period combined for both CTGHRSGs. BACT, for each CTGHRSG separately, is 198.9 lb/hr during startup and 419.7 lb/hr during shutdown.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: Startup &amp; Shutdown | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified seperately for the startup and shutdown periods associated with the process equipment included in FG-CTGHRSG. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 198.9 | LB/H | EACH, DURING STARTUP | BACT-PSD |  | N | 85 | N | 419.7 | LB/H | EACH, DURING SHUTDOWN | 0 |  |  | 0 | 0 | N |  | Startup and shutdown operations are limited to 635 hours per 12-month rolling time period combined for both CTGHRSGs.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation Catalyst Technology and Good Combustion Practices | 4 | PPM | TEST PROTOCOL WILL SPECIFY | BACT-PSD |  | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is 4 ppmvd at 15%O2 and is for EACH CTGHRSG. Startup and shutdown operations are limited to 500 hours per 12-month rolling time period for each CTGHRSG train. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the startup and shutdown emission minimization plan. The efficiency range is 85-90 percent.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 4 | PPM AT 15% O2 | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is 4 ppmvd at 15% O2 and is for each CTGHRSG. Startup and shutdown operations are limited to 635 hours per 12-month rolling time period combined for both CTGHRSGs.
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | An oxidation catalyst and good combustion practices. | 1 | PPMVD | HOURLY; EACH CT/HRSG TRAIN | BACT-PSD | SIP | N | 0 | N | 48 | T/YR | EACH CT/HRSG TRAIN; 12-MO ROLL TIME PER. | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above does not include startup and shutdown. Emission limit 2 above is 48 ton/year based on a 12-month rolling time period as determined at the end of each calendar month.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 4 | PPMVD | AT 15%O2; NOT INCL. STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 4 | PPMVD | AT 15%O2; HOURLY | BACT-PSD | SIP | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above does not include startup and shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 0.0026 | LB/MMBTU | EACH UNIT; HOURLY EXCEPT S.S. | BACT-PSD | SIP | N | 0 | N | 0.0013 | LB/MMBTU | EACH UNIT W/O DUCT BURNER FIRING; NOT SS | 0 |  |  | 0 | 0 | N |  | The emission limits above are described further below: Emission limit 1 applies to each unit and is 0.0026 LB/MMBTU, hourly except during startup and shutdown. Emission limit 2 applies to each unit without duct burner firing and is 0.0013 LB/MMBTU, hourly except during startup and shutdown.
*MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2019-10-22 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2--A 667 MMBTU/H natural gas fired CTG with a HRSG. | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2 is a nominally rated 667 MMBTU/H natural gas fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas fired duct burner rated at 204 MMBTU/h to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR and oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | An oxidation catalyst for VOC control and good combustion practices. | 3 | PPM | PPMVD@15%O2; HOURLY; SEE NOTES | BACT-PSD |  | N | 0 | U | 5 | LB/H | HOURLY EXCEPT STARTUP/SHUTDOWN; SEE NOTE | 0 |  |  | 17102 | 0 | N | 2017 | Emission limit 1 is 3 ppmvd at 15% O2 and is an hourly limit except during startup and shutdown. The limit applies when the unit is in combined cycle mode. Emission limit 2 is 5 lb/h and is an hourly limit except during startup and shutdown. The limit applies when the unit is in HRSG bypass mode.
*MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2019-10-22 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1--A 667 MMBTU/H NG fired combustion turbine generator coupled with a heat recovery steam generator (HRSG) | 15.21 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR) and oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | An oxidation catalyst for VOC control for each CTG/HRSG unit, good combustion practices. | 3 | PPM | PPMVD@15%O2; HOURLY EXC.START/SHUT; NOTE | BACT-PSD |  | N | 0 | U | 5 | LB/H | HOURLY EXCEPT STARTUP/SHUTDOWN; SEE NOTE | 0 |  |  | 17102 | 0 | N | 2017 | VOC Emission Limit 1 above is 3 ppmvd at 15%O2 when the unit is in combined cycle mode. The limit is hourly except during startup and shutdown. VOC Emission Limit 2 above is 5 lb/h when the unit is in HRSG bypass mode and is hourly except during startup and shutdown.
*MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2019-12-19 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices. | 0.004 | LB/MMBTU | HOURLY; NOT STARTUP/SHUTDOWN;EACH UNIT | BACT-PSD |  | N | 70 | U | 377 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 = 0.004 lb/MMBTU, applies to each unit and is hourly except during startup/shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the combustion process ends at flame-off. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in special condition (SC) III.2 of the permit. Thermal oxidation, EMxGT, NSCR are not technically feasible control options for VOCs.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Siemens, without duct burners | 15.21 | Natural Gas | 515600 | MMSCF/rolling 12-months | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process without duct burners. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 3.9 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 28.6 | T/YR | PER ROLLING 12 MONTHS | 1 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | BACT: 2.0 ppmvd VOC at 15% O2. Methods: 18, 25, or 25A. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Siemens, with duct burners | 15.21 | Natural Gas | 51560 | MMSCF/rolling 12-MO | Two Siemens 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process with duct burners. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 5.9 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 28.6 | T/YR | PER ROLLING 12-MONTHS | 1.9 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | BACT: 2.0 ppmvd at 15% O2. Methods 18, 25, or 25A. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Mitsubishi, without duct burners | 15.21 | Natural Gas | 47917 | MMSCF/rolling 12-MO | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process without duct burners. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 7.9 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 56 | T/YR | PER ROLLING 12-MONTHS | 2 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | BACT: 2.0 ppmvd VOC at 15% O2. Methods: 18, 25, or 25A. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Mitsubishi, with duct burners | 15.21 | Natural Gas | 47917 | MMSCF/rolling 12-MO | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process with duct burners. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 7.3 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 56 | T/YR | PER ROLLING 12-MONTHS | 2 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | BACT: 2.0 ppmvd VOC at 15% O2. Methods: 18, 25, or 25A. T/YR limit is for 2 turbines.
OH-0356 | DUKE ENERGY HANGING ROCK ENERGY | DUKE ENERGY HANGING ROCK, LLC | LAWRENCE | OH | 28207 | USA | ANDREW ROEBEL | 513-287-2356 | ANDREW.ROEBEL@DUKE-ENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110487 | 4911 | 221112 | 110012567203 | 07/17/2012 &nbsp;ACT | 12/18/2012 &nbsp;ACT | 2013-10-01 | 2016-05-04 | C |  | Four Natural Gas Fired Combustion Turbines, with Duct Burners; Combined Cycle, each 172 MW | This is a modification of RBLC OH-0252 to remove operating hour restrictions on duct burners, with changes to hourly limits without increasing the annual emission limitations. Original PTI # was 07-00503 | Turbines (4) (model GE 7FA) Duct Burners Off | 15.21 | NATURAL GAS | 172 | MW | Four GE 7FA combined cycle turbines, dry low NOx burners and selective catalytic reduction. These limits are for each of the 4 turbines individually, while operating with the duct burners off. This permit is a modification to RBLC OH-0252 to remove hourly restrictions on duct burners. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | P | Using efficient combustion technology | 3.2 | LB/H |  | BACT-PSD | SIP | U | 0 | N | 44.1 | T/YR | PER ROLLING 12 MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for each individual turbine. If required Methods 1 through 4 and 25.
OH-0356 | DUKE ENERGY HANGING ROCK ENERGY | DUKE ENERGY HANGING ROCK, LLC | LAWRENCE | OH | 28207 | USA | ANDREW ROEBEL | 513-287-2356 | ANDREW.ROEBEL@DUKE-ENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110487 | 4911 | 221112 | 110012567203 | 07/17/2012 &nbsp;ACT | 12/18/2012 &nbsp;ACT | 2013-10-01 | 2016-05-04 | C |  | Four Natural Gas Fired Combustion Turbines, with Duct Burners; Combined Cycle, each 172 MW | This is a modification of RBLC OH-0252 to remove operating hour restrictions on duct burners, with changes to hourly limits without increasing the annual emission limitations. Original PTI # was 07-00503 | Turbines (4) (model GE 7FA) Duct Burners On | 15.21 | NATURAL GAS | 172 | MW | Four GE 7FA combined cycle turbines, dry low NOx burners and selective catalytic reduction. These limits are for each of the 4 turbines individually, while operating with the duct burners on. This permit is a modification to RBLC OH-0252 to remove hourly restrictions on duct burners. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | P | Using efficient combustion technology | 7.3 | LB/H |  | BACT-PSD | SIP | U | 0 | N | 44.1 | T/YR | PER ROLLING 12 MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for each individual turbine. If required Methods 1 through 4 and 25.
OH-0360 | CARROLL COUNTY ENERGY | CARROLL COUNTY ENERGY | CARROLL | OH | 44615 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0113762 | 4911 | 221112 | 110064671127 | 04/11/2013 &nbsp;ACT | 11/05/2013 &nbsp;ACT | 2015-12-30 | 2019-04-01 | A |  | Natural gas fired combined cycle gas turbine electric generating station of nominal capacity of 742 MW | Installation of a natural gas-fired combined cycle combustion turbine electric utility power plant, nominally rated at 742 MW. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural Gas | 2045 | MMBTU/H | Two identical General Electric 7FA combined cycle combustion turbine (each at 2,045 mmBtu/hr heat input turbine at ISO conditions and 566 mmBtu/hr heat input duct burner, HHV) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. All throughputs and emission limits are for each turbine. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 7.1 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 40.2 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | Limits are for each turbine. 0.0026 lb/mmbtu and 7.1 lb/h with duct burner (except startup and shutdown). 0.0013 lb/mmbtu and 2.8 lb/h turbine only (except startup and shutdown). 40.2 t/yr per rolling 12 month period including startup and shutdown. 140.2 lb/h for cold startup, 53.8 lb/h for hot startup, 151.7 lb/h for warm startup and 75.6 for shutdown. Pound per hour emissions rates as presented are averaged over the duration of the event where (for the lead/lag turbine) the duration of a cold start is 245/220 minutes, the duration of a warm start is 140/115 minutes, the duration of a hot start is 83/58 minutes, and the duration of a shutdown is less than 1 hour. Emissions reflect the higher of the lead or lag turbine, on a pollutant-specific basis.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 1 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2022 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices along with clean fuels | 611.38 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | BACT-PSD |  | U | 0 | U | 0 |  | SEE NOTES. | 1.4 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | Limits are for single turbine except as noted. 1.4 ppm by volume, dry basis (ppmvd) at 15% oxygen, 3-hour average, turbine only without duct burners. 3.1 ppm by volume, dry basis (ppmvd) at 15% oxygen, 3-hour average, turbine with duct burners. 1004 lb/cold startup, 440 lb/hot startup, 740 lb/warm startup and 261 lb/shutdown. 611.38 t/yr per rolling 12 month period total for all 4 turbines.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 2 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2144 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices along with clean fuels | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0.84 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | Limits are for single turbine except as noted. 0.84 ppm by volume, dry basis (ppmvd) at 15% oxygen, 3-hour average, turbine only without duct burners. 2.6 ppm by volume, dry basis (ppmvd) at 15% oxygen, 3-hour average, turbine with duct burners. 1004 lb/cold startup, 440 lb/hot startup, 740 lb/warm startup and 261 lb/shutdown. 600.62 t/yr per rolling 12 month period total for all 4 turbines.
OH-0366 | CLEAN ENERGY FUTURE - LORDSTOWN, LLC | CLEAN ENERGY FUTURE - LORDSTOWN, LLC | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0117655 | 4911 | 221112 | 110070396317 | 09/17/2014 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2019-02-27 | 2019-06-19 | A |  | 962 MW (gross winter output) combined cycle gas turbine (CCGT) facility | Initial installation permit for the construction of the Lordstown Energy Center - a nominal 940 MW combined cycle gas turbine (CCGT) facility. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 2725 | MMBTU/H | Combined cycle combustion turbine (2,725 MMBtu/hr heat input turbine at ISO conditions and 179 MMBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Limits and throughputs are for single turbine. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | B | Good combustion controls and oxidation catalyst | 8.2 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 47.1 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen with ductburner. 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen turbine only. 8.2 lb/h, with duct burner (except startup and shutdown). 3.9 lb/h without duct burner (except startup and shutdown). 47.1 t/yr per rolling 12 month period for all operating modes, including startup. 64.4 lb/h during cold startup, 60.1 lb/h during hot startup, 59.6 lb/h during warm startup, and 62.8 lb/h during shutdown.
OH-0367 | SOUTH FIELD ENERGY LLC | SOUTH FIELD ENERGY LLC | COLUMBIANA | OH | 43968 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0119495 | 4911 | 221112 | Not Found | 09/14/2015 &nbsp;ACT | 09/23/2016 &nbsp;ACT | 2019-02-28 | 2019-06-19 | A |  | 1150 MW combined-cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the South Field Energy facility, a nominal 1,150 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in Wellsville, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3131 | MMBTU/H | Two identical combined cycle combustion turbine (3,131 MMBtu/hr heat input turbine at ISO conditions, natural gas firing with evaporative cooler on and 800 MMBtu/hr maximum heat input natural gas-fired duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), catalytic oxidizer, and wet injection for ULSD firing. Heat input for ULSD firing at ISO conditions, with evaporative cooler on is 3,173 MMBtu/hr. Throughputs and limits are for single turbine except as noted. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Good combustion controls and oxidation catalyst | 10.64 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 50.6 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen, hourly average, natural gas, with duct burner. 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen, hourly average, natural gas, turbine only. 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen, hourly average, ultra low sulfur diesel. 10.64 lb/h with duct burner (except startup and shutdown). 4.35 lb/h without duct burner (except startup and shutdown). 9.25 lb/h for ultra low sulfur diesel (except startup and shutdown). 50.6 t/yr per rolling 12 month period for all operating modes, including startup and shutdown. When firing natural gas, 21.4 lb/h during startup and 55.2 lb/h during shutdown. When firing ultra low sulfur diesel, 109.0 lb/h during startup and 41.3 lb/h during shutdown.
OH-0370 | TRUMBULL ENERGY CENTER | TRUMBULL ENERGY CENTER | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122331 | 4911 | 221112 | Not Found | 03/23/2017 &nbsp;ACT | 09/07/2017 &nbsp;ACT | 2019-03-05 | 2019-06-19 | A |  | 940 MW combined cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the Trumbull Energy Center, a nominal 940 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in the Village of Lordstown, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3025 | MMBTU/H | Two identical combined cycle combustion turbine (3,025 mmBtu/hr heat input turbine at ISO conditions and 237 mmBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Throughputs and limits are for single turbine except as noted. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | B | Good combustion controls and oxidation catalyst | 8.8 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 50.3 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen with duct burner, 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen without duct burner, 8.8 lb/h with duct burner, 4.1 lb/h without duct burner (each limit except startup and shutdown). 50.3 t/yr per rolling 12 month period for all operating modes, including startup and shutdown. 64.4 lb/h during cold startup, 60.1 lb/h during hot startup, 59.6 lb/h during warm startup, and 67.9 lb/h during shutdown.
OH-0372 | OREGON ENERGY CENTER | OREGON ENERGY CENTER | LUCAS | OH | 43616 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0121049 | 4911 | 221112 | Not Found | 06/27/2016 &nbsp;ACT | 09/27/2017 &nbsp;ACT | 2019-03-06 | 2019-06-19 | A |  | Combined cycle gas turbine (CCGT) facility | Installation of natural gas-fired combined cycle combustion turbine power plant. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3055 | MMBTU/H | Combined cycle combustion turbine (3,055 mmBtu/hr heat input turbine at ISO conditions and 221.3 mmBtu/hr heat input duct burner) with dry low NOX combustors, selective catalytic reduction (SCR), and catalytic oxidation. All heat values are on a HHV basis. Throughputs and limits are for single turbine except as noted. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | B | oxidation catalyst and good combustion control | 8.8 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 50.28 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen, with duct burner. 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen, without duct burner. 8.8 lb/h with duct burner. 4.1 lb/h without duct burner. Each limit except startup and shutdown. 50.28 t/yr per rolling 12 month period for all operating modes, including startup. 64.4 lb/h during cold startup, 60.1 lb/h during hot startup, 59.6 lb/h during warm startup, and 62.8 lb/h during shutdown.
OH-0374 | GUERNSEY POWER STATION LLC | GUERNSEY POWER STATION LLC | GUERNSEY | OH | 43723 | USA | MARY KING | (317)447-4513 | MARY@APEXPOWERGROUP.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122594 | 4911 | 221112 | 110070379546 | 04/14/2017 &nbsp;ACT | 10/23/2017 &nbsp;ACT | 2019-03-08 | 2019-06-19 | A |  | 1,650 MW combined cycle combustion turbine electrical generating facility | Installation PTI for a new 1,650 MW combined cycle natural-gas fired turbine plant and associated auxiliary boiler, firewater pumps, emergency generators and fuel gas heaters | Combined Cycle Combustion Turbines (3, identical) (P001 to P003) | 15.21 | Natural gas | 3516 | MMBTU/H | Three identical Combustion Turbines; GE 7HA.02 natural gas-fired lean pre-mix combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,516 MMBtu/hr HHV at 100% load and -18Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 997 MMBtu/hr HHV controlled with catalytic oxidation and selective catalytic reduction (SCR) and cooled with an air-cooled condenser (ACC) used to generate electricity. Throughputs and limits are for a single turbine except as noted. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | B | oxidation catalyst and good combustion practices as recommended by the manufacturer | 11.73 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 4.92 | LB/H | WITHOUT DUCT BURNERS. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | Limits are for single turbine except as noted. 2.0 ppm by volume, dry basis (ppmvd) at 15% oxygen turbine with duct burners. 1.0 ppm by volume, dry basis (ppmvd) at 15% oxygen without duct burners. Both excluding startup and shutdown. 4.92 lb/h without duct burners. 11.73 lb/h with duct burners. Both excluding startup and shutdown. 55.9 lb/cold startup, 13.7 lb/hot startup, 16.5 lb/warm startup and 34.9 lb/shutdown. 146.91 t/yr per rolling 12 month period total for all 3 turbines.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | General Electric Combustion Turbine (P004) | 15.21 | Natural gas | 3544 | MMBTU/H | General Electric model 7HA.02 natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,544 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices as recommended by the manufacturer. | 4.54 | LB/H | EXCEPT STARTUP AND SHUTDOWN. SEE NOTES | BACT-PSD |  | U | 0 | U | 26.4 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 1 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 1.0 ppmvd at 15% oxygen (O2) and 4.54 pounds per hour, excluding periods of startup and shutdown. 26.4 tons of NOx per rolling, 12-month period, including start-up and shutdown emissions. 78.1 lb/h during cold startup, 11.5 lb/h during hot startup, 12.0 lb/h during warm startup, and 29.6 lb/h during shutdown.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Mitsubishi Combustion Turbine (P005) | 15.21 | Natural gas | 3320 | MMBTU/H | Mitsubishi Model 501JAC natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,320 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 108 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | oxidation catalyst and shall operate the emissions unit in accordance with good combustion practices as recommended by the manufacturer | 8.8 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 79.3 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen and 8.80 lb/h with duct burner (except startup and shutdown). 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen and 4.60 lb/h without duct burner (except startup and shutdown). 79.3 t/yr per rolling 12 month period for all operating modes, including startup. 224.7 lb/h during cold startup, 225.1 lb/h during warm startup, 185.9 lb/h during hot startup, and 97.0 lb/h during shutdown.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Siemens Combustion Turbine (P006) | 15.21 | Natural gas | 3602 | MMBTU/H | Siemens Model SCC6-8000H natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,602 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 667 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | oxidation catalyst and shall operate the emissions unit in accordance with good combustion practices as recommended by the manufacturer | 9.5 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 50.8 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen and 9.5 lb/h with duct burner (except startup and shutdown). 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen and 3.9 lb/h without duct burner (except startup and shutdown). 50.8 t/yr per rolling 12 month period for all operating modes, including startup. 40.4 lb/h during cold startup, 40.2 lb/h during warm startup, 40.7 lb/h during hot startup, and 39.4 lb/h during shutdown.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Good combustion practices and oxidation catalyst | 4.36 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 49.1 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen on a 24-hr block averaging period and 10.3 lb/h with duct burner, except startup and shutdown. 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen on a 24-hr block averaging period and 4.36 lb/h without duct burner, except startup and shutdown. 49.1 tons per rolling 12 month period for all operating modes, including startup and shutdown. 4.81 tons per rolling 12 month period for startup and shutdown periods.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Good combustion practices and oxidation catalyst | 9.8 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 84.7 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen and 9.8 lb/h with duct burner, except startup and shutdown. 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen and 4.7 lb/h without duct burner, except startup and shutdown. 84.7 tons per rolling 12 month period for all operating modes, including startup and shutdown. 42.50 tons per rolling 12 month period for startup and shutdown periods.
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | Combustion Turbine | 15.21 | Natural Gas | 360 | MW | This process represents the GE option for the project - One GE 7FA.05 natural gas-fired combustion turbine generator with an 820.5 MMBTUH duct burner. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices. | 5 | PPMVD@15%O2 | 30-DAY | BACT-PSD | N/A | U | 0 | U | 17 | LB/HR | 30-DAY | 0 |  |  | 0 | 0 | N
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | COMBUSTION TURBINE | 15.21 | NATURAL GAS | 360 | MW | This process represents the Siemens option for the project - One Siemens SGT6-5000F5 natural gas-fired combustion turbine generator with an 820.3 MMBTUH duct burner. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES. | 5 | PPMVD@15% O2 | 30-DAY | BACT-PSD | N/A | U | 0 | U | 17 | LB/HR | 30-DAY | 0 |  |  | 0 | 0 | N
PA-0286 | MOXIE ENERGY LLC/PATRIOT GENERATION PLT | MOXIE ENERGY LLC | LYCOMING COUNTY | PA |  | USA | KENT MORTON | (571) 594 - 0150 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MUHAMMAD Q. ZAMAN, ENVIRONMENTAL PROGRAM MANAGER NORTHCENTRAL REGION 208 West Third St, Suite 101 Williamsport, PA 17701 570-327-3648 | 41-00084A | 4911 | 221112 | 110057116124 | 07/18/2012 &nbsp;ACT | 01/31/2013 &nbsp;ACT | 2013-03-27 | 2020-03-02 | A |  | This plan approval is for the construction of two natural-gas-fired combined cycle powerblocks where each powerblock consists of a combustion turbine and heat recovery steam generator with duct burner. The two powerblocks constructed pursuant to this plan approval will be either the two powerblocks rated 472 megawatts (MW) (P101 and P102) or the powerblocks rated 458 MW (P103 and P104). Additionally, this plan approval is for the construction of a 1464 bhp diesel-fired emergency generator, 460 bhp dieselfired fire pump, 1600 gallon diesel tank, 300 gallon diesel tank, two 15,000 gallon (each) lube oil tanks and ancillary electrical equipment. |  | Combined Cycle Power Blocks 472 MW - (2) | 15.21 | Natural Gas | 0 |  | Two natural-gas-fired combined cycle powerblocks where each powerblock consists of a combustion turbine and heat recovery steam generator with duct burner. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | CO Catalyst | 1 | PPMDV | WITHOUT DUCT BURNER | BACT-PSD | OTHER | U | 0 | U | 1.5 | PPMDV | WITH DUCT BURNER | 33.8 | T/YR | EACH UNIT | 0 | 0 | N
*PA-0298 | FUTURE POWER PA/GOOD SPRINGS NGCC FACILITY | FUTURE POWER PA INC | SCHUYLKILL | PA | 17980 | USA | JAMES PALUMBO | 570-342-5200 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MARK J. WEJKSZNER NORTHEAST REGION AIR PROGRAM MANAGER 2 Public Square Wilkes-Barre, PA 18711 570-826-2357 | 54-00082A | 4911 | 221112 | 110062854870 | 05/03/2013 &nbsp;ACT | 03/04/2014 &nbsp;ACT | 2014-04-17 | 2020-02-19 | A |  | Natural gas-fired combined-cycle electric generation facility that is designed to generate up to 346 MW nominal, using a combustion turbine generator and a heat recovery steam generator that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. The Turbine is rated at 2,267 MMBTU/hr HHV (2,042 MMBTU/hr LHV). The Duct burner is rated at 134.3 MMBTU/hr HHV (120 MMBTU/hr LHV). The proposed project will also include a diesel engine-driven emergency generator; a diesel engine-driven firewater pump; a multi-cell evaporative cooling tower; and associated emission control systems, tanks, and other plant equipment. |  | Turbine, COMBINED CYCLE UNIT (Siemens 5000) | 15.21 | Natural Gas | 2267 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | CO Catalyst | 2 | PPMVD | @ 15% OXYGEN | BACT-PSD | NSPS | U | 0 | U | 7.4 | LB/H | WITH DUCT BURNER | 34.1 | TPY | ON A 12-MONTH ROLLING TOTAL | 0 | 0 | N
PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG without duct burner NG only | 15.21 | Natural gas | 0 |  | Emission limits are for each turbine fueled by NG and operating without duct burner being fired and do not include startup/shutdown emissions. | Volatile Organic Compounds (VOC) | Other - EPA/OAR Method 18 and 25A | (Volatile Organic Compounds (VOC)) | VOC | N |  | 1 | PPMDV @ 15% O2 |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit is for each turbine and HRSG with the duct burner not fired.
TX-0600 | THOMAS C. FERGUSON POWER PLANT | LOWER COLORADO RIVER AUTHORITY | LLANO | TX | 7657 | USA | JOE BENTLEY | 512-473-3272 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tan Nguyen 512-239-3445 tan.nguyen@tceq.texas.gov | PSDTX1244 & 93938 | 4911 | 221112 | 110035336222 | 07/27/2011 &nbsp;ACT | 09/01/2011 &nbsp;ACT | 2011-09-02 | 2020-02-03 | B |  | Power Plant. Two natural gas-fired combined cycle turbine generators (GE 7FA) with unfired HRSG | 93938 | Natural gas-fired turbines | 15.21 | natural gas | 390 | MW | (2) GE7FA at 195 MW each, (1) steam turbine at 200 MW. Each turbine is equipped with an unfired heat recovery steam generator (HRSG), which provides steam for the steam turbine. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Natural gas, good combustion practices and oxidation catalyst | 2 | PPMVD | 3-HR AT 15% OXYGEN | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0618 | CHANNEL ENERGY CENTER LLC | CHANNEL ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX955M1, N021M1, 42179 | 4911 | 221112 | 110034690564 | 09/04/2012 &nbsp;ACT | 10/15/2012 &nbsp;ACT | 2012-10-24 | 2020-02-03 | B |  | Combustion turbine (Siemens 501F)/duct burners (475 MMBtu/hr) with heat recovery steam generator | 42179 and N021M1 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | The turbine is a Siemens 501F rated at a nominal 180 MW and the duct burner will have a maximum design heat input of 475 MMBtu/hr. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion | 2 | PPMVD | @15% O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Compliance is demonstrated during initial stack testing
TX-0619 | DEER PARK ENERGY CENTER | DEER PARK ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX979M2, N036M2, 45642 | 4911 | 221112 | 110017743254 | 08/13/2012 &nbsp;ACT | 09/26/2012 &nbsp;ACT | 2012-10-25 | 2020-02-03 | B |  | The Deer Park Energy Center is a combined cycle cogeneration facility consisting of five Siemens/Westinghouse 501F combustion turbine generators, each with a 725 MMBtu/hr duct burner and heat recovery steam generator. | 45642 and N036M2 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | natural gas-fired combined cycle turbine generator with a heat recovery steam generator equipped with a duct burner. The turbine is a Siemens 501F rated at a nominal 180 megawatts and the DB will have a maximum design rate capability of 725 million British thermal units per hour | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion, use of natural gas | 2 | PPMVD | @15% O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Compliance demonstrated by initial stack test
TX-0620 | ES JOSLIN POWER PLANT | CALHOUN PORT AUTHORITY | CALHOUN | TX |  | USA | CHARLES HAUSMANN | 361-987-2813 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1256, 96336 | 4911 | 221112 | 110001866641 | 05/31/2012 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2012-11-14 | 2020-02-03 | B |  | Three gas-fired combined cycle turbine generators, including a steam turbine generator, to replace the existing steam boiler/turbine generator. | 96336 | Combined cycle gas turbine | 15.21 | natural gas | 195 | MW | The three combustion turbine generators (CTG) will be the General Electric 7FA, each with a maximum base-load electric power output of approximately 195 megawatts (MW). The steam turbine is rated at approximately 235 MW. This project also includes the installation of two emergency generators, one fire water pump, and auxiliary equipment. No duct burners. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion and natural gas as fuel | 2 | PPMVD | @15% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Compliance demonstrated during initial stack sampling
TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 | 221122 | Not Found | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2019-03-06 | A |  | Combinec Cycle Electric Generating Plant | 103839 | combined cycle turbine | 15.21 | natural gas | 700 | MW | The generating equipment consists of two natural gas-fired combustion turbines (CTs), each exhausting to a fired heat recovery steam generator (HRSG) to produce steam to drive a shared steam turbine generator. The steam turbine is rated at 271 MW of electric output. Three models of combustion turbines are being considered for this site: the General Electric 7FA.05, the Siemens SGT6-5000F(4), and the Siemens SGT6-5000F(5). The final selection of the combustion turbine will not be made until after the permit is issued. Plant output will range between 637 and 735 MW, depending on the model turbine selected. Duct Burners are rated at 750 MMBtu/hr each. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 2 | PPMVD | INITIAL STACK TEST, 15% OXYGEN | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0660 | FGE TEXAS POWER I AND FGE TEXAS POWER II | FGE POWER LLC | MITCHELL | TX | 79565 | USA | EMERSON FARRELL | 281-362-2830 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX1364 & 110025 | 3511 | 221112 | NOT FOUND | 10/23/2013 &nbsp;ACT | 03/24/2014 &nbsp;ACT | 2014-06-13 | 2020-03-05 | U |  | Electric Generating Utility | TCEQ Permit No. 110025 | Alstom Turbine | 15.21 | Natural Gas | 230.7 | MW | Four (4) Alstom GT24 CTGs, each with a HRSG and DBs, max design capacity 409 MMBtu/hr | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst, good combustion practices | 2 | PPMVD | CORRECTED TO 15% O2, ROLLING 3 HR AVE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057188626 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.21 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (6) GE LM2500+ DLE turbines that drive the ethylene section compressors with waste heat recovery for amine solution regeneration. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0.6 | LB/H | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Combustion Turbine | 15.21 | natural gas | 87 | MW | The exhaust heat from the turbine will be used to heat a heating medium which is used to regenerate rich amine from the acid gas removal system. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 2 | PPMVD | 1 HOUR BASED ON STACK TEST | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | (2) combined cycle turbines | 15.21 | natural gas | 650 | MW | The specific equipment includes two combustion turbines (CTs) connected to electric generators, producing between 183 and 232 MW of electricity, depending on ambient temperature and the selected CT. The two HRSGs use duct burners rated at 750 MMBtu/hr each to supplement the heat energy from the CTs. The steam from the two HRSGs is combined and routed to a single steam turbine driving a third electric generator with an electricity output capacity of 271 MW. Depending on the selected CT, total plant output at 59Â°F is between 637 MW and 735 MW. The applicant is considering three models of CT; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) Siemens SGT6-5000F(4); or (3) Siemens SGT6-5000F(5). | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 2 | PPMVD | @15% O2, 3-HR ROLLING | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0709 | SAND HILL ENERGY CENTER | CITY OF AUSTIN | TRAVIS | TX |  | USA | JOSEPH RAVI | (512) 322-6284 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez (512) 239-5220 Ruth.alvirez@tceq.texas.gov | 48106, PSDTX1012M2 | 4911 | 221112 | 110008975804 | 03/20/2015 &nbsp;ACT | 09/13/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | GE 7FA Natural Gas-fired Combined Cycle Turbine with DB fired HRSG |  | Natural gas-fired combined cycle turbines | 15.21 | Natural Gas | 173.9 | MW |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 2 | PPM | 1HR. AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Natural Gas fired.
TX-0710 | VICTORIA POWER STATION | VICTORIA WLE L.P. | VICTORIA | TX |  | USA | GARY CLARK | (361) 947-9934 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | 108258 PSDTX1348 | 4911 | 221112 | 110000501154 | 02/14/2013 &nbsp;ACT | 12/01/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | The facility is currently authorized under Standard Permit No. 80878 and several Permits by Rule (PBR), including Â§106.263 for maintenance, startup, and shutdown (MSS) (PBR Registration No. 94387) and Title V Permit No. O-35. Victoria proposes to install an additional natural gas-fired turbine (GT) and HRSG with duct burners at the Victoria Station. The resulting new facility will be a combined cycle generating facility in a 2x2x1 configuration (two combustion turbines, two HRSGs with duct burners, and one steam turbine). |  | combined cycle turbine | 15.21 | natural gas | 197 | MW | General Electric 7FA.04 at 197 MW nominal ouput. The duct burners will be capable of a maximum natural gas firing rate of up to 483 MMBtu/hr (HHV). The duct burners may be fired additional hours; however, total annual firing will not exceed the equivalent of 4,375 hours at maximum capacity per duct burner. The available capacity of the existing steam turbine will be increased from 125 MW in its existing 1x1x1 configuration to approximately 185 MW in the 2x2x1 configuration. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 4 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0712 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER COMPANY | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | (205) 257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tzvi Shalem 512-239-1310 tzvi.shalem@tceq.texas.gov | 111393 PSDTX1368 | 4911 | 221112 | 110007199735 | 06/27/2013 &nbsp;ACT | 11/20/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | Southern Power Company (SPC) is proposing to construct an electric generating facility near Trinidad, Henderson County, Texas. The Trinidad Generating Facility (TGF) will include a natural gas-fired combined cycle combustion turbine generator (CTG) equipped with heat recovery steam generator (HRSG) and duct burners (DB). |  | combined cycle turbine | 15.21 | natural gas | 497 | MW | The facility will consist of a Mitsubishi Heavy Industries (MHI) J model gas fired combustion turbine nominally rated at 497 megawatts (MW) equipped with a HRSG and DB with a maximum design capacity of 402 million British thermal units per hour (MMBtu/hr). The gross nominal output of the CTG with HRSG and DB is 530 MW. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 4 | PPMVD | @15% O2 1-HR | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0713 | TENASKA BROWNSVILLE GENERATING STATION | TENASKA BROWNSVILLE PARTNERS, LLC | CAMERON | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 108411 PSDTX1350 | 4911 | 221112 | unknown | 02/21/2013 &nbsp;ACT | 04/29/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | Tenaska proposes a new electric power plant, using combined cycle gas turbine (CCGT) technology and fueled by pipeline quality natural gas. The proposed permit authorizes two CTs (2x1 CCGT), although the final design selected by Tenaska may only consist of one CT (1x1 CCGT). |  | (2) combined cycle turbines | 15.21 | natural gas | 274 | MW | Each CTG is site-rated at 274 MW gross electric output at 62Â°F ambient temperature. At this condition, two HRSGs with full duct burner firing produce enough steam to generate an additional 336 MW, for a total of 884 MW gross, or with about 5% losses, about 840 MW net electric output. Under summertime conditions, the net output is approximately 800 MW with the 2x1 CCGT configuration or about 400 MW with the 1x1 CCGT configuration. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 2 | PPMVD | @15% O2, 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0714 | S R BERTRON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | HARRIS | TX |  | USA | CRAIG ECKBERG | (713) 537-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | 102731 PSDTX1294 | 4911 | 221112 | 110034988413 | 05/10/2012 &nbsp;ACT | 12/19/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | NRG Texas is proposing to construct an additional electric power generation station at the Bertron Power Project which will generate electric power for sale on the wholesale electric market. The Bertron Power Project will include two power blocks that can be operated in combined cycle mode. |  | (2) combined cycle turbines | 15.21 | natural gas | 240 | MW | The gas turbines will be one of three options: (1) Two Siemens Model F5 (SF5) CTGs each rated at nominal capability of 225 megawatts (MW). Each CTG will have a duct fired HRSG with a maximum heat input of 688 million British thermal units per hour (MMBtu/hr). (2) Two General Electric Model 7FA (GE7FA) CTGs each rated at nominal capability of 215 MW. Each CTG will have a duct fired HRSG with a maximum heat input of 523 MMBtu/hr. (3) Two Mitsubishi Heavy Industry G Frame (MHI501G) CTGs each rated at a nominal electric output of 263 MW. Each CTG will have a duct fired HRSG with a maximum heat input of 686 MMBtu/hr. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 1 | PPMVD | @15% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041470431 | 02/24/2015 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2020-01-31 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | SCR and oxidation catalyst | 4 | PPMVD @ 15% O2 | 3-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0756 | CCI CORPUS CHRISTI CONDENSATE SPLITTER FACILITY | CASTLETON COMMODITIES INTERNATIONAL (CCI) CORPUS C | NUECES | TX |  | USA | BRAD BURMASTER | 281-378-1190 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tony Ionescu, 512-239-1277, tony.ionescu@tceq.texas.gov | 116072 AND PSDTX1388 | 2911 | 324110 | unknown | 09/22/2014 &nbsp;ACT | 06/19/2015 &nbsp;ACT | 2015-07-20 | 2016-07-06 | A |  | Two identical condensate splitter trains each capable of processing 50,000 barrels per day (BPD) of condensate. A bulk petroleum terminal consisting of two ship docks and a barge dock that will handle processed product from the condensate splitters and export to up 500,000 barrels per day of crude condensate. |  | Boilers, BL-1 and BL-2 | 15.21 | natural gas | 37 | MMBtu/hr (max) |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices will limit VOC emissions to 0.005 lb per 1000 scf. Fuel flow will be measured. | 0.005 | LB/100 SCF | EACH BOILER | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 40CFR60 Subparts A and Dc
TX-0767 | LON C. HILL POWER STATION | LON C. HILL, L.P. | NUECES | TX |  | USA | MATTHEW LINDSEY | 713-358-9734 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem, 512-239-1310, Tzvi.Shalem@tceq.texas.gov | 114911 AND PSDTX1380 | 4911 | 221122 | 110000501127 | 07/15/2015 &nbsp;ACT | 10/02/2015 &nbsp;ACT | 2015-09-23 | 2016-07-06 | A |  | The Lon C. Hill Power Station (LCHP) will include two natural gas-fired combined cycle combustion turbines (CTGs) equipped with dry low NOx burners (DLNs), heat recovery steam generators (HRSG), and natural gas-fired duct burners (DBs). Ancillary equipment includes evaporative coolers or inlet chillers, a single steam turbine (ST), auxiliary boiler, emergency generator, firewater pump, two cooling towers, oil water separator, degreaser, two diesel storage tanks, gasoline storage tank, selective catalytic reduction (SCR) and ammonia (NH3) handling systems including an NH3 storage tank, and two water tanks. The LCHP will be a 2x1 combined cycle power plant consisting of two CTGs, two HRSGs and one ST. The CTGs and ST will be one of two options: two Siemens SCC6-5000 CTGs and a SST6-5000 ST, or two General Electric 7FA CTGs and a D-11 ST. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 195 | MW | Two power configuration options authorized Siemens â€“ 240 MW + 250 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 195 MW + 670 MMBtu/hr duct burner | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 2 | PPM |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0773 | FGE EAGLE PINES PROJECT | FGE EAGLE PINES, LLC | CHEROKEE | TX |  | USA | EMERSON FARRELL | 281-407-7749 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, 512-239-1095, Erik.Hendrickson@tceq.texas.gov | 131316, PSDTX1454, AND GHGPSDT | 4911 | 221112 | UNKNOWN | 09/10/2015 &nbsp;ACT | 11/04/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | The FGEEP Project will include three natural gas-fired combined cycle (NGCC) power blocks, each block comprised of two gas-fired combustion turbines, two supplemental fired duct burners (DBs) heat recovery steam generators (HRSGs), and one steam turbine. FGEEP selected Alstom GT36 combustion turbines (CTs), each nominally rated at 321 megawatts (MW). Each HRSG is equipped with DBs that will have a maximum design heat input capacity of 799 million British thermal units per hour (MMBtu/hr). The CTs and DBs are fueled with pipeline quality natural gas. Each power block will also have a steam turbine generator designed to produce approximately 502 MW with the additional duct firing. Each of the three blocks will include the following ancillary equipment: one multi-cell condenser/cooling tower, one emergency generator, one firewater pump, two diesel storage tanks, and pressurized aqueous ammonia storage tanks. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 321 | MW | Alstom GT36 combustion turbines (321 MW)+ 799 million British thermal units per hour (MMBtu/hr) duct burner | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 2 | PPM |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDATION CATALYST | 2 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK AND TTTT
TX-0789 | DECORDOVA STEAM ELECTRIC STATION | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas.gov | 107569 AND PSDTX1432 | 4911 | 221112 | 110008149217 | 12/23/2015 &nbsp;ACT | 03/08/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | The DeCordova Station will consist of two combustion turbine generators (CTGs) operating in simple cycle or combined cycle modes. The gas turbines will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE). Simple cycle operations limited to 2,500 hr/yr. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDATION CATALYST | 2 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.21 | natural gas | 10 | M TONNES/YR | Four GE Frame 7E gas turbines for refrigeration and compression at the site | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Dry low NOx burners and good combustion practices | 2 | PPM | 3-HR AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Simple Cycle Electrical Generation Gas Turbines 15.210 | 15.21 | natural gas | 34 | MW | Nine GE PGT25+G4 gas turbines for electrical generation at the site at 34 MW/turbine | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDATION CATALYST | 2 | PPM | 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0817 | CHOCOLATE BAYOU STEAM GENERATING (CBSG) STATION | INEOS USALLC | BRAZORIA | TX |  | USA | THERESA VITEK | 281-581-3498 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | 123117, PSDTX1460, GHGPSDTX135 | 4911 | 221112 | Not Found | 12/22/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-28 | 2017-11-16 | A |  | support facility providing steam and electricity |  | Combined Cycle Cogeneration | 15.21 | NATURAL GAS | 50 | MW | 2 UNITS EACH 50 MW GE LM6000 | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDATION CATALYST | 1 | PPMDV |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Combined Cycle Turbine with Heat Recovery Steam Generator, fired Duct Burners, and Steam Turbine Generator | 15.21 | NATURAL GAS | 426 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines with HRSGs and Steam Turbine Generators | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices | 3.5 | PPMVD | 15% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0315 | WARREN COUNTY POWER PLANT - DOMINION | VIRGINIA ELECTRIC AND POWER COMPANY | WARREN | VA | 22630 | USA | ROBERT BISHA | 804-273-3010 | ROBERT.M.BISHA@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Manager, Mr. Janardan Pandey, by phone at (540) 574-7817 or by e-mail: Janardan.Pandey@deq.virginia.gov | 81391-007 | 4911 | 221112 | 110040513110 | 09/03/2010 &nbsp;ACT | 12/17/2010 &nbsp;ACT | 2012-09-28 | 2015-03-30 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Virginia Electric and Power Company (Dominion) has proposed to construct and operate a combined-cycle electric power generating facility in Warren County with a nominal generating capacity of 1280 megawatts (MW) at ISO (International Organization for Standardization) conditions. | Equipment to be constructed at ths facility consists of: 3 Mitsubishi Model M501 GAC natural gas-fired combined-cylce turbines, each rated at 299,600 kW (2,996 MMBtu/hr. Each equipped with a heat recovery steam generator (HRSG) having a duct burner with a design rating of 500 MMBtu/hr. This permit supersedes the previous permit issued on 7/30/2004 to CPV Warren LLC. | COMBINED CYCLE TURBINE &amp; DUCT BURNER, 3 | 15.21 | Natural Gas | 2996 | MMBTU/H | Emissions are for one of three units (Mitsubishi natural gas-fired combustion turbine (CT) generator,Model M501 GAC). | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices. | 2.6 | LB/H | 3 HR AVG. (WITHOUT DUCT BURNER FIRING) | BACT-PSD |  | U | 0 | U | 6.1 | LB/H | 3 HR. AVG. (WITH DUCT BURNER FIRING) | 0 |  |  | 0 | 0 | N
VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404 | 4911 | 221112 | 110055066440 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2019-06-19 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | COMBUSTION TURBINE GENERATORS, (3) | 15.21 | Natural Gas | 3442 | MMBTU/H | Three (3) Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners (natural gas-fired). | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst; good combustion practices. | 0.7 | PPMVD | 3 H AVG/WITHOUT DUCT BURNING | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Option 1 - Normal Operation | 15.21 | natural gas | 34000 | MMCF/YR | Option 1: Two on one configuration: 3,482 MMBtu/hr combustion turbine with 475 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices | 0.7 | PPMVD @ 15% O2 | 3 HR AV/WITHOUT DB | BACT-PSD | SIP , NSPS | U | 0 | N | 1.4 | PPMVD @ 15% O2 | 3 HR AV/WITH DB | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combusion Turbine - Option 2 - Normal Operation | 15.21 | Natural Gas | 35000 | MMCF/YR | Option 2: Two on one configuration: 3,116 MMBtu/hr combustion turbine with 991 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practice | 1 | PPMVD @ 15% O2 | 3 H AV/WITHOUT DB | BACT-PSD | NSPS , SIP | N | 0 | N | 2 | PPMVD @ 15% O2 | 3 H AV/WITH DB | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Startup and Shutdown | 15.21 | natural gas | 34000 | MMCF/YR | Startup and Shutdown | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices | 60 | LB/TURBINE/EVENT | COLD START 60 MIN OR LESS | BACT-PSD | SIP | N | 0 | N | 0 | LB/TURBINE/EVENT | WARM START 50 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 14 lb/turbine/event hot start - 30 minutes or less 65 lb/turbine/event shutdown - 30 minutes or less Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combustion Turbine - Startup &amp; Shutdown | 15.21 | Natural Gas | 35000 | MMCF/YR | Startup and Shutdown | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices | 37 | LB/TURBINE/EVENT | COLD START 55 MIN OR LESS | BACT-PSD | SIP | N | 0 | N | 34 | LB/TURBINE/EVENT | WARM START 55 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 34 lb/turbine/event hot start - 50 minutes or less 56 lb/turbine/event shutdown - 38 minutes or less Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS
*VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2020-03-18 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/hr natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/hr combustion turbine. Emission limits reflect the operation of each of the three turbines. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Controlled by an oxidation catalyst and good combustion practices (e.g. controlled fuel/air mixing, adequate temperature, and gas residence time) | 0.7 | PPMVD @ 15% O2 | 3 HR AVG | BACT-PSD | NSPS , SIP | N | 0 | N | 68.1 | T/YR | 12 MO ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS. VOC emissions during tuning are limited by the duration of the tuning event.
*VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2020-03-18 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/hr natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | Startup and Shutdown | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices | 216 | LB/TURBINE/EVENT | COLD START 42 MIN OR LESS | BACT-PSD | NSPS , SIP | N | 0 | N | 216 | LB/TURBINE/EVENT | WARM START 42 MIN OR LESS | 0 |  |  | 0 | 0 | N |  | 168 lb/turbine/event hot start - 42 minutes or less 216 lb/turbine/event shutdown - 42 minutes or less Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS.
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Combined Cycle Turbine/Duct Burner | 15.21 | Natural Gas | 2419.61 | mmBtu/Hr | This entry is for both of two identical units at the facility. Nominal 197 mW General Electric Frame 7FA.04 Turbine w/ Duct Burner - throughput denotes aggregate heat input of turbine and duct burner (HHV). | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 18 | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation Catalyst & Good Combustion Practices | 5.3 | LB/H |  | BACT-PSD |  | U | 0 | U | 0.0022 | LB/MMBTU |  | 2 | PPM | @ 15% O2 | 0 | 0 | N |  | The above VOC limit is applicable with duct firing. The limit without duct firing is 1 ppm @ 15% O2.
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2018-06-25 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.02 Turbine | 15.21 | Natural Gas | 3496.2 | mmBtu/hr | Nominal 640 mWe All emission limits steady-state and include 1000 mmBtu/hr Duct Burner in operation Short Term startup and shutdown limits in lb/event given in permit. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation Catalyst, Good Combustion Practices | 11.4 | LB/HR |  | BACT-PSD |  | U | 0 | U | 54.8 | TONS/YEAR |  | 2 | PPM |  | 0 | 0 | N |  | VOC BACT is different for no Duct Firing = 1ppm
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP01) | 15.21 | Natural Gas | 40 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 3 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD |  | N | 0 | U | 3 | LB/H | 3-HOUR AVERAGE | 14.7 | T/YR |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP02) | 15.21 | Natural Gas | 40 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 3 | PPMV AT 15% O2 | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 3 | LB/H | 3-HOUR AVERAGE | 14.7 | T/YR |  | 0 | 0 | N
ID-0018 | LANGLEY GULCH POWER PLANT | IDAHO POWER COMPANY | PAYETTE | ID |  | USA |  | 2083885820 | TMAHLUM@IDAHOPOWER.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2009.0092 | 4911 | 221112 | UNKNOWN | 06/07/2009 &nbsp;ACT | 06/25/2010 &nbsp;ACT | 2010-08-09 | 2010-10-05 | A |  | ONE-ON-ONE COMBINED CYCLE PLANT CONSISTING OF (1) NATURAL GAS-FIRED COMBUSTION TURBINE (CT) AND (1) STEAM TURBINE. THE CT IS EQUIPPED WITH (1) HEAT RECOVERY STEAM GENERATOR (HRSG) AND DUCT BURNER. ANCILLARY EQUIPMENT INCLUDES (1) DIESEL-FIRED EMERGENCY GENERATOR, (1) DIESEL-FIRED FIRE PUMP, (1) WET COOLING TOWER, AND (6) DRY CHEMICAL STORAGE SILOS. |  | COMBUSTION TURBINE, COMBINED CYCLE W/ DUCT BURNER | 15.21 | NATURAL GAS (ONLY) | 2375.28 | MMBTU/H | SIEMENS SGT6-5000F COMBUSTION TURBINE (NGCT, CCGT) FOR ELECTRICAL GENERATION, NOMINAL 269 MW AND 2.1466 MMSCF/HR | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | CATALYTIC OXIDATION (CATOX), DRY LOW NOX (DLN), GOOD COMBUSTION PRACTICES (GCP) | 2 | PPMVD | 3-HR ROLLING / 15% O2 | BACT-PSD |  | N | 0 |  | 11.5 | PPMVD | 3-HR ROLLING / 15% O2 DURING LL | 0 |  |  | 0 | 0 | N |  | LIMITS APPLY TO COMBUSTION TURBINE AND DUCT BURNER COMBINED EMISSIONS. SECONDARY LIMIT APPLIES DURING STARTUP, SHUTDOWN, AND LOW-LOAD EVENTS (SU/SD/LL). EMISSION LIMIT NOT SPECIFIED DURING SU/SD (GCP ONLY).
*WV-0032 | BROOKE COUNTY POWER PLANT | ESC BROOKE COUNTY POWER I, LLC | BROOKE | WV | 26035 | USA | ANDREW DORN | 7163121042 | DREW.DORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 Steven.R.Pursley@wv.gov | R14-0035 | 4911 | 221112 | Not Found | 03/30/2018 &nbsp;ACT | 09/18/2018 &nbsp;ACT | 2018-12-20 | 2019-01-02 | A |  | Nominal 925 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.01 Turbine | 15.21 | Natural Gas/Ethane | 2737.7 | mmBtu/hr | Facility has 2 identical units, only 1 entry in RBLC. Nominal 462.5 mWe. All emission limits steady-state and include 424 mmBtu/hr Duct Burner in operation. Short Term startup and shutdown limits in lb/event given in permit. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Oxidation Catalyst, Good Combustion Practices | 8.1 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 2 | PPM |  | 0 | 0 | N |  | VOC BACT is different for no Duct Firing = 1ppm
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | Mitsubishi M501-GAC combustion turbine, combined cycle configuration with duct burner. | 15.21 | natural gs | 2988 | MMBTU/H | or ULSD; Duct burner 499 MMBtu/hr, natural gas | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst; Limit the time in startup or shutdown. | 2 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON NG | BACT-PSD |  | U | 0 | U | 5 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON ULSD | 0 |  |  | 0 | 0 | N