## PM_Large Combined Cycle Gas-Fir
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas, combustion inlet air filter. | 0.0025 | LB/MMBTU |  | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Fabric filter control: over $260,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5). Electrostatic Precipitator (ESP): over $188,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5). Wet ESP: over $165,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5). Venturi Scrubber: over $112,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5).
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110070000000 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Combustion turbine with duct burner | 15.21 | Natural gas | 3304.3 | MMBtu/hr | Limits are for each CCCT and yearly limits are for cumulative turbine and duct burner. Duct burner throughput is 637.9 MMBtu/hr. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive natural gas, high-efficiency inlet air filters and DLN | 0.003 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 24.1 | TONS | YEAR | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion air filters; efficient combustion control; low sulfur natural gas fuel. | 0.0033 | LB/MMBTU | TEST PROTOCOL; (3 1-H TESTS IF POSSIBLE) | BACT-PSD | OTHER | N | 90 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit applies to each CTG/HRSG. Limit applies at all times and includes duct burner operation. Other applicable requirement: state rule
*VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404-001 | 4911 | 221112 | 110055000000 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2016-07-07 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | COMBUSTION TURBINE GENERATORS, (3) | 15.21 | Natural Gas | 3442 | MMBTU/H | Three (3) Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners (natural gas-fired). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur/carbon fuel and good combustion practices. | 0.0033 | LB/MMBTU | 3 H AVG/WITHOUT DUCT BURNING | BACT-PSD | NSPS | U | 0 | U | 9.7 | LB/H | 3 H AVG/WITHOUT DUCT BURNING | 0 |  |  | 0 | 0 | N
*VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404-001 | 4911 | 221112 | 110055000000 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2016-07-07 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | COMBUSTION TURBINE GENERATORS, (3) | 15.21 | Natural Gas | 3442 | MMBTU/H | Three (3) Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners (natural gas-fired). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur/carbon fuel and good combustion practices. | 0.0033 | LB/MMBTU | 3 H AVG/WITHOUT DUCT BURNING | BACT-PSD | NSPS | U | 0 | U | 9.7 | LB/H | 3 H AVG/WITHOUT DUCT BURNING | 0 |  |  | 0 | 0 | N
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110060000000 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large combustion turbine | 15.21 | Natural Gas | 0 |  | This process entry is for operations with the duct burner. Limits entered are for each turbine. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices with the use of low ash/sulfer fuels | 0.0039 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 11.8 | LB/HR |  | 0 |  |  | 0 | 0 | N
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110060000000 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large combustion turbine | 15.21 | Natural Gas | 0 |  | This process entry is for operations with the duct burner. Limits entered are for each turbine. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0039 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 11.8 | LB/HR |  | 0 |  |  | 0 | 0 | N
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110060000000 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large combustion turbine | 15.21 | Natural Gas | 0 |  | This process entry is for operations with the duct burner. Limits entered are for each turbine. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices with the use of low ash/sulfer fuels | 0.0039 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 11.8 | LB/HR |  | 0 |  |  | 0 | 0 | N
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.004 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2012 | Cost effectiveness information: Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet scrubber = $16,663/ton
PA-0278 | MOXIE LIBERTY LLC/ASYLUM POWER PL T | MOXIE ENERGY LLC | BRADFORD COUNTY | PA |  | USA | KENT J MORTON | (571) 594 - 0150 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MUHAMMAD Q. ZAMAN, ENVIRONMENTAL PROGRAM MANAGER, NORTHCENTRAL REGION | 08Â·00045A | 491 | 221112 | 45-2015223-1 | 09/26/2011 &nbsp;ACT | 10/10/2012 &nbsp;ACT | 2012-12-03 | 2015-04-03 | A |  |  | The project consists of two identical 1 x 1 power blocks, and each block includes a combustion gas turbine and a steam turbine. Each combined-cycle process will also include a heat recovery steam generator and supplemental duct burners. Additionally, one diesel-fired emergency generator, one diesel-fired fire water pump, two diesel fuel storage tanks, two lube oil storage tanks, and one aqueous ammonia storage tank were proposed to be constructed and operated. Each combined-cycle process will be rated at 468 MW or less. | Combined-cycle Turbines (2) - Natural gas fired | 15.21 | Natural Gas | 3277 | MMBTU/H | Two combine cycle Turbines, each with a combustion turbine and heat recovery steam generator with duct burner. Each combined-cycle process will be rated at 468 MW or less. The heat input rating of each combustion gas turbine is 2890 MMBtu/hr (HHV) or less, and the heat input rating of each supplemental duct burner is equal to 387 MMBtu/hr (HHV) or less. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Using fuel with little or no ash and sulfur content. | 0.004 | LB/MMBTU | FOR 468 MW POWERBLOCK | BACT-PSD |  | U | 0 | U | 0.0057 | LB/MMBTU | FOR 454 MW POWERBLOCK | 0 |  |  | 0 | 0 | N |  | FUel sulfur content of 0.4 grain/100scf
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0042 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0042 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 9 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Emission limit 1 & 2 are for each unit operating without the DB.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0042 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 9 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Emission limit 1 & 2 are for each unit operating without the DB.
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/o Duct Firing | 15.21 | Natural Gas | 2969 | MMBtu/hr | Throughput is for turbine only | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.0044 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA METHODS 5 & 202, OR METHODS 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 0.0048 | LB/MMBTU | 9-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0.0049 | LB/MMBTU | 9-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA METHODS 5 & 202, OR METHODS 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 0.0048 | LB/MMBTU | 9-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0.0049 | LB/MMBTU | 9-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Particulate matter, total (TPM) | Other - EPA METHODS 5 & 202, OR METHODS 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 0.0048 | LB/MMBTU | 9-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0.0049 | LB/MMBTU | 9-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 725 | MEGAWATT | TWO GENERAL ELECTRIC (GE) F-CLASS ADVANCED COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 725 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE-QUALITY NATURAL GAS EXCLUSIVELY AND GOOD COMBUSTION PRACTICE | 0.005 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0.004 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | EMISSION #1 IS WITHOUT DUCT FIRING (FILTERABLE ONLY) EMISSION #2 IS WITH DUCT FIRING (FILTERABLE ONLY)
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/Duct Firing | 15.21 | Natural Gas | 2639 | MMBtu/hr | Duct burner MRC is 946 MMbtu/hr | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.005 | LB/MMBTU |  | BACT-PSD | OPERATING PERMIT , SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110065000000 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG with duct burner NG only | 15.21 | Natural Gas | 3338 | MMBtu/hr | Emission limits are for each turbine operating with duct burner and do not include startup/shutdown emissions. Tons per year limits is a cumulative value for all three CCCT. CEMS for NOx, CO, and O2. Each CCCT and duct burner have 5 operational scenarios: 1 CCCT with duct burner fired - fueled by NG only 2 CCCT with duct burner fired - fueled by NG blend with ethane 3 CCCT without duct burner fired - fueled by NG only 4 CCCT without duct burner fired - fueled by NG blend with ethane 5 CCCT without duct burner fired - fueled by ULSD (Limited to emergency use only) | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuel, good combustion practices | 0.005 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 131.5 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N |  | lb/MMBtu limit is for each turbine and duct burner, TPY is a cumulative total
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/Duct Firing | 15.21 | Natural Gas | 2639 | MMBtu/hr | Duct burner MRC is 946 MMbtu/hr | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.005 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110065000000 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG with duct burner NG only | 15.21 | Natural Gas | 3338 | MMBtu/hr | Emission limits are for each turbine operating with duct burner and do not include startup/shutdown emissions. Tons per year limits is a cumulative value for all three CCCT. CEMS for NOx, CO, and O2. Each CCCT and duct burner have 5 operational scenarios: 1 CCCT with duct burner fired - fueled by NG only 2 CCCT with duct burner fired - fueled by NG blend with ethane 3 CCCT without duct burner fired - fueled by NG only 4 CCCT without duct burner fired - fueled by NG blend with ethane 5 CCCT without duct burner fired - fueled by ULSD (Limited to emergency use only) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuel, good combustion practices | 0.005 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 131.5 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N |  | lb/MMBtu limit is for each turbine and duct burner, TPY is a cumulative total
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110065000000 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG with duct burner NG only | 15.21 | Natural Gas | 3338 | MMBtu/hr | Emission limits are for each turbine operating with duct burner and do not include startup/shutdown emissions. Tons per year limits is a cumulative value for all three CCCT. CEMS for NOx, CO, and O2. Each CCCT and duct burner have 5 operational scenarios: 1 CCCT with duct burner fired - fueled by NG only 2 CCCT with duct burner fired - fueled by NG blend with ethane 3 CCCT without duct burner fired - fueled by NG only 4 CCCT without duct burner fired - fueled by NG blend with ethane 5 CCCT without duct burner fired - fueled by ULSD (Limited to emergency use only) | Particulate matter, total (TPM) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuel, good combustion practicies | 0.005 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 131.5 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N |  | lb/MMBtu limit is for each turbine and duct burner, TPY is a cumulative total
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | MR. RANDY THOMPSON | (615) 532-6825 | randall.thompson@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000000000 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Natural Gas-Fired Combustion Turbine with HRSG | 15.21 | Natural Gas | 1339 | MMBtu/hr | Turbine throughput is 1019.7 MMBtu/hr when burning natural gas and 1083.7 MMBtu/hr when burning No. 2 oil. Duct burner throughput is 319.3 MMBtu/hr. Duct burner firing will occur during natural gas combustion only. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion design and practices | 0.005 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0.015 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N |  | Limit #1 is for gas combustion, limit #2 is for No. 2 oil combustion
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110070000000 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Combustion turbine with duct burner | 15.21 | Natural gas | 3304.3 | MMBtu/hr | Limits are for each CCCT and yearly limits are for cumulative turbine and duct burner. Duct burner throughput is 637.9 MMBtu/hr. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive natural gas, high-efficiency inlet air filters and DLN | 0.0059 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 48.2 | TONS | YEAR | 0 |  |  | 0 | 0 | N
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110070000000 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Combustion turbine with duct burner | 15.21 | Natural gas | 3304.3 | MMBtu/hr | Limits are for each CCCT and yearly limits are for cumulative turbine and duct burner. Duct burner throughput is 637.9 MMBtu/hr. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive natural gas, high-efficiency inlet air filters and DLN | 0.0059 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 48.2 | TONS | YEAR | 0 |  |  | 0 | 0 | N
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.006 | LB/MMBTU | EACH CTG; TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0.012 | LB/MMBTU | EACH CTG; TEST PROTOCOL | 0 |  |  | 0 | 0 | N | 2012 | No additional costs were calculated for PM10 or PM2.5 since additional costs to remove condensable particulate would only inflate the costs calculated for PM. Therefore, the costs for PM were considered to be conservative. Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton West ESP = $42,780/ton West Scrubber = $16,663/ton
*IL-0112 | NELSON ENERGY CENTER | INVENERGY NELSON, LLC | LEE | IL | 61071-9722 | USA | JOEL SCHROEDER | 312-224-1417 | JSCHROEDER@INVENERGYLLC.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Manish Patel, Permit Analyst Manish.Patel@illinois.gov 217-785-1722 | 98080039 | 4911 | 221112 | 110007000000 | 11/12/2009 &nbsp;EST | 12/28/2010 &nbsp;ACT | 2013-02-21 | 2018-03-23 | A |  | Natural gas-fired electic power generation facility with two &quot;combined cycle&quot; turbines followed by heat recovery steam generators (HRSG) and the capability for supplemental fuel firing in the HRSG for each turbine using duct burners. NOx emissions will be controlled by SCR and low NOx combustors. | LSP-Nelson Energy started construction pursuant to a permit issued in year 2000 for a facility that was not completed due to financial difficulties, which eventually resulted in LSP-Nelson entering bankruptcy. Substantial construction of foundations and infrastructure for all units and physical installation of one turbine were completed, including construction of HRSGs. | Electric Generation Facility | 15.21 | Natural Gas | 220 | MW each | Two combined cycle combustion turbines followed by HRSGs with capability for supplemental fuel firing in HRSG for each combustion turbine using duct burners. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | N |  | 0.006 | LB/MMBTU | HOURLY AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.006 | LB/MMBTU | EACH CTG; TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0.012 | LB/MMBTU | EACH CTG; TEST PROTOCOL | 0 |  |  | 0 | 0 | N | 2012 | Cost Effectiveness Information: No additional costs were calculated for PM10 or PM2.5 since additional costs to remove condensable particulate would only inflate the costs calculated for PM. Therefore, the costs for PM were considered to be conservative. Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet Scrubber = $16,663/ton
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.006 | LB/MMBTU | EACH CTG; TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 11432 | 0 | N | 2012 | Cost effectiveness information: Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet scrubber = $16,663/ton
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000000000 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 2449 | MMBTU/H | two 315 MW (nominal) GE Energy 7F Series 5 Rapid Response Combined Cycle Combustion Turbines with Duct Burners and 31 MW (estimated) steam turbine generators | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0062 | LB/MMBTU | 1 HR AVG/DO NOT APPLY DURING SS | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 13 | LB/H | 1 HR AVG/DO NOT APPLY DURING SS | 0 |  |  | 0 | 0 | N |  | PM10(no duct firing): â‰¤0.0071lb/MMBtu, â‰¤8.8 lb/hr during start-ups(â‰¤ 45 minutes): PM/PM10/PM2.5 â‰¤ 6.60 lb per event during shutdowns (â‰¤ 27 minutes): PM/PM10/PM2.5 â‰¤ 3.96 lb per event
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000000000 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 2449 | MMBTU/H | two 315 MW (nominal) GE Energy 7F Series 5 Rapid Response Combined Cycle Combustion Turbines with Duct Burners and 31 MW (estimated) steam turbine generators | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0062 | LB/MMBTU | 1 HR AVG/DO NOT APPLY DURING SS | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 13 | LB/H | 1 HR AVG/DO NOT APPLY DURING SS | 0 |  |  | 0 | 0 | N |  | PM 2.5 (no duct firing): â‰¤0.0071lb/MMBtu, â‰¤8.8 lb/hr during start-ups (â‰¤ 45 minutes): PM/PM10/PM2.5 â‰¤ 6.60 lb per event during shutdowns (â‰¤ 27 minutes): PM/PM10/PM2.5 â‰¤ 3.96 lb per event
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064000000 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine With Duct Burner | 15.21 | Natural Gas | 3727 | MMBtu/hr | DLN burner, SCR, Oxidation Catalyst and shall maintain and operate the sources and associated air cleaning devices in accordance with good engineering practice. shall install, certify, maintain and operate continuous emission monitoring systems (CEMS) for nitrogen oxides, carbon monoxide, carbon dioxide, and ammonia emissions on the exhaust of each combined-cycle powerblock. Emissions limits are for each combustion turbine/duct burner block. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 0.0063 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 13.9 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 58 tpy 12-month rolling basis
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064000000 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine without Duct Burner | 15.21 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 0.0063 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 11.7 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 58 tpy on 12-month rolling basis
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064000000 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine With Duct Burner | 15.21 | Natural Gas | 3727 | MMBtu/hr | DLN burner, SCR, Oxidation Catalyst and shall maintain and operate the sources and associated air cleaning devices in accordance with good engineering practice. shall install, certify, maintain and operate continuous emission monitoring systems (CEMS) for nitrogen oxides, carbon monoxide, carbon dioxide, and ammonia emissions on the exhaust of each combined-cycle powerblock. Emissions limits are for each combustion turbine/duct burner block. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA/OAR Method 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 0.0063 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 13.9 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 13.9 tpy 12-month rolling basis
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064000000 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine without Duct Burner | 15.21 |  | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA/OAR 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 0.0063 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 11.7 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 58 tpy on 12-month rolling basis
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064000000 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine With Duct Burner | 15.21 | Natural Gas | 3727 | MMBtu/hr | DLN burner, SCR, Oxidation Catalyst and shall maintain and operate the sources and associated air cleaning devices in accordance with good engineering practice. shall install, certify, maintain and operate continuous emission monitoring systems (CEMS) for nitrogen oxides, carbon monoxide, carbon dioxide, and ammonia emissions on the exhaust of each combined-cycle powerblock. Emissions limits are for each combustion turbine/duct burner block. | Particulate matter, total (TPM) | Other - EPA/OAR Method 5 | (Particulate Matter (PM)) | PM | N |  | 0.0063 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 13.9 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 58.0 tpy 12-month rolling basis
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064000000 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine without Duct Burner | 15.21 |  | 0 |  |  | Particulate matter, total (TPM) | Other - EPA/OAR Method 5 | (Particulate Matter (PM)) | PM | N |  | 0.0063 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 11.7 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 58 tpy on 12-month rolling basis
AK-0073 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION | ANCHORAGE | AK | 99518 | USA | GREGORY ARTHUR | 907 762 4492 |  | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Kwame Agyei, Permit Engineer, kwame.agyei@alaska.gov | AQ0164CPT01 | 4911 | 221112 | 110046000000 | 04/14/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2012-02-22 | 2014-01-08 | D |  | Power plant that contains four combustion turbines, four duct burners, a black start generator, and an auxiliary heater. |  | Fuel Combustion | 15.21 | Natural Gas | 59900 | HP | EU IDs 5-8 Combined Cycle Natural Gas-fired Combustion Turbines rated at 59,900 hp (44.7 MW) | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion Turbines EU IDs 5-8 use good combustion practices involve increasing the residence time and excess oxygen to ensure complete combustion which in turn minimize particulates without an add-on control technology. | 0.0066 | LB/MMBTU | 3-HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion air filters; efficient combustion control; low sulfur natural gas fuel. | 0.0066 | LB/MMBTU | TEST PROTOCOL (3 1-H TESTS IF POSSIBLE) | BACT-PSD |  | N | 90 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit applies to each CTG/HRSG. Limit applies at all times and includes duct burner operation.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas, combustion inlet air filter. | 0.0066 | LB/MMBTU |  | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Fabric Filter Control: over $260,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5). Electrostatic Precipitator (ESP): over $188,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5). Wet ESP: over $165,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5). Venturi Scrubber: over $112,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5).
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043000000 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two Combine Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 3001.57 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. . (Operational limits are for each CCCT NG-fired with duct burner) | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA/OAR 201 or 201A, and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.0066 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 159.1 | TONS | ANY 12-MONTH PERIOD | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative emissions from both CCCT in any 12-month period
MI-0402 | SUMPTER POWER PLANT | WOLVERINE POWER SUPPLY COOPERATIVE INC. | WAYNE | MI | 48111 | USA | BRIAN WARNER | 231-775-5700 | BWARNER@WPSCI.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Julie Brunner at 517-373-7088 or brunnerj1@michigan.gov for questions related to this permit. Thank you. | 81-11 | 4911 | 221112 | 2616305315 | 05/27/2011 &nbsp;ACT | 11/17/2011 &nbsp;ACT | 2012-11-30 | 2016-05-04 | D |  | Utility--Natural gas fired combustion turbine | Other Facility Wide Pollutants not listed below: PM10 = 14.8 tpy PM2.5 = 14.8 tpy CO2e = 232,639 tpy | Combined cycle combustion turbine w/ HRSG | 15.21 | Natural gas | 130 | MW electrical output | This is a combined-cycle combustion turbine with a non-fired heat recovery steam generator (HRSG). Natural gas-fired combustion turbine conversion to combined-cycle. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0066 | LB/MMBTU | TEST | BACT-PSD | OTHER | N | 0 | N | 7.4 | LB/H | TEST | 0 |  |  | 0 | 0 | N |  | Top ranking option 'Other' is due to NAAQS.
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion air filters, efficient combustion control, low sulfur natural gas fuel. | 0.0066 | LB/MMBTU | TEST PROTOCOL (3 1-H TESTS IF POSSIBLE) | BACT-PSD |  | N | 90 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit applies to each CTG/HRSG. Limit applies at all times and includes duct burner operation.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas, combustion inlet air filter. | 0.0066 | LB/MMBTU |  | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Fabric filter control: over $260,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5). Electrostatic precipitator (ESP): OVER $188,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5). Wet ESP: over $165,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5). Venturi Scrubber: over $112,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5).
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043000000 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two Combine Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 3001.57 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. . (Operational limits are for each CCCT NG-fired with duct burner) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - 201or 201 A, and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.0066 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 159.1 | TONS | ANY 12-MONTH PERIOD | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative emissions from both CCCT in any 12-month period
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043000000 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two Combine Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 3001.57 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. . (Operational limits are for each CCCT NG-fired with duct burner) | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.0066 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 159.1 | TONS | ANY 12-MONTH PERIOD | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative emissions from both CCCT in any 12-month period
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043000000 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two combined cycle turbines with out duct burner | 15.21 | Natural Gas | 2291.64 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode, the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. (Operational limits are for each CCCT NG-fired without duct burner) | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA/OAR 201 or 201A, and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.0068 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative Emissions from both CCCT in any 12-month period
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110065000000 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG without duct burner NG only | 15.21 | Natural gas | 0 |  | Emission limits are for each turbine fueled by NG and operating without duct burner being fired and do not include startup/shutdown emissions. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuels and good combustion practices | 0.0068 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit is for each turbine and HRSG with the duct burner not fired.
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043000000 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two combined cycle turbines with out duct burner | 15.21 | Natural Gas | 2291.64 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode, the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. (Operational limits are for each CCCT NG-fired without duct burner) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA/OAR 201A, and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.0068 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative Emissions from both CCCT in any 12-month period
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110065000000 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG without duct burner NG only | 15.21 | Natural gas | 0 |  | Emission limits are for each turbine fueled by NG and operating without duct burner being fired and do not include startup/shutdown emissions. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuels and good combustion practices | 0.0068 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit is for each turbine and HRSG with the duct burner not fired.
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043000000 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Two combined cycle turbines with out duct burner | 15.21 | Natural Gas | 2291.64 | MCF/hr | Two (2) Combustion Turbine, 235 MW / 2512.5 MMBtu/hr, will fire NG and with the design having no bypasss from the CT to HRSG the CT will always be in combined cycle mode, the HRSG with NG-fired Duct Burner maximum rated heat input capacity 722 MMBtu/hr. CT will employ dry low NOx burner technology (NG firing), controled by SCR and oxidation catalyst. (Operational limits are for each CCCT NG-fired without duct burner) | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.0068 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Tons per year limit is for cumulative Emissions from both CCCT in any 12-month period
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110065000000 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG without duct burner NG only | 15.21 | Natural gas | 0 |  | Emission limits are for each turbine fueled by NG and operating without duct burner being fired and do not include startup/shutdown emissions. | Particulate matter, total (TPM) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuels and good combustion practices | 0.0068 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit is for each turbine and HRSG with the duct burner not fired.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 0.007 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 0.007 lb/MMBTU for each CTGHRSG. Test protocol will specify averaging time. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2013. Pulse Jet Fabric Filter Baghouse: minimum of $62,842 per ton. Mechanical Shaker Fabric Filter Baghouse: minimum of $53,684 per ton. Reverse-Air Fabric Filter Bathouse: minimum of $77,328 per ton. Dry ESP (Wire-Plate Type): minimum of $44,525 per ton. Dry ESP (Wire-Pipe Type): minimum of $66,472 per ton. Wet ESP (Wire-Plate Type): minimum of $77,761 per ton. Wet ESP (Wire-Pipe Type): minimum of $110,364 per ton. Venturi Scrubber: minimum of $52,773 per ton.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 0.007 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. Pulse jet fabric filter baghouse: minimum of $64,473 per ton. Mechanical shaker fabric filter baghouse: minimum of $55,077 per ton. Reverse-air fabric filter baghouse: minimum of $79,336 per ton. Dry ESP (Wire-plate type): minimum of $45,681 per ton. Dry ESP (Wire-pipe type): minimum of $68,197 per ton. Wet ESP (Wire-plate type): minimum of $79,780 per ton. West ESP (Wire-pipe type): minimum of $113,229 per ton. Venturi scrubber: minimum of $54,143 per ton.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0073 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0104 | CPV VALLEY ENERGY CENTER | CPV VALLEY LLC | ORANGE | NY | 10940 | USA |  |  |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-335600136/00001 | 4911 | 221112 | 110043000000 | 08/01/2013 &nbsp;ACT | 08/01/2013 &nbsp;ACT | 2017-08-25 | 2017-09-28 | A |  | CPV Valley Energy Center is a 680 MW combined cycle electric generating facility located in Middletown, NY. The combustion turbines are rated at 2,234 MMBTU/H firing natural gas and 2,145 MMBTU/H firing diesel fuel. The duct burners are rated for 500 MMBTU/H firing natural gas. In addition to the turbines their emission limits for the auxiliary boiler (73.5 MMBTU/H), emergency generator, fire pump, and gas heater. | State Facility Permit | Turbines and duct burners - NG | 15.21 | natural gas | 0 |  | Combined cycle units heat rate 7,605 BTU/KW-H (HHV) or less without duct burner firing to achieve design thermal efficiency of 57.4% (LHV). | Particulate matter, filterable (FPM) | Other - Methods 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Natural gas | 0.0073 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Also PM-10
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0073 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 15.6 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Emission limit 1 & 2 are for each unit operating with the DB.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0073 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 15.6 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Emission limit 1 & 2 are for each unit operating with the DB.
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 725 | MEGAWATT | TWO GENERAL ELECTRIC (GE) F-CLASS ADVANCED COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 725 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE-QUALITY NATURAL GAS EXCLUSIVELY AND GOOD COMBUSTION PRACTICE | 0.008 | LB/MMBTU | AVERAGE OF THREE STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.006 | LB/MMBTU | AVERAGE OF THREE STACK TEST RUNS | 0 |  |  | 0 | 0 | N |  | EMISSIONS #1 IS WITHOUT DUCT FIRING EMISSIONS #2 IS WITH DUCT FIRING
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.008 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 19.9 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N | 2012 | Cost effectiveness information: No additional costs were calculated for PM10 or PM2.5 since additional costs to remove condensable particulate would only inflate the costs calculated for PM. Therefore, the costs for PM were considered to be conservative. Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet scrubber = $16,663/ton
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.008 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 19.9 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N | 2012 | Cost Effectiveness Information: No additonal costs were calculated for PM10 or PM2.5 since additional costs to remove condensable particulate would only inflate the costs calculated for PM. Therefore, the costs for PM were considered to be conservative. Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet scrubber = $16,663/ton
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #1 - combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr | two identical Siemens SGT6-5000F combined cycle turbines without duct firing, each at 2258 mmBtu/hr generating approx. 300 MW each. | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | N |  | 0.01 | LB/MMBTU | AVG. OF 3 ONE HOUR TEST RUNS | BACT-PSD |  | U | 0 | U | 77.1 | TON/YR | 12-MONTH ROLLING | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #2 -combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | N |  | 0.01 | LB/MMBTU | AVERAGE OF 3 ONE-HOUR TEST RUNS | BACT-PSD |  | U | 0 | U | 77.1 | TON/YR | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | 0.01 lb/mmBtu at steady state operation 77.1 tpy includes startup, shutdown and malfunction
*IL-0112 | NELSON ENERGY CENTER | INVENERGY NELSON, LLC | LEE | IL | 61071-9722 | USA | JOEL SCHROEDER | 312-224-1417 | JSCHROEDER@INVENERGYLLC.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Manish Patel, Permit Analyst Manish.Patel@illinois.gov 217-785-1722 | 98080039 | 4911 | 221112 | 110007000000 | 11/12/2009 &nbsp;EST | 12/28/2010 &nbsp;ACT | 2013-02-21 | 2018-03-23 | A |  | Natural gas-fired electic power generation facility with two &quot;combined cycle&quot; turbines followed by heat recovery steam generators (HRSG) and the capability for supplemental fuel firing in the HRSG for each turbine using duct burners. NOx emissions will be controlled by SCR and low NOx combustors. | LSP-Nelson Energy started construction pursuant to a permit issued in year 2000 for a facility that was not completed due to financial difficulties, which eventually resulted in LSP-Nelson entering bankruptcy. Substantial construction of foundations and infrastructure for all units and physical installation of one turbine were completed, including construction of HRSGs. | Electric Generation Facility | 15.21 | Natural Gas | 220 | MW each | Two combined cycle combustion turbines followed by HRSGs with capability for supplemental fuel firing in HRSG for each combustion turbine using duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 0.012 | LB/MMBTU | HOURLY AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 0.014 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 0.014 lb/MMBTU and applies to each CTGHRSG. Test protocol will specify the averaging time. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM10 emissions were assumed the same as PM2.5, so the cost analysis is equivalent. The dollar value year used was 2013. Pulse Jet Fabric Filter Baghouse: minimum of $62,842 per ton. Mechanical Shaker Fabric Filter Baghouse: minimum of $53,684 per ton. Reverse-Air Fabric Filter Bathouse: minimum of $77,328 per ton. Dry ESP (Wire-Plate Type): minimum of $44,525 per ton. Dry ESP (Wire-Pipe Type): minimum of $66,472 per ton. Wet ESP (Wire-Plate Type): minimum of $77,761 per ton. Wet ESP (Wire-Pipe Type): minimum of $110,364 per ton. Venturi Scrubber: minimum of $52,773 per ton.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 0.014 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is for each CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. â€¢ Pulse Jet Fabric Filter Baghouse: minimum of $64,473 per ton â€¢ Mechanical Shaker Fabric Filter Baghouse: minimum of $55,077 per ton â€¢ Reverse-Air Fabric Filter Baghouse: minimum of $79,336 per ton â€¢ Dry ESP (Wire-Plate Type): minimum of $45,681 per ton â€¢ Dry ESP (Wire-Pipe Type): minimum of $68,197 per ton â€¢ Wet ESP (Wire-Plate Type): minimum of $79,780 per ton â€¢ Wet ESP (Wire-Pipe Type): minimum of $113,229 per ton â€¢ Venturi Scrubber: minimum of $54,143 per ton
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 0.014 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 0.014 lb/MMBTU for each CTGHRSG. Test protocol will specify averaging time. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10 which are higher emitting than PM. PM10 emissions were assumed the same as PM2.5, so the cost analysis is equivalent. The dollar value year used was 2013. Pulse Jet Fabric Filter Baghouse: minimum of $62,842 per ton. Mechanical Shaker Fabric Filter Baghouse: minimum of $53,684 per ton. Reverse-Air Fabric Filter Bathouse: minimum of $77,328 per ton. Dry ESP (Wire-Plate Type): minimum of $44,525 per ton. Dry ESP (Wire-Pipe Type): minimum of $66,472 per ton. Wet ESP (Wire-Plate Type): minimum of $77,761 per ton. Wet ESP (Wire-Pipe Type): minimum of $110,364 per ton. Venturi Scrubber: minimum of $52,773 per ton.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 0.014 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is for each CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. â€¢ Pulse Jet Fabric Filter Baghouse: minimum of $64,473 per ton â€¢ Mechanical Shaker Fabric Filter Baghouse: minimum of $55,077 per ton â€¢ Reverse-Air Fabric Filter Baghouse: minimum of $79,336 per ton â€¢ Dry ESP (Wire-Plate Type): minimum of $45,681 per ton â€¢ Dry ESP (Wire-Pipe Type): minimum of $68,197 per ton â€¢ Wet ESP (Wire-Plate Type): minimum of $79,780 per ton â€¢ Wet ESP (Wire-Pipe Type): minimum of $113,229 per ton â€¢ Venturi Scrubber: minimum of $54,143 per ton
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/o Duct Firing | 15.21 | Natural Gas | 2969 | MMBtu/hr | Throughput is for turbine only | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and OTM 28 | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.044 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
[40 empty] | Range Low | 0.0025 | LB/MMBTU
[40 empty] | Range High | 0.044 | LB/MMBTU
[40 empty] | Mean | 0.0069557 | LB/MMBTU
[40 empty] | Median | 0.0063 | LB/MMBTU
[40 empty] | Mode | 0.0066 | LB/MMBTU