## PM_Large Combined Cycle Gas (2
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057000000 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.21 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (6) GE LM2500+ DLE turbines that drive the ethylene section compressors with waste heat recovery for amine solution regeneration. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.72 | LB/H | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Natural gas is the fuel. PM and PM10 are equal to PM2.5.
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110031000000 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Combined Cycle Refrigeration Compressor Turbines (8) | 15.21 | natural gas | 286 | MMBTU/H | GE LM2500+G4 | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and fueled by natural gas | 2.08 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | also for PM10 and PM2.5
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Simple Cycle Electrical Generation Gas Turbines 15.210 | 15.21 | natural gas | 34 | MW | Nine GE PGT25+G4 gas turbines for electrical generation at the site at 34 MW/turbine | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Equipment specifications & work practices - Good combustion practices and use of low carbon, low sulfur fuel | 2.32 | LB/H |  | BACT-PSD |  | N | 0 | U | 8.84 | T/YR |  | 0 |  |  | 0 | 0 | N
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Simple Cycle Electrical Generation Gas Turbines 15.210 | 15.21 | natural gas | 34 | MW | Nine GE PGT25+G4 gas turbines for electrical generation at the site at 34 MW/turbine | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Equipment specifications & work practices - Good combustion practices and use of low carbon, low sulfur fuel | 2.32 | LB/H |  | BACT-PSD |  | N | 0 | U | 8.84 | T/YR |  | 0 |  |  | 0 | 0 | N
LA-0256 | COGENERATION PLANT | WESTLAKE VINYLS COMPANY LP | ASCENSION | LA | 70734 | USA | KAREN KHONSARI | (225) 673-0647 | KKHONSARI@WESTLAKE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: DAN NGUYEN, 225-219-3417 | PSD-LA-754 | 4939 | 221112 | 110001000000 | 01/12/2011 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2011-12-21 | 2012-04-03 | B |  | COGENERATION PLANT AT SYNTHETIC ORGANIC CHEMICAL MANUFACTURING FACILITY | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS &lsquo;&lsquo;FWE&lsquo;&lsquo; REPRESENT POTENTIAL EMISSIONS ASSOCIATED WITH THE COGENERATION PLANT. NOX &lsquo;&lsquo;NETTED OUT&lsquo;&lsquo; OF PSD/NNSR. | COGENERATION TRAINS 1-3 (1-10, 2-10, 3-10) | 15.21 | NATURAL GAS | 475 | MMBTU/H | EACH COGEN TRAIN CONSISTS OF A 50 MW GE LM6000 PF SPRINT TURBINE AND A HEAT RECOVERY STEAM GENERATOR EQUIPPED WITH A 70 MM BTU/HR DUCT BURNER. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS AS FUEL AND GOOD COMBUSTION PRACTICES | 3.72 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | IN ADDITION, AN ANNUAL LIMIT OF 16.31 TPY WAS ESTABLISHED BY THE ACCOMPANYING TITLE V PERMIT (3090-V0).
LA-0256 | COGENERATION PLANT | WESTLAKE VINYLS COMPANY LP | ASCENSION | LA | 70734 | USA | KAREN KHONSARI | (225) 673-0647 | KKHONSARI@WESTLAKE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: DAN NGUYEN, 225-219-3417 | PSD-LA-754 | 4939 | 221112 | 110001000000 | 01/12/2011 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2011-12-21 | 2012-04-03 | B |  | COGENERATION PLANT AT SYNTHETIC ORGANIC CHEMICAL MANUFACTURING FACILITY | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS &lsquo;&lsquo;FWE&lsquo;&lsquo; REPRESENT POTENTIAL EMISSIONS ASSOCIATED WITH THE COGENERATION PLANT. NOX &lsquo;&lsquo;NETTED OUT&lsquo;&lsquo; OF PSD/NNSR. | COGENERATION TRAINS 1-3 (1-10, 2-10, 3-10) | 15.21 | NATURAL GAS | 475 | MMBTU/H | EACH COGEN TRAIN CONSISTS OF A 50 MW GE LM6000 PF SPRINT TURBINE AND A HEAT RECOVERY STEAM GENERATOR EQUIPPED WITH A 70 MM BTU/HR DUCT BURNER. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS AS FUEL AND GOOD COMBUSTION PRACTICES | 3.72 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | IN ADDITION, AN ANNUAL LIMIT OF 16.31 TPY WAS ESTABLISHED BY THE ACCOMPANYING TITLE V PERMIT (3090-V0).
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 3.878 | LB/H | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP01) | 15.21 | Natural Gas | 40 | MW |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 4 | LB/H | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 17.5 | TONS | CALENDAR YEAR | 0 |  |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP02) | 15.21 | Natural Gas | 40 | MW |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 4 | LB/H | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 17.5 | TONS | CALENDAR YEAR | 0 |  |  | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055000000 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Four combined cycle combution turbines | 15.21 | natural gas | 373 | MMBTU/H | Three GE, LMS6000 PF, natural gas-fired, combined cycle CTG, rated at 373 MMBtu per hour each, based on HHV and one (1) HRSG each with no Duct Burners | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustor design | 4.3 | LB/H | AVE OVER STACK TEST LENGTH | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055000000 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Four combined cycle combution turbines | 15.21 | natural gas | 373 | MMBTU/H | Three GE, LMS6000 PF, natural gas-fired, combined cycle CTG, rated at 373 MMBtu per hour each, based on HHV and one (1) HRSG each with no Duct Burners | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustor design | 4.3 | LB/H | AVE OVER STACK TEST LENGTH | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas without Duct Burner | 15.21 | Natural Gas | 8040 | H/YR |  | Particulate matter, filterable (FPM) | Other - NJ TEST METHOD | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 4.4 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY STACK TESTING
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 4.529 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. Pulse jet fabric filter baghouse: minimum of $64,473 per ton. Mechanical shaker fabric filter baghouse: minimum of $55,077 per ton. Reverse-air fabric filter baghouse: minimum of $79,336 per ton. Dry ESP (Wire-plate type): minimum of $45,681 per ton. Dry ESP (Wire-pipe type): minimum of $68,197 per ton. Wet ESP (Wire-plate type): minimum of $79,780 per ton. West ESP (Wire-pipe type): minimum of $113,229 per ton. Venturi scrubber: minimum of $54,143 per ton.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas, combustion inlet air filter. | 4.8368 | LB/H |  | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Fabric filter control: over $260,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5). Electrostatic Precipitator (ESP): over $188,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5). Wet ESP: over $165,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5). Venturi Scrubber: over $112,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5).
VA-0319 | GATEWAY COGENERATION 1, LLC - SMART WATER PROJECT | GATEWAY GREEN ENERGY | PRINCE GEORGE | VA | 23875-3000 | USA | T. EDWARD MCDANIEL | 972-638-8798 | EMCDANIEL@GGEHLLC.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52375-002 | 4911 | 221112 | 110045000000 | 01/11/2012 &nbsp;ACT | 08/27/2012 &nbsp;ACT | 2013-01-16 | 2015-05-29 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Combined cycle electrical power generating facility (160 MW), consisting of two combusion turbines (Rolls Royce Trent 60 WLE) with associated HRSG and no duct burning. |  | COMBUSTION TURBINES, (2) | 15.21 | Natural Gas | 593 | MMBTU/H | Burns primarily natural gas but has the capacity to burn up to 500 hours of ultra low sulfur diesel fuel (ULSD) as backup. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean burning fuels and good combustion practices. | 5 | LB/H | 3 H AVG | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Stack testing and visible emission evaluation.
VA-0319 | GATEWAY COGENERATION 1, LLC - SMART WATER PROJECT | GATEWAY GREEN ENERGY | PRINCE GEORGE | VA | 23875-3000 | USA | T. EDWARD MCDANIEL | 972-638-8798 | EMCDANIEL@GGEHLLC.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52375-002 | 4911 | 221112 | 110045000000 | 01/11/2012 &nbsp;ACT | 08/27/2012 &nbsp;ACT | 2013-01-16 | 2015-05-29 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Combined cycle electrical power generating facility (160 MW), consisting of two combusion turbines (Rolls Royce Trent 60 WLE) with associated HRSG and no duct burning. |  | COMBUSTION TURBINES, (2) | 15.21 | Natural Gas | 593 | MMBTU/H | Burns primarily natural gas but has the capacity to burn up to 500 hours of ultra low sulfur diesel fuel (ULSD) as backup. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean-burning fuels and good combustion practices. | 5 | LB/H | 3 H AVG | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Stack testing and visible emission evaluation.
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110039000000 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 6 | LB/H | TURBINE SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 6 | LB/EVENT | TURBINE SHUTDOWN PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF SHUTDOWN NOT TO EXCEED 30 MINUTES; 2) SHUTDOWN MEANS THE PERIOD BEGINNING WITH THE LOWERING OF EQUIPMENT FROM BASE LOAD AND LASTING UNTIL FUEL FLOW IS COMPLETELY OFF AND COMBUSTION HAS CEASED
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110039000000 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 6 | LB/H | TURBINE SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 6 | LB/EVENT | TURBINE SHUTDOWN PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF SHUTDOWN NOT TO EXCEED 30 MINUTES; 2) SHUTDOWN MEANS THE PERIOD BEGINNING WITH THE LOWERING OF EQUIPMENT FROM BASE LOAD AND LASTING UNTIL FUEL FLOW IS COMPLETELY OFF AND COMBUSTION HAS CEASED
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063000000 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine without Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burner. | Particulate matter, filterable (FPM) | Other - NJ Test Method | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 6 | LB/H | AVERAGE OF THREE ONE HOUR STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110070000000 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Combustion turbine with duct burner | 15.21 | Natural gas | 3304.3 | MMBtu/hr | Limits are for each CCCT and yearly limits are for cumulative turbine and duct burner. Duct burner throughput is 637.9 MMBtu/hr. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive natural gas, high-efficiency inlet air filters and DLN | 6.695 | LB/H |  | BACT-PSD |  | U | 0 | U | 48.2 | TONS | YEAR | 0 |  |  | 0 | 0 | N
TX-0817 | CHOCOLATE BAYOU STEAM GENERATING (CBSG) STATION | INEOS USALLC | BRAZORIA | TX |  | USA | THERESA VITEK | 281-581-3498 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | 123117, PSDTX1460, GHGPSDTX135 | 4911 | 221112 | Not Found | 12/22/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-28 | 2017-11-16 | A |  | support facility providing steam and electricity |  | Combined Cycle Cogeneration | 15.21 | NATURAL GAS | 50 | MW | 2 UNITS EACH 50 MW GE LM6000 | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 6.98 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0817 | CHOCOLATE BAYOU STEAM GENERATING (CBSG) STATION | INEOS USALLC | BRAZORIA | TX |  | USA | THERESA VITEK | 281-581-3498 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | 123117, PSDTX1460, GHGPSDTX135 | 4911 | 221112 | Not Found | 12/22/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-28 | 2017-11-16 | A |  | support facility providing steam and electricity |  | Combined Cycle Cogeneration | 15.21 | NATURAL GAS | 50 | MW | 2 UNITS EACH 50 MW GE LM6000 | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 6.98 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0817 | CHOCOLATE BAYOU STEAM GENERATING (CBSG) STATION | INEOS USALLC | BRAZORIA | TX |  | USA | THERESA VITEK | 281-581-3498 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | 123117, PSDTX1460, GHGPSDTX135 | 4911 | 221112 | Not Found | 12/22/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-28 | 2017-11-16 | A |  | support facility providing steam and electricity |  | Combined Cycle Cogeneration | 15.21 | NATURAL GAS | 50 | MW | 2 UNITS EACH 50 MW GE LM6000 | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 6.98 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/o Duct Firing | 15.21 | Natural Gas | 2969 | MMBtu/hr | Throughput is for turbine only | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and OTM 28 | (Particulate Matter (PM)) | PM | P | Good Combustion | 7.756 | LB/H |  | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 7.756 | LB/H | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 0.014 lb/MMBTU for each CTGHRSG. Test protocol will specify averaging time. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10 which are higher emitting than PM. PM10 emissions were assumed the same as PM2.5, so the cost analysis is equivalent. The dollar value year used was 2013. Pulse Jet Fabric Filter Baghouse: minimum of $62,842 per ton. Mechanical Shaker Fabric Filter Baghouse: minimum of $53,684 per ton. Reverse-Air Fabric Filter Bathouse: minimum of $77,328 per ton. Dry ESP (Wire-Plate Type): minimum of $44,525 per ton. Dry ESP (Wire-Pipe Type): minimum of $66,472 per ton. Wet ESP (Wire-Plate Type): minimum of $77,761 per ton. Wet ESP (Wire-Pipe Type): minimum of $110,364 per ton. Venturi Scrubber: minimum of $52,773 per ton.
VA-0315 | WARREN COUNTY POWER PLANT - DOMINION | VIRGINIA ELECTRIC AND POWER COMPANY | WARREN | VA | 22630 | USA | ROBERT BISHA | 804-273-3010 | ROBERT.M.BISHA@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Manager, Mr. Janardan Pandey, by phone at (540) 574-7817 or by e-mail: Janardan.Pandey@deq.virginia.gov | 81391-007 | 4911 | 221112 | 110041000000 | 09/03/2010 &nbsp;ACT | 12/17/2010 &nbsp;ACT | 2012-09-28 | 2015-03-30 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Virginia Electric and Power Company (Dominion) has proposed to construct and operate a combined-cycle electric power generating facility in Warren County with a nominal generating capacity of 1280 megawatts (MW) at ISO (International Organization for Standardization) conditions. | Equipment to be constructed at ths facility consists of: 3 Mitsubishi Model M501 GAC natural gas-fired combined-cylce turbines, each rated at 299,600 kW (2,996 MMBtu/hr. Each equipped with a heat recovery steam generator (HRSG) having a duct burner with a design rating of 500 MMBtu/hr. This permit supersedes the previous permit issued on 7/30/2004 to CPV Warren LLC. | COMBINED CYCLE TURBINE &amp; DUCT BURNER, 3 | 15.21 | Natural Gas | 2996 | MMBTU/H | Emissions are for one of three units (Mitsubishi natural gas-fired combustion turbine (CT) generator,Model M501 GAC). | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Natural Gas only, fuel has maximum sulfur content of 0.0003% by weight. | 8 | LB/H | 3 HR AVG. (WITHOUT DUCT BURNER FIRING) | BACT-PSD |  | U | 0 | U | 14 | LB/H | 3 HR. AVG. (WITH DUCT BURNER FIRING) | 0 |  |  | 0 | 0 | N |  | PM-10 includes condensable PM. Emissions are for one of three units.
VA-0315 | WARREN COUNTY POWER PLANT - DOMINION | VIRGINIA ELECTRIC AND POWER COMPANY | WARREN | VA | 22630 | USA | ROBERT BISHA | 804-273-3010 | ROBERT.M.BISHA@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Manager, Mr. Janardan Pandey, by phone at (540) 574-7817 or by e-mail: Janardan.Pandey@deq.virginia.gov | 81391-007 | 4911 | 221112 | 110041000000 | 09/03/2010 &nbsp;ACT | 12/17/2010 &nbsp;ACT | 2012-09-28 | 2015-03-30 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Virginia Electric and Power Company (Dominion) has proposed to construct and operate a combined-cycle electric power generating facility in Warren County with a nominal generating capacity of 1280 megawatts (MW) at ISO (International Organization for Standardization) conditions. | Equipment to be constructed at ths facility consists of: 3 Mitsubishi Model M501 GAC natural gas-fired combined-cylce turbines, each rated at 299,600 kW (2,996 MMBtu/hr. Each equipped with a heat recovery steam generator (HRSG) having a duct burner with a design rating of 500 MMBtu/hr. This permit supersedes the previous permit issued on 7/30/2004 to CPV Warren LLC. | COMBINED CYCLE TURBINE &amp; DUCT BURNER, 3 | 15.21 | Natural Gas | 2996 | MMBTU/H | Emissions are for one of three units (Mitsubishi natural gas-fired combustion turbine (CT) generator,Model M501 GAC). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Natural Gas only, fuel has maximum sulfur content of 0.0003% by weight. | 8 | LB/H | 3 HR AVG. (WITHOUT DUCT BURNER FIRING) | BACT-PSD |  | U | 0 | U | 14 | LB/H | 3 HR. AVG. (WITH DUCT BURNER FIRING) | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion air filters; efficient combustion control; low sulfur natural gas fuel. | 8.5371 | LB/H | TEST PROTOCOL; (3 1-H TESTS IF POSSIBLE) | BACT-PSD | OTHER | N | 90 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit applies to each CTG/HRSG. Limit applies at all times and includes duct burner operation. Other applicable requirement: state rule
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110001000000 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITHOUT DUCT BURNER - GENERAL ELECTRIC | 15.21 | Natural Gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each General Electric combustion turbine will be 2,312 MMBtu/hr(HHV) | Particulate matter, filterable (FPM) | Other - NJ Test Method | (Particulate Matter (PM)) | PM | P | Use of Natural Gas as a clean burning fuel | 8.7 | LB/H | AVERAGE OF THREE ONE-HOUR TESTS | BACT-PSD | OPERATING PERMIT | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS. HEAT INPUT LIMITED TO 6,802 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR KEYS TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS KEYS PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE-QUALITY NATURAL GAS EXCLUSIVELY AND GOOD COMBUSTION PRACTICE | 8.8 | LB/H | 3-HOUR BLOCK AVERAGE, W/OUT DUCT FIRING | BACT-PSD |  |  | 0 |  | 12.2 | LB/H | WITH DUCT FIRING | 0 |  |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Combined Cycle Turbine/Duct Burner | 15.21 | Natural Gas | 2419.61 | mmBtu/Hr | This entry is for both of two identical units at the facility. Nominal 197 mW General Electric Frame 7FA.04 Turbine w/ Duct Burner - throughput denotes aggregate heat input of turbine and duct burner (HHV). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Good Combustion Practices, Inlet Air Filtration, & use of Natural Gas | 8.9 | LB/H |  | BACT-PSD |  | U | 0 | U | 0.0037 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N |  | Assume all PM is PM2.5 or less. PM2.5 limit is applicable with and without duct firing.
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST. HEAT RATE LIMITED TO 6,793 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR MATTAWOMAN TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS MATTAWOMAN PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE-QUALITY NATURAL GAS EXCLUSIVELY AND GOOD COMBUSTION PRACTICE | 8.9 | LB/H | 3-HOUR BLOCK AVERAGE (W/OUT DUCT FIRING) | BACT-PSD |  |  | 0 |  | 13.9 | LB/H | 3-HOUR BLOCK AVERAGE (WITH DUCT FIRING) | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110044000000 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 8.91 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110044000000 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 8.91 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110044000000 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total (TPM) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 8.91 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110044000000 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total (TPM) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 8.91 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 9.0174 | LB/H | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 9.0174 | LB/H | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 9 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Emission limit 1 & 2 are for each unit operating without the DB.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 9.0174 | LB/H | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 9 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Emission limit 1 & 2 are for each unit operating without the DB.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 9.058 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is for each CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. â€¢ Pulse Jet Fabric Filter Baghouse: minimum of $64,473 per ton â€¢ Mechanical Shaker Fabric Filter Baghouse: minimum of $55,077 per ton â€¢ Reverse-Air Fabric Filter Baghouse: minimum of $79,336 per ton â€¢ Dry ESP (Wire-Plate Type): minimum of $45,681 per ton â€¢ Dry ESP (Wire-Pipe Type): minimum of $68,197 per ton â€¢ Wet ESP (Wire-Plate Type): minimum of $79,780 per ton â€¢ Wet ESP (Wire-Pipe Type): minimum of $113,229 per ton â€¢ Venturi Scrubber: minimum of $54,143 per ton
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 9.058 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is for each CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. â€¢ Pulse Jet Fabric Filter Baghouse: minimum of $64,473 per ton â€¢ Mechanical Shaker Fabric Filter Baghouse: minimum of $55,077 per ton â€¢ Reverse-Air Fabric Filter Baghouse: minimum of $79,336 per ton â€¢ Dry ESP (Wire-Plate Type): minimum of $45,681 per ton â€¢ Dry ESP (Wire-Pipe Type): minimum of $68,197 per ton â€¢ Wet ESP (Wire-Plate Type): minimum of $79,780 per ton â€¢ Wet ESP (Wire-Pipe Type): minimum of $113,229 per ton â€¢ Venturi Scrubber: minimum of $54,143 per ton
CT-0157 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo james.grillo@ct.cov 860-424-3570 | 144-0023 | 4911 | 221112 | 110041000000 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-03 | 2016-02-19 | A |  | 805 MW Combined Cycle Power Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/12 months |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 9.73 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 20.4 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
CT-0158 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo; james.grillo@ct.gov; 860-424-3570 | 144-0024 | 4911 | 221112 | 110041000000 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-04 | 2016-02-19 | A |  | 805 MW Combined Cycle Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/yr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 9.73 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 20.4 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110001000000 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITH DUCT BURNER - GENERAL ELECTRIC | 15.21 | Natural gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each General Electric combustion each turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 MMBtu/hr duct burner | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Other - NJ Test Method | (Particulate Matter (PM)) | PM | P | Use of Natural Gas a clean burning fuel | 9.8 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | BACT-PSD | OPERATING PERMIT | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 9.9 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit in the table above is for EACH CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. Pulse jet fabric filter baghouse: minimum of $364,528 per ton. Mechanical shaker fabric filter baghouse: minimum of $404,724 per ton. Reverse-air fabric filter baghouse: minimum of $476,689 per ton. Dry ESP (Wire-plate type): minimum of $478,806 Dry ESP (Wire-pipe type): minimum of $303,809 per ton. Wet ESP (Wire-plate type): minimum of $576,763 per ton. Wet ESP (Wire-pipe type): minimum of $440,047 per ton. Venturi Scrubber: minimum of $1,445,564 per ton.
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110070000000 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Combustion turbine with duct burner | 15.21 | Natural gas | 3304.3 | MMBtu/hr | Limits are for each CCCT and yearly limits are for cumulative turbine and duct burner. Duct burner throughput is 637.9 MMBtu/hr. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive natural gas, high-efficiency inlet air filters and DLN | 9.9129 | LB/H |  | BACT-PSD |  | U | 0 | U | 24.1 | TONS | YEAR | 0 |  |  | 0 | 0 | N
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 9.944 | LB/H | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N | 2012 | Cost effectiveness information: Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet scrubber = $16,663/ton
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063000000 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine without Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burner. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 10 | LB/H | AVERAGE OF THREE ONE HOUR STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063000000 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine without Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burner. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 10 | LB/H | AVERAGE OF THREE ONE HOUR STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110065000000 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Mitsubishi, with duct burners | 15.21 | Natural Gas | 47917 | MMSCF/rolling 12-MO | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process with duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | clean burning fuel, only natural gas | 10.1 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 44.2 | T/YR | PER ROLLING 12-MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for both PM10 and PM2.5 together. Additional limit: 0.00373 LB PM10/PM2.5 per MMBtu of heat input. T/YR limit is for 2 turbines.
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas with Duct Burner | 15.21 | natural gas | 4000 | h/yr |  | Particulate matter, filterable (FPM) | Other - NJ TEST METHOD | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 10.4 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY STACK TESTING
*PA-0298 | FUTURE POWER PA/GOOD SPRINGS NGCC FACILITY | FUTURE POWER PA INC | SCHUYLKILL | PA | 17980 | USA | JAMES PALUMBO | 570-342-5200 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MARK J. WEJKSZNER NORTHEAST REGION AIR PROGRAM MANAGER 2 Public Square Wilkes-Barre, PA 18711 570-826-2357 | 54-00082A | 4911 | 221112 | 26-3703407-1 | 05/03/2013 &nbsp;ACT | 03/04/2014 &nbsp;ACT | 2014-04-17 | 2018-03-23 | A |  | Natural gas-fired combined-cycle electric generation facility that is designed to generate up to 346 MW nominal, using a combustion turbine generator and a heat recovery steam generator that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. The Turbine is rated at 2,267 MMBTU/hr HHV (2,042 MMBTU/hr LHV). The Duct burner is rated at 134.3 MMBTU/hr HHV (120 MMBTU/hr LHV). The proposed project will also include a diesel engine-driven emergency generator; a diesel engine-driven firewater pump; a multi-cell evaporative cooling tower; and associated emission control systems, tanks, and other plant equipment. |  | Turbine, COMBINED CYCLE UNIT (Siemens 5000) | 15.21 | Natural Gas | 2267 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 10.4 | LB/H | WITH DUCT BURNER | BACT-PSD | NSPS | U | 0 | U | 38.95 | T/YR | BASED ON A 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110001000000 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | Combined Cycle Combustion Turbine -Siemens turbine without Duct Burner | 15.21 | Natural gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each Siemens combustion turbine will be 2,356 MMBtu/hr(HHV) | Particulate matter, filterable (FPM) | Other - NJ Test Method | (Particulate Matter (PM)) | PM | P | Use of Natural Gas as a clean burning fuel | 10.5 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110001000000 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITH DUCT BURNER - SIEMENS | 15.21 | Natural Gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two Siemens turbines and two associated duct burners) The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). | Particulate matter, filterable (FPM) | Other - NJ Test Method | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 10.6 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | BACT-PSD | OPERATING PERMIT | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0080 | HESS NEWARK ENERGY CENTER | HESS NEWARK ENERGY CENTER, LLC | ESSEX | NJ | 7105 | USA | PETER HAID | (774) 750-7088 | PHAID@HESS.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Supervisor: Yogesh Doshi - yogesh.doshi@dep.state.nj.us Phone: 609-633-7249 Permit Evaluator: Michael Hogan - michael.hogan@dep.state.nj.us. Phone: (609)-633-1124 | 08857/BOP110001 | 4911 | 221112 | 110045000000 | 12/10/2011 &nbsp;ACT | 11/01/2012 &nbsp;ACT | 2013-04-04 | 2018-04-17 | A |  | Combined Cycle Electric Generating Facility HESS Newark Energy Center (Hess-NEC), proposed at City of Newark (Essex County), New Jersey, would be a new, highly efficient, 655 MW combined-cycle power generating facility. Hess-NEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,320 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, a 12-cell mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Facility-wide Greenhouse Gas (GHG) emissions as CO2e emissions = 2,003,654 tpy | Combined Cycle Combustion Turbine | 15.21 | natural gas | 39463 | MMCubic ft/yr | Fuel: Annual throughput is for 2 turbines, 2 duct burners and 1 auxiliary boiler CO2e = 2,000,268 t/yr for the facility (2 turbines, 2 duct burners and 1 auxiliary boiler, 1 emergency generator and 1 fire pump) | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Other - EPA/OAR Method 201A and 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 11 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 235 | MW | TWO SIEMENS F-CLASS (SGT6-500FEE) SERIES COMBUSTION TURBINES (CTS) WITH DUCT BURNERS, WITH A NOMINAL GENERATING CAPACITY OF 735 MW, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), DRY LOW-NOX COMBUSTORS, SCR, OXIDATION CATALYST, AND FUELED EXCLUSIVELY ON PIPELINE QUALITY NATURAL GAS. HEAT INPUT LIMITED TO 6,802 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR KEYS TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS KEYS PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE-QUALITY NATURAL GAS EXCLUSIVELY AND GOOD COMBUSTION PRACTICES. | 11 | LB/H | W/OUT DUCT FIRING, AVG. OF 3 STACK TESTS | BACT-PSD |  |  | 0 |  | 15 | LB/H | WITH DUCT FIRING, AVG. OF 3 STACK TESTS | 0 |  |  | 0 | 0 | N |  | AT ALL TIMES
CA-1198 | MORRO BAY POWER PLANT | DYNERGY MORRO BAY LLC | SAN LUIS OBISPO | CA | 93443 | USA | STEVE GOSCHKE |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SCC 2005-01 | 4911 | 221112 | 110001000000 | 06/23/2005 &nbsp;ACT | 09/25/2008 &nbsp;ACT | 2012-11-09 | 2014-01-14 | B | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | POWER PLANT | PSD permit is for a modernization Project which consists of replacing four existing 1950/1960-era fossil-fuel-fired electric utility steam generators (1002 megawatt [MW] total) with two combined cycle gas turbine block units. Each new block unit will be capable of producing 600 MW. Each new block unit will consist of two GE Frame 7, Model PG7241, 180 MW gas-fired turbines, two HRSGs with duct burners, and one 240 MW steam turbine. The modernization project also includes, in part, demolition of the existing fuel oil tank farm, demolition of three existing 450-foot exhaust stacks, installation of two new 145-foot exhaust stacks, and refurbishment of the sea-water cooling intake structure. | COMBUSTION TURBINE GENERATOR | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA Method 5 and 202 | (Particulate Matter (PM)) | PM | P | USE PIPELINE QUALITY NATURAL GAS, OPERATE DUCT BURNERS NO MORE THAN 4000 HRS PER YEAR (12-MONTH ROLLING AVG BASIS) | 11 | LB/H | 6-HR ROLLING AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 13.3 | LB/H | 6-HR ROLLING AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N |  | A third emission limit was entered into the Standard Limit field, however, this pollutant, TPM10, is not listed in Appendix E of the RBLC User's Manual, Volume 3. Below is the 3rd emission limit: 203.2 T/YR, 12-MONTH ROLLING AVG. PSD PERMIT ONLY FOR PM/PM10. FACILITY NET OUT OF PSD REVIEW FOR NOX, CO, AND VOC. SOX EMISSION LESS THAN SIGNIFICANT AND NOT SUBJECT TO PSD REVIEW.
CA-1198 | MORRO BAY POWER PLANT | DYNERGY MORRO BAY LLC | SAN LUIS OBISPO | CA | 93443 | USA | STEVE GOSCHKE |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SCC 2005-01 | 4911 | 221112 | 110001000000 | 06/23/2005 &nbsp;ACT | 09/25/2008 &nbsp;ACT | 2012-11-09 | 2014-01-14 | B | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | POWER PLANT | PSD permit is for a modernization Project which consists of replacing four existing 1950/1960-era fossil-fuel-fired electric utility steam generators (1002 megawatt [MW] total) with two combined cycle gas turbine block units. Each new block unit will be capable of producing 600 MW. Each new block unit will consist of two GE Frame 7, Model PG7241, 180 MW gas-fired turbines, two HRSGs with duct burners, and one 240 MW steam turbine. The modernization project also includes, in part, demolition of the existing fuel oil tank farm, demolition of three existing 450-foot exhaust stacks, installation of two new 145-foot exhaust stacks, and refurbishment of the sea-water cooling intake structure. | COMBUSTION TURBINE GENERATOR | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA Method 5 and 202 | (Particulate Matter (PM)) | PM | P | USE PIPELINE QUALITY NATURAL GAS, OPERATE DUCT BURNERS NO MORE THAN 4000 HRS PER YEAR (12-MONTH ROLLING AVG BASIS) | 11 | LB/H | 6-HR ROLLING AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 13.3 | LB/H | 6-HR ROLLING AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N |  | A third emission limit was entered into the Standard Limit field, however, this pollutant, TPM10, is not listed in Appendix E of the RBLC User's Manual, Volume 3. Below is the 3rd emission limit: 203.2 T/YR, 12-MONTH ROLLING AVG. PSD PERMIT ONLY FOR PM/PM10. FACILITY NET OUT OF PSD REVIEW FOR NOX, CO, AND VOC. SOX EMISSION LESS THAN SIGNIFICANT AND NOT SUBJECT TO PSD REVIEW.
CA-1198 | MORRO BAY POWER PLANT | DYNERGY MORRO BAY LLC | SAN LUIS OBISPO | CA | 93443 | USA | STEVE GOSCHKE |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SCC 2005-01 | 4911 | 221112 | 110001000000 | 06/23/2005 &nbsp;ACT | 09/25/2008 &nbsp;ACT | 2012-11-09 | 2014-01-14 | B | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | POWER PLANT | PSD permit is for a modernization Project which consists of replacing four existing 1950/1960-era fossil-fuel-fired electric utility steam generators (1002 megawatt [MW] total) with two combined cycle gas turbine block units. Each new block unit will be capable of producing 600 MW. Each new block unit will consist of two GE Frame 7, Model PG7241, 180 MW gas-fired turbines, two HRSGs with duct burners, and one 240 MW steam turbine. The modernization project also includes, in part, demolition of the existing fuel oil tank farm, demolition of three existing 450-foot exhaust stacks, installation of two new 145-foot exhaust stacks, and refurbishment of the sea-water cooling intake structure. | COMBUSTION TURBINE GENERATOR | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | USE PIPELINE QUALITY NATURAL GAS, OPERATE DUCT BURNERS NO MORE THAN 4000 HRS PER YEAR (12-MONTH ROLLING AVG BASIS) | 11 | LB/H | 6-HR ROLLING AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 13.3 | LB/H | 6-HR ROLLING AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N |  | A third emission limit was entered into the Standard Limit field, however, this pollutant, TPM, is not listed in Appendix E of the RBLC User's Manual, Volume 3. Below is the 3rd emission limit: 203.2 T/YR, 12-MONTH ROLLING AVG. PSD PERMIT ONLY FOR PM/PM10. FACILITY NET OUT OF PSD REVIEW FOR NOX, CO, AND VOC. SOX EMISSION LESS THAN SIGNIFICANT AND NOT SUBJECT TO PSD REVIEW.
CA-1198 | MORRO BAY POWER PLANT | DYNERGY MORRO BAY LLC | SAN LUIS OBISPO | CA | 93443 | USA | STEVE GOSCHKE |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SCC 2005-01 | 4911 | 221112 | 110001000000 | 06/23/2005 &nbsp;ACT | 09/25/2008 &nbsp;ACT | 2012-11-09 | 2014-01-14 | B | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | POWER PLANT | PSD permit is for a modernization Project which consists of replacing four existing 1950/1960-era fossil-fuel-fired electric utility steam generators (1002 megawatt [MW] total) with two combined cycle gas turbine block units. Each new block unit will be capable of producing 600 MW. Each new block unit will consist of two GE Frame 7, Model PG7241, 180 MW gas-fired turbines, two HRSGs with duct burners, and one 240 MW steam turbine. The modernization project also includes, in part, demolition of the existing fuel oil tank farm, demolition of three existing 450-foot exhaust stacks, installation of two new 145-foot exhaust stacks, and refurbishment of the sea-water cooling intake structure. | COMBUSTION TURBINE GENERATOR | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | USE PIPELINE QUALITY NATURAL GAS, OPERATE DUCT BURNERS NO MORE THAN 4000 HRS PER YEAR (12-MONTH ROLLING AVG BASIS) | 11 | LB/H | 6-HR ROLLING AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 13.3 | LB/H | 6-HR ROLLING AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N |  | A third emission limit was entered into the Standard Limit field, however, this pollutant, TPM, is not listed in Appendix E of the RBLC User's Manual, Volume 3. Below is the 3rd emission limit: 203.2 T/YR, 12-MONTH ROLLING AVG. PSD PERMIT ONLY FOR PM/PM10. FACILITY NET OUT OF PSD REVIEW FOR NOX, CO, AND VOC. SOX EMISSION LESS THAN SIGNIFICANT AND NOT SUBJECT TO PSD REVIEW.
CT-0151 | KLEEN ENERGY SYSTEMS, LLC | KLEEN ENERGY SYSTEMS, LLC | MIDDLESEX | CT | 6457 | USA | JASON FARREN | 8607042515 |  | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | CASE CONTACT: MR. LOUIS CORSINO, CT DEP, 79 ELM STREET, HARTFORD, CT 06106 | 104-0131 AND 104-0133 | 4911 | 221210 | UNKNOWN | &nbsp; | 02/25/2008 &nbsp;ACT | 2008-04-24 | 2012-04-10 | A |  | 580 MW NOMINAL (620 MW PEAK) BASE LOAD NATURAL GAS FIRED POWER PLANT WITH NO.2 OIL BACKUP. TWO SIEMENS SGT6-5000F COMBUSTION TURBINE TRAINS WITH HRSG AND NATURAL GAS DUCT BURNER. | FACILITY CONSISTS OF TWO TURBINE TRAINS. EACH TURBINE TRAIN CONSISTS OF A SIEMENS SGT6-5000F COMBUSTION TURBINE WITH NATURAL GAS AS PRIMARY AND OIL AS BACKUP, A 445 MMBTU/HR NATURAL GAS ONLY DUCT BURNER AND AN HRSG. CONTROL EQUIPMENT ON EACH TRAIN CONSISTS OF AN SCR AND CO CATALYST. EMISSION RATES PRESENTED WITHIN ARE FOR EACH TURINE TRAIN INDIVIDUALLY. SHORT -TERM EMISSION RATES ARE REPRESENTATIVE OF STEADY STATE OPERATION. TRANSIENT OPERATION (START-UP, SHUT DOWN, ETC) SHORT-TERM EMISSION RATES ARE INCLUDED IN THE PERMITS FACILITY-WIDE EMISSIONS ARE REPRESENTATIVE OF EMISSIONS FROM EACH TURBINE TRAIN ONLY AND INCLUDE EMISSIONS FROM TRANSIENT OPERATIONS. | SIEMENS SGT6-5000F COMBUSTION TURBINE #1 AND #2 (NATURAL GAS FIRED) WITH 445 MMBTU/HR NATURAL GAS DUCT BURNER | 15.21 | NATURAL GAS | 2.1 | MMCF/H | THROUGHPUT IS FOR TURBINE ONLY WHEN FIRING NATURAL GAS TURBINE: 2136 MMBTU/HR (2.095 MMCF/HR) DUCT BURNER: 445 MMBTU/HR (0.436 MMCF/HR) EMISSION RATES ARE FOR EACH COMBUSTION TURBINE FIRING NATURAL GAS, NOT COMBINED. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 11 | LB/H | W/OUT DUCT BURNER | BACT-PSD | OPERATING PERMIT | U | 0 | Y | 15.2 | LB/H | W/ DUCT BURNER | 0 |  |  | 0 | 0 | N |  | EMISSIONS ARE FOR EACH TURBINE TRAIN, NOT COMBINED.
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.21 | natural gas | 10 | M TONNES/YR | Four GE Frame 7E gas turbines for refrigeration and compression at the site | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 11.07 | LB/H |  | BACT-PSD |  | N | 0 | U | 42.15 | T/YR |  | 0 |  |  | 0 | 0 | N |  | Dry low NOx burners, good combustion practices, pipeline quality sweet natural gas fuel
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.21 | natural gas | 10 | M TONNES/YR | Four GE Frame 7E gas turbines for refrigeration and compression at the site | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 11.07 | LB/H |  | BACT-PSD |  | N | 0 | U | 42.15 | T/YR |  | 0 |  |  | 0 | 0 | N |  | Dry low NOx burners, good combustion practices, pipeline quality sweet natural gas fuel
TX-0590 | KING POWER STATION | PONDERA CAPITAL MANAGEMENT GP INC | HARRIS | TX | 77044 | USA | MARK CHRISOS | (781) 993-3036 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Katherine Stinchcomb (512) 239-1583 katherine.stinchcomb@tceq.texas.gov | PSDTX1125 | 4911 | 221119 | 110040000000 | 03/07/2008 &nbsp;ACT | 08/05/2010 &nbsp;ACT | 2011-08-26 | 2011-09-14 | A |  | Four combined-cycle natural gas-fired combustion turbines | State permit number 84289 Nonattainment permit number N75 | Turbine | 15.21 | natural gas | 1350 | MW | The plant will be designed to generate 1,350 nominal megawatts of power. There are two configuration scenarios: either four Siemens SGT6-5000F CTGs in combined-cycle mode (Scenario A) or four GE Frame 7FA CTGs in combined cycle mode (Scenario B). Scenario B also includes one or two auxiliary boilers. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | use low ash fuel (natural gas or low sulfur diesel as a backup) and good combustion practices | 11.1 | LB/H |  | BACT-PSD |  | N | 0 | U | 19.8 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 represents Scenario A (Siemens turbines) and Emission Limit 2 represents Scenario B (GE turbines)
TX-0590 | KING POWER STATION | PONDERA CAPITAL MANAGEMENT GP INC | HARRIS | TX | 77044 | USA | MARK CHRISOS | (781) 993-3036 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Katherine Stinchcomb (512) 239-1583 katherine.stinchcomb@tceq.texas.gov | PSDTX1125 | 4911 | 221119 | 110040000000 | 03/07/2008 &nbsp;ACT | 08/05/2010 &nbsp;ACT | 2011-08-26 | 2011-09-14 | A |  | Four combined-cycle natural gas-fired combustion turbines | State permit number 84289 Nonattainment permit number N75 | Turbine | 15.21 | natural gas | 1350 | MW | The plant will be designed to generate 1,350 nominal megawatts of power. There are two configuration scenarios: either four Siemens SGT6-5000F CTGs in combined-cycle mode (Scenario A) or four GE Frame 7FA CTGs in combined cycle mode (Scenario B). Scenario B also includes one or two auxiliary boilers. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | use of low ash fuel (natural gas or low sulfur diesel as a backup) | 11.1 | LB/H |  | BACT-PSD |  | U | 0 | U | 19.8 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 represents Scenario A (Siemens turbines) and Emission Limit 2 represents Scenario B (GE turbines).
TX-0590 | KING POWER STATION | PONDERA CAPITAL MANAGEMENT GP INC | HARRIS | TX | 77044 | USA | MARK CHRISOS | (781) 993-3036 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Katherine Stinchcomb (512) 239-1583 katherine.stinchcomb@tceq.texas.gov | PSDTX1125 | 4911 | 221119 | 110040000000 | 03/07/2008 &nbsp;ACT | 08/05/2010 &nbsp;ACT | 2011-08-26 | 2011-09-14 | A |  | Four combined-cycle natural gas-fired combustion turbines | State permit number 84289 Nonattainment permit number N75 | Turbine | 15.21 | natural gas | 1350 | MW | The plant will be designed to generate 1,350 nominal megawatts of power. There are two configuration scenarios: either four Siemens SGT6-5000F CTGs in combined-cycle mode (Scenario A) or four GE Frame 7FA CTGs in combined cycle mode (Scenario B). Scenario B also includes one or two auxiliary boilers. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | use of low ash fuel (natural gas or low sulfur diesel as a backup) | 11.1 | LB/H |  | BACT-PSD |  | U | 0 | U | 19.8 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 represents Scenario A (Siemens turbines) and Emission Limit 2 represents Scenario B (GE turbines).
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110065000000 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Mitsubishi, without duct burners | 15.21 | Natural Gas | 47917 | MMSCF/rolling 12-MO | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process without duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | clean burning fuel, only natural gas | 11.3 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 44.2 | T/YR | PER ROLLING 12-MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for both PM10 and PM2.5 together. Additional limit: 0.00384 LB PM/PM2.5 per MMBtu of heat input. T/YR limit is for 2 turbines.
*VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404-001 | 4911 | 221112 | 110055000000 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2016-07-07 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | COMBUSTION TURBINE GENERATORS, (3) | 15.21 | Natural Gas | 3442 | MMBTU/H | Three (3) Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners (natural gas-fired). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur/carbon fuel and good combustion practices. | 11.3586 | LB/H | 3 H AVG/WITHOUT DUCT BURNING | BACT-PSD | NSPS | U | 0 | U | 9.7 | LB/H | 3 H AVG/WITHOUT DUCT BURNING | 0 |  |  | 0 | 0 | N
*VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404-001 | 4911 | 221112 | 110055000000 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2016-07-07 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | COMBUSTION TURBINE GENERATORS, (3) | 15.21 | Natural Gas | 3442 | MMBTU/H | Three (3) Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners (natural gas-fired). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur/carbon fuel and good combustion practices. | 11.3586 | LB/H | 3 H AVG/WITHOUT DUCT BURNING | BACT-PSD | NSPS | U | 0 | U | 9.7 | LB/H | 3 H AVG/WITHOUT DUCT BURNING | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas without Duct Burner | 15.21 | Natural Gas | 8040 | H/YR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 11.7 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY STACK TESTING
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas without Duct Burner | 15.21 | Natural Gas | 8040 | H/YR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 11.7 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY STACK TESTING
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110044000000 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 11.78 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110044000000 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 11.78 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110044000000 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total (TPM) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 11.78 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110044000000 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 180 | MW |  | Particulate matter, total (TPM) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 11.78 | LB/H | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110041000000 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA Method 5 and 202, or CTM 039 or CTM 040 | (Particulate Matter (PM)) | PM | P | PUC QUALITY NATURAL GAS | 12 | LB/H | PUC QUALITY NATURAL GAS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110041000000 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | Natural Gas | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA Method 5 and 202, or CTM 039 or CTM 040 | (Particulate Matter (PM)) | PM | P | PUC QUALITY NATURAL GAS | 12 | LB/H | 12-MONTH ROLLING AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110041000000 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | PUC QUALITY NATURAL GAS | 12 | LB/H | 12-MONTH ROLLING AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110041000000 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (NORMAL OPERATION, NO DUCT BURNING) | 15.21 | Natural Gas | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | PUC QUALITY NATURAL GAS | 12 | LB/H | 12-MONTH ROLLING AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110039000000 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (COLD STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 12 | LB/H | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 48.8 | LB/EVENT | COLD START UP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF COLD STARTUPS NOT TO EXCEED 270 MINUTES; 2) COLD STARTUP MEANS STARTUP WHEN THE COMBUSTION TURBINE HAS NOT BEEN IN OPERATION DURING THE PRECEDING 72 HOURS
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110039000000 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (WARM STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 12 | LB/H | WARM STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 30.8 | LB/EVENT | WARM STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF WARM STARTUPS NOT TO EXCEED 180 MINUTES; 2) WARM STARTUP MEANS A STARTUP THAT IS NOT A HOT OR COLD STARTUP
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110039000000 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (HOT STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 12 | LB/H | HOT STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 12.8 | LB/EVENT | HOT STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF HOT STARTUPS NOT TO EXCEED 90 MINUTES; 2) HOT STARTUP MEANS A STARTUP WHEN THE COMBUSTION TURBINE HAS BEEN IN OPERATION DURING THE PRECEDING 8 HOURS
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110039000000 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (COLD STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 12 | LB/H | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 48 | LB/EVENT | COLD STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF COLD STARTUPS NOT TO EXCEED 270 MINUTES; 2) COLD STARTUP MEANS STARTUP WHEN THE COMBUSTION TURBINE HAS NOT BEEN IN OPERATION DURING THE PRECEDING 72 HOURS
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110039000000 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (WARM STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 12 | LB/H | WARM STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 30.8 | LB/EVENT | WARM STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF WARM STARTUPS NOT TO EXCEED 180 MINUTES; 2) WARM STARTUP MEANS A STARTUP THAT IS NOT A HOT OR COLD STARTUP
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110039000000 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (HOT STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 12 | LB/H | HOT STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 12.8 | LB/EVENT | HOT STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF HOT STARTUPS NOT TO EXCEED 90 MINUTES; 2) HOT STARTUP MEANS A STARTUP WHEN THE COMBUSTION TURBINE HAS BEEN IN OPERATION DURING THE PRECEDING 8 HOURS
LA-0308 | MORGAN CITY POWER PLANT | LOUISIANA ENERGY AND POWER AUTHORITY (LEPA) | ST. MARY | LA | 70380 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-767 | 4911 | 221112 | Not Found | 09/24/2012 &nbsp;ACT | 09/26/2013 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  |  |  | Combustion Turbine with SCR/HRSG | 15.21 | Natural Gas | 607.1 | MMBTU/hr |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean burning fuel (natural gas) | 12.03 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 52.68 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit: PM2.5 = 0.0197 lb/MMBTU (12 month average)
LA-0308 | MORGAN CITY POWER PLANT | LOUISIANA ENERGY AND POWER AUTHORITY (LEPA) | ST. MARY | LA | 70380 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-767 | 4911 | 221112 | Not Found | 09/24/2012 &nbsp;ACT | 09/26/2013 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  |  |  | Combustion Turbine with SCR/HRSG | 15.21 | Natural Gas | 607.1 | MMBTU/hr |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean burning fuels (natural gas) | 12.03 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 52.68 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit: PM10 = 0.0197 lb/MMBTU (12 month average)
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110001000000 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITHOUT DUCT BURNER - GENERAL ELECTRIC | 15.21 | Natural Gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each General Electric combustion turbine will be 2,312 MMBtu/hr(HHV) | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of Natural Gas as a clean burning fuel | 12.7 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | BACT-PSD | OPERATING PERMIT | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion air filters, efficient combustion control, low sulfur natural gas fuel. | 12.769 | LB/H | TEST PROTOCOL (3 1-H TESTS IF POSSIBLE) | BACT-PSD |  | N | 90 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit applies to each CTG/HRSG. Limit applies at all times and includes duct burner operation.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 12.769 | LB/H | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 0.007 lb/MMBTU for each CTGHRSG. Test protocol will specify averaging time. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2013. Pulse Jet Fabric Filter Baghouse: minimum of $62,842 per ton. Mechanical Shaker Fabric Filter Baghouse: minimum of $53,684 per ton. Reverse-Air Fabric Filter Bathouse: minimum of $77,328 per ton. Dry ESP (Wire-Plate Type): minimum of $44,525 per ton. Dry ESP (Wire-Pipe Type): minimum of $66,472 per ton. Wet ESP (Wire-Plate Type): minimum of $77,761 per ton. Wet ESP (Wire-Pipe Type): minimum of $110,364 per ton. Venturi Scrubber: minimum of $52,773 per ton.
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110001000000 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | Combined Cycle Combustion Turbine -Siemens turbine without Duct Burner | 15.21 | Natural gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each Siemens combustion turbine will be 2,356 MMBtu/hr(HHV) | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 13 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/o Duct Firing | 15.21 | Natural Gas | 2969 | MMBtu/hr | Throughput is for turbine only | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 13.0636 | LB/H |  | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
PA-0278 | MOXIE LIBERTY LLC/ASYLUM POWER PL T | MOXIE ENERGY LLC | BRADFORD COUNTY | PA |  | USA | KENT J MORTON | (571) 594 - 0150 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MUHAMMAD Q. ZAMAN, ENVIRONMENTAL PROGRAM MANAGER, NORTHCENTRAL REGION | 08Â·00045A | 491 | 221112 | 45-2015223-1 | 09/26/2011 &nbsp;ACT | 10/10/2012 &nbsp;ACT | 2012-12-03 | 2015-04-03 | A |  |  | The project consists of two identical 1 x 1 power blocks, and each block includes a combustion gas turbine and a steam turbine. Each combined-cycle process will also include a heat recovery steam generator and supplemental duct burners. Additionally, one diesel-fired emergency generator, one diesel-fired fire water pump, two diesel fuel storage tanks, two lube oil storage tanks, and one aqueous ammonia storage tank were proposed to be constructed and operated. Each combined-cycle process will be rated at 468 MW or less. | Combined-cycle Turbines (2) - Natural gas fired | 15.21 | Natural Gas | 3277 | MMBTU/H | Two combine cycle Turbines, each with a combustion turbine and heat recovery steam generator with duct burner. Each combined-cycle process will be rated at 468 MW or less. The heat input rating of each combustion gas turbine is 2890 MMBtu/hr (HHV) or less, and the heat input rating of each supplemental duct burner is equal to 387 MMBtu/hr (HHV) or less. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Using fuel with little or no ash and sulfur content. | 13.108 | LB/H | FOR 468 MW POWERBLOCK | BACT-PSD |  | U | 0 | U | 0.0057 | LB/MMBTU | FOR 454 MW POWERBLOCK | 0 |  |  | 0 | 0 | N |  | FUel sulfur content of 0.4 grain/100scf
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/Duct Firing | 15.21 | Natural Gas | 2639 | MMBtu/hr | Duct burner MRC is 946 MMbtu/hr | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 13.195 | LB/H |  | BACT-PSD | OPERATING PERMIT , SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110065000000 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG with duct burner NG only | 15.21 | Natural Gas | 3338 | MMBtu/hr | Emission limits are for each turbine operating with duct burner and do not include startup/shutdown emissions. Tons per year limits is a cumulative value for all three CCCT. CEMS for NOx, CO, and O2. Each CCCT and duct burner have 5 operational scenarios: 1 CCCT with duct burner fired - fueled by NG only 2 CCCT with duct burner fired - fueled by NG blend with ethane 3 CCCT without duct burner fired - fueled by NG only 4 CCCT without duct burner fired - fueled by NG blend with ethane 5 CCCT without duct burner fired - fueled by ULSD (Limited to emergency use only) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuel, good combustion practices | 13.195 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 131.5 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N |  | lb/MMBtu limit is for each turbine and duct burner, TPY is a cumulative total
NJ-0080 | HESS NEWARK ENERGY CENTER | HESS NEWARK ENERGY CENTER, LLC | ESSEX | NJ | 7105 | USA | PETER HAID | (774) 750-7088 | PHAID@HESS.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Supervisor: Yogesh Doshi - yogesh.doshi@dep.state.nj.us Phone: 609-633-7249 Permit Evaluator: Michael Hogan - michael.hogan@dep.state.nj.us. Phone: (609)-633-1124 | 08857/BOP110001 | 4911 | 221112 | 110045000000 | 12/10/2011 &nbsp;ACT | 11/01/2012 &nbsp;ACT | 2013-04-04 | 2018-04-17 | A |  | Combined Cycle Electric Generating Facility HESS Newark Energy Center (Hess-NEC), proposed at City of Newark (Essex County), New Jersey, would be a new, highly efficient, 655 MW combined-cycle power generating facility. Hess-NEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,320 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, a 12-cell mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Facility-wide Greenhouse Gas (GHG) emissions as CO2e emissions = 2,003,654 tpy | Combined cylce turbine with duct burner | 15.21 | natural gas | 39463 | mmcubic ft/year* | * Annual throughput is for 2 turbines, 2 duct burners and 1 auxiliary boiler | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Other - EPA/OAR method 201A and 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 13.2 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110065000000 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Siemens, without duct burners | 15.21 | Natural Gas | 515600 | MMSCF/rolling 12-months | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process without duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | clean burning fuel, only natural gas | 13.3 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 61.3 | T/YR | PER ROLLING 12-MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for both PM10 and PM2.5 together. Additional limit: 0.0047 lb PM10/PM2.5 per MMBtu of heat input. T/YR limit is for 2 turbines.
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 13.422 | LB/H | EACH CTG; TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0.012 | LB/MMBTU | EACH CTG; TEST PROTOCOL | 0 |  |  | 0 | 0 | N | 2012 | Cost Effectiveness Information: No additional costs were calculated for PM10 or PM2.5 since additional costs to remove condensable particulate would only inflate the costs calculated for PM. Therefore, the costs for PM were considered to be conservative. Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet Scrubber = $16,663/ton
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 13.422 | LB/H | EACH CTG; TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 11432 | 0 | N | 2012 | Cost effectiveness information: Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet scrubber = $16,663/ton
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000000000 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 2449 | MMBTU/H | two 315 MW (nominal) GE Energy 7F Series 5 Rapid Response Combined Cycle Combustion Turbines with Duct Burners and 31 MW (estimated) steam turbine generators | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 13.422 | LB/H | 1 HR AVG/DO NOT APPLY DURING SS | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 13 | LB/H | 1 HR AVG/DO NOT APPLY DURING SS | 0 |  |  | 0 | 0 | N |  | PM10(no duct firing): â‰¤0.0071lb/MMBtu, â‰¤8.8 lb/hr during start-ups(â‰¤ 45 minutes): PM/PM10/PM2.5 â‰¤ 6.60 lb per event during shutdowns (â‰¤ 27 minutes): PM/PM10/PM2.5 â‰¤ 3.96 lb per event
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110039000000 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 13.5 | LB/H | STACK TEST | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110039000000 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - SEE POLLUTANT NOTES | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS | 13.5 | LB/H | STACK TEST | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | PM10 TEST METHOD: USE EPA METHODS 5 & 202, OR CTM-039 OR CTM-040 IN LIEU OF METHOD 202
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110065000000 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Siemens, with duct burners | 15.21 | Natural Gas | 51560 | MMSCF/rolling 12-MO | Two Siemens 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process with duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | clean burning fuel, only natural gas | 14 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 61.3 | T/YR | PER ROLLING 12-MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for both PM10 and PM2.5 together. Additional limit: 0.0055 lb PM10/PM2.5 per MMBtu of heat input. T/YR limit is for 2 turbines.
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110001000000 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITH DUCT BURNER - SIEMENS | 15.21 | Natural Gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two Siemens turbines and two associated duct burners) The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 14 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110001000000 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | COMBINED CYCLE COMBUSTION TURBINE WITH DUCT BURNER - GENERAL ELECTRIC | 15.21 | Natural gas | 33691 | MMCF/YR | Natural Gas Usage <= 33,691 MMft^3/yr per 365 consecutive day period, rolling one day basis (per two turbines and two duct burners) The heat input rate of each General Electric combustion each turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 MMBtu/hr duct burner | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas only as a clean burning fuel | 14.6 | LB/H | AVERAGE OF THREE ONE HOUR TESTS | BACT-PSD | OPERATING PERMIT | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This project not subject to BACT for PM<2.5 microns.
OH-0356 | DUKE ENERGY HANGING ROCK ENERGY | DUKE ENERGY HANGING ROCK, LLC | LAWRENCE | OH | 28207 | USA | ANDREW ROEBEL | 513-287-2356 | ANDREW.ROEBEL@DUKE-ENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110487 | 4911 | 221112 | 110013000000 | 07/17/2012 &nbsp;ACT | 12/18/2012 &nbsp;ACT | 2013-10-01 | 2016-05-04 | C |  | Four Natural Gas Fired Combustion Turbines, with Duct Burners; Combined Cycle, each 172 MW | This is a modification of RBLC OH-0252 to remove operating hour restrictions on duct burners, with changes to hourly limits without increasing the annual emission limitations. Original PTI # was 07-00503 | Turbines (4) (model GE 7FA) Duct Burners Off | 15.21 | NATURAL GAS | 172 | MW | Four GE 7FA combined cycle turbines, dry low NOx burners and selective catalytic reduction. These limits are for each of the 4 turbines individually, while operating with the duct burners off. This permit is a modification to RBLC OH-0252 to remove hourly restrictions on duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Burning natural gas in an efficient combustion turbine | 15 | LB/H |  | BACT-PSD | NSPS , SIP | U | 0 | N | 87.2 | T/YR | PER ROLLING 12 MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for each individual turbine. Subject to Part 60 Subparts Da. If required test Methods 1 through 5 and Method 202.
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110063000000 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITHOUT DUCT FIRING | 15.21 | NATURAL GAS | 270 | MW |  | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND EFFICIENT TURBINE DESIGN | 15 | LB/H | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063000000 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burners. | Particulate matter, filterable (FPM) | Other - NJ TEST METHOD | (Particulate Matter (PM)) | PM | P | Use of Natural gas a clean burning fuel | 15.1 | LB/H | AVERAGE OF THREE STACK TEST RUNS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0.0048 | LB/MMBTU | AVERAGE OF THREE STACK TEST RUNS | 0 |  |  | 0 | 0 | N
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000000000 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 2449 | MMBTU/H | two 315 MW (nominal) GE Energy 7F Series 5 Rapid Response Combined Cycle Combustion Turbines with Duct Burners and 31 MW (estimated) steam turbine generators | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 15.1838 | LB/H | 1 HR AVG/DO NOT APPLY DURING SS | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 13 | LB/H | 1 HR AVG/DO NOT APPLY DURING SS | 0 |  |  | 0 | 0 | N |  | PM 2.5 (no duct firing): â‰¤0.0071lb/MMBtu, â‰¤8.8 lb/hr during start-ups (â‰¤ 45 minutes): PM/PM10/PM2.5 â‰¤ 6.60 lb per event during shutdowns (â‰¤ 27 minutes): PM/PM10/PM2.5 â‰¤ 3.96 lb per event
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064000000 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine With Duct Burner | 15.21 | Natural Gas | 3727 | MMBtu/hr | DLN burner, SCR, Oxidation Catalyst and shall maintain and operate the sources and associated air cleaning devices in accordance with good engineering practice. shall install, certify, maintain and operate continuous emission monitoring systems (CEMS) for nitrogen oxides, carbon monoxide, carbon dioxide, and ammonia emissions on the exhaust of each combined-cycle powerblock. Emissions limits are for each combustion turbine/duct burner block. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 15.1838 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 13.9 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 58 tpy 12-month rolling basis
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027000000 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Combustion Turbine | 15.21 | natural gas | 87 | MW | The exhaust heat from the turbine will be used to heat a heating medium which is used to regenerate rich amine from the acid gas removal system. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 15.22 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0298 | FUTURE POWER PA/GOOD SPRINGS NGCC FACILITY | FUTURE POWER PA INC | SCHUYLKILL | PA | 17980 | USA | JAMES PALUMBO | 570-342-5200 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MARK J. WEJKSZNER NORTHEAST REGION AIR PROGRAM MANAGER 2 Public Square Wilkes-Barre, PA 18711 570-826-2357 | 54-00082A | 4911 | 221112 | 26-3703407-1 | 05/03/2013 &nbsp;ACT | 03/04/2014 &nbsp;ACT | 2014-04-17 | 2018-03-23 | A |  | Natural gas-fired combined-cycle electric generation facility that is designed to generate up to 346 MW nominal, using a combustion turbine generator and a heat recovery steam generator that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. The Turbine is rated at 2,267 MMBTU/hr HHV (2,042 MMBTU/hr LHV). The Duct burner is rated at 134.3 MMBTU/hr HHV (120 MMBTU/hr LHV). The proposed project will also include a diesel engine-driven emergency generator; a diesel engine-driven firewater pump; a multi-cell evaporative cooling tower; and associated emission control systems, tanks, and other plant equipment. |  | Turbine, COMBINED CYCLE UNIT (Siemens 5000) | 15.21 | Natural Gas | 2267 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 15.6 | LB/H | WITH DUCT BURNER | BACT-PSD | NSPS | U | 0 | U | 58.7 | T/YR | BASED ON A 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N
TX-0767 | LON C. HILL POWER STATION | LON C. HILL, L.P. | NUECES | TX |  | USA | MATTHEW LINDSEY | 713-358-9734 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem, 512-239-1310, Tzvi.Shalem@tceq.texas.gov | 114911 AND PSDTX1380 | 4911 | 221122 | 110001000000 | 07/15/2015 &nbsp;ACT | 10/02/2015 &nbsp;ACT | 2015-09-23 | 2016-07-06 | A |  | The Lon C. Hill Power Station (LCHP) will include two natural gas-fired combined cycle combustion turbines (CTGs) equipped with dry low NOx burners (DLNs), heat recovery steam generators (HRSG), and natural gas-fired duct burners (DBs). Ancillary equipment includes evaporative coolers or inlet chillers, a single steam turbine (ST), auxiliary boiler, emergency generator, firewater pump, two cooling towers, oil water separator, degreaser, two diesel storage tanks, gasoline storage tank, selective catalytic reduction (SCR) and ammonia (NH3) handling systems including an NH3 storage tank, and two water tanks. The LCHP will be a 2x1 combined cycle power plant consisting of two CTGs, two HRSGs and one ST. The CTGs and ST will be one of two options: two Siemens SCC6-5000 CTGs and a SST6-5000 ST, or two General Electric 7FA CTGs and a D-11 ST. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 195 | MW | Two power configuration options authorized Siemens â€“ 240 MW + 250 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 195 MW + 670 MMBtu/hr duct burner | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and use of pipeline quality natural gas | 16 | LB/HR |  | BACT-PSD | NSPS | N | 0 | U | 109.5 | TPY |  | 0 |  |  | 0 | 0 | N |  | Lbs/hr limit based on one stack and TPY is based on both turbines
TX-0767 | LON C. HILL POWER STATION | LON C. HILL, L.P. | NUECES | TX |  | USA | MATTHEW LINDSEY | 713-358-9734 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem, 512-239-1310, Tzvi.Shalem@tceq.texas.gov | 114911 AND PSDTX1380 | 4911 | 221122 | 110001000000 | 07/15/2015 &nbsp;ACT | 10/02/2015 &nbsp;ACT | 2015-09-23 | 2016-07-06 | A |  | The Lon C. Hill Power Station (LCHP) will include two natural gas-fired combined cycle combustion turbines (CTGs) equipped with dry low NOx burners (DLNs), heat recovery steam generators (HRSG), and natural gas-fired duct burners (DBs). Ancillary equipment includes evaporative coolers or inlet chillers, a single steam turbine (ST), auxiliary boiler, emergency generator, firewater pump, two cooling towers, oil water separator, degreaser, two diesel storage tanks, gasoline storage tank, selective catalytic reduction (SCR) and ammonia (NH3) handling systems including an NH3 storage tank, and two water tanks. The LCHP will be a 2x1 combined cycle power plant consisting of two CTGs, two HRSGs and one ST. The CTGs and ST will be one of two options: two Siemens SCC6-5000 CTGs and a SST6-5000 ST, or two General Electric 7FA CTGs and a D-11 ST. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 195 | MW | Two power configuration options authorized Siemens â€“ 240 MW + 250 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 195 MW + 670 MMBtu/hr duct burner | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and use of pipeline quality natural gas | 16 | LB/HR |  | BACT-PSD | NSPS | N | 0 | U | 109.5 | TPY |  | 0 |  |  | 0 | 0 | N
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | MR. RANDY THOMPSON | (615) 532-6825 | randall.thompson@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000000000 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Natural Gas-Fired Combustion Turbine with HRSG | 15.21 | Natural Gas | 1339 | MMBtu/hr | Turbine throughput is 1019.7 MMBtu/hr when burning natural gas and 1083.7 MMBtu/hr when burning No. 2 oil. Duct burner throughput is 319.3 MMBtu/hr. Duct burner firing will occur during natural gas combustion only. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion design and practices | 16.69 | LB/H |  | BACT-PSD |  | N | 0 | U | 0.015 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N |  | Limit #1 is for gas combustion, limit #2 is for No. 2 oil combustion
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110065000000 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG with duct burner NG only | 15.21 | Natural Gas | 3338 | MMBtu/hr | Emission limits are for each turbine operating with duct burner and do not include startup/shutdown emissions. Tons per year limits is a cumulative value for all three CCCT. CEMS for NOx, CO, and O2. Each CCCT and duct burner have 5 operational scenarios: 1 CCCT with duct burner fired - fueled by NG only 2 CCCT with duct burner fired - fueled by NG blend with ethane 3 CCCT without duct burner fired - fueled by NG only 4 CCCT without duct burner fired - fueled by NG blend with ethane 5 CCCT without duct burner fired - fueled by ULSD (Limited to emergency use only) | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuel, good combustion practices | 16.69 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 131.5 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N |  | lb/MMBtu limit is for each turbine and duct burner, TPY is a cumulative total
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110065000000 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG with duct burner NG only | 15.21 | Natural Gas | 3338 | MMBtu/hr | Emission limits are for each turbine operating with duct burner and do not include startup/shutdown emissions. Tons per year limits is a cumulative value for all three CCCT. CEMS for NOx, CO, and O2. Each CCCT and duct burner have 5 operational scenarios: 1 CCCT with duct burner fired - fueled by NG only 2 CCCT with duct burner fired - fueled by NG blend with ethane 3 CCCT without duct burner fired - fueled by NG only 4 CCCT without duct burner fired - fueled by NG blend with ethane 5 CCCT without duct burner fired - fueled by ULSD (Limited to emergency use only) | Particulate matter, total (TPM) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Low sulfur fuel, good combustion practicies | 16.69 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 131.5 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N |  | lb/MMBtu limit is for each turbine and duct burner, TPY is a cumulative total
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas, combustion inlet air filter. | 17.0742 | LB/H |  | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Fabric Filter Control: over $260,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5). Electrostatic Precipitator (ESP): over $188,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5). Wet ESP: over $165,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5). Venturi Scrubber: over $112,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5).
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas, combustion inlet air filter. | 17.0742 | LB/H |  | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Fabric filter control: over $260,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5). Electrostatic precipitator (ESP): OVER $188,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5). Wet ESP: over $165,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5). Venturi Scrubber: over $112,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5).
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1B | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean burning fuel (natural gas) | 17.52 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 73.35 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.008 LB/MMBTU (3-hour average)
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1A | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean burning fuels (natural gas) | 17.52 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 73.35 | T/YR |  | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.008 LB/MMBTU (3-Hour Average)
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1B | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean burning fuels (natural gas) | 17.52 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 73.35 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.0082 LB/MMBTU (3-hour average)
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1A | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and clean burning fuels (natural gas) | 17.52 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 73.35 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.008 LB/MMBTU (3-Hour Average)
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST. HEAT RATE LIMITED TO 6,793 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR MATTAWOMAN TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS MATTAWOMAN PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE QUALITY NATURAL GAS EXCLUSIVELY AND GOOD COMBUSTION PRACTICES | 17.9 | LB/H | W/OUT DUCT FIRING, AVG. OF 3 STACK TESTS | BACT-PSD |  |  | 0 |  | 27.7 | LB/H | WITH DUCT FIRING, AVG. OF 3 STACK TESTS | 0 |  |  | 0 | 0 | N |  | AT ALL TIMES
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | 2 COMBINED-CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 286 | MW | TWO SIEMENS H-CLASS (SGT-8000H VERSION 1.4-OPTIMIZED) COMBINED CYCLE COMBUSTION TURBINES (CTS) WITH A NOMINAL GENERATING CAPACITY OF 286 MW (EACH), COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX BURNERS, SCR, OXIDATION CATALYST. HEAT RATE LIMITED TO 6,793 BTU/KWH (NET) AT ALL TIMES WHEN THE CTS/HRSGS ARE OPERATING (LHV). INITIAL COMPLIANCE WITH THE HEAT RATE LIMITATION SHALL BE DEMONSTRATED USING ASME PTC-46 TEST METHOD. ANNUAL THERMAL EFFICIENCY TEST CONDUCTED ACCORDING TO ASME PTC-46, OR ANOTHER METHODOLOGY APPROVED BY MDE-ARMA, AND COMPARE RESULTS TO DESIGN THERMAL EFFICIENCY VALUE. AN EXCEEDANCE OF THE HEAT RATE LIMIT IS NOT CONSIDERED A VIOLATION OF THIS PERMIT, BUT TRIGGERS A REQUIREMENT FOR MATTAWOMAN TO SUBMIT A MAINTENANCE PLAN TO MDE-ARMA WHICH SPECIFIES THE ACTIONS MATTAWOMAN PLANS TO TAKE IN ORDER TO ACHIEVE THE HEAT RATE LIMIT. THE PLAN SHALL INCLUDE A TIMEFRAME THAT THE HEAT RATE LIMIT WILL BE MET NOT TO EXCEED 60 DAYS UNLESS AGREED TO BY MDE-ARMA. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE QUALITY NATURAL GAS EXCLUSIVELY AND GOOD COMBUSTION PRACTICES. | 17.9 | LB/H | W/OUT DUCT FIRING, AVG. OF 3 STACK TESTS | BACT-PSD |  |  | 0 |  | 27.7 | LB/H | WITH DUCT FIRING, AVG. OF 3 STACK TESTS | 0 |  |  | 0 | 0 | N |  | AT ALL TIMES
TX-0620 | ES JOSLIN POWER PLANT | CALHOUN PORT AUTHORITY | CALHOUN | TX |  | USA | CHARLES HAUSMANN | 361-987-2813 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1256 | 4911 | 221112 | 110002000000 | 05/27/2011 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2012-11-14 | 2013-09-25 | B |  | Three gas-fired combined cycle turbine generators, including a steam turbine generator, to replace the existing steam boiler/turbine generator. | 96336 | Combined cycle gas turbine | 15.21 | natural gas | 195 | MW | The three combustion turbine generators (CTG) will be the General Electric 7FA, each with a maximum base-load electric power output of approximately 195 megawatts (MW). The steam turbine is rated at approximately 235 MW. This project also includes the installation of two emergency generators, one fire water pump, and auxiliary equipment. No duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion and natural gas as fuel | 18 | LB/H | PER TURBINE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0620 | ES JOSLIN POWER PLANT | CALHOUN PORT AUTHORITY | CALHOUN | TX |  | USA | CHARLES HAUSMANN | 361-987-2813 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1256 | 4911 | 221112 | 110002000000 | 05/27/2011 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2012-11-14 | 2013-09-25 | B |  | Three gas-fired combined cycle turbine generators, including a steam turbine generator, to replace the existing steam boiler/turbine generator. | 96336 | Combined cycle gas turbine | 15.21 | natural gas | 195 | MW | The three combustion turbine generators (CTG) will be the General Electric 7FA, each with a maximum base-load electric power output of approximately 195 megawatts (MW). The steam turbine is rated at approximately 235 MW. This project also includes the installation of two emergency generators, one fire water pump, and auxiliary equipment. No duct burners. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion and natural gas as fuel | 18 | LB/H | PER TURBINE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110055000000 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICE AND FUEL SPECIFICATION | 18 | LB/H | 3 HOURS | BACT-PSD |  |  | 0 |  | 0.0078 | LB/MMBTU | 3 HOURS | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: 15 LBS/HR FOURTH LIMIT: 0.0092 LBS/MMBTU LIMITS ONE AND TWO ARE USED WITH DUCT FIRING. LIMITS THREE AND FOUR ARE USED WITHOUT DUCT FIRING.
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110055000000 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD CUMBUSTION PRACTICE AND FUEL SPECIFICATION | 18 | LB/H | 3 HOURS | BACT-PSD |  |  | 0 |  | 0.0078 | LB/MMBTU | 3 HOURS | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: 15 LBS/HR FOURTH LIMIT: 0.0092 LBS/MMBTU LIMITS ONE AND TWO ARE USED WITH DUCT FIRING. LIMITIS THREE AND FOUR ARE USED WITHOUT DUCT FIRING.
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110055000000 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD CUMBUSTION PRACTICE AND FUEL SPECIFICATION | 18 | LB/H | 3 HOURS | BACT-PSD |  |  | 0 |  | 0.0078 | LB/MMBTU | 3 HOURS | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: 15 LBS/HR FOURTH LIMIT: 0.0092 LBS/MMBTU LIMITS ONE AND TWO ARE USED WITH DUCT FIRING. LIMITS THREE AND FOUR ARE USED WITHOUT DUCT FIRING.
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110041000000 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA Method 5 and 202, or CTM 039 or CTM 040 | (Particulate Matter (PM)) | PM | P | PUC QUALITY NATURAL GAS | 18 | LB/H | 12-MONTH ROLLING AVG (W/ DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110041000000 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA Method 5 and 202, or CTM 039 or CTM 040 | (Particulate Matter (PM)) | PM | P | PUC QUALITY NATURAL GAS | 18 | LB/H | 12-MONTH ROLLING AVG (W/ DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110041000000 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #2 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | PUC QUALITY NATURAL GAS | 18 | LB/H | 12-MONTH ROLLING AVG (W/ DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110041000000 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | COMBUSTION TURBINE #1 (NORMAL OPERATION, WITH DUCT BURNING) | 15.21 | NATURAL GAS | 154 | MW | 154 MW Combined Cycle Combustion Turbine Generator | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 18 | LB/H | 12-MONTH ROLLING AVG (W/ DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0620 | ES JOSLIN POWER PLANT | CALHOUN PORT AUTHORITY | CALHOUN | TX |  | USA | CHARLES HAUSMANN | 361-987-2813 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1256 | 4911 | 221112 | 110002000000 | 05/27/2011 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2012-11-14 | 2013-09-25 | B |  | Three gas-fired combined cycle turbine generators, including a steam turbine generator, to replace the existing steam boiler/turbine generator. | 96336 | Combined cycle gas turbine | 15.21 | natural gas | 195 | MW | The three combustion turbine generators (CTG) will be the General Electric 7FA, each with a maximum base-load electric power output of approximately 195 megawatts (MW). The steam turbine is rated at approximately 235 MW. This project also includes the installation of two emergency generators, one fire water pump, and auxiliary equipment. No duct burners. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 18 | LB/H | PER TURBINE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2018-06-25 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.02 Turbine | 15.21 | Natural Gas | 3496.2 | mmBtu/hr | Nominal 640 mWe All emission limits steady-state and include 1000 mmBtu/hr Duct Burner in operation Short Term startup and shutdown limits in lb/event given in permit. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Air Filter, Use of Natural Gas, Good Combustion Practices | 18.2 | LB/HR |  | BACT-PSD |  | U | 0 | U | 100.1 | TONS/YEAR |  | 18.2 | LB/HR |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas with Duct Burner | 15.21 | natural gas | 4000 | h/yr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | COMPLIANCE BY STACK TESTING | 18.3 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY STACK TESTING
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | Combined Cycle Combustion Turbine firing Natural Gas with Duct Burner | 15.21 | natural gas | 4000 | h/yr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | COMPLIANCE BY STACK TESTING | 18.3 | LB/H | AV OF THREE ONE H STACK TESTS EVERY 5 YR | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMPLIANCE BY STACK TESTING
NJ-0079 | WOODBRIDGE ENERGY CENTER | CPV SHORE, LLC | MIDDLESEX | NJ | 7095 | USA | MARK TURNER | (415)293-1463 | MTURNER@CPV.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Mr. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS, yogesh.doshi@dep.state.nj.us; phone 609-633-7249 | 18940 - BOP110003 | 4911 | 221112 | 110056000000 | 10/12/2011 &nbsp;ACT | 07/25/2012 &nbsp;ACT | 2012-11-27 | 2018-04-17 | A |  | Woodbridge Energy Center (WEC), proposed at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, would be a new, highly efficient, 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) with a heat input rate of 2,307 MMBtu/hr, that will utilize pipeline natural gas only. Heat recovery steam generators (HRSGs) downstream of the combustion turbines will recover heat from the exhaust gases to generate steam. The HRSGs will be equipped with natural gas-fired duct burners for supplementary firing and will share a single steam turbine generator (STG). Supporting ancillary equipment includes a natural gas fired auxiliary boiler, one small dew point fuel gas heater (fuel gas heater), a mechanical draft cooling tower, an emergency diesel generator and an emergency diesel fire pump. | Other Permitting Information: Facility-Wide Greenhouse Gas (GHG) emissions as CO2e emissions= 2,073,645 tons per year | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural gas | 40297.6 | mmcubic ft/year | Woodbridge Energy Center (WEC), located at Riverside Drive in Woodbridge Township (Middlesex County), New Jersey, 07095, will be a new 700 MW combined-cycle power generating facility. WEC will consist of two General Electric (GE) combustion turbine generators (CTGs) each with a maximum rated heat input of 2,307 million British thermal units per hour (MMBtu/hr), that will utilize pipeline natural gas only, with 2 HRSGs, 2 Duct Burners (each 500 MMbtu/hr). | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Good Combustion Practices and use of Natural gas,a clean burning fuel. | 19.1 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD |  | U | 0 | Y | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Compliance Verified by Stack test in 2016, TPM10 Emission limit 1 was 5.47 LB/H
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110065000000 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND LOW SULFUR FUEL | 19.35 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110065000000 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES, LOW SULFUR FUEL | 19.35 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110070000000 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Combustion turbine with duct burner | 15.21 | Natural gas | 3304.3 | MMBtu/hr | Limits are for each CCCT and yearly limits are for cumulative turbine and duct burner. Duct burner throughput is 637.9 MMBtu/hr. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Exclusive natural gas, high-efficiency inlet air filters and DLN | 19.4954 | LB/H |  | BACT-PSD |  | U | 0 | U | 48.2 | TONS | YEAR | 0 |  |  | 0 | 0 | N
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 19.4954 | LB/H | EACH CTG; TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0.012 | LB/MMBTU | EACH CTG; TEST PROTOCOL | 0 |  |  | 0 | 0 | N | 2012 | No additional costs were calculated for PM10 or PM2.5 since additional costs to remove condensable particulate would only inflate the costs calculated for PM. Therefore, the costs for PM were considered to be conservative. Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton West ESP = $42,780/ton West Scrubber = $16,663/ton
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.8 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit in the table above applies to EACH CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10 which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. Pulse Jet Fabric Filter Baghouse: minimum of $364,528 per ton Mechanical Shaker Fabric Filter Baghouse: minimum of $404,724 per ton Reverse-Air Fabric Filter Baghouse: minimum of $476,689 per ton Dry ESP (Wire-Plate Type): minimum of $478,806 per ton Dry ESP (Wire-Pipe Type): minimum of $303,809 per ton Wet ESP (Wire-Plate Type): minimum of $576,763 per ton Wet ESP (Wire-Pipe Type): minimum of $440,047 per ton Venturi Scrubber: minimum of $1,445,564 per ton
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.8 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit in the table above is for EACH CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. Pulse Jet Fabric Filter Baghouse: minimum of $364,528 per ton Mechanical Shaker Fabric Filter Baghouse: minimum of $404,724 per ton Reverse-Air Fabric Filter Baghouse: minimum of $476,689 per ton Dry ESP (Wire-Plate Type): minimum of $478,806 per ton Dry ESP (Wire-Pipe Type): minimum of $303,809 per ton Wet ESP (Wire-Plate Type): minimum of $576,763 per ton Wet ESP (Wire-Pipe Type): minimum of $440,047 per ton Venturi Scrubber: minimum of $1,445,564 per ton
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 19.888 | LB/H | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 19.9 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N | 2012 | Cost Effectiveness Information: No additonal costs were calculated for PM10 or PM2.5 since additional costs to remove condensable particulate would only inflate the costs calculated for PM. Therefore, the costs for PM were considered to be conservative. Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet scrubber = $16,663/ton
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #1 - combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr | two identical Siemens SGT6-5000F combined cycle turbines without duct firing, each at 2258 mmBtu/hr generating approx. 300 MW each. | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | N |  | 19.888 | LB/H | AVG. OF 3 ONE HOUR TEST RUNS | BACT-PSD |  | U | 0 | U | 77.1 | TON/YR | 12-MONTH ROLLING | 0 |  |  | 0 | 0 | N
OH-0356 | DUKE ENERGY HANGING ROCK ENERGY | DUKE ENERGY HANGING ROCK, LLC | LAWRENCE | OH | 28207 | USA | ANDREW ROEBEL | 513-287-2356 | ANDREW.ROEBEL@DUKE-ENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110487 | 4911 | 221112 | 110013000000 | 07/17/2012 &nbsp;ACT | 12/18/2012 &nbsp;ACT | 2013-10-01 | 2016-05-04 | C |  | Four Natural Gas Fired Combustion Turbines, with Duct Burners; Combined Cycle, each 172 MW | This is a modification of RBLC OH-0252 to remove operating hour restrictions on duct burners, with changes to hourly limits without increasing the annual emission limitations. Original PTI # was 07-00503 | Turbines (4) (model GE 7FA) Duct Burners On | 15.21 | NATURAL GAS | 172 | MW | Four GE 7FA combined cycle turbines, dry low NOx burners and selective catalytic reduction. These limits are for each of the 4 turbines individually, while operating with the duct burners on. This permit is a modification to RBLC OH-0252 to remove hourly restrictions on duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Burning natural gas in an efficient combustion turbine | 19.9 | LB/H |  | BACT-PSD | NSPS , SIP | U | 0 | N | 87.2 | T/YR | PER ROLLING 12 MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for each turbine individually. Subject to Part 60 Subparts Da. If required test Methods 1 through 5 and Method 202.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 20.4911 | LB/H | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 15.6 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Emission limit 1 & 2 are for each unit operating with the DB.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 20.4911 | LB/H | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 15.6 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Emission limit 1 & 2 are for each unit operating with the DB.
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 20.4911 | LB/H | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 19.9 | LB/H | TEST PROTOCOL | 0 |  |  | 0 | 0 | N | 2012 | Cost effectiveness information: No additional costs were calculated for PM10 or PM2.5 since additional costs to remove condensable particulate would only inflate the costs calculated for PM. Therefore, the costs for PM were considered to be conservative. Fabric filter baghouse = $11,432/ton Dry ESP = $19,229/ton Wet ESP = $42,780/ton Wet scrubber = $16,663/ton
TX-0773 | FGE EAGLE PINES PROJECT | FGE EAGLE PINES, LLC | CHEROKEE | TX |  | USA | EMERSON FARRELL | 281-407-7749 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, 512-239-1095, Erik.Hendrickson@tceq.texas.gov | 131316, PSDTX1454, AND GHGPSDT | 4911 | 221112 | UNKNOWN | 09/10/2015 &nbsp;ACT | 11/04/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | The FGEEP Project will include three natural gas-fired combined cycle (NGCC) power blocks, each block comprised of two gas-fired combustion turbines, two supplemental fired duct burners (DBs) heat recovery steam generators (HRSGs), and one steam turbine. FGEEP selected Alstom GT36 combustion turbines (CTs), each nominally rated at 321 megawatts (MW). Each HRSG is equipped with DBs that will have a maximum design heat input capacity of 799 million British thermal units per hour (MMBtu/hr). The CTs and DBs are fueled with pipeline quality natural gas. Each power block will also have a steam turbine generator designed to produce approximately 502 MW with the additional duct firing. Each of the three blocks will include the following ancillary equipment: one multi-cell condenser/cooling tower, one emergency generator, one firewater pump, two diesel storage tanks, and pressurized aqueous ammonia storage tanks. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 321 | MW | Alstom GT36 combustion turbines (321 MW)+ 799 million British thermal units per hour (MMBtu/hr) duct burner | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 21.4 | LB/H |  | BACT-PSD |  | U | 0 | U | 93.7 | T/YR |  | 0 |  |  | 0 | 0 | N
TX-0773 | FGE EAGLE PINES PROJECT | FGE EAGLE PINES, LLC | CHEROKEE | TX |  | USA | EMERSON FARRELL | 281-407-7749 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, 512-239-1095, Erik.Hendrickson@tceq.texas.gov | 131316, PSDTX1454, AND GHGPSDT | 4911 | 221112 | UNKNOWN | 09/10/2015 &nbsp;ACT | 11/04/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | The FGEEP Project will include three natural gas-fired combined cycle (NGCC) power blocks, each block comprised of two gas-fired combustion turbines, two supplemental fired duct burners (DBs) heat recovery steam generators (HRSGs), and one steam turbine. FGEEP selected Alstom GT36 combustion turbines (CTs), each nominally rated at 321 megawatts (MW). Each HRSG is equipped with DBs that will have a maximum design heat input capacity of 799 million British thermal units per hour (MMBtu/hr). The CTs and DBs are fueled with pipeline quality natural gas. Each power block will also have a steam turbine generator designed to produce approximately 502 MW with the additional duct firing. Each of the three blocks will include the following ancillary equipment: one multi-cell condenser/cooling tower, one emergency generator, one firewater pump, two diesel storage tanks, and pressurized aqueous ammonia storage tanks. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 321 | MW | Alstom GT36 combustion turbines (321 MW)+ 799 million British thermal units per hour (MMBtu/hr) duct burner | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 21.4 | LB/H |  | BACT-PSD |  | N | 0 | U | 93.7 | T/YR |  | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063000000 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burners. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Use of Natural gas a clean burning fuel | 21.55 | LB/H | AVERAGE OF THREE STACK TEST RUNS | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0.0069 | LB/MMBTU | AVERAGE OF THREE STACK TEST RUNS | 0 |  |  | 0 | 0 | N
NJ-0082 | WEST DEPTFORD ENERGY STATION | WEST DEPTFORD ENERGY ASSOCIATES | GLOUCESTER | NJ | 8086 | USA | DOUG MULVEY | (636)532-2200 | DMULVEY@LSPOWER.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | Yogesh Doshi- Supervisor (609)633-7249; permit writer: Piyush Desai | 56078/BOP120001 | 4911 | 221112 | 110063000000 | 01/19/2012 &nbsp;ACT | 07/18/2014 &nbsp;ACT | 2015-03-12 | 2016-05-02 | B | http://www.state.nj.us/dep/aqpp/ | An existing Electric Generating Facility with a PSD permit. A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility. The new project is subject to BACT/LAER | A new project consisting of a 427 MW Siemens Combined Cycle combustion turbine unit is being added to the existing facility | Combined Cycle Combustion Turbine with Duct Burner | 15.21 | Natural Gas | 20282 | MMCF/YR | This is a 427 MW Siemens Combined Cycle Turbine with duct burner Heat Input rate of the turbine = 2276 MMbtu/hr (HHV) Heat Input rate of the Duct burner= 777 MMbtu/hr(HHV) The fuel use of 20,282 MMCF/YR is for three turbines and three Duct burners. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of Natural Gas a clean burning fuel | 21.55 | LB/H | AVERAGE OF THREE STACK TEST RUNS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0.0069 | LB/MMBTU | AVERAGE OF THREE STACK TEST RUNS | 0 |  |  | 0 | 0 | N
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | Combustion Turbine | 15.21 | Natural Gas | 360 | MW | This process represents the GE option for the project - One GE 7FA.05 natural gas-fired combustion turbine generator with an 820.5 MMBTUH duct burner. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | LOW ASH FUEL AND COMBUSTION CONTROL. | 22.1 | LB/HR | >50% LOAD W/O DUCT FIRING | BACT-PSD | N/A | U | 0 | U | 31.8 | LB/HR | >50% LOAD WITH DUCT FIRING | 0 |  |  | 0 | 0 | N
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | COMBUSTION TURBINE | 15.21 | NATURAL GAS | 360 | MW | This process represents the Siemens option for the project - One Siemens SGT6-5000F5 natural gas-fired combustion turbine generator with an 820.3 MMBTUH duct burner. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | LOW ASH FUEL AND COMBUSTION CONTROL. | 22.2 | LB/HR | >50% LOAD W/O DUCT FIRING | BACT-PSD | N/A | U | 0 | U | 31.6 | LB/HR | >50% LOAD WITH DUCT FIRING | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas. | 22.58 | LB/H | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 0.014 lb/MMBTU and applies to each CTGHRSG. Test protocol will specify the averaging time. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM10 emissions were assumed the same as PM2.5, so the cost analysis is equivalent. The dollar value year used was 2013. Pulse Jet Fabric Filter Baghouse: minimum of $62,842 per ton. Mechanical Shaker Fabric Filter Baghouse: minimum of $53,684 per ton. Reverse-Air Fabric Filter Bathouse: minimum of $77,328 per ton. Dry ESP (Wire-Plate Type): minimum of $44,525 per ton. Dry ESP (Wire-Pipe Type): minimum of $66,472 per ton. Wet ESP (Wire-Plate Type): minimum of $77,761 per ton. Wet ESP (Wire-Pipe Type): minimum of $110,364 per ton. Venturi Scrubber: minimum of $52,773 per ton.
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #2 -combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | N |  | 22.58 | LB/H | AVERAGE OF 3 ONE-HOUR TEST RUNS | BACT-PSD |  | U | 0 | U | 77.1 | TON/YR | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | 0.01 lb/mmBtu at steady state operation 77.1 tpy includes startup, shutdown and malfunction
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110063000000 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITH DUCT FIRING | 15.21 | NATURAL GAS | 1000 | MW | TWO MITSUBISHI &lsquo;&lsquo;G&lsquo;&lsquo; MODEL COMBUSTION TURBINE GENERATORS (CTS) WITH A NOMINAL GENERATING CAPACITY OF 270 MW CAPACITY EACH, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR), OXIDATION CATALYST | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND EFFICIENT TURBINE DESIGN | 22.8 | LB/H | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGCCA or FGCCB--4 nat. gas fired CTG w/ DB for HRSG | 15.21 | natural gas | 2587 | MMBTU/H heat input, each CTG | Natural gas fired CTG with DB for HRSG; 4 total. Technology A (4 total) is 2587 MMBTU/H design heat input each CTG. Technology B (4 total) is 2688 MMBTU/H design heat input each CTG. Permit was issued for either of two F Class turbine technologies with slight variations in emission rates. Applicant will select one technology. Installation is two separate CTG/HRSG trains driving one steam turbine electrical generator; Two 2X1 Blocks. Each CTG will be rated at 211 to 230 MW (gross) output and the station nominal generating capacity will be up to 1,400 MW. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion air filters; efficient combustion control; low sulfur natural gas fuel. | 23.4801 | LB/H | TEST PROTOCOL (3 1-H TESTS IF POSSIBLE) | BACT-PSD |  | N | 90 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit applies to each CTG/HRSG. Limit applies at all times and includes duct burner operation.
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064000000 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine With Duct Burner | 15.21 | Natural Gas | 3727 | MMBtu/hr | DLN burner, SCR, Oxidation Catalyst and shall maintain and operate the sources and associated air cleaning devices in accordance with good engineering practice. shall install, certify, maintain and operate continuous emission monitoring systems (CEMS) for nitrogen oxides, carbon monoxide, carbon dioxide, and ammonia emissions on the exhaust of each combined-cycle powerblock. Emissions limits are for each combustion turbine/duct burner block. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA/OAR Method 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 23.4801 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 13.9 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 13.9 tpy 12-month rolling basis
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064000000 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Combustion Turbine With Duct Burner | 15.21 | Natural Gas | 3727 | MMBtu/hr | DLN burner, SCR, Oxidation Catalyst and shall maintain and operate the sources and associated air cleaning devices in accordance with good engineering practice. shall install, certify, maintain and operate continuous emission monitoring systems (CEMS) for nitrogen oxides, carbon monoxide, carbon dioxide, and ammonia emissions on the exhaust of each combined-cycle powerblock. Emissions limits are for each combustion turbine/duct burner block. | Particulate matter, total (TPM) | Other - EPA/OAR Method 5 | (Particulate Matter (PM)) | PM | N |  | 23.4801 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 13.9 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | 58.0 tpy 12-month rolling basis
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057000000 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | Mitsubishi M501-GAC combustion turbine, combined cycle configuration with duct burner. | 15.21 | natural gs | 2988 | MMBTU/H | or ULSD; Duct burner 499 MMBtu/hr, natural gas | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Utilize only natural gas or ULSD fuel; Limit the time in startup or shutdown. | 23.6 | LB/H TOTAL PM | 6-HR AVERAGE ON NG | BACT-PSD |  | U | 0 | U | 42.3 | LB/H TOTAL PM | 6-HR AVERAGE ON ULSD | 0 |  |  | 0 | 0 | N
LA-0224 | ARSENAL HILL POWER PLANT | SOUTHWEST ELECTRIC POWER COMPANY (SWEPCO) | CADDO | LA | 71101 | USA | KRIS GAUS | 2147771113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-726 | 4911 | 221112 | 110001000000 | 01/07/2008 &nbsp;ACT | 03/20/2008 &nbsp;ACT | 2008-04-18 | 2012-05-18 | B |  | NATURAL GAS FIRED ELECTRICAL GENERATION PLANT. |  | TWO COMBINED CYCLE GAS TURBINES | 15.21 | NATURAL GAS | 2110 | MMBTU/H | CTG-1 TURBINE/DUCT BURNER (EQT012) CTG-2 TURBINE/DUCT BURNER(EQT013) | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N | GOOD COMBUSTION DESIGN/ PROPER OPERATING PRACTICES/ PIPELINE QUALITY NATURAL GAS AS FUEL | 24.23 | LB/H | MAX | BACT-PSD | NSPS , OPERATING PERMIT |  | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110063000000 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITHOUT DUCT FIRING | 15.21 | NATURAL GAS | 270 | MW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND EFFICIENT TURBINE DESIGN | 25.1 | LB/H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110063000000 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITHOUT DUCT FIRING | 15.21 | NATURAL GAS | 270 | MW |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND EFFICIENT TURBINE DESIGN | 25.1 | LB/H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 |  |  | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2017-11-17 | A |  | Combinec Cycle Electric Generating Plant | 103839 | combined cycle turbine | 15.21 | natural gas | 700 | MW | The generating equipment consists of two natural gas-fired combustion turbines (CTs), each exhausting to a fired heat recovery steam generator (HRSG) to produce steam to drive a shared steam turbine generator. The steam turbine is rated at 271 MW of electric output. Three models of combustion turbines are being considered for this site: the General Electric 7FA.05, the Siemens SGT6-5000F(4), and the Siemens SGT6-5000F(5). The final selection of the combustion turbine will not be made until after the permit is issued. Plant output will range between 637 and 735 MW, depending on the model turbine selected. Duct Burners are rated at 750 MMBtu/hr each. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | pipeline quality natural gas and good combustion practices | 26.2 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Turbine models ranged from 25.5-26.2 lb/hr
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002000000 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | COMBINED CYCLE TURBINE GENERATORS (UNITS 6A &amp; 6B) | 15.21 | NATURAL GAS | 7146 | MMBTU/H | TURBINES ALSO PERMITTED TO BURN NO. 2 FUEL OIL AND ULTRA LOW SULFUR DIESEL. FUEL OIL USE IS LIMITED TO 1000 HOURS PER YEAR. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | WHILE FIRING NATURAL GAS: USE OF PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES WHILE FIRING FUEL OIL: USE OF ULTRA LOW SULFUR FUEL OIL AND GOOD COMBUSTION PRACTICES | 26.23 | LB/H | HOURLY AVERAGE W/O DUCT BURNER | BACT-PSD | OPERATING PERMIT | U | 0 | U | 33.16 | LB/H | HOURLY AVERAGE W/ DUCT BURNER | 0 |  |  | 0 | 0 | N |  | WHILE FIRING FUEL OIL, THE BACT LIMIT FOR PM10 IS 36.37 LB/HR (HOURLY AVERAGE) BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE).
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002000000 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | COMBINED CYCLE TURBINE GENERATORS (UNITS 6A &amp; 6B) | 15.21 | NATURAL GAS | 7146 | MMBTU/H | TURBINES ALSO PERMITTED TO BURN NO. 2 FUEL OIL AND ULTRA LOW SULFUR DIESEL. FUEL OIL USE IS LIMITED TO 1000 HOURS PER YEAR. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - METHOD 201A | (Particulate Matter (PM)) | PM | P | WHILE FIRING NATURAL GAS: USE OF PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES WHILE FIRING FUEL OIL: USE OF ULTRA LOW SULFUR FUEL OIL AND GOOD COMBUSTION PRACTICES | 26.23 | LB/H | HOURLY AVERAGE W/O DUCT BURNER | BACT-PSD | OPERATING PERMIT | U | 0 | U | 33.16 | LB/H | HOURLY AVERAGE W/ DUCT BURNER | 0 |  |  | 0 | 0 | N |  | WHILE FIRING FUEL OIL, THE BACT LIMIT FOR PM2.5 IS 36.37 LB/HR (HOURLY AVERAGE) BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE).
TX-0618 | CHANNEL ENERGY CENTER LLC | CHANNEL ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX955M1 | 4911 | 221112 | 110035000000 | 11/03/2011 &nbsp;ACT | 10/15/2012 &nbsp;ACT | 2012-10-24 | 2014-01-06 | B |  | Combustion turbine (Siemens 501F)/duct burners (475 MMBtu/hr) with heat recovery steam generator | 42179 and N021M1 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | The turbine is a Siemens 501F rated at a nominal 180 MW and the duct burner will have a maximum design heat input of 475 MMBtu/hr. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion and the use of gaseous fuel | 27 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0618 | CHANNEL ENERGY CENTER LLC | CHANNEL ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX955M1 | 4911 | 221112 | 110035000000 | 11/03/2011 &nbsp;ACT | 10/15/2012 &nbsp;ACT | 2012-10-24 | 2014-01-06 | B |  | Combustion turbine (Siemens 501F)/duct burners (475 MMBtu/hr) with heat recovery steam generator | 42179 and N021M1 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | The turbine is a Siemens 501F rated at a nominal 180 MW and the duct burner will have a maximum design heat input of 475 MMBtu/hr. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion and the use of gaseous fuel | 27 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0618 | CHANNEL ENERGY CENTER LLC | CHANNEL ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX955M1 | 4911 | 221112 | 110035000000 | 11/03/2011 &nbsp;ACT | 10/15/2012 &nbsp;ACT | 2012-10-24 | 2014-01-06 | B |  | Combustion turbine (Siemens 501F)/duct burners (475 MMBtu/hr) with heat recovery steam generator | 42179 and N021M1 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | The turbine is a Siemens 501F rated at a nominal 180 MW and the duct burner will have a maximum design heat input of 475 MMBtu/hr. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion and the use of gaseous fuel | 27 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0619 | DEER PARK ENERGY CENTER | DEER PARK ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX979M2 | 4911 | 221112 | 110018000000 | 09/01/2011 &nbsp;ACT | 09/26/2012 &nbsp;ACT | 2012-10-25 | 2013-09-25 | B |  | The Deer Park Energy Center is a combined cycle cogeneration facility consisting of five Siemens/Westinghouse 501F combustion turbine generators, each with a 725 MMBtu/hr duct burner and heat recovery steam generator. | 45642 and N036M2 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | natural gas-fired combined cycle turbine generator with a heat recovery steam generator equipped with a duct burner. The turbine is a Siemens 501F rated at a nominal 180 megawatts and the DB will have a maximum design rate capability of 725 million British thermal units per hour | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion and the use of natural gas | 27 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0619 | DEER PARK ENERGY CENTER | DEER PARK ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX979M2 | 4911 | 221112 | 110018000000 | 09/01/2011 &nbsp;ACT | 09/26/2012 &nbsp;ACT | 2012-10-25 | 2013-09-25 | B |  | The Deer Park Energy Center is a combined cycle cogeneration facility consisting of five Siemens/Westinghouse 501F combustion turbine generators, each with a 725 MMBtu/hr duct burner and heat recovery steam generator. | 45642 and N036M2 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | natural gas-fired combined cycle turbine generator with a heat recovery steam generator equipped with a duct burner. The turbine is a Siemens 501F rated at a nominal 180 megawatts and the DB will have a maximum design rate capability of 725 million British thermal units per hour | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion and use of natural gas | 27 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0619 | DEER PARK ENERGY CENTER | DEER PARK ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX979M2 | 4911 | 221112 | 110018000000 | 09/01/2011 &nbsp;ACT | 09/26/2012 &nbsp;ACT | 2012-10-25 | 2013-09-25 | B |  | The Deer Park Energy Center is a combined cycle cogeneration facility consisting of five Siemens/Westinghouse 501F combustion turbine generators, each with a 725 MMBtu/hr duct burner and heat recovery steam generator. | 45642 and N036M2 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | natural gas-fired combined cycle turbine generator with a heat recovery steam generator equipped with a duct burner. The turbine is a Siemens 501F rated at a nominal 180 megawatts and the DB will have a maximum design rate capability of 725 million British thermal units per hour | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 27 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Combined cycle combustion turbine | 15.21 | Natural gas | 250 | MW | Combined cycle combustion unit; this unit includes a heat recovery steam generator (HRSG) with supplemental natural gas duct firing (duct burners) and a condensing steam turbine generator with SCR and CO catalyst. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | dry low NOx burners heat recovery steam generator (HRSG) | 30.2 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Combined cycle combustion turbine | 15.21 | Natural gas | 250 | MW | Combined cycle combustion unit; this unit includes a heat recovery steam generator (HRSG) with supplemental natural gas duct firing (duct burners) and a condensing steam turbine generator with SCR and CO catalyst. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | dry low NOx burners heat recovery steam generator (HRSG) | 30.2 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0600 | THOMAS C. FERGUSON POWER PLANT | LOWER COLORADO RIVER AUTHORITY | LLANO | TX | 7657 | USA | JOE BENTLEY | 512-473-3272 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tan Nguyen 512-239-3445 tan.nguyen@tceq.texas.gov | PSDTX1244 | 4911 | 221112 | 110035000000 | 10/29/2010 &nbsp;ACT | 09/01/2011 &nbsp;ACT | 2011-09-02 | 2011-09-14 | B |  | Power Plant. Two natural gas-fired combined cycle turbine generators (GE 7FA) with unfired HRSG | 93938 | Natural gas-fired turbines | 15.21 | natural gas | 390 | MW | (2) GE7FA at 195 MW each, (1) steam turbine at 200 MW. Each turbine is equipped with an unfired heat recovery steam generator (HRSG), which provides steam for the steam turbine. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | pipeline quality natural gas | 33.43 | LB/H | 1-H | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit applies to total PM and PM10 also
LA-0136 | PLAQUEMINE COGENERATION FACILITY | THE DOW CHEMICAL COMPANY | IBERVILLE | LA | 70765 | USA | KRIS GAUS | 2147771113 | KPGAUS@AEP.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-659(M2) | 4911 | 221112 | 110017000000 | 06/13/2006 &nbsp;ACT | 07/23/2008 &nbsp;ACT | 2002-08-14 | 2009-04-28 | A |  | STEAM AND POWER GENERATION FACILITY COMPRISED OF FOUR NATURAL GAS FIRED GE FRAME 7 FA GAS TURBINES, EACH WITH A NOMINAL POWER RATING OF 170 MW, EACH EQUIPPED WITH DRY LOW NOX COMBUSTORS AND STEAM INJECTION CAPABILITIES, HEAT RECOVERY STEAM GENERATOR (HRSG), SUPPLEMENTARY FIRED DUCT BURNER SYSTEM, SELECTIVE CATALYTIC REDUCTION (SCR) SYSTEM. | LOCATED WITHIN THE DOW CHEMICAL COMPANY'S LOUISIANA OPERATIONS COMPLEX. PSD-LA-659(M-1), ISSUED 10/3/03, REVISED LB/HR & TPY LIMITS ASSOCIATED WITH THE COOLING TOWER. THE UPDATED RATES ARE REFLECTED HEREIN. PSD-LA-659(M-1), ISSUED JULY 23, 2008 REVISE THE MAXIMUM NOX EMISSIONS TO 240 LBS/HR AND INCLUDE MAXIMUM NOX EMISSIONS DURING STARTUPS AND SHUTDOWNS AS 480 LBS/HR | (4) GAS TURBINES/DUCT BURNERS | 15.21 | NATURAL GAS | 2876 | MMBTU/H | VISUAL INSPECTION FOR OPACITY ON A WEEKLY BASIS, STACK TESTS FOR PM, NOX, SO2, OPACITY, CO EMISSION POINTS GT-500, -600, -700, -800. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE OF CLEAN BURNING FUELS | 33.5 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 139 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | ADDITIONAL COMBINED EMISSION LIMIT: .02 LB/MMBTU.
TX-0789 | DECORDOVA STEAM ELECTRIC STATION | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas.gov | 107569 AND PSDTX1432 | 4911 | 221112 | 110008000000 | 12/23/2015 &nbsp;ACT | 03/08/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | The DeCordova Station will consist of two combustion turbine generators (CTGs) operating in simple cycle or combined cycle modes. The gas turbines will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE). Simple cycle operations limited to 2,500 hr/yr. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND LOW SULFUR FUEL | 35.47 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0789 | DECORDOVA STEAM ELECTRIC STATION | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas.gov | 107569 AND PSDTX1432 | 4911 | 221112 | 110008000000 | 12/23/2015 &nbsp;ACT | 03/08/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | The DeCordova Station will consist of two combustion turbine generators (CTGs) operating in simple cycle or combined cycle modes. The gas turbines will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE). Simple cycle operations limited to 2,500 hr/yr. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND LOW SULFUR FUEL | 35.47 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0751 | EAGLE MOUNTAIN STEAM ELECTRIC STATION | EAGLE MOUNTAIN POWER COMPANY LLC | TARRANT | TX |  | USA | PAUL COON | 214-875-8647 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.Alvirez@tceq.texas.com | 117026, PSDTX1390, N194 | 4911 | 221122 | 110005000000 | 03/26/2015 &nbsp;ACT | 06/18/2015 &nbsp;ACT | 2015-06-22 | 2016-07-06 | B |  | Eagle is proposing to construct two new combined cycle combustion turbines (CTG) which will generate electric power for sale on the wholesale electric market. The ancillary equipment includes an auxiliary boiler, a firewater pump, an emergency generator, a steam turbine, and various support facilities. |  | Combined Cycle Turbines (&gt;25 MW) â€“ natural gas | 15.21 | natural gas | 210 | MW | Two power configuration options authorized Siemens â€“ 231 MW + 500 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 210 MW + 349.2 MMBtu/hr duct burner | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 35.47 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 81.88 | T/YR |  | 0 |  |  | 0 | 0 | N |  | Good combustion practices, low sulfur fuel
TX-0751 | EAGLE MOUNTAIN STEAM ELECTRIC STATION | EAGLE MOUNTAIN POWER COMPANY LLC | TARRANT | TX |  | USA | PAUL COON | 214-875-8647 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.Alvirez@tceq.texas.com | 117026, PSDTX1390, N194 | 4911 | 221122 | 110005000000 | 03/26/2015 &nbsp;ACT | 06/18/2015 &nbsp;ACT | 2015-06-22 | 2016-07-06 | B |  | Eagle is proposing to construct two new combined cycle combustion turbines (CTG) which will generate electric power for sale on the wholesale electric market. The ancillary equipment includes an auxiliary boiler, a firewater pump, an emergency generator, a steam turbine, and various support facilities. |  | Combined Cycle Turbines (&gt;25 MW) â€“ natural gas | 15.21 | natural gas | 210 | MW | Two power configuration options authorized Siemens â€“ 231 MW + 500 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 210 MW + 349.2 MMBtu/hr duct burner | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 35.47 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 81.88 | T/YR |  | 0 |  |  | 0 | 0 | N |  | Good combustion practices, low sulfur fuel
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110063000000 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITH DUCT FIRING | 15.21 | NATURAL GAS | 1000 | MW | TWO MITSUBISHI &lsquo;&lsquo;G&lsquo;&lsquo; MODEL COMBUSTION TURBINE GENERATORS (CTS) WITH A NOMINAL GENERATING CAPACITY OF 270 MW CAPACITY EACH, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR), OXIDATION CATALYST | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND EFFICIENT TURBINE DESIGN | 38 | LB/H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110063000000 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | 2 COMBINED CYCLE COMBUSTION TURBINES, WITH DUCT FIRING | 15.21 | NATURAL GAS | 1000 | MW | TWO MITSUBISHI &lsquo;&lsquo;G&lsquo;&lsquo; MODEL COMBUSTION TURBINE GENERATORS (CTS) WITH A NOMINAL GENERATING CAPACITY OF 270 MW CAPACITY EACH, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT BURNERS, DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR), OXIDATION CATALYST | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND EFFICIENT TURBINE DESIGN | 38 | LB/H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041000000 | 04/18/2014 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2016-05-16 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | efficient combustion, natural gas fuel | 43 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041000000 | 04/18/2014 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2016-05-16 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | efficient combustion, natural gas fuel | 43 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041000000 | 04/18/2014 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2016-05-16 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | efficient combustion, natural gas fuel | 43 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
[40 empty] | Range Low | 0.72 | LB/H
[40 empty] | Range High | 43 | LB/H
[40 empty] | Mean | 15.4252 | LB/H
[40 empty] | Median | 13.195 | LB/H
[40 empty] | Mode | 12 | LB/H