## PermitSearchResults (27)
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | Emission Limit PPMV Sulf | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.21 | natural gas | 10 | M TONNES/YR | Four GE Frame 7E gas turbines for refrigeration and compression at the site | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Dry low NOx burners, good combustion practices, pipeline quality sweet natural gas fuel (low sulfur fuel) | 5 | GR/100 SCF |  | 84.6 | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041000000 | 04/18/2014 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2016-05-16 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | efficient combustion, natural gas fuel | 2 | GR/100 SCF | 1-HOUR | 33.84 | BACT-PSD |  | N | 0 | U | 0.5 | GR/100 SCF | ANNUAL | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110055000000 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | FUEL SPECIFICATION | 0.75 | GR S/100 SCF FUEL |  | 12.69 | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0304 | CANE ISLAND POWER PARK | FLORIDA MUNICIPAL POWER AGENCY (FMPA | OSCEOLA | FL | 33848 | USA | ROGER FONTES | 4073557767 | ROGER.FONTES@FMPA.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | ALVARO LINERO, PE. SPECIAL PROJECT SECTION ADMINISTRATOR BUREAU OF AIR REGULATION | PSD-FL-400 (0970043-014-AC) | 4911 | 221112 | 110014000000 | 04/01/2008 &nbsp;ACT | 09/08/2008 &nbsp;ACT | 2009-02-16 | 2009-04-20 | B |  | FMPA AND THE KISSIMMEE UTILITIES AUTHORITY (KUA) JOINTLY OWN THE CIPP, WHICH IS LOCATED IN OSCEOLA COUNTY AT 6075 OLD TAMPA HIGHWAY, INTERCESSION CITY, FLORIDA. THE CIPP PRESENTLY CONSISTS OF ONE 40 MEGAWATT (MW) SIMPLE CYCLE COMBUSTION TURBINE (UNIT 1), A 120 MW COMBINED CYCLE UNIT INCLUDING A HEAT RECOVERY STEAM GENERATOR (HRSG) (UNIT 2) AND A 250 MW COMBINED CYCLE UNIT (UNIT 3). THE THREE EXISTING UNITS FIRE NATURAL GAS AS THE PRIMARY FUEL, WITH DISTILLATE FUEL AS BACKUP. THE NEW UNIT WILL BE A NATURAL GAS 300 MW COMBINED CYCLE UNIT AND ASSOCIATED EQUIPMENT. | THE PROJECT WILL BE A Â¿ONE-ON-ONEÂ¿ 300 MW NATURAL GAS-FUELED COMBINED CYCLE UNIT (CIPP UNIT 4) AND ASSOCIATED AUXILIARY EQUIPMENT. UNIT 4 AND ASSOCIATED AUXILIARY EQUIPMENT WILL CONSIST OF: Â¿ A NOMINAL 150 MW GAS-FUELED GENERAL ELECTRIC 7241 FA CTG; Â¿ A SUPPLEMENTARY-FIRED HRSG WITH NATURAL GAS FUELED DUCT BURNERS (DB); Â¿ A NOMINAL 150 MW STG; Â¿ A NOMINAL 160-FOOT STACK; Â¿ AN EMERGENCY DIESEL ENGINE FIRE PUMP AND SMALL ULTRALOW SULFUR DIESEL (ULSD) FUEL OIL (FO)STORAGE TANK; Â¿ A NOMINAL 750 KILOWATTS (KW) SAFE SHUTDOWN DIESEL GENERATOR WITH A ULSD FO STORAGE TANK; AND Â¿ A MECHANICAL DRAFT COOLING TOWER WITH DRIFT ELIMINATORS. | 300 MW COMBINED CYCLE COMBUSTION TURBINE | 15.21 | NATURAL GAS | 1860 | MMBTU/H |  | Sulfur Dioxide (SO2) | Other - Fuel specifications | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | FUEL SPECIFICATIONS. | 2 | GR S/100 SCF GAS |  | 33.84 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0789 | DECORDOVA STEAM ELECTRIC STATION | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas.gov | 107569 AND PSDTX1432 | 4911 | 221112 | 110008000000 | 12/23/2015 &nbsp;ACT | 03/08/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | The DeCordova Station will consist of two combustion turbine generators (CTGs) operating in simple cycle or combined cycle modes. The gas turbines will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE). Simple cycle operations limited to 2,500 hr/yr. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD COMBUSTION PRACTICES AND LOW SULFUR FUEL | 5 | GR/100 SCF | HOURLY | 84.6 | BACT-PSD | NSPS | N | 0 | U | 1 | GR/100 SCF | ANNUAL | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110065000000 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD COMBUSTION PRACTICES, LOW SULFUR FUEL | 1 | GR/100 SCF | HOURLY | 16.92 | BACT-PSD | NSPS | N | 0 | U | 0.25 | GR/100 SCF | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
*TX-0660 | FGE TEXAS POWER I AND FGE TEXAS POWER II | FGE POWER LLC | MITCHELL | TX | 79565 | USA | EMERSON FARRELL | 281-362-2830 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX1364 | 3511 |  |  | 05/06/2013 &nbsp;EST | 03/24/2014 &nbsp;ACT | 2014-06-13 | 2017-11-17 | U |  | Electric Generating Utility | TCEQ Permit No. 110025 | Alstom Turbine | 15.21 | Natural Gas | 230.7 | MW | Four (4) Alstom GT24 CTGs, each with a HRSG and DBs, max design capacity 409 MMBtu/hr | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Low sulfur fuel, good combustion practices | 1 | GR S / 100 DSCF | HOURLY | 16.92 | BACT-PSD |  | N | 0 | U | 0.25 | GS S / 100 DSCF | ANNUAL | 0 |  |  | 0 | 0 | N
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Combined Cycle Turbine with Heat Recovery Steam Generator, fired Duct Burners, and Steam Turbine Generator | 15.21 | NATURAL GAS | 426 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines with HRSGs and Steam Turbine Generators | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Pipeline quality natural gas | 1.54 | GR/100 DSCF |  | 26.0568 | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
*TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2018-05-11 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | PIPELINE QUALITY NATURAL GAS | 1 | GR/100 DSCF |  | 16.92 | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Sulfur Dioxide (SO2) | Other - No test required | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Use of low-sulfur fuels | 2 | GR. S/100 SCF GAS | FOR NATURAL GAS | 33.84 | BACT-PSD | NSPS | U | 0 | U | 0.0015 | % S IN ULSD | FOR ULSD | 0 |  |  | 0 | 0 | N
FL-0337 | POLK POWER STATION | TAMPA ELECTRIC COMPANY | POLK | FL | 33860 | USA | PAUL CARPINONE | 813-228-4528 | PLCARPINONE@TECOENERGY.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Leigh Ann Pell, Project Engineer Phone; 850-717-9033 | 1050233-034-AC | 4911 | 221112 | 110000000000 | 05/15/2013 &nbsp;ACT | 10/14/2012 &nbsp;ACT | 2013-08-06 | 2014-11-07 | D | http://appprod.dep.state.fl.us/air/emission/apds/listpermits.asp | The Polk Power Station consists of: a nominal 250 MW (net) solid fuel-based integrated gasification and combined cycle (Unit 1) including a sulfuric acid plant and an auxiliary boiler; four natural gas-fueled nominal 165 MW simple cycle combustion turbine-electrical generators (CTGs) designated as Units 2, 3, 4 and 5; and ancillary equipment. Units 2 and 3 are equipped with backup fuel oil-firing capability. | GHG(e) emissions: 4,307,862 | Combine cycle power block (4 on 1) | 15.21 | natural gas | 1160 | MW | Basis for the emission standard is either NSPS Subpart KKKK or Department BACT determinations. The BACT emission standards for NOX while operating in combined cycle are more stringent than the corresponding Subpart KKKK emissions standards of 15 and 42 ppmvd @15% O2 on a 30-day rolling average for natural gas and fuel oil, respectively. | Sulfur Dioxide (SO2) | Other - Fuel Specifications | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 2 | GR S/100 SCF GAS |  | 33.84 | BACT-PSD | NSPS | U | 0 | U | 0.0015 | % S FUEL OIL |  | 0 |  |  | 0 | 0 | N |  | The applicant requested the stated sulfur fuel limits. These BACT values are more stringent and insure compliance with the corresponding Subpart KKKK SO2 emission standard.
[40 empty] | Range Low | 0.75 | GR/100 DSCF | Range Low | 12.69 | ppmv Sulf
[40 empty] | Range High | 5 | GR/100 DSCF | Range High | 84.6 | ppmv Sulf
[40 empty] | Mean | 2.1173 | GR/100 DSCF | Mean | 35.8243 | ppmv Sulf
[40 empty] | Median | 2 | GR/100 DSCF | Median | 33.84 | ppmv Sulf
[40 empty] | Mode | 2 | GR/100 DSCF | Mode | 33.84 | ppmv Sulf

## Clean Fuels
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | Limit PPMV Sulf | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.21 | natural gas | 10 | M TONNES/YR | Four GE Frame 7E gas turbines for refrigeration and compression at the site | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Dry low NOx burners, good combustion practices, pipeline quality sweet natural gas fuel (low sulfur fuel) | 5 | GR/100 SCF |  | 84.6 | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041000000 | 04/18/2014 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2016-05-16 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | efficient combustion, natural gas fuel | 2 | GR/100 SCF | 1-HOUR | 33.84 | BACT-PSD |  | N | 0 | U | 0.5 | GR/100 SCF | ANNUAL | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110055000000 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | FUEL SPECIFICATION | 0.75 | GR S/100 SCF FUEL |  | 12.69 | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0304 | CANE ISLAND POWER PARK | FLORIDA MUNICIPAL POWER AGENCY (FMPA | OSCEOLA | FL | 33848 | USA | ROGER FONTES | 4073557767 | ROGER.FONTES@FMPA.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | ALVARO LINERO, PE. SPECIAL PROJECT SECTION ADMINISTRATOR BUREAU OF AIR REGULATION | PSD-FL-400 (0970043-014-AC) | 4911 | 221112 | 110014000000 | 04/01/2008 &nbsp;ACT | 09/08/2008 &nbsp;ACT | 2009-02-16 | 2009-04-20 | B |  | FMPA AND THE KISSIMMEE UTILITIES AUTHORITY (KUA) JOINTLY OWN THE CIPP, WHICH IS LOCATED IN OSCEOLA COUNTY AT 6075 OLD TAMPA HIGHWAY, INTERCESSION CITY, FLORIDA. THE CIPP PRESENTLY CONSISTS OF ONE 40 MEGAWATT (MW) SIMPLE CYCLE COMBUSTION TURBINE (UNIT 1), A 120 MW COMBINED CYCLE UNIT INCLUDING A HEAT RECOVERY STEAM GENERATOR (HRSG) (UNIT 2) AND A 250 MW COMBINED CYCLE UNIT (UNIT 3). THE THREE EXISTING UNITS FIRE NATURAL GAS AS THE PRIMARY FUEL, WITH DISTILLATE FUEL AS BACKUP. THE NEW UNIT WILL BE A NATURAL GAS 300 MW COMBINED CYCLE UNIT AND ASSOCIATED EQUIPMENT. | THE PROJECT WILL BE A Â¿ONE-ON-ONEÂ¿ 300 MW NATURAL GAS-FUELED COMBINED CYCLE UNIT (CIPP UNIT 4) AND ASSOCIATED AUXILIARY EQUIPMENT. UNIT 4 AND ASSOCIATED AUXILIARY EQUIPMENT WILL CONSIST OF: Â¿ A NOMINAL 150 MW GAS-FUELED GENERAL ELECTRIC 7241 FA CTG; Â¿ A SUPPLEMENTARY-FIRED HRSG WITH NATURAL GAS FUELED DUCT BURNERS (DB); Â¿ A NOMINAL 150 MW STG; Â¿ A NOMINAL 160-FOOT STACK; Â¿ AN EMERGENCY DIESEL ENGINE FIRE PUMP AND SMALL ULTRALOW SULFUR DIESEL (ULSD) FUEL OIL (FO)STORAGE TANK; Â¿ A NOMINAL 750 KILOWATTS (KW) SAFE SHUTDOWN DIESEL GENERATOR WITH A ULSD FO STORAGE TANK; AND Â¿ A MECHANICAL DRAFT COOLING TOWER WITH DRIFT ELIMINATORS. | 300 MW COMBINED CYCLE COMBUSTION TURBINE | 15.21 | NATURAL GAS | 1860 | MMBTU/H |  | Sulfur Dioxide (SO2) | Other - Fuel specifications | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | FUEL SPECIFICATIONS. | 2 | GR S/100 SCF GAS |  | 33.84 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0789 | DECORDOVA STEAM ELECTRIC STATION | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas.gov | 107569 AND PSDTX1432 | 4911 | 221112 | 110008000000 | 12/23/2015 &nbsp;ACT | 03/08/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | The DeCordova Station will consist of two combustion turbine generators (CTGs) operating in simple cycle or combined cycle modes. The gas turbines will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE). Simple cycle operations limited to 2,500 hr/yr. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD COMBUSTION PRACTICES AND LOW SULFUR FUEL | 5 | GR/100 SCF | HOURLY | 84.6 | BACT-PSD | NSPS | N | 0 | U | 1 | GR/100 SCF | ANNUAL | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110065000000 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD COMBUSTION PRACTICES, LOW SULFUR FUEL | 1 | GR/100 SCF | HOURLY | 16.92 | BACT-PSD | NSPS | N | 0 | U | 0.25 | GR/100 SCF | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
*TX-0660 | FGE TEXAS POWER I AND FGE TEXAS POWER II | FGE POWER LLC | MITCHELL | TX | 79565 | USA | EMERSON FARRELL | 281-362-2830 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX1364 | 3511 |  |  | 05/06/2013 &nbsp;EST | 03/24/2014 &nbsp;ACT | 2014-06-13 | 2017-11-17 | U |  | Electric Generating Utility | TCEQ Permit No. 110025 | Alstom Turbine | 15.21 | Natural Gas | 230.7 | MW | Four (4) Alstom GT24 CTGs, each with a HRSG and DBs, max design capacity 409 MMBtu/hr | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Low sulfur fuel, good combustion practices | 1 | GR S / 100 DSCF | HOURLY | 16.92 | BACT-PSD |  | N | 0 | U | 0.25 | GS S / 100 DSCF | ANNUAL | 0 |  |  | 0 | 0 | N
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Combined Cycle Turbine with Heat Recovery Steam Generator, fired Duct Burners, and Steam Turbine Generator | 15.21 | NATURAL GAS | 426 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines with HRSGs and Steam Turbine Generators | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Pipeline quality natural gas | 1.54 | GR/100 DSCF |  | 26.0568 | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
*TX-0834 | MONTGOMERY COUNTY POWER STATIOIN | ENTERGY TEXAS INC | MONTGOMERY | TX |  | USA | CHRISTOPHER BURKE | 281-297-3369 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., 512-239-2175 laura.gibson@tceq.texas.gov | N256, PSDTX1510, AND GHGPSDTX1 | 4911 | 221112 | Not Found | 01/18/2018 &nbsp;ACT | 03/30/2018 &nbsp;ACT | 2018-04-26 | 2018-05-11 | A |  |  |  | Combined Cycle Turbine | 15.21 | NATURAL GAS | 2635 | MMBTU/HR/UNIT | Two Mitsubishi M501GAC turbines (without fast start) | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | PIPELINE QUALITY NATURAL GAS | 1 | GR/100 DSCF |  | 16.92 | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & TTTT, MACT YYYY
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Sulfur Dioxide (SO2) | Other - No test required | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Use of low-sulfur fuels | 2 | GR. S/100 SCF GAS | FOR NATURAL GAS | 33.84 | BACT-PSD | NSPS | U | 0 | U | 0.0015 | % S IN ULSD | FOR ULSD | 0 |  |  | 0 | 0 | N
[40 empty] | Range Low | 0.75 | GR/100 DSCF | Range Low | 12.69 | ppmv Sulf
[40 empty] | Range High | 5 | GR/100 DSCF | Range High | 84.6 | ppmv Sulf
[40 empty] | Mean | 2.129 | GR/100 DSCF | Mean | 36.0227 | ppmv Sulf
[40 empty] | Median | 1.77 | GR/100 DSCF | Median | 29.9484 | ppmv Sulf
[40 empty] | Mode | 2 | GR/100 DSCF | Mode | 33.84 | ppmv Sulf

## No Controls
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
FL-0337 | POLK POWER STATION | TAMPA ELECTRIC COMPANY | POLK | FL | 33860 | USA | PAUL CARPINONE | 813-228-4528 | PLCARPINONE@TECOENERGY.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Leigh Ann Pell, Project Engineer Phone; 850-717-9033 | 1050233-034-AC | 4911 | 221112 | 110000000000 | 05/15/2013 &nbsp;ACT | 10/14/2012 &nbsp;ACT | 2013-08-06 | 2014-11-07 | D | http://appprod.dep.state.fl.us/air/emission/apds/listpermits.asp | The Polk Power Station consists of: a nominal 250 MW (net) solid fuel-based integrated gasification and combined cycle (Unit 1) including a sulfuric acid plant and an auxiliary boiler; four natural gas-fueled nominal 165 MW simple cycle combustion turbine-electrical generators (CTGs) designated as Units 2, 3, 4 and 5; and ancillary equipment. Units 2 and 3 are equipped with backup fuel oil-firing capability. | GHG(e) emissions: 4,307,862 | Combine cycle power block (4 on 1) | 15.21 | natural gas | 1160 | MW | Basis for the emission standard is either NSPS Subpart KKKK or Department BACT determinations. The BACT emission standards for NOX while operating in combined cycle are more stringent than the corresponding Subpart KKKK emissions standards of 15 and 42 ppmvd @15% O2 on a 30-day rolling average for natural gas and fuel oil, respectively. | Sulfur Dioxide (SO2) | Other - Fuel Specifications | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 2 | GR S/100 SCF GAS |  | BACT-PSD | NSPS | U | 0 | U | 0.0015 | % S FUEL OIL |  | 0 |  |  | 0 | 0 | N |  | The applicant requested the stated sulfur fuel limits. These BACT values are more stringent and insure compliance with the corresponding Subpart KKKK SO2 emission standard.
[40 empty] | Range Low | 2 | GR/100 DSCF
[40 empty] | Range High | 2 | GR/100 DSCF
[40 empty] | Mean | 2 | GR/100 DSCF
[40 empty] | Median | 2 | GR/100 DSCF
[40 empty] | Mode | #N/A | GR/100 DSCF