## Combined Cycle Turbines 15.210
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
TX-0756 | CCI CORPUS CHRISTI CONDENSATE SPLITTER FACILITY | CASTLETON COMMODITIES INTERNATIONAL (CCI) CORPUS C | NUECES | TX |  | USA | BRAD BURMASTER | 281-378-1190 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tony Ionescu, 512-239-1277, tony.ionescu@tceq.texas.gov | 116072 AND PSDTX1388 | 2911 | 324110 | unknown | 09/22/2014 &nbsp;ACT | 06/19/2015 &nbsp;ACT | 2015-07-20 | 2016-07-06 | A |  | Two identical condensate splitter trains each capable of processing 50,000 barrels per day (BPD) of condensate. A bulk petroleum terminal consisting of two ship docks and a barge dock that will handle processed product from the condensate splitters and export to up 500,000 barrels per day of crude condensate. |  | Boilers, BL-1 and BL-2 | 15.21 | natural gas | 37 | MMBtu/hr (max) |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices will limit VOC emissions to 0.005 lb per 1000 scf. Fuel flow will be measured. | 0.005 | LB/100 SCF | EACH BOILER | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 40CFR60 Subparts A and Dc
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (WARM STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 27.7 | LB/H | WARM STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 47.4 | LB/EVENT | WARM STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF WARM STARTUPS NOT TO EXCEED 180 MINUTES; 2) WARM STARTUP MEANS A STARTUP THAT IS NOT A HOT OR COLD STARTUP
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (HOT STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 27.7 | LB/H | HOT STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 38 | LB/EVENT | HOT STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF HOT STARTUPS NOT TO EXCEED 90 MINUTES; 2) HOT STARTUP MEANS A STARTUP WHEN THE COMBUSTION TURBINE HAS BEEN IN OPERATION DURING THE PRECEDING 8 HOURS
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 23.9 | LB/H | TURBINE SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 23.9 | LB/EVENT | TURBINE SHUTDOWN PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF SHUTDOWN NOT TO EXCEED 30 MINUTES; 2) SHUTDOWN MEANS THE PERIOD BEGINNING WITH THE LOWERING OF EQUIPMENT FROM BASE LOAD AND LASTING UNTIL FUEL FLOW IS COMPLETELY OFF AND COMBUSTION HAS CEASED
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (COLD STARTUP PERIODS) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 27.7 | LB/H | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 106.7 | LB/EVENT | COLD STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | 1) DURATION OF COLD STARTUPS NOT TO EXCEED 270 MINUTES; 2) COLD STARTUP MEANS STARTUP WHEN THE COMBUSTION TURBINE HAS NOT BEEN IN OPERATION DURING THE PRECEDING 72 HOURS
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Combined Cycle Refrigeration Compressor Turbines (8) | 15.21 | natural gas | 286 | MMBTU/H | GE LM2500+G4 | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices and fueled by natural gas | 0.66 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1A | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Catalytic oxidation and good combustion practices for normal operations, and good combustion practices for startup/shutdown operations. | 61.27 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 226.16 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 2.0 PPM@15% O2 during normal operations only (not during startup/shutdown conditions) (3-hour average)
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Combined Cycle Unit 1B | 15.21 | Natural Gas | 3625 | MMBTU/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Catalytic oxidation and good combustion practices during normal operations, and good combustion practices during startup/shutdown operations. | 61.27 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 226.16 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 2.0 PPM@15% O2 during normal operations only (not during startup/shutdown conditions) (3-hour average)
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: Startup &amp; Shutdown | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified seperately for the startup and shutdown periods associated with the process equipment included in FG-CTGHRSG. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 198.9 | LB/H | EACH, DURING STARTUP | BACT-PSD |  | N | 85 | N | 419.7 | LB/H | EACH, DURING SHUTDOWN | 0 |  |  | 0 | 0 | N |  | Startup and shutdown operations are limited to 635 hours per 12-month rolling time period combined for both CTGHRSGs.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Siemens, without duct burners | 15.21 | Natural Gas | 515600 | MMSCF/rolling 12-months | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process without duct burners. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 3.9 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 28.6 | T/YR | PER ROLLING 12 MONTHS | 1 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | BACT: 2.0 ppmvd VOC at 15% O2. Methods: 18, 25, or 25A. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Siemens, with duct burners | 15.21 | Natural Gas | 51560 | MMSCF/rolling 12-MO | Two Siemens 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process with duct burners. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 5.9 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 28.6 | T/YR | PER ROLLING 12-MONTHS | 1.9 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | BACT: 2.0 ppmvd at 15% O2. Methods 18, 25, or 25A. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Mitsubishi, without duct burners | 15.21 | Natural Gas | 47917 | MMSCF/rolling 12-MO | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process without duct burners. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 7.9 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 56 | T/YR | PER ROLLING 12-MONTHS | 2 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | BACT: 2.0 ppmvd VOC at 15% O2. Methods: 18, 25, or 25A. T/YR limit is for 2 turbines.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | 2 Combined Cycle Combustion Turbines-Mitsubishi, with duct burners | 15.21 | Natural Gas | 47917 | MMSCF/rolling 12-MO | Two Mitsubishi 2932 MMBtu/H combined cycle combustion turbines , both with 300 MMBtu/H duct burners, with dry low NOx combustors, SCR, and catalytic oxidizer. Will install either 2 Siemens or 2Mitsubishi, not both (not determined). Short term limits are different with and without duct burners. This process with duct burners. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 7.3 | LB/H |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 56 | T/YR | PER ROLLING 12-MONTHS | 2 | PPM | PPMVD AT 15% O2 | 0 | 0 | N |  | BACT: 2.0 ppmvd VOC at 15% O2. Methods: 18, 25, or 25A. T/YR limit is for 2 turbines.
OH-0356 | DUKE ENERGY HANGING ROCK ENERGY | DUKE ENERGY HANGING ROCK, LLC | LAWRENCE | OH | 28207 | USA | ANDREW ROEBEL | 513-287-2356 | ANDREW.ROEBEL@DUKE-ENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110487 | 4911 | 221112 | 110012567203 | 07/17/2012 &nbsp;ACT | 12/18/2012 &nbsp;ACT | 2013-10-01 | 2016-05-04 | C |  | Four Natural Gas Fired Combustion Turbines, with Duct Burners; Combined Cycle, each 172 MW | This is a modification of RBLC OH-0252 to remove operating hour restrictions on duct burners, with changes to hourly limits without increasing the annual emission limitations. Original PTI # was 07-00503 | Turbines (4) (model GE 7FA) Duct Burners Off | 15.21 | NATURAL GAS | 172 | MW | Four GE 7FA combined cycle turbines, dry low NOx burners and selective catalytic reduction. These limits are for each of the 4 turbines individually, while operating with the duct burners off. This permit is a modification to RBLC OH-0252 to remove hourly restrictions on duct burners. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | P | Using efficient combustion technology | 3.2 | LB/H |  | BACT-PSD | SIP | U | 0 | N | 44.1 | T/YR | PER ROLLING 12 MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for each individual turbine. If required Methods 1 through 4 and 25.
OH-0356 | DUKE ENERGY HANGING ROCK ENERGY | DUKE ENERGY HANGING ROCK, LLC | LAWRENCE | OH | 28207 | USA | ANDREW ROEBEL | 513-287-2356 | ANDREW.ROEBEL@DUKE-ENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110487 | 4911 | 221112 | 110012567203 | 07/17/2012 &nbsp;ACT | 12/18/2012 &nbsp;ACT | 2013-10-01 | 2016-05-04 | C |  | Four Natural Gas Fired Combustion Turbines, with Duct Burners; Combined Cycle, each 172 MW | This is a modification of RBLC OH-0252 to remove operating hour restrictions on duct burners, with changes to hourly limits without increasing the annual emission limitations. Original PTI # was 07-00503 | Turbines (4) (model GE 7FA) Duct Burners On | 15.21 | NATURAL GAS | 172 | MW | Four GE 7FA combined cycle turbines, dry low NOx burners and selective catalytic reduction. These limits are for each of the 4 turbines individually, while operating with the duct burners on. This permit is a modification to RBLC OH-0252 to remove hourly restrictions on duct burners. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | P | Using efficient combustion technology | 7.3 | LB/H |  | BACT-PSD | SIP | U | 0 | N | 44.1 | T/YR | PER ROLLING 12 MONTHS | 0 |  |  | 0 | 0 | N |  | Limits are for each individual turbine. If required Methods 1 through 4 and 25.
OH-0366 | CLEAN ENERGY FUTURE - LORDSTOWN, LLC | CLEAN ENERGY FUTURE - LORDSTOWN, LLC | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0117655 | 4911 | 221112 | 110070396317 | 09/17/2014 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2019-02-27 | 2019-06-19 | A |  | 962 MW (gross winter output) combined cycle gas turbine (CCGT) facility | Initial installation permit for the construction of the Lordstown Energy Center - a nominal 940 MW combined cycle gas turbine (CCGT) facility. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 2725 | MMBTU/H | Combined cycle combustion turbine (2,725 MMBtu/hr heat input turbine at ISO conditions and 179 MMBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Limits and throughputs are for single turbine. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | B | Good combustion controls and oxidation catalyst | 8.2 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 47.1 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen with ductburner. 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen turbine only. 8.2 lb/h, with duct burner (except startup and shutdown). 3.9 lb/h without duct burner (except startup and shutdown). 47.1 t/yr per rolling 12 month period for all operating modes, including startup. 64.4 lb/h during cold startup, 60.1 lb/h during hot startup, 59.6 lb/h during warm startup, and 62.8 lb/h during shutdown.
OH-0367 | SOUTH FIELD ENERGY LLC | SOUTH FIELD ENERGY LLC | COLUMBIANA | OH | 43968 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0119495 | 4911 | 221112 | Not Found | 09/14/2015 &nbsp;ACT | 09/23/2016 &nbsp;ACT | 2019-02-28 | 2019-06-19 | A |  | 1150 MW combined-cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the South Field Energy facility, a nominal 1,150 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in Wellsville, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3131 | MMBTU/H | Two identical combined cycle combustion turbine (3,131 MMBtu/hr heat input turbine at ISO conditions, natural gas firing with evaporative cooler on and 800 MMBtu/hr maximum heat input natural gas-fired duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), catalytic oxidizer, and wet injection for ULSD firing. Heat input for ULSD firing at ISO conditions, with evaporative cooler on is 3,173 MMBtu/hr. Throughputs and limits are for single turbine except as noted. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Good combustion controls and oxidation catalyst | 10.64 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 50.6 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen, hourly average, natural gas, with duct burner. 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen, hourly average, natural gas, turbine only. 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen, hourly average, ultra low sulfur diesel. 10.64 lb/h with duct burner (except startup and shutdown). 4.35 lb/h without duct burner (except startup and shutdown). 9.25 lb/h for ultra low sulfur diesel (except startup and shutdown). 50.6 t/yr per rolling 12 month period for all operating modes, including startup and shutdown. When firing natural gas, 21.4 lb/h during startup and 55.2 lb/h during shutdown. When firing ultra low sulfur diesel, 109.0 lb/h during startup and 41.3 lb/h during shutdown.
OH-0370 | TRUMBULL ENERGY CENTER | TRUMBULL ENERGY CENTER | TRUMBULL | OH | 44481 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122331 | 4911 | 221112 | Not Found | 03/23/2017 &nbsp;ACT | 09/07/2017 &nbsp;ACT | 2019-03-05 | 2019-06-19 | A |  | 940 MW combined cycle gas turbine (CCGT) facility | Permit-to-install for the construction of the Trumbull Energy Center, a nominal 940 megawatt (MW) combined cycle gas turbine (CCGT) facility to be located in the Village of Lordstown, Ohio. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3025 | MMBTU/H | Two identical combined cycle combustion turbine (3,025 mmBtu/hr heat input turbine at ISO conditions and 237 mmBtu/hr heat input duct burner) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. Throughputs and limits are for single turbine except as noted. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | B | Good combustion controls and oxidation catalyst | 8.8 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 50.3 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen with duct burner, 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen without duct burner, 8.8 lb/h with duct burner, 4.1 lb/h without duct burner (each limit except startup and shutdown). 50.3 t/yr per rolling 12 month period for all operating modes, including startup and shutdown. 64.4 lb/h during cold startup, 60.1 lb/h during hot startup, 59.6 lb/h during warm startup, and 67.9 lb/h during shutdown.
OH-0372 | OREGON ENERGY CENTER | OREGON ENERGY CENTER | LUCAS | OH | 43616 | USA | WILLIAM SIDEREWICZ | (617)501-7094 | BILLS@PERPOWER.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0121049 | 4911 | 221112 | Not Found | 06/27/2016 &nbsp;ACT | 09/27/2017 &nbsp;ACT | 2019-03-06 | 2019-06-19 | A |  | Combined cycle gas turbine (CCGT) facility | Installation of natural gas-fired combined cycle combustion turbine power plant. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural gas | 3055 | MMBTU/H | Combined cycle combustion turbine (3,055 mmBtu/hr heat input turbine at ISO conditions and 221.3 mmBtu/hr heat input duct burner) with dry low NOX combustors, selective catalytic reduction (SCR), and catalytic oxidation. All heat values are on a HHV basis. Throughputs and limits are for single turbine except as noted. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | B | oxidation catalyst and good combustion control | 8.8 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 50.28 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen, with duct burner. 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen, without duct burner. 8.8 lb/h with duct burner. 4.1 lb/h without duct burner. Each limit except startup and shutdown. 50.28 t/yr per rolling 12 month period for all operating modes, including startup. 64.4 lb/h during cold startup, 60.1 lb/h during hot startup, 59.6 lb/h during warm startup, and 62.8 lb/h during shutdown.
OH-0374 | GUERNSEY POWER STATION LLC | GUERNSEY POWER STATION LLC | GUERNSEY | OH | 43723 | USA | MARY KING | (317)447-4513 | MARY@APEXPOWERGROUP.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122594 | 4911 | 221112 | 110070379546 | 04/14/2017 &nbsp;ACT | 10/23/2017 &nbsp;ACT | 2019-03-08 | 2019-06-19 | A |  | 1,650 MW combined cycle combustion turbine electrical generating facility | Installation PTI for a new 1,650 MW combined cycle natural-gas fired turbine plant and associated auxiliary boiler, firewater pumps, emergency generators and fuel gas heaters | Combined Cycle Combustion Turbines (3, identical) (P001 to P003) | 15.21 | Natural gas | 3516 | MMBTU/H | Three identical Combustion Turbines; GE 7HA.02 natural gas-fired lean pre-mix combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,516 MMBtu/hr HHV at 100% load and -18Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 997 MMBtu/hr HHV controlled with catalytic oxidation and selective catalytic reduction (SCR) and cooled with an air-cooled condenser (ACC) used to generate electricity. Throughputs and limits are for a single turbine except as noted. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | B | oxidation catalyst and good combustion practices as recommended by the manufacturer | 11.73 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 4.92 | LB/H | WITHOUT DUCT BURNERS. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | Limits are for single turbine except as noted. 2.0 ppm by volume, dry basis (ppmvd) at 15% oxygen turbine with duct burners. 1.0 ppm by volume, dry basis (ppmvd) at 15% oxygen without duct burners. Both excluding startup and shutdown. 4.92 lb/h without duct burners. 11.73 lb/h with duct burners. Both excluding startup and shutdown. 55.9 lb/cold startup, 13.7 lb/hot startup, 16.5 lb/warm startup and 34.9 lb/shutdown. 146.91 t/yr per rolling 12 month period total for all 3 turbines.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | General Electric Combustion Turbine (P004) | 15.21 | Natural gas | 3544 | MMBTU/H | General Electric model 7HA.02 natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,544 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices as recommended by the manufacturer. | 4.54 | LB/H | EXCEPT STARTUP AND SHUTDOWN. SEE NOTES | BACT-PSD |  | U | 0 | U | 26.4 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 1 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 1.0 ppmvd at 15% oxygen (O2) and 4.54 pounds per hour, excluding periods of startup and shutdown. 26.4 tons of NOx per rolling, 12-month period, including start-up and shutdown emissions. 78.1 lb/h during cold startup, 11.5 lb/h during hot startup, 12.0 lb/h during warm startup, and 29.6 lb/h during shutdown.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Mitsubishi Combustion Turbine (P005) | 15.21 | Natural gas | 3320 | MMBTU/H | Mitsubishi Model 501JAC natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,320 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 108 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | oxidation catalyst and shall operate the emissions unit in accordance with good combustion practices as recommended by the manufacturer | 8.8 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 79.3 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen and 8.80 lb/h with duct burner (except startup and shutdown). 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen and 4.60 lb/h without duct burner (except startup and shutdown). 79.3 t/yr per rolling 12 month period for all operating modes, including startup. 224.7 lb/h during cold startup, 225.1 lb/h during warm startup, 185.9 lb/h during hot startup, and 97.0 lb/h during shutdown.
OH-0375 | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | LONG RIDGE ENERGY GENERATION LLC - HANNIBAL POWER | MONROE | OH | 43931 | USA | KENNETH NICHOLSON | (212)478-4128 | RSTEWART@FORTRESS.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122829 | 4911 | 221112 | 110070396014 | 06/05/2017 &nbsp;ACT | 11/07/2017 &nbsp;ACT | 2019-03-12 | 2019-06-19 | A |  | Combined cycle combustion turbine power generation facility | Initial installation permit for a 485 MW combined cycle electric generating facility in Monroe County. The emissions units include a combustion turbine with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, emergency fire pump engine, and an eight-cell mechanical draft low-mist wet cooling tower. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Siemens Combustion Turbine (P006) | 15.21 | Natural gas | 3602 | MMBTU/H | Siemens Model SCC6-8000H natural gas or natural gas+ethane fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,602 MMBtu/hr at 100% load and -5Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 667 MMBtu/hr controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The Project will use either a GE Model 7HA.02 (P004), Mitsubishi Model 501JAC (P005) or Siemens Model SCC6-8000H (P006) combustion turbine (CT) with duct firing in the HRSG to increase steam generation in the steam turbine. Only one turbine will be built but each of these turbines are included in this RBLC entry. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | oxidation catalyst and shall operate the emissions unit in accordance with good combustion practices as recommended by the manufacturer | 9.5 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 50.8 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen and 9.5 lb/h with duct burner (except startup and shutdown). 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen and 3.9 lb/h without duct burner (except startup and shutdown). 50.8 t/yr per rolling 12 month period for all operating modes, including startup. 40.4 lb/h during cold startup, 40.2 lb/h during warm startup, 40.7 lb/h during hot startup, and 39.4 lb/h during shutdown.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | General Electric (GE) Combustion Turbines (P005 &amp; P006) | 15.21 | Natural gas | 3459.6 | MMBTU/H | Two identical GE Combustion Turbines 1 and 2; GE model 7HA.02 natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,459.6 MMBtu/hr (HHV) at 100% load and -2Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 570.45 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate additional electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Good combustion practices and oxidation catalyst | 4.36 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 49.1 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen on a 24-hr block averaging period and 10.3 lb/h with duct burner, except startup and shutdown. 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen on a 24-hr block averaging period and 4.36 lb/h without duct burner, except startup and shutdown. 49.1 tons per rolling 12 month period for all operating modes, including startup and shutdown. 4.81 tons per rolling 12 month period for startup and shutdown periods.
OH-0377 | HARRISON POWER | HARRISON POWER | HARRISON | OH | 43907 | USA | JIM PALUMBO | (570)793-6012 | JPALUMBO@EMBERCLEAR.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0122266 | 4911 | 221112 | Not Found | 02/02/2017 &nbsp;ACT | 04/19/2018 &nbsp;ACT | 2019-03-21 | 2019-06-19 | A |  | 1000 MW natural gas-fired combined cycle combustion turbine plant | Initial installation permit for a 1000 MW combined cycle electric generating facility in Harrison County that includes two (2) combustion turbines with a heat recovery stream generator (HRSG) and duct burners, auxiliary boiler, emergency diesel generator engine, and emergency fire pump engine. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). The facility-wide pollutants table below is for the GE turbines. The Mitsubishi emissions are as follows: PM10/2.5 155.2, SO2 59.2, NOx 249.9, CO 219.7, VOC 169.5 | Mitsubishi Hitachi Power Systems (MHPS) Combustion Turbines (P007 &amp; P008) | 15.21 | Natural gas | 3231 | MMBTU/H | Two identical MHPS Combustion Turbines 1 and 2; Mitsubishi Model M501JAC natural gas-fired combined cycle combustion turbine generator equipped with dry low-NOx (DLN) burners nominally rated at 3,231 MMBtu/hr (HHV) at 100% load and 51Â° F exhausting through a heat recovery steam generator (HRSG) with supplemental natural gas-fired duct burners nominally rated at 306 MMBtu/hr (HHV) controlled with catalytic oxidation and selective catalytic reduction (SCR) used to generate electricity. The permit includes the option to install either General Electric turbines (with 80 MMBTU aux boiler B002) or Mitsubishi turbines (with 44.55 MMBTU aux boiler B001). Limits and throughputs are for single turbine except as noted. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Good combustion practices and oxidation catalyst | 9.8 | LB/H | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 84.7 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 2 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | 2.0 ppm by volume dry basis (ppmvd) at 15% oxygen and 9.8 lb/h with duct burner, except startup and shutdown. 1.0 ppm by volume dry basis (ppmvd) at 15% oxygen and 4.7 lb/h without duct burner, except startup and shutdown. 84.7 tons per rolling 12 month period for all operating modes, including startup and shutdown. 42.50 tons per rolling 12 month period for startup and shutdown periods.
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057188626 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.21 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (6) GE LM2500+ DLE turbines that drive the ethylene section compressors with waste heat recovery for amine solution regeneration. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0.6 | LB/H | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0315 | WARREN COUNTY POWER PLANT - DOMINION | VIRGINIA ELECTRIC AND POWER COMPANY | WARREN | VA | 22630 | USA | ROBERT BISHA | 804-273-3010 | ROBERT.M.BISHA@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Manager, Mr. Janardan Pandey, by phone at (540) 574-7817 or by e-mail: Janardan.Pandey@deq.virginia.gov | 81391-007 | 4911 | 221112 | 110040513110 | 09/03/2010 &nbsp;ACT | 12/17/2010 &nbsp;ACT | 2012-09-28 | 2015-03-30 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Virginia Electric and Power Company (Dominion) has proposed to construct and operate a combined-cycle electric power generating facility in Warren County with a nominal generating capacity of 1280 megawatts (MW) at ISO (International Organization for Standardization) conditions. | Equipment to be constructed at ths facility consists of: 3 Mitsubishi Model M501 GAC natural gas-fired combined-cylce turbines, each rated at 299,600 kW (2,996 MMBtu/hr. Each equipped with a heat recovery steam generator (HRSG) having a duct burner with a design rating of 500 MMBtu/hr. This permit supersedes the previous permit issued on 7/30/2004 to CPV Warren LLC. | COMBINED CYCLE TURBINE &amp; DUCT BURNER, 3 | 15.21 | Natural Gas | 2996 | MMBTU/H | Emissions are for one of three units (Mitsubishi natural gas-fired combustion turbine (CT) generator,Model M501 GAC). | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices. | 2.6 | LB/H | 3 HR AVG. (WITHOUT DUCT BURNER FIRING) | BACT-PSD |  | U | 0 | U | 6.1 | LB/H | 3 HR. AVG. (WITH DUCT BURNER FIRING) | 0 |  |  | 0 | 0 | N
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2018-06-25 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.02 Turbine | 15.21 | Natural Gas | 3496.2 | mmBtu/hr | Nominal 640 mWe All emission limits steady-state and include 1000 mmBtu/hr Duct Burner in operation Short Term startup and shutdown limits in lb/event given in permit. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation Catalyst, Good Combustion Practices | 11.4 | LB/HR |  | BACT-PSD |  | U | 0 | U | 54.8 | TONS/YEAR |  | 2 | PPM |  | 0 | 0 | N |  | VOC BACT is different for no Duct Firing = 1ppm
*WV-0032 | BROOKE COUNTY POWER PLANT | ESC BROOKE COUNTY POWER I, LLC | BROOKE | WV | 26035 | USA | ANDREW DORN | 7163121042 | DREW.DORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 Steven.R.Pursley@wv.gov | R14-0035 | 4911 | 221112 | Not Found | 03/30/2018 &nbsp;ACT | 09/18/2018 &nbsp;ACT | 2018-12-20 | 2019-01-02 | A |  | Nominal 925 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | GE 7HA.01 Turbine | 15.21 | Natural Gas/Ethane | 2737.7 | mmBtu/hr | Facility has 2 identical units, only 1 entry in RBLC. Nominal 462.5 mWe. All emission limits steady-state and include 424 mmBtu/hr Duct Burner in operation. Short Term startup and shutdown limits in lb/event given in permit. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Oxidation Catalyst, Good Combustion Practices | 8.1 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 2 | PPM |  | 0 | 0 | N |  | VOC BACT is different for no Duct Firing = 1ppm
OH-0360 | CARROLL COUNTY ENERGY | CARROLL COUNTY ENERGY | CARROLL | OH | 44615 | USA | AMY FRAZIER | (617)456-2209 | AFRAZIER@ADVANCEDPOWERNA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0113762 | 4911 | 221112 | 110064671127 | 04/11/2013 &nbsp;ACT | 11/05/2013 &nbsp;ACT | 2015-12-30 | 2019-04-01 | A |  | Natural gas fired combined cycle gas turbine electric generating station of nominal capacity of 742 MW | Installation of a natural gas-fired combined cycle combustion turbine electric utility power plant, nominally rated at 742 MW. | Combined Cycle Combustion Turbines (two, identical) (P001 and P002) | 15.21 | Natural Gas | 2045 | MMBTU/H | Two identical General Electric 7FA combined cycle combustion turbine (each at 2,045 mmBtu/hr heat input turbine at ISO conditions and 566 mmBtu/hr heat input duct burner, HHV) with dry low NOx combustors, selective catalytic reduction (SCR), and catalytic oxidizer. All throughputs and emission limits are for each turbine. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 0.0026 | LB/MMBTU | WITH DUCT BURNER. SEE NOTES. | BACT-PSD |  | U | 0 | U | 40.2 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | 0 |  | SEE NOTES | 0 | 0 | N |  | Limits are for each turbine. 0.0026 lb/mmbtu and 7.1 lb/h with duct burner (except startup and shutdown). 0.0013 lb/mmbtu and 2.8 lb/h turbine only (except startup and shutdown). 40.2 t/yr per rolling 12 month period including startup and shutdown. 140.2 lb/h for cold startup, 53.8 lb/h for hot startup, 151.7 lb/h for warm startup and 75.6 for shutdown. Pound per hour emissions rates as presented are averaged over the duration of the event where (for the lead/lag turbine) the duration of a cold start is 245/220 minutes, the duration of a warm start is 140/115 minutes, the duration of a hot start is 83/58 minutes, and the duration of a shutdown is less than 1 hour. Emissions reflect the higher of the lead or lag turbine, on a pollutant-specific basis.
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Combined Cycle Turbine/Duct Burner | 15.21 | Natural Gas | 2419.61 | mmBtu/Hr | This entry is for both of two identical units at the facility. Nominal 197 mW General Electric Frame 7FA.04 Turbine w/ Duct Burner - throughput denotes aggregate heat input of turbine and duct burner (HHV). | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 18 | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation Catalyst & Good Combustion Practices | 0.0022 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0.0022 | LB/MMBTU |  | 2 | PPM | @ 15% O2 | 0 | 0 | N |  | The above VOC limit is applicable with duct firing. The limit without duct firing is 1 ppm @ 15% O2.
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG | 15.21 | Natural gas | 2237 | MMBTU/H | Throughput is 2,237 MMBTU/H for each CTG Equipment is permitted as following flexible group (FG): FG-CTG1-2: Two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equpped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 0.0018 | LB/MMBTU | EACH CTG; TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 57386 | 0 | N | 2012 | The cost was estimated for a catalytic oxidation system (COS). VOC = $57,386/TON CO + VOC = $8,948/TON
MI-0405 | MIDLAND COGENERATION VENTURE | MIDLAND COGENERATION VENTURE | MIDLAND | MI | 48640 | USA | BRIAN VOKAL | 989-633-7840 | BJVOKAL@MIDCOGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank You. | 103-12 | 4911 | 221112 | 2611100016 | 11/19/2012 &nbsp;ACT | 04/23/2013 &nbsp;ACT | 2014-02-14 | 2016-05-04 | C |  | Electricity and steam generation | Facility wide increase of other pollutants not listed below: PM10 = +174.0 TPY PM2.5 = +174.0 TPY Lead = +0.0214 TPY CO2e = +2,545,965.0 TPY Sulfuric Acid Mist = +0.77 TPY | Natural gas fueled combined cycle combustion turbine generators (CTG) with HRSG and duct burner (DB) | 15.21 | Natural gas | 2486 | MMBTU/H | This process is permitted in a flexible group format, identified in the permit as FG-CTG/DB1-2 and is for two natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSG) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system. Additionally, the HRSG is operating with a natural gas fired duct burner for supplemental firing. The throughput is 2,486 MMBTU/H for each CTG/DB. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 0.004 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 57386 | 0 | N | 2012 | Cost effectiveness information: The cost was estimated for a catalytic oxidation system (COS) VOC = $57,386/TON CO + VOC = $8,948/ton
MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2019-02-19 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | FGCTGHRSG (EUCTGHRSG1 &amp; EUCTGHRSG2) | 15.21 | Natural gas | 0 |  | Two (2) combined-cycle natural gas-fired combustion turbine generators, each with a heat recovery steam generator (CTGHRSG). Plant nominal 1,150 MW electricity production. Turbines are each rated at 3,658 MMBTU/H and HRSG duct burners are each rated at 800 MMBTU/H. The HRSGs are not capable of operating independently from the CTGs. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 0.0026 | LB/MMBTU | EACH UNIT; HOURLY EXCEPT S.S. | BACT-PSD | SIP | N | 0 | N | 0.0013 | LB/MMBTU | EACH UNIT W/O DUCT BURNER FIRING; NOT SS | 0 |  |  | 0 | 0 | N |  | The emission limits above are described further below: Emission limit 1 applies to each unit and is 0.0026 LB/MMBTU, hourly except during startup and shutdown. Emission limit 2 applies to each unit without duct burner firing and is 0.0013 LB/MMBTU, hourly except during startup and shutdown.
*MI-0442 | THOMAS TOWNSHIP ENERGY, LLC | THOMAS TOWNSHIP ENERGY, LLC | SAGINAW | MI | 48626-9409 | USA | DAN EWAN | 312-582-1504 | DEWAN@INVENERGYLLC.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions, please contact the permit engineer, Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you! | 210-18 | 4911 | 221112 | Not Found | 06/10/2019 &nbsp;ACT | 08/21/2019 &nbsp;ACT | 2019-11-18 | 2019-12-19 | A |  | New power plant | Thomas Township Energy is proposing to install two combustion turbine generators (CTG). Each CTG is connected to a heat recovery steam generator (HRSG), together referred to as a CTGHRSG. To reduce emissions of nitrogen oxides (NOx), the high-efficiency CTGHRSGs will be equipped with dry low-NOx burners and selective catalytic reduction (SCR). To reduce the emissions of carbon monoxide (CO) and volatile organic compounds (VOCs), each CTGHRSG will be equipped with an oxidation catalyst. | FGCTGHRSG | 15.21 | Natural gas | 625 | MW | Two (2) combined-cycle natural gas-fired combustion turbine generators (CTGs), each with a heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG). Each CTGHRSG has a combined nominal 625 MW electricity production (ISO) and a maximum combined heat input rating of 4,200 MMBTU/hr (HHV). Each HRSG is equipped with a natural gas-fired duct burner with a maximum rating of 560 MMBTU/hr (HHV) (ISO) to provide heat for additional steam production. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices. | 0.004 | LB/MMBTU | HOURLY; NOT STARTUP/SHUTDOWN;EACH UNIT | BACT-PSD |  | N | 70 | U | 377 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 = 0.004 lb/MMBTU, applies to each unit and is hourly except during startup/shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the combustion process ends at flame-off. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in special condition (SC) III.2 of the permit. Thermal oxidation, EMxGT, NSCR are not technically feasible control options for VOCs.
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #1 - combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr | two identical Siemens SGT6-5000F combined cycle turbines without duct firing, each at 2258 mmBtu/hr generating approx. 300 MW each. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | A | catalytic oxidizer | 1 | PPM | AVG. OF 3 ONE HOUR TEST RUNS | BACT-PSD |  | U | 95 | U | 71.2 | TON/YR | 12-MONTH ROLLING | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | Combustion turbine #2 -combined cycle | 15.21 | natural gas | 2258 | mmBtu/hr |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | N |  | 1 | PPM | AVERAGE 0F 3 ONE-HOUR TEST RUNS | BACT-PSD |  | N | 0 | U | 71.2 | TON/YR | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | 71.2 ton/yr limit includes startup, shutdown and malfunction
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | FG-CTGHRSG: 2 Combined cycle CTGs with HRSGs with duct burners | 15.21 | natural gas | 647 | MMBTU/H for each CTGHRSG | This process is identified in the permit as FGCTGHRSG; it is 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with Heat Recovery Steam Generators (HRSGs) equipped with duct burners for supplemental firing (EUCTGHRSG1 & EUCTGHRSG2 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. Each CTGHRSG shall not exceed 647 MMBtu/hr on a fuel heat input basis. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 4 | PPM | TEST PROTOCOL | BACT-PSD |  | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The VOC emisison limit is 4 ppmdv at 15% O2 and applies to each CTGHRSG. Test protocol will specify averaging time. Startup and shutdown operations are limited to 635 hours per 12-month rolling time period combined for both CTGHRSGs. BACT, for each CTGHRSG separately, is 198.9 lb/hr during startup and 419.7 lb/hr during shutdown.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation Catalyst Technology and Good Combustion Practices | 4 | PPM | TEST PROTOCOL WILL SPECIFY | BACT-PSD |  | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is 4 ppmvd at 15%O2 and is for EACH CTGHRSG. Startup and shutdown operations are limited to 500 hours per 12-month rolling time period for each CTGHRSG train. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the startup and shutdown emission minimization plan. The efficiency range is 85-90 percent.
*MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2019-10-22 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG2--A 667 MMBTU/H natural gas fired CTG with a HRSG. | 15.21 | Natural gas | 667 | MMBTU/H | EUCTGHRSG2 is a nominally rated 667 MMBTU/H natural gas fired CTG coupled with a HRSG. The HRSG is equipped with a natural gas fired duct burner rated at 204 MMBTU/h to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a DLNB, SCR and oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | An oxidation catalyst for VOC control and good combustion practices. | 3 | PPM | PPMVD@15%O2; HOURLY; SEE NOTES | BACT-PSD |  | N | 0 | U | 5 | LB/H | HOURLY EXCEPT STARTUP/SHUTDOWN; SEE NOTE | 0 |  |  | 17102 | 0 | N | 2017 | Emission limit 1 is 3 ppmvd at 15% O2 and is an hourly limit except during startup and shutdown. The limit applies when the unit is in combined cycle mode. Emission limit 2 is 5 lb/h and is an hourly limit except during startup and shutdown. The limit applies when the unit is in HRSG bypass mode.
*MI-0441 | LBWL--ERICKSON STATION | LANSING BOARD OF WATER AND LIGHT | EATON | MI | 48917 | USA | LORI MYOTT | 517-702-6639 | LORI.MYOTT@LBWL.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Melissa Byrnes, for technical questions regarding this permit. She may be reached at 517-284-6790 or at byrnesm@michigan.gov. Thank you. | 74-18 | 4911 | 221112 | 110040958425 | 10/16/2018 &nbsp;ACT | 12/21/2018 &nbsp;ACT | 2019-10-18 | 2019-10-22 | D |  | Natural gas combined-cycle power plant. | The proposed new plant will be replacing the electrical generating capacity of both BWL's existing coal-fired power plants. BWL intends to retire those coal-fired power plants from service by 2025. However, before they can be retired, the new natural gas power plant must be operational. Emissions in the area will increase for a short period if the new combined-cycle plant is built. However, there will be overall reductions in emissions when the existing coal fired power plants are taken out of service. | EUCTGHRSG1--A 667 MMBTU/H NG fired combustion turbine generator coupled with a heat recovery steam generator (HRSG) | 15.21 | Natural gas | 667 | MMBTU/H | A nominally rated 667 MMBTU/hr natural gas-fired combustion turbine generator (CTG) coupled with a heat recovery steam generator (HRSG). The HRSG is equipped with a natural gas-fired duct burner rated at 204 MMBTU/hr to provide heat for additional steam production. The CTG is capable of operating in combined-cycle mode where the exhaust is routed to the HRSG or in simple-cycle mode where the HRSG is bypassed. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with a dry low NOx burner (DLNB), selective catalytic reduction (SCR) and oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | An oxidation catalyst for VOC control for each CTG/HRSG unit, good combustion practices. | 3 | PPM | PPMVD@15%O2; HOURLY EXC.START/SHUT; NOTE | BACT-PSD |  | N | 0 | U | 5 | LB/H | HOURLY EXCEPT STARTUP/SHUTDOWN; SEE NOTE | 0 |  |  | 17102 | 0 | N | 2017 | VOC Emission Limit 1 above is 3 ppmvd at 15%O2 when the unit is in combined cycle mode. The limit is hourly except during startup and shutdown. VOC Emission Limit 2 above is 5 lb/h when the unit is in HRSG bypass mode and is hourly except during startup and shutdown.
TX-0709 | SAND HILL ENERGY CENTER | CITY OF AUSTIN | TRAVIS | TX |  | USA | JOSEPH RAVI | (512) 322-6284 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez (512) 239-5220 Ruth.alvirez@tceq.texas.gov | 48106, PSDTX1012M2 | 4911 | 221112 | 110008975804 | 03/20/2015 &nbsp;ACT | 09/13/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | GE 7FA Natural Gas-fired Combined Cycle Turbine with DB fired HRSG |  | Natural gas-fired combined cycle turbines | 15.21 | Natural Gas | 173.9 | MW |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 2 | PPM | 1HR. AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Natural Gas fired.
TX-0767 | LON C. HILL POWER STATION | LON C. HILL, L.P. | NUECES | TX |  | USA | MATTHEW LINDSEY | 713-358-9734 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem, 512-239-1310, Tzvi.Shalem@tceq.texas.gov | 114911 AND PSDTX1380 | 4911 | 221122 | 110000501127 | 07/15/2015 &nbsp;ACT | 10/02/2015 &nbsp;ACT | 2015-09-23 | 2016-07-06 | A |  | The Lon C. Hill Power Station (LCHP) will include two natural gas-fired combined cycle combustion turbines (CTGs) equipped with dry low NOx burners (DLNs), heat recovery steam generators (HRSG), and natural gas-fired duct burners (DBs). Ancillary equipment includes evaporative coolers or inlet chillers, a single steam turbine (ST), auxiliary boiler, emergency generator, firewater pump, two cooling towers, oil water separator, degreaser, two diesel storage tanks, gasoline storage tank, selective catalytic reduction (SCR) and ammonia (NH3) handling systems including an NH3 storage tank, and two water tanks. The LCHP will be a 2x1 combined cycle power plant consisting of two CTGs, two HRSGs and one ST. The CTGs and ST will be one of two options: two Siemens SCC6-5000 CTGs and a SST6-5000 ST, or two General Electric 7FA CTGs and a D-11 ST. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 195 | MW | Two power configuration options authorized Siemens â€“ 240 MW + 250 million British thermal units per hour (MMBtu/hr) duct burner GE â€“ 195 MW + 670 MMBtu/hr duct burner | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 2 | PPM |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0773 | FGE EAGLE PINES PROJECT | FGE EAGLE PINES, LLC | CHEROKEE | TX |  | USA | EMERSON FARRELL | 281-407-7749 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, 512-239-1095, Erik.Hendrickson@tceq.texas.gov | 131316, PSDTX1454, AND GHGPSDT | 4911 | 221112 | UNKNOWN | 09/10/2015 &nbsp;ACT | 11/04/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | The FGEEP Project will include three natural gas-fired combined cycle (NGCC) power blocks, each block comprised of two gas-fired combustion turbines, two supplemental fired duct burners (DBs) heat recovery steam generators (HRSGs), and one steam turbine. FGEEP selected Alstom GT36 combustion turbines (CTs), each nominally rated at 321 megawatts (MW). Each HRSG is equipped with DBs that will have a maximum design heat input capacity of 799 million British thermal units per hour (MMBtu/hr). The CTs and DBs are fueled with pipeline quality natural gas. Each power block will also have a steam turbine generator designed to produce approximately 502 MW with the additional duct firing. Each of the three blocks will include the following ancillary equipment: one multi-cell condenser/cooling tower, one emergency generator, one firewater pump, two diesel storage tanks, and pressurized aqueous ammonia storage tanks. |  | Combined Cycle Turbines (&gt;25 MW) | 15.21 | natural gas | 321 | MW | Alstom GT36 combustion turbines (321 MW)+ 799 million British thermal units per hour (MMBtu/hr) duct burner | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 2 | PPM |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE) Simple cycle operations limited to 2,500 hr/yr. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDATION CATALYST | 2 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK AND TTTT
TX-0789 | DECORDOVA STEAM ELECTRIC STATION | DECORDOVA II POWER COMPANY LLC | HOOD | TX |  | USA | PAUL COON | 214-875-8376 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas.gov | 107569 AND PSDTX1432 | 4911 | 221112 | 110008149217 | 12/23/2015 &nbsp;ACT | 03/08/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | The DeCordova Station will consist of two combustion turbine generators (CTGs) operating in simple cycle or combined cycle modes. The gas turbines will be one of two options: Siemens or General Electric. |  | Combined Cycle &amp; Cogeneration | 15.21 | natural gas | 231 | MW | 2 CTGs to operate in simple cycle & combined cycle modes. 231 MW (Siemens) or 210 MW (GE). Simple cycle operations limited to 2,500 hr/yr. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDATION CATALYST | 2 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK AND TTTT
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Refrigeration Compression Turbines | 15.21 | natural gas | 10 | M TONNES/YR | Four GE Frame 7E gas turbines for refrigeration and compression at the site | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Dry low NOx burners and good combustion practices | 2 | PPM | 3-HR AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0790 | PORT ARTHUR LNG EXPORT TERMINAL | PORT ARTHUR LNG, LLC | JEFFERSON | TX |  | USA | J.D. MORRIS | 713-298-5479 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 131769, PSDTX1456, GHGPSDTX134 | 4922 | 486210 | UNKNOWN | 12/21/2015 &nbsp;ACT | 02/17/2016 &nbsp;ACT | 2016-02-26 | 2016-07-29 | A |  | Liquefied natural gas (LNG) export terminal |  | Simple Cycle Electrical Generation Gas Turbines 15.210 | 15.21 | natural gas | 34 | MW | Nine GE PGT25+G4 gas turbines for electrical generation at the site at 34 MW/turbine | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDATION CATALYST | 2 | PPM | 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | FGCTGHRSG (2 Combined cycle CTGs with HRSGs; EUCTGHRSG10 &amp; EUCTGHRSG11) | 15.21 | Natural gas | 554 | MMBTU/H, each | Two combined cycle natural gas fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) (EUCTGHRSG10 & EUCTGHRSG11 in FGCTGHRSG). The total hours for both units combined for startup and shutdown shall not exceed 635 hours per 12-month rolling time period. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 4 | PPM AT 15% O2 | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is 4 ppmvd at 15% O2 and is for each CTGHRSG. Startup and shutdown operations are limited to 635 hours per 12-month rolling time period combined for both CTGHRSGs.
GA-0138 | LIVE OAKS POWER PLANT | LIVE OAKS COMPANY, LLC | GLYNN | GA | 31525 | USA | BURT WALLACE | 478 943-2331 | BURT_1@BELLSOUTH.NET | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-127-0075-P-02-0 | 4911 | 221122 | UNKNOWN | 11/19/2008 &nbsp;ACT | 04/08/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | A |  | LIVE OAKS POWER PLANT PROPOSED FACILITY WILL OPERATE AS A FULLY DISPATCHABLE ELECTRIC GENERATING FACILITY. THE COMBINED CYCLE SYSTEM WILL UTILIZE TWO COMBUSTION TURBINES AND ONE STEAM TURBINE, CONFIGURED IN A TWO-ON-ONE ARRANGEMENT. THE HEAT CONTENT OF THE EXHAUST GASSES WIL BE RECOVERED BY A HEAT RECOVERY STEAM GENERATOR (HRSG), AND USED TO DRIVE A STEAM TURBINE. DURING PEAK LOADS A DUCT BURNER IN THE HRSG CAN BE FIRED TO AD ADDITIONAL HEAT ENERGY TO THE GAS TURBINE EXHAUST, INCREASING THE PRODUCTION OF STEAM SENT TO THE STEAM TURBINE. THE COMBUSTION TURBINES (CTs) SELECTED ARE SIEMENS MODEL SGT6-5000F. EACH COMBUSTION TURBINE WILL GENERATE 200 MW OF ELECTRIC POWER. THE GROSS ELECTRICAL CAPACITY OF THE COMBINED CYCLE FACILITY FIRING NATURAL GAS WILL THEN BE 600 MW. | PM10 74.3(+) EMISSIONS (T/YR) | COMBINED CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.21 | NATURAL GAS | 600 | MW |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | GOOD COMBUSTION PRACTICES, CATALYTIC OXIDATION | 2 | PPM@15%02 | 3-HOUR AVERAGE/CONDITION 2.11 | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
PA-0286 | MOXIE ENERGY LLC/PATRIOT GENERATION PLT | MOXIE ENERGY LLC | LYCOMING COUNTY | PA |  | USA | KENT MORTON | (571) 594 - 0150 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MUHAMMAD Q. ZAMAN, ENVIRONMENTAL PROGRAM MANAGER NORTHCENTRAL REGION 208 West Third St, Suite 101 Williamsport, PA 17701 570-327-3648 | 41-00084A | 4911 | 221112 | 110057116124 | 07/18/2012 &nbsp;ACT | 01/31/2013 &nbsp;ACT | 2013-03-27 | 2020-03-02 | A |  | This plan approval is for the construction of two natural-gas-fired combined cycle powerblocks where each powerblock consists of a combustion turbine and heat recovery steam generator with duct burner. The two powerblocks constructed pursuant to this plan approval will be either the two powerblocks rated 472 megawatts (MW) (P101 and P102) or the powerblocks rated 458 MW (P103 and P104). Additionally, this plan approval is for the construction of a 1464 bhp diesel-fired emergency generator, 460 bhp dieselfired fire pump, 1600 gallon diesel tank, 300 gallon diesel tank, two 15,000 gallon (each) lube oil tanks and ancillary electrical equipment. |  | Combined Cycle Power Blocks 472 MW - (2) | 15.21 | Natural Gas | 0 |  | Two natural-gas-fired combined cycle powerblocks where each powerblock consists of a combustion turbine and heat recovery steam generator with duct burner. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | CO Catalyst | 1 | PPMDV | WITHOUT DUCT BURNER | BACT-PSD | OTHER | U | 0 | U | 1.5 | PPMDV | WITH DUCT BURNER | 33.8 | T/YR | EACH UNIT | 0 | 0 | N
TX-0817 | CHOCOLATE BAYOU STEAM GENERATING (CBSG) STATION | INEOS USALLC | BRAZORIA | TX |  | USA | THERESA VITEK | 281-581-3498 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | 123117, PSDTX1460, GHGPSDTX135 | 4911 | 221112 | Not Found | 12/22/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-28 | 2017-11-16 | A |  | support facility providing steam and electricity |  | Combined Cycle Cogeneration | 15.21 | NATURAL GAS | 50 | MW | 2 UNITS EACH 50 MW GE LM6000 | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDATION CATALYST | 1 | PPMDV |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2018-12-21 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Combustion turbine and HRSG without duct burner NG only | 15.21 | Natural gas | 0 |  | Emission limits are for each turbine fueled by NG and operating without duct burner being fired and do not include startup/shutdown emissions. | Volatile Organic Compounds (VOC) | Other - EPA/OAR Method 18 and 25A | (Volatile Organic Compounds (VOC)) | VOC | N |  | 1 | PPMDV @ 15% O2 |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit is for each turbine and HRSG with the duct burner not fired.
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | Mitsubishi M501-GAC combustion turbine, combined cycle configuration with duct burner. | 15.21 | natural gs | 2988 | MMBTU/H | or ULSD; Duct burner 499 MMBtu/hr, natural gas | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst; Limit the time in startup or shutdown. | 2 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON NG | BACT-PSD |  | U | 0 | U | 5 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON ULSD | 0 |  |  | 0 | 0 | N
LA-0331 | CALCASIEU PASS LNG PROJECT | VENTURE GLOBAL CALCASIEU PASS, LLC | CAMERON | LA | 70631 | USA | GRAHAM MCARTHUR | 202-759-6741 | GMCARTHUR@VGLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Ms. Mei Wu, (225)219-3180 | PDS-LA-805 | 4925 | 221210 | Not Found | 06/25/2018 &nbsp;ACT | 09/21/2018 &nbsp;ACT | 2019-02-14 | 2019-06-19 | A |  | New Liquefied Natural Gas (LNG) production, storage, and export terminal. | Application Received September 2, 2015. | Combined Cycle Combustion Turbines (CCCT1 to CCCT5) | 15.21 | Natural Gas | 921 | MM BTU/h |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Catalytic Oxidation, Proper Equipment Design and Good Combustion Practices. | 1.1 | PPMV | 3 HOUR AVERAGE | BACT-PSD | OPERATING PERMIT , NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Units are in ppmv @ 15% O2; Averaging Time 3-Hour Average During Normal Operations.
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP01) | 15.21 | Natural Gas | 40 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 3 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD |  | N | 0 | U | 3 | LB/H | 3-HOUR AVERAGE | 14.7 | T/YR |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Combined Cycle Turbine (EP02) | 15.21 | Natural Gas | 40 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 3 | PPMV AT 15% O2 | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 3 | LB/H | 3-HOUR AVERAGE | 14.7 | T/YR |  | 0 | 0 | N
CA-1211 | COLUSA GENERATING STATION | PACIFIC GAS & ELECTRIC COMPANY | COLUSA | CA | 95955 | USA | STEVE ROYALL |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SAC 06-01 | 4911 | 221112 | 110038892115 | 01/07/2011 &nbsp;ACT | 03/11/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 660 MW NATURAL GAS FIRED POWER PLANT | PSD Permit issued on 9/29/2008, amended on 3/19/2010 to revise startup and shutdown emission limits, and amended again on 3/11/2011 to incorporate technical corrections. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 172 | MW | TWO (2) NATURAL GAS FIRED TURBINES AT 172 MW EACH. BOTH TURBINES EQUIPPED WITH A 688 MMBTU/HR DUCT BURNER AND HRSG. | Volatile Organic Compounds (VOC) | Other - EPA METHOD 25A OR 25B | (Volatile Organic Compounds (VOC)) | VOC | N |  | 2 | PPMVD | @15% O2, 1-HR ROLLING AVG | BACT-PSD |  | U | 0 | U | 11 | LB/H | 1-HR ROLLING AVG | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES | 15.21 | NATURAL GAS | 2300 | MMBTU/H | EACH TURBINE IS EQUIPED WITH DRY LOW NOX BURNERS, NATURAL GAS FIRED DUCT BURNERS, AND A HEAT RECOVERY STEAM GENERATOR IDENTIFIED AS HRSG#. NOX EMISSIONS CONTROLLED BY SELECTIVE CATALYTIC REDUCTION SYSTEMS (SCR##) ALONG WITH CO AND VOC EMISSSIONS CONTROLLED BY OXIDATION CATAYLST SYSTEMS (CAT##) IN EACH TURBINE. EACH STACK HAS CONTINUOUS EMISSIONS MONITORS FOR NOX AND CO. COMBINED NOMIAL POWER OUTPUT IS 1.350 MW. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDIZED CATALYST | 1 | PPMVD | 3 HOURS | BACT-PSD |  |  | 40 |  | 2 | PPMVD | 3 HOURS | 0 |  |  | 0 | 0 | N |  | LIMIT ONE IS USED UNDER CONDITIONS OF 15% O2 WITHOUT DUCT BURNERS IN USE. LIMIT TWO IS USED UNDER CONDITIONS OF 15% O2 WITH DUCT BURNERS IN USE.
MI-0432 | NEW COVERT GENERATING FACILITY | NEW COVERT GENERATING COMPANY, LLC | VAN BUREN | MI | 49043 | USA | JOHN REESE | 212-792-0897 | JREESE@EASTERNGEN.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit, please contact the permit engineer Ms. Michelle Rogers, at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 186-17 | 4911 | 221112 | Not Found | 04/17/2018 &nbsp;ACT | 07/30/2018 &nbsp;ACT | 2018-08-13 | 2019-02-19 | C |  | Power plant | The equipment consists of three advanced firing temperature Mitsubishi 501G combustion turbines, three heat recovery steam generators supplemented with gas-fired duct burners each with a max firing rate of 256 million British thermal units per hour (MMBtu/hr), three steam turbine generators. Auxiliary equipment includes three mechanical draft evaporative cooling towers, one natural gas auxiliary boiler, one diesel emergency generator, one diesel fire water pump, one aqueous parts cleaner, and one gas heater. | FG-TURB/DB1-3 (3 combined cycle combustion turbine and heat recovery steam generator trains) | 15.21 | Natural gas | 1230 | MW | Three (3) combined-cycle combustion turbine (CT) / heat recovery steam generator (HRSG) trains. Each CT is a natural gas fired Mitsubishi model 501G, equipped with dry low NOx combustor and inlet air evaporative cooling. Each HRSG includes a natural gas fired duct burner with a 256 MMBtu/hr heat input capacity and a dry low NOx burner. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | An oxidation catalyst and good combustion practices. | 1 | PPMVD | HOURLY; EACH CT/HRSG TRAIN | BACT-PSD | SIP | N | 0 | N | 48 | T/YR | EACH CT/HRSG TRAIN; 12-MO ROLL TIME PER. | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above does not include startup and shutdown. Emission limit 2 above is 48 ton/year based on a 12-month rolling time period as determined at the end of each calendar month.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (South Plant): A combined cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/H (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/H (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR and an oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 4 | PPMVD | AT 15%O2; NOT INCL. STARTUP/SHUTDOWN | BACT-PSD | SIP | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2 in the permit. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2019-02-19 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUCTGHRSG (North Plant): A combined-cycle natural gas-fired combustion turbine generator with heat recovery steam generator. | 15.21 | Natural gas | 500 | MW | Nominal 500 MW electricity production. Turbine rating of 3,080 MMBTU/hr (HHV) and HRSG duct burner rating of 755 MMBTU/hr (HHV). A combined-cycle natural gas-fired combustion turbine generator (CTG) with heat recovery steam generator (HRSG) in a 1x1 configuration with a steam turbine generator (STG) for a nominal 500 MW electricity production. The CTG is a H-class turbine with a rating of 3,080 MMBTU/hr (HHV). The HRSG is equipped with a natural gas-fired duct burner rated at 755 MMBTU/hr (HHV) at ISO conditions to provide heat for additional steam production. The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx burner (DLNB), SCR, and an oxidation catalyst. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst technology and good combustion practices. | 4 | PPMVD | AT 15%O2; HOURLY | BACT-PSD | SIP | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above does not include startup and shutdown. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the plan required in Special Condition III.2. Startup and Shutdown hours are limited to 300 hours per 12 month rolling time period.
*PA-0298 | FUTURE POWER PA/GOOD SPRINGS NGCC FACILITY | FUTURE POWER PA INC | SCHUYLKILL | PA | 17980 | USA | JAMES PALUMBO | 570-342-5200 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov | MARK J. WEJKSZNER NORTHEAST REGION AIR PROGRAM MANAGER 2 Public Square Wilkes-Barre, PA 18711 570-826-2357 | 54-00082A | 4911 | 221112 | 110062854870 | 05/03/2013 &nbsp;ACT | 03/04/2014 &nbsp;ACT | 2014-04-17 | 2020-02-19 | A |  | Natural gas-fired combined-cycle electric generation facility that is designed to generate up to 346 MW nominal, using a combustion turbine generator and a heat recovery steam generator that will provide steam to drive a single steam turbine generator. Each heat recovery steam generator will be equipped with a duct burner which may be utilized at time of peak power demands to supplement power output. The Turbine is rated at 2,267 MMBTU/hr HHV (2,042 MMBTU/hr LHV). The Duct burner is rated at 134.3 MMBTU/hr HHV (120 MMBTU/hr LHV). The proposed project will also include a diesel engine-driven emergency generator; a diesel engine-driven firewater pump; a multi-cell evaporative cooling tower; and associated emission control systems, tanks, and other plant equipment. |  | Turbine, COMBINED CYCLE UNIT (Siemens 5000) | 15.21 | Natural Gas | 2267 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | CO Catalyst | 2 | PPMVD | @ 15% OXYGEN | BACT-PSD | NSPS | U | 0 | U | 7.4 | LB/H | WITH DUCT BURNER | 34.1 | TPY | ON A 12-MONTH ROLLING TOTAL | 0 | 0 | N
TX-0600 | THOMAS C. FERGUSON POWER PLANT | LOWER COLORADO RIVER AUTHORITY | LLANO | TX | 7657 | USA | JOE BENTLEY | 512-473-3272 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tan Nguyen 512-239-3445 tan.nguyen@tceq.texas.gov | PSDTX1244 & 93938 | 4911 | 221112 | 110035336222 | 07/27/2011 &nbsp;ACT | 09/01/2011 &nbsp;ACT | 2011-09-02 | 2020-02-03 | B |  | Power Plant. Two natural gas-fired combined cycle turbine generators (GE 7FA) with unfired HRSG | 93938 | Natural gas-fired turbines | 15.21 | natural gas | 390 | MW | (2) GE7FA at 195 MW each, (1) steam turbine at 200 MW. Each turbine is equipped with an unfired heat recovery steam generator (HRSG), which provides steam for the steam turbine. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Natural gas, good combustion practices and oxidation catalyst | 2 | PPMVD | 3-HR AT 15% OXYGEN | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0618 | CHANNEL ENERGY CENTER LLC | CHANNEL ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX955M1, N021M1, 42179 | 4911 | 221112 | 110034690564 | 09/04/2012 &nbsp;ACT | 10/15/2012 &nbsp;ACT | 2012-10-24 | 2020-02-03 | B |  | Combustion turbine (Siemens 501F)/duct burners (475 MMBtu/hr) with heat recovery steam generator | 42179 and N021M1 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | The turbine is a Siemens 501F rated at a nominal 180 MW and the duct burner will have a maximum design heat input of 475 MMBtu/hr. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion | 2 | PPMVD | @15% O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Compliance is demonstrated during initial stack testing
TX-0619 | DEER PARK ENERGY CENTER | DEER PARK ENERGY CENTER LLC | HARRIS | TX |  | USA | MS. JAN STAVINOHA | 713-570-4814 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX979M2, N036M2, 45642 | 4911 | 221112 | 110017743254 | 08/13/2012 &nbsp;ACT | 09/26/2012 &nbsp;ACT | 2012-10-25 | 2020-02-03 | B |  | The Deer Park Energy Center is a combined cycle cogeneration facility consisting of five Siemens/Westinghouse 501F combustion turbine generators, each with a 725 MMBtu/hr duct burner and heat recovery steam generator. | 45642 and N036M2 | Combined Cycle Turbine | 15.21 | natural gas | 180 | MW | natural gas-fired combined cycle turbine generator with a heat recovery steam generator equipped with a duct burner. The turbine is a Siemens 501F rated at a nominal 180 megawatts and the DB will have a maximum design rate capability of 725 million British thermal units per hour | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion, use of natural gas | 2 | PPMVD | @15% O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Compliance demonstrated by initial stack test
TX-0620 | ES JOSLIN POWER PLANT | CALHOUN PORT AUTHORITY | CALHOUN | TX |  | USA | CHARLES HAUSMANN | 361-987-2813 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1256, 96336 | 4911 | 221112 | 110001866641 | 05/31/2012 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2012-11-14 | 2020-02-03 | B |  | Three gas-fired combined cycle turbine generators, including a steam turbine generator, to replace the existing steam boiler/turbine generator. | 96336 | Combined cycle gas turbine | 15.21 | natural gas | 195 | MW | The three combustion turbine generators (CTG) will be the General Electric 7FA, each with a maximum base-load electric power output of approximately 195 megawatts (MW). The steam turbine is rated at approximately 235 MW. This project also includes the installation of two emergency generators, one fire water pump, and auxiliary equipment. No duct burners. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion and natural gas as fuel | 2 | PPMVD | @15% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Compliance demonstrated during initial stack sampling
TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 | 221122 | Not Found | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2019-03-06 | A |  | Combinec Cycle Electric Generating Plant | 103839 | combined cycle turbine | 15.21 | natural gas | 700 | MW | The generating equipment consists of two natural gas-fired combustion turbines (CTs), each exhausting to a fired heat recovery steam generator (HRSG) to produce steam to drive a shared steam turbine generator. The steam turbine is rated at 271 MW of electric output. Three models of combustion turbines are being considered for this site: the General Electric 7FA.05, the Siemens SGT6-5000F(4), and the Siemens SGT6-5000F(5). The final selection of the combustion turbine will not be made until after the permit is issued. Plant output will range between 637 and 735 MW, depending on the model turbine selected. Duct Burners are rated at 750 MMBtu/hr each. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 2 | PPMVD | INITIAL STACK TEST, 15% OXYGEN | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0660 | FGE TEXAS POWER I AND FGE TEXAS POWER II | FGE POWER LLC | MITCHELL | TX | 79565 | USA | EMERSON FARRELL | 281-362-2830 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX1364 & 110025 | 3511 | 221112 | NOT FOUND | 10/23/2013 &nbsp;ACT | 03/24/2014 &nbsp;ACT | 2014-06-13 | 2020-03-05 | U |  | Electric Generating Utility | TCEQ Permit No. 110025 | Alstom Turbine | 15.21 | Natural Gas | 230.7 | MW | Four (4) Alstom GT24 CTGs, each with a HRSG and DBs, max design capacity 409 MMBtu/hr | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst, good combustion practices | 2 | PPMVD | CORRECTED TO 15% O2, ROLLING 3 HR AVE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Combustion Turbine | 15.21 | natural gas | 87 | MW | The exhaust heat from the turbine will be used to heat a heating medium which is used to regenerate rich amine from the acid gas removal system. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 2 | PPMVD | 1 HOUR BASED ON STACK TEST | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | (2) combined cycle turbines | 15.21 | natural gas | 650 | MW | The specific equipment includes two combustion turbines (CTs) connected to electric generators, producing between 183 and 232 MW of electricity, depending on ambient temperature and the selected CT. The two HRSGs use duct burners rated at 750 MMBtu/hr each to supplement the heat energy from the CTs. The steam from the two HRSGs is combined and routed to a single steam turbine driving a third electric generator with an electricity output capacity of 271 MW. Depending on the selected CT, total plant output at 59Â°F is between 637 MW and 735 MW. The applicant is considering three models of CT; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) Siemens SGT6-5000F(4); or (3) Siemens SGT6-5000F(5). | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 2 | PPMVD | @15% O2, 3-HR ROLLING | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0710 | VICTORIA POWER STATION | VICTORIA WLE L.P. | VICTORIA | TX |  | USA | GARY CLARK | (361) 947-9934 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | 108258 PSDTX1348 | 4911 | 221112 | 110000501154 | 02/14/2013 &nbsp;ACT | 12/01/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | The facility is currently authorized under Standard Permit No. 80878 and several Permits by Rule (PBR), including Â§106.263 for maintenance, startup, and shutdown (MSS) (PBR Registration No. 94387) and Title V Permit No. O-35. Victoria proposes to install an additional natural gas-fired turbine (GT) and HRSG with duct burners at the Victoria Station. The resulting new facility will be a combined cycle generating facility in a 2x2x1 configuration (two combustion turbines, two HRSGs with duct burners, and one steam turbine). |  | combined cycle turbine | 15.21 | natural gas | 197 | MW | General Electric 7FA.04 at 197 MW nominal ouput. The duct burners will be capable of a maximum natural gas firing rate of up to 483 MMBtu/hr (HHV). The duct burners may be fired additional hours; however, total annual firing will not exceed the equivalent of 4,375 hours at maximum capacity per duct burner. The available capacity of the existing steam turbine will be increased from 125 MW in its existing 1x1x1 configuration to approximately 185 MW in the 2x2x1 configuration. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 4 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0712 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER COMPANY | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | (205) 257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tzvi Shalem 512-239-1310 tzvi.shalem@tceq.texas.gov | 111393 PSDTX1368 | 4911 | 221112 | 110007199735 | 06/27/2013 &nbsp;ACT | 11/20/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | Southern Power Company (SPC) is proposing to construct an electric generating facility near Trinidad, Henderson County, Texas. The Trinidad Generating Facility (TGF) will include a natural gas-fired combined cycle combustion turbine generator (CTG) equipped with heat recovery steam generator (HRSG) and duct burners (DB). |  | combined cycle turbine | 15.21 | natural gas | 497 | MW | The facility will consist of a Mitsubishi Heavy Industries (MHI) J model gas fired combustion turbine nominally rated at 497 megawatts (MW) equipped with a HRSG and DB with a maximum design capacity of 402 million British thermal units per hour (MMBtu/hr). The gross nominal output of the CTG with HRSG and DB is 530 MW. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 4 | PPMVD | @15% O2 1-HR | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0713 | TENASKA BROWNSVILLE GENERATING STATION | TENASKA BROWNSVILLE PARTNERS, LLC | CAMERON | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 108411 PSDTX1350 | 4911 | 221112 | unknown | 02/21/2013 &nbsp;ACT | 04/29/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | Tenaska proposes a new electric power plant, using combined cycle gas turbine (CCGT) technology and fueled by pipeline quality natural gas. The proposed permit authorizes two CTs (2x1 CCGT), although the final design selected by Tenaska may only consist of one CT (1x1 CCGT). |  | (2) combined cycle turbines | 15.21 | natural gas | 274 | MW | Each CTG is site-rated at 274 MW gross electric output at 62Â°F ambient temperature. At this condition, two HRSGs with full duct burner firing produce enough steam to generate an additional 336 MW, for a total of 884 MW gross, or with about 5% losses, about 840 MW net electric output. Under summertime conditions, the net output is approximately 800 MW with the 2x1 CCGT configuration or about 400 MW with the 1x1 CCGT configuration. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 2 | PPMVD | @15% O2, 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0714 | S R BERTRON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | HARRIS | TX |  | USA | CRAIG ECKBERG | (713) 537-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | 102731 PSDTX1294 | 4911 | 221112 | 110034988413 | 05/10/2012 &nbsp;ACT | 12/19/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | NRG Texas is proposing to construct an additional electric power generation station at the Bertron Power Project which will generate electric power for sale on the wholesale electric market. The Bertron Power Project will include two power blocks that can be operated in combined cycle mode. |  | (2) combined cycle turbines | 15.21 | natural gas | 240 | MW | The gas turbines will be one of three options: (1) Two Siemens Model F5 (SF5) CTGs each rated at nominal capability of 225 megawatts (MW). Each CTG will have a duct fired HRSG with a maximum heat input of 688 million British thermal units per hour (MMBtu/hr). (2) Two General Electric Model 7FA (GE7FA) CTGs each rated at nominal capability of 215 MW. Each CTG will have a duct fired HRSG with a maximum heat input of 523 MMBtu/hr. (3) Two Mitsubishi Heavy Industry G Frame (MHI501G) CTGs each rated at a nominal electric output of 263 MW. Each CTG will have a duct fired HRSG with a maximum heat input of 686 MMBtu/hr. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 1 | PPMVD | @15% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Combined Cycle Turbine with Heat Recovery Steam Generator, fired Duct Burners, and Steam Turbine Generator | 15.21 | NATURAL GAS | 426 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines with HRSGs and Steam Turbine Generators | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices | 3.5 | PPMVD | 15% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404 | 4911 | 221112 | 110055066440 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2019-06-19 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | COMBUSTION TURBINE GENERATORS, (3) | 15.21 | Natural Gas | 3442 | MMBTU/H | Three (3) Mitsubishi M501 GAC combustion turbine generators with HRSG duct burners (natural gas-fired). | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst; good combustion practices. | 0.7 | PPMVD | 3 H AVG/WITHOUT DUCT BURNING | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0018 | LANGLEY GULCH POWER PLANT | IDAHO POWER COMPANY | PAYETTE | ID |  | USA |  | 2083885820 | TMAHLUM@IDAHOPOWER.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2009.0092 | 4911 | 221112 | UNKNOWN | 06/07/2009 &nbsp;ACT | 06/25/2010 &nbsp;ACT | 2010-08-09 | 2010-10-05 | A |  | ONE-ON-ONE COMBINED CYCLE PLANT CONSISTING OF (1) NATURAL GAS-FIRED COMBUSTION TURBINE (CT) AND (1) STEAM TURBINE. THE CT IS EQUIPPED WITH (1) HEAT RECOVERY STEAM GENERATOR (HRSG) AND DUCT BURNER. ANCILLARY EQUIPMENT INCLUDES (1) DIESEL-FIRED EMERGENCY GENERATOR, (1) DIESEL-FIRED FIRE PUMP, (1) WET COOLING TOWER, AND (6) DRY CHEMICAL STORAGE SILOS. |  | COMBUSTION TURBINE, COMBINED CYCLE W/ DUCT BURNER | 15.21 | NATURAL GAS (ONLY) | 2375.28 | MMBTU/H | SIEMENS SGT6-5000F COMBUSTION TURBINE (NGCT, CCGT) FOR ELECTRICAL GENERATION, NOMINAL 269 MW AND 2.1466 MMSCF/HR | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | CATALYTIC OXIDATION (CATOX), DRY LOW NOX (DLN), GOOD COMBUSTION PRACTICES (GCP) | 2 | PPMVD | 3-HR ROLLING / 15% O2 | BACT-PSD |  | N | 0 |  | 11.5 | PPMVD | 3-HR ROLLING / 15% O2 DURING LL | 0 |  |  | 0 | 0 | N |  | LIMITS APPLY TO COMBUSTION TURBINE AND DUCT BURNER COMBINED EMISSIONS. SECONDARY LIMIT APPLIES DURING STARTUP, SHUTDOWN, AND LOW-LOAD EVENTS (SU/SD/LL). EMISSION LIMIT NOT SPECIFIED DURING SU/SD (GCP ONLY).
IL-0112 | NELSON ENERGY CENTER | INVENERGY NELSON, LLC | LEE | IL | 61071-9722 | USA | JOEL SCHROEDER | 312-224-1417 | JSCHROEDER@INVENERGYLLC.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Manish Patel, Permit Analyst Manish.Patel@illinois.gov 217-785-1722 | 98080039 | 4911 | 221112 | 110007399644 | 11/19/2010 &nbsp;ACT | 12/28/2010 &nbsp;ACT | 2013-02-21 | 2020-04-16 | A |  | Natural gas-fired electic power generation facility with two &quot;combined cycle&quot; turbines followed by heat recovery steam generators (HRSG) and the capability for supplemental fuel firing in the HRSG for each turbine using duct burners. NOx emissions will be controlled by SCR and low NOx combustors. | LSP-Nelson Energy started construction pursuant to a permit issued in year 2000 for a facility that was not completed due to financial difficulties, which eventually resulted in LSP-Nelson entering bankruptcy. Substantial construction of foundations and infrastructure for all units and physical installation of one turbine were completed, including construction of HRSGs. | Electric Generation Facility | 15.21 | Natural Gas | 220 | MW each | Two combined cycle combustion turbines followed by HRSGs with capability for supplemental fuel firing in HRSG for each combustion turbine using duct burners. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 18 | (Volatile Organic Compounds (VOC)) | VOC | N |  | 4 | PPMVD @ 15% O2 | HOURLY AVG EXCEPT DURING SSM OR TUNING | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | USEPA Method 18 or 25A
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002049328 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | COMBINED CYCLE TURBINE GENERATORS (UNITS 6A &amp; 6B) | 15.21 | NATURAL GAS | 7146 | MMBTU/H | TURBINES ALSO PERMITTED TO BURN NO. 2 FUEL OIL AND ULTRA LOW SULFUR DIESEL. FUEL OIL USE IS LIMITED TO 1000 HOURS PER YEAR. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 1.4 | PPMVD @ 15% O2 | HOURLY AVERAGE W/O DUCT BURNER | BACT-PSD | OPERATING PERMIT | U | 0 | U | 3.8 | PPMVD @ 15% O2 | HOURLY AVERAGE W/ DUCT BURNER | 0 |  |  | 0 | 0 | N |  | WHILE FIRING FUEL OIL, THE BACT LIMIT FOR VOC IS 3.1 PPMVD @ 15% O2 (HOURLY AVERAGE) STARTUP/SHUTDOWN: PROGRESS THROUGH THE SU/SD EVENT AS QUICKLY AS POSSIBLE WHILE FOLLOWING THE MANUFACTURER'S RECOMMENDED PROCEDURES. SU/SD OPERATIONS LIMITED TO 1302 HR/YR. BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE).
TX-0730 | COLORADO BEND ENERGY CENTER | COLORADO BEND II POWER, LLC | WHARTON | TX |  | USA | AL HATTON | (610) 765-5316 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512) 239-1512, randy.hamilton@tceq.texas.gov | 119365, PSDTX1410, GHGPSDTX112 | 4911 | 221112 | 110041470431 | 02/24/2015 &nbsp;ACT | 04/01/2015 &nbsp;ACT | 2015-04-02 | 2020-01-31 | B |  | Combined cycle combustion turbine electric generating facility. These will be the first two General Electric (GE) Model 7HA.02 Combustion Turbines in a combined cycle power plant that uses two combustion turbines and one steam turbine using air-cooled condensers and controlled with Selective catalytic reduction (SCR) and oxidation catalyst. |  | Combined-cycle gas turbine electric generating facility | 15.21 | natural gas | 1100 | MW | combined cycle power plant that uses two combustion turbines and one steam turbine, model GE 7HA.02 | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | SCR and oxidation catalyst | 4 | PPMVD @ 15% O2 | 3-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | GE Combustion Turbine - Option 1 - Normal Operation | 15.21 | natural gas | 34000 | MMCF/YR | Option 1: Two on one configuration: 3,482 MMBtu/hr combustion turbine with 475 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices | 0.7 | PPMVD @ 15% O2 | 3 HR AV/WITHOUT DB | BACT-PSD | SIP , NSPS | U | 0 | N | 1.4 | PPMVD @ 15% O2 | 3 HR AV/WITH DB | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS.
VA-0328 | C4GT, LLC | NOVI ENERGY | USA | VA | 23030 | USA | ANAND GANGADHARAN | (248) 735-6684 | AGANGADH@NOVIENERGY.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer, Alison Sinclair: Email: Alison.Sinclair@deq.virginia.gov Phone: 804-527-5155 | 52588 | 4911 | 221112 | Not Found | 11/15/2017 &nbsp;ACT | 04/26/2018 &nbsp;ACT | 2018-05-09 | 2019-06-19 | A |  | Natural gas-fired combined cycle power plant | The permit was written with two options for the turbines: Option 1 - GE 7HA.02 Option 2 - Siemens SGT6-8000H Facility Wide Pollutants for Siemens: CO: 293.5 NOx: 295.8 PM: 253.8 SOx: 39.3 VOC: 113.7 | Siemens Combusion Turbine - Option 2 - Normal Operation | 15.21 | Natural Gas | 35000 | MMCF/YR | Option 2: Two on one configuration: 3,116 MMBtu/hr combustion turbine with 991 MMBtu/hr duct-fired HRSG. Emission limits reflect the operation of one turbine with or without duct firing. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practice | 1 | PPMVD @ 15% O2 | 3 H AV/WITHOUT DB | BACT-PSD | NSPS , SIP | N | 0 | N | 2 | PPMVD @ 15% O2 | 3 H AV/WITH DB | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS.
*VA-0332 | CHICKAHOMINY POWER LLC | CHICKAHOMINY POWER LLC | CHARLES CITY | VA | 23030 | USA | IRFAN ALI | (703) 226-0192 | IRFANKALI@BALICO.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | PAT CORBETT | (804)698-4016 | patrick.corbett@deq.virginia.gov | Permit Writer: Alison K. Sinclair Phone: (804)-527-5155 Email: Alison.Sinclair@deq.virginia.gov | 52610-1 | 4911 | 221112 | Not Found | 11/05/2018 &nbsp;ACT | 06/24/2019 &nbsp;ACT | 2019-08-07 | 2020-03-18 | A |  | Natural gas-fired combined cycle power plant, three 1 x1 configuration, 310 MW each, no duct firing, air cooled with two 84 MMBtu/hr natural gas-fired auxiliary boilers, three fuel gas heaters, an emergency generator, fire water pump, and circuit breakers. | The proposed project will be a new combined-cycle electrical power generating facility utilizing three power blocks consisting of a combustion turbine with a heat recovery steam generator (HRSG) and a reheat condensing steam turbine generator (three 1 x 1 configuration). The turbine model proposed is a MHPS M501JAC turbine. The project will have a nominal net generating capacity of 1,650 MW. The proposed fuel for the turbines is pipeline-quality natural gas. Emissions from the turbines will be controlled by the use of low carbon fuels and high efficiency design (for GHG), clean fuels and GCPs (for PM, PM10 and PM2.5), SCR and dry low NOx burners (for NOx), and oxidation catalyst (for CO and VOC). Other equipment at the site, including two natural gas-fired auxiliary boilers, three fuel gas heaters, a diesel-fired emergency fire water pump, and a diesel-fired emergency generator, are also proposed and will be subject to emission controls. Natural gas piping components and electrical circuit breakers potentially emit GHG pollutants (expressed as carbon dioxide equivalents, or CO2e) and they will also be covered in the permit. This facility is not proposing duct firing in the HRSGs and is proposing air-cooled turbines that will not require cooling towers. | Three (3) Mitsubishi Hitachi Power Systems combustion turbine generators | 15.21 | natural gas | 35000 | MMCF/YR | One on one configuration: 4,066 MMBtu/hr combustion turbine. Emission limits reflect the operation of each of the three turbines. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Controlled by an oxidation catalyst and good combustion practices (e.g. controlled fuel/air mixing, adequate temperature, and gas residence time) | 0.7 | PPMVD @ 15% O2 | 3 HR AVG | BACT-PSD | NSPS , SIP | N | 0 | N | 68.1 | T/YR | 12 MO ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Alternative emission limits apply during startup and shutdown. Compliance is based on compliance with CO limits, determined by CEMS. VOC emissions during tuning are limited by the duration of the tuning event.
CT-0157 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo james.grillo@ct.cov 860-424-3570 | 144-0023 | 4911 | 221112 | 110040589672 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-03 | 2016-02-19 | A |  | 805 MW Combined Cycle Power Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/12 months |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 1 | PPMVD @15% O2 |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 2 | PPMVD @15% O2 |  | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
CT-0158 | CPV TOWANTIC, LLC | CPV TOWANTIC, LLC | NEW HAVEN | CT | 6478 | USA | ANDREW BAZINET | 781-848-3611 | ABAZINET@CPV.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo; james.grillo@ct.gov; 860-424-3570 | 144-0024 | 4911 | 221112 | 110040589672 | 09/24/2014 &nbsp;ACT | 11/30/2015 &nbsp;ACT | 2015-12-04 | 2016-02-19 | A |  | 805 MW Combined Cycle Plant |  | Combined Cycle Power Plant | 15.21 | Natural Gas | 21200000 | MMBtu/yr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 1 | PPMVD @15% O2 |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 2 | PPMVD @15% O2 |  | 0 |  |  | 0 | 0 | N |  | Emission 1: turbine w/o duct firing Emission 2: turbine w/ duct firing
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/o Duct Firing | 15.21 | Natural Gas | 2969 | MMBtu/hr | Throughput is for turbine only | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 0.7 | PPMVD @15% O2 |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CT-0161 | KILLINGLY ENERGY CENTER | NTE CONNECTICUT, LLC | WINDHAM | CT | 6241 | USA | MARK MIRABITO | 904-687-1857 | MMIRABITO@NTEENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | James Grillo 860-424-3570 | 089-0107 | 4911 | 221112 | Not Found | 05/31/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-08-28 | 2018-05-11 | A |  | 550 MW Combined Cycle Plant |  | Natural Gas w/Duct Firing | 15.21 | Natural Gas | 2639 | MMBtu/hr | Duct burner MRC is 946 MMbtu/hr | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 1.6 | PPMVD @15% O2 |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0337 | POLK POWER STATION | TAMPA ELECTRIC COMPANY | POLK | FL | 33860 | USA | PAUL CARPINONE | 813-228-4528 | PLCARPINONE@TECOENERGY.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Leigh Ann Pell, Project Engineer Phone; 850-717-9033 | 1050233-034-AC | 4911 | 221112 | 110000365113 | 05/15/2013 &nbsp;ACT | 10/14/2012 &nbsp;ACT | 2013-08-06 | 2014-11-07 | D | http://appprod.dep.state.fl.us/air/emission/apds/listpermits.asp | The Polk Power Station consists of: a nominal 250 MW (net) solid fuel-based integrated gasification and combined cycle (Unit 1) including a sulfuric acid plant and an auxiliary boiler; four natural gas-fueled nominal 165 MW simple cycle combustion turbine-electrical generators (CTGs) designated as Units 2, 3, 4 and 5; and ancillary equipment. Units 2 and 3 are equipped with backup fuel oil-firing capability. | GHG(e) emissions: 4,307,862 | Combine cycle power block (4 on 1) | 15.21 | natural gas | 1160 | MW | Basis for the emission standard is either NSPS Subpart KKKK or Department BACT determinations. The BACT emission standards for NOX while operating in combined cycle are more stringent than the corresponding Subpart KKKK emissions standards of 15 and 42 ppmvd @15% O2 on a 30-day rolling average for natural gas and fuel oil, respectively. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | fuel Sulfur limits | 1.4 | PPMVD @15% O2 |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An initial VOC stack test shall be conducted on each CTG while firing natural gas and operating in combined cycle mode. Separate tests with duct burners are not required. Separate tests while operating in simple cycle are not required. Fuel shall not exceed 2 gr S/100 SCF of gas, 0.0015% S fuel oil.
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055426409 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Four combined cycle combution turbines | 15.21 | natural gas | 373 | MMBTU/H | Three GE, LMS6000 PF, natural gas-fired, combined cycle CTG, rated at 373 MMBtu per hour each, based on HHV and one (1) HRSG each with no Duct Burners | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | good combustion control and catalytic oxidation | 4 | PPMVD AT 15% O2 | AVE OVER STACK TEST LENGTH | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*FL-0363 | DANIA BEACH ENERGY CENTER | FLORIDA POWER AND LIGHT COMPANY | BROWARD | FL | 33314 | USA | JOHN HAMPP | 561-691-2894 | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-017-AC | 4911 | 221112 | 110002044065 | 07/27/2017 &nbsp;ACT | 12/04/2017 &nbsp;ACT | 2018-04-03 | 2018-04-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.F.ZIP | 1200 megawatt 2-on-1 combined cycle facility, natural gas-fired, with limited ULSD use. GE 7HA turbines | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.D.ZIP | 2-on-1 combined cycle unit (GE 7HA) | 15.21 | Natural gas | 4000 | MMBtu/hr | Two nominal 430 MW combustion turbines, coupled to a steam turbine generator | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | Clean fuels | 1 | PPMVD@15% O2 | FOR NATURAL GAS OPERATION | BACT-PSD |  | U | 0 | U | 2.6 | PPMVD@15% O2 | FOR OIL OPERATION | 0 |  |  | 0 | 0 | N |  | Initial stack test only; CO used as proxy thereafter
FL-0364 | SEMINOLE GENERATING STATION | SEMINOLE ELECTRIC COOPERATIVE, INC. | PUTNAM | FL | 32177 | USA | CHRIS WEBER | 813-739-1359 | CWEBER@SEMINOLE-ELECTRIC.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 1070025-028-AC / PSD-FL-443 | 4911 | 221112 | 110041142304 | 12/11/2017 &nbsp;ACT | 03/21/2018 &nbsp;ACT | 2018-04-13 | 2018-05-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/1070025.028.AC.F.ZIP | Existing fossil-fueled power plant. Two coal-fired units each rated at 736 MW. Project entails retirement of one coal-fired unit and construction of a 2-on-1 natural gas combined cycle unit. | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/1070025.028.AC.D.ZIP | 2-on-1 natural gas combined-cycle unit (GE 7HA.02) | 15.21 | Natural gas | 3514 | MMBtu/hr | Two GE 7HA.02 combustion turbines, each rated at 415 MW. Total unit capacity is approximately 1,183 MW (gross) and 1,050 MW (net). Due to netting, triggered PSD only for VOC. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 18 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation catalyst | 1 | PPMVD@15% O2 | WITHOUT DUCT BURNER FIRING | BACT-PSD |  | U | 0 | U | 2 | PPMVD@15% O2 | CT + DUCT BURNER OPERATION | 0 |  |  | 0 | 0 | N |  | Methods 18 and 25A are permitted. Compliance by stack test upon Title V permit renewal. Separate tests with and without duct burner firing are required.
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | COMBUSTION TURBINE | 15.21 | NATURAL GAS | 360 | MW | This process represents the Siemens option for the project - One Siemens SGT6-5000F5 natural gas-fired combustion turbine generator with an 820.3 MMBTUH duct burner. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES. | 5 | PPMVD@15% O2 | 30-DAY | BACT-PSD | N/A | U | 0 | U | 17 | LB/HR | 30-DAY | 0 |  |  | 0 | 0 | N
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Combined-cycle electric generating unit | 15.21 | Natural gas | 3096 | MMBtu/hr per turbine | 3-on-1 combined cycle unit. GE 7HA.02 turbines, approximately 350 MW per turbine. Total unit generating capacity is approximately 1,600 MW. Primarily fueled with natural gas. Permitted to burn the base-load equivalent of 500 hr/yr per turbine on ULSD. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | Complete combustion minimizes VOC | 1 | PPMVD@15%O2 | GAS OPERATION | BACT-PSD |  | U | 0 | U | 2 | PPMVD@15%O2 | ULSD OPERATION | 0 |  |  | 0 | 0 | N |  | Method 18 or 25A. Initial test only -- CO used as proxy thereafter.
OK-0154 | MOORELAND GENERATING STA | WESTERN FARMERS ELECTRIC COOPERATIVE | WOODWARD | OK | 73852 | USA | GERALD BUTCHER | 405-247-4341 | G_BUTCHER@WFEC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2008-302-C(M-1)PSD | 4911 | 221112 | 153-00002 | 08/22/2012 &nbsp;ACT | 07/02/2013 &nbsp;ACT | 2014-06-18 | 2016-07-29 | B |  | WFEC operates the Mooreland Generating Station to generate wholesale electricity which is transmitted over WFECâ€™s system. The facility was originally constructed in 1963. The electricity is sold in rural areas of approximately 3/4 of the state of Oklahoma and part of New Mexico. The Mooreland Generating Station currently consists of three high-pressure boilers that burn locally-produced natural gas. The three high-pressure boilers used to generate electricity and the auxiliary boiler used to heat the facility were constructed before May 31, 1972, and are considered â€œgrandfatheredâ€ from construction permitting requirements. | WFEC submitted a Prevention of Significant Deterioration (PSD) construction permit application for the proposed addition of a combined-cycle combustion turbine and associated support equipment to the existing Mooreland Generating Station | Combustion Turbine | 15.21 | Natural Gas | 360 | MW | This process represents the GE option for the project - One GE 7FA.05 natural gas-fired combustion turbine generator with an 820.5 MMBTUH duct burner. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation catalyst and good combustion practices. | 5 | PPMVD@15%O2 | 30-DAY | BACT-PSD | N/A | U | 0 | U | 17 | LB/HR | 30-DAY | 0 |  |  | 0 | 0 | N
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG1-4 Natural gas fueled combined cycle combustion turbine generators (CTG) | 15.21 | Natural gas | 2147 | MMBTU/H | FG-CTG1-4: Four natural gas fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. Two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner, a selective catalytic reduction (SCR) system, and a catalytic oxidation system. The throughput capacity is 2,147 MMBtu/hr for each CTG. The turbines are existing simple cycle turbines that will be retrofit to be combined cycle units. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Catalytic oxidation system (COS) | 2 | PPMVOL | DRY AT 15% OXYGEN | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Test protocol will specify averaging time.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-CTG/DB1-4 Natural gas fueled combined cycle combustion turbine generators; duct burner on HRSG | 15.21 | Natural gas | 2807 | MMBTU/H | Four natural gas-fired CTGs with each turbine containing a heat recovery steam generator (HRSG) to operate in combined cycle. The two CTGs (with HRSGs) are connected to one steam turbine generator. Each CTG is equipped with a dry low NOx (DLN) burner and a selective catalytic reduction (SCR) system, and a catalytic oxidation system. Additionally, the HRSG is operated with a natural gas fired duct burner during supplemental firing. The turbines are existing simple cycle turbines which will be retrofit to be combined cycle. Operational restriction is 4000 hrs/year that each DB can operate. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Catalytic oxidation system (COS) | 2 | PPMVOL | DRY AT 15% OXYGEN | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Test protocol will specify averaging time.
OH-0365 | ROLLING HILLS GENERATING, LLC |  | VINTON | OH | 45695 | USA | TODD JONAS | (402)691-9500 | TJONAS@TENASKA.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MICHAEL MALESKI | (614) 644-3613 | Michael.Maleski@epa.ohio.gov |  | P0110152 | 4911 | 221112 | 110013300052 | 06/07/2012 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2019-02-26 | 2019-06-19 | C |  | Electrical services | Note: The proposed modification was not installed. Chapter 31 major modification to convert four of the existing five simple cycle peaking units, SW501F turbines nominally rated at 209 megawatts (MW) each, to combined cycle configuration consisting of two 2x1 combined cycle blocks, the addition of four heat recovery steam generators (HRSGs), each of which will be equipped with duct burners, and two steam turbine generators. Permit includes 2 options for the units. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. Emissions increase noted below is for scenario 1. Scenario 2 = 5101.7 CO, 449.31 NOx, 346.8 PM and 600.62 VOC. | Combustion Turbines, Scenario 1 (4, identical) (P001, P002, P004, P005) | 15.21 | Natural gas | 2022 | MMBTU/H | Scenario 1 only. Other scenario added as separate process. Siemens Westinghouse Power Corp. SW501F, (Scenario 1: 200 MW, with 2022 MMBtu/hr input & 550 MMBtu/hr duct burner. Scenario 2: 207.5 MW with 2144 MMbtu/hr input & 550 MMBtu/hr duct burner.) combined cycle natural gas fired turbine with Dry Low-NOX combusters, SCR and duct burner. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices along with clean fuels | 611.38 | T/YR | PER ROLLING 12 MONTH PERIOD. SEE NOTES. | BACT-PSD |  | U | 0 | U | 0 |  | SEE NOTES. | 1.4 | PPM | BY VOLUME, DRY AT 15% O2. SEE NOTES. | 0 | 0 | N |  | Limits are for single turbine except as noted. 1.4 ppm by volume, dry basis (ppmvd) at 15% oxygen, 3-hour average, turbine only without duct burners. 3.1 ppm by volume, dry basis (ppmvd) at 15% oxygen, 3-hour average, turbine with duct burners. 1004 lb/cold startup, 440 lb/hot startup, 740 lb/warm startup and 261 lb/shutdown. 611.38 t/yr per rolling 12 month period total for all 4 turbines.
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | FOUR (4) NATURAL GAS COMBINED CYCLE COMBUSTION TURBINES - START UP/SHUTDOWN CYCLE | 15.21 | NATURAL GAS | 2300 | MMBTU/H | A STARTUP/SHUTDOWN CYCLE IS A PAIR OF SUBSEQUENT SHUTDOWN AND STARTUP EVENTS (I.E., ONE STARTUP FOLLOWED BY ONE SHUTDOWN REPRESENTS ONE STARTUP/SHUTDOWN CYCLE). | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 22 | TONS | 12 CONSECUTIVE MONTH PERIOD | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LIMIT TWO IS COMBINED EMISSIONS FROM CCCT1 THROUGH CCCT4 FUR THE DURATION OF THE COMBINED STARTUP/CHUTDOWN EVENTS