## PermitSearchResults (47)
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
FL-0354 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-013-AC | 4911 | 221112 | 110002044065 | 04/20/2015 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2016-02-17 | 2016-07-06 | D | https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | Re-affirmed BACT determinations in Permit No. 0110037-011-AC. Also, new GHG BACT determination. Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2100 | MMBtu/hr (approx) | Five simple cycle GE 7F.05 turbines. Max of 3390 hours per year per turbine. Of the 3390 hours per year, up to 500 hour may be on ULSD fuel oil. | Carbon Dioxide | Other - CO2 CEMS or fuel use monitoring | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | Use of natural gas with restricted use of ULSD as backup fuel | 1372 | LB/MWH | NAT GAS OPERATION, 12- OR 36- MO ROLLING | BACT-PSD | NSPS | U | 0 | U | 1871 | LB/MWH | ULSD OPERATION, 12- OR 36- MO ROLLING | 0 |  |  | 0 | 0 | N |  | Composite standard weighted by use of each fuel during the compliance period. The five turbines are treated collectively for the first 36 months, 12-month rolling average. Thereafter, the turbines demonstrate compliance individually, on a 36-month rolling average.
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER | 15.11 | NATURAL GAS | 92.5 | MMBTU/H | NATURAL GAS USAGE SHALL NOT EXCEED 18.14 MMCF/YEAR. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN, USE NATURAL GAS | 59.61 | T/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER | 15.11 | NATURAL GAS | 92.5 | MMBTU/H | NATURAL GAS USAGE SHALL NOT EXCEED 18.14 MMCF/YEAR. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN, USE NATURAL GAS | 59.61 | TON/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0264 | MONTPELIER GENERATING STATION | AES OHIO GENERATION, LLC | WELLS | IN | 46781 | USA | DREW PARKER | 9373314993 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: MADHURIMA MOULIK 317-233-6663 MMOULIK@IDEM.IN.GOV SECTION CHIEF: JASON KRAWCZYK 317-234-5174 | 179-37209-00026 | 4911 | 221112 | 110021089061 | 05/23/2016 &nbsp;ACT | 01/06/2017 &nbsp;ACT | 2017-07-07 | 2017-11-17 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/37209F.PDF | COMBUSTION TURBINES |  | PRATT &amp; TWIN-PAC SIMPLE CYCLE TURBINES | 15.11 | NATURAL GAS | 270.9 | MMBTU/H | NO. 2 DIESEL OIL BACKUP FUEL | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | NATURAL GAS AS PRIMARY FUEL; GOOD COMBUSTION PRACTICES | 118 | LB/MMBTU | FOR NATURAL GAS | BACT-PSD |  |  | 0 |  | 162 | LB/MMBTU | FOR FUEL OIL | 0 |  |  | 0 | 0 | N |  | TOTAL CO2 FOR 8 TURBINES LIMITED TO 606,264 TONS PER 12 MONTH PERIOD; EACH TURBINE LIMITED TO 500 HOURS FUEL OIL COMBUSTION PER 12 MONTH PERIOD
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110000801614 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine with Duct Burner firing natural gas | 15.11 | Natural Gas | 0 |  |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | Use of natural gas which is a clean burning fuel | 888 | LB/MW-H | CONSECUTIVE 12 MONTH ROLLING MONTHLY | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO2 <= 888 lb/MW-hr (gross output) for turbine and its associated duct burner including MWhs from ULSD firing and steam turbine
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110000801614 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine without Duct Burner Firing Natural Gas | 15.11 | Natural Gas | 28169501 | MMBTU/YR | Natural Gas Usage: <=28,169,501 MMBtu/year which includes maximum ultra low sulfur distillate oil usage of =2,371,943 MMBTU/year | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 888 | LB/MW-H | CONSECUTIVE 12 MONTH ROLLING MONTHLY | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO2 <= 888 lb/MW-hr (gross output) for turbine and its associated duct burner including MWhs from ULSD firing and steam turbine
NY-0106 | GREENIDGE STATION | GREENIDGE GENERATION LLC | YATES | NY | 14441-0187 | USA |  | 315-536-2359 |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov |  | 8-5736-00004/00017 | 4911 | 221112 | 110000327619 | 09/07/2016 &nbsp;ACT | 09/07/2016 &nbsp;ACT | 2017-08-30 | 2017-09-28 | C | http://www.dec.ny.gov/chemical/32249.html | Greenidge Generation LLC has submitted a revised application for a Title V Air Permit in accordance with the requirements of Title 6 of the New York compilation of Codes, Rules, and Regulations, Part 201-6 (6 NYCRR Part 201-6). The application is for conversion of the Greenidge Electricity Generating Station, located in the Town of Torrey, Yates County to operate primarily on natural gas with up to 19% biomass co-firing. Greenidge Station is comprised of Unit 4, which includes a Combustion Engineering, tangentially-fired dry bottom boiler (Boiler No. 6) with a maximum heat input rating of 1,117 MMBtu/hr, and a steam generating turbine with a maximum rated output of 107 Megawatts (MW) of electricity. The facility is equipped with a suite of air pollution control (both pre-combustion and post-combustion) systems to control pollutant nitrogen oxides, carbon monoxide, and particulate matter (PM, PM10 and PM2.5) emissions from facility operations. Greenhouse gases will be reduced substantially primarily by the use of cleaner fuels. Under the proposal, Unit 4 will not burn coal or fuel oil any longer. | Also NAICS 221117 - biomass with wood | Turbine - natural gas | 15.11 | natural gas | 107 | MW |  | Carbon Dioxide | Other - 40 CFR 60 App A | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 130.17 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0113 | EDGEWOOD ENERGY LLC | EDGEWOOD ENERGY LLC | SUFFOLK | NY | 11717 | USA |  | 631-643-1560 |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 1 631-444-0200 | 1-4728-03244/00005 | 4911 | 221112 | 110038105993 | 07/09/2013 &nbsp;ACT | 07/09/2013 &nbsp;ACT | 2017-09-14 | 2017-09-28 | C | http://www.dec.ny.gov/chemical/32249.html | Edgewood Energy LLC is a power is a simple cycle combustion turbine plant located in Edgewood, Suffolk County, New York that contains two GE LM6000 combustion turbines that fire only natural gas. The facility has an optimum electrical output of 95 megawatts (MW) firing only natural gas. This electrical output represents an increase from the 79.9 MW limit. This increase was allowed through a declaratory ruling that the Department of Public Service issued. The facility is subject to PSD for greenhouse gases (GHGs) and PM-10 emissions. The facility is not subject to non-attainment NSR for any non-attainment contaminant. |  | Turbines - NG | 15.11 | natural gas | 0 |  |  | Carbon Dioxide | Other - 40 CFR 75 | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 1300 | LB/MWH |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
SC-0161 | DUKE ENERGY CAROLINAS LLC, W.S. LEE STEAM STATION |  | ANDERSON | SC | 29627 | USA |  | SYSNULL |  | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MR. DENNIS CAMIT | (803)898-4284 | camitdr@dhec.sc.gov | SHEILA WATTS (803) 898-4123 | 0200-0004-CG | 4911 | 221112 | 110004937864 | 01/16/2013 &nbsp;ACT | 02/19/2014 &nbsp;ACT | 2015-08-25 | 2017-07-24 | B |  |  |  | COMBINED CYCLE COMBUSTION TURBINES (SIEMENS) | 15.11 |  | 0 |  | THE FACILITY PLANS TO INSTALL EITHER TWO GE 7FA.05 OR TWO SIEMENS SGT-5000F(5) NATURAL GAS FIRED COMBUSTION TURBINE GENERATORS, EACH EQUIPPED WITH A DUCT-FIRED HEAT RECOVERY STEAM GENERATOR. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | ENERGY EFFICIENT PROCESSES, PRACTICES, AND DESIGN | 1000 | LB/MWH CO2 | 12-OPERATING MONTH ROLLING AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 1000 | LB/MWH CO2 | 12-OPERATING MONTH ROLLING AVERAGE | 0 | 0 | N |  | CO2 EQUIVALENT PSD LIMIT IS 1,000 POUNDS OF CO2 PER GROSS MEGAWATT-HOUR (LB CO2/MWH) ON A 12-OPERATING MONTH ROLLING AVERAGE FOR THE GROSS ELECTRIC OUTPUT FROM ONE COMBUSTION TURBINE PLUS THE COMMON STEAM TURBINE GENERATOR.
SC-0161 | DUKE ENERGY CAROLINAS LLC, W.S. LEE STEAM STATION |  | ANDERSON | SC | 29627 | USA |  | SYSNULL |  | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MR. DENNIS CAMIT | (803)898-4284 | camitdr@dhec.sc.gov | SHEILA WATTS (803) 898-4123 | 0200-0004-CG | 4911 | 221112 | 110004937864 | 01/16/2013 &nbsp;ACT | 02/19/2014 &nbsp;ACT | 2015-08-25 | 2017-07-24 | B |  |  |  | COMBINED CYCLE COMBUSTION TURBINES (GE) | 15.11 |  | 0 |  | THE FACILITY PLANS TO INSTALL EITHER TWO GE 7FA.05 OR TWO SIEMENS SGT-5000F(5) NATURAL GAS FIRED COMBUSTION TURBINE GENERATORS, EACH EQUIPPED WITH A DUCT-FIRED HEAT RECOVERY STEAM GENERATOR. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | ENERGY EFFICIENT PROCESSES, PRACTICES, AND DESIGN | 1000 | LB/MWH CO2 | 12-OPERATING MONTH ROLLING AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 1000 | LB/MWH CO2 | 12-OPERATING MONTH ROLLING AVERAGE | 0 | 0 | N |  | CO2 EQUIVALENT PSD LIMIT IS 1,000 POUNDS OF CO2 PER GROSS MEGAWATT-HOUR (LB CO2/MWH) ON A 12-OPERATING MONTH ROLLING AVERAGE FOR THE GROSS ELECTRIC OUTPUT FROM ONE COMBUSTION TURBINE PLUS THE COMMON STEAM TURBINE GENERATOR.
*TX-0638 | MONT BELVIEU COMPLEX | ENTERPRISE PRODUCTS OPERATING LLC | CHAMBERS | TX | 77580 | USA | TERRY HURLBURT | 713-381-6595 | SNOLAN@EPROD.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | PSD-TX-1286-GHG | 1321 | 325110 |  | 06/06/2012 &nbsp;ACT | 10/12/2012 &nbsp;ACT | 2013-10-25 | 2015-03-16 | D |  | the facility will add two new natural gas liquids (NGL) fractionation (Eagleford Fractionation) units and a deisobutanizer (DIB) unit at the Enterprise Mont Belvieu Complex in Mont Belvieu, Texas. The Eagleford Fractionation units will be capable of separating an NGL feed into separate ethane, propane, butane, and gasoline fractions. Each fractionation unit will have a nominal feed capacity of 110,000 barrels per day. The DIB unit will be capable of separating isobutene and normal butane from mixed butane streams. The Eagleford Fractionation and DIB unit will consist of two fractionation unit deethanizer distillation columns, two fractionation unit debutanizer distillation columns, two depropanizer colwnns, two hot oil heaters, two regenerant gas heaters, one flare, one deisobutanizer distillation column, and supporting equipment. |  | 2 Regenerant Heaters | 15.11 |  | 28.8 |  | 2 Regenerant Heaters (Combustion Units). Each unit has a maximum design beat input rate of28.5 MMBTU/HR and fired with natural gas, tired with natural gas. HR15.002A and HR15.002B. | Carbon Dioxide | Other - equation C-2a in 40 CPR Part 98 Subpart C | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 14858 | T/YR | 12-MONTH ROLLING BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Minimum Thermal Efficiency of 85%. The emission rate is for each of the two regenerant heaters.
TX-0761 | SR BERTRON ELECTRIC GENERATING STATION | NRG TEXAS POWER | HARRIS | TX |  | USA | CRAIG ECKBERT | (713) 795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, (512) 239-5220 Ruth.Alvirez@tceq.texas.gov | GHGPSDTX104, 102731, PSDTX129 | 4911 | 221112 | 110034988413 | 03/06/2015 &nbsp;ACT | 09/15/2015 &nbsp;ACT | 2015-08-25 | 2016-07-06 | B |  | Electric Generating Utility: The project will consist of two gas fired combustion turbines (CTGs) each equipped with a supplementary fired [duct burners (DBs)] heat recovery steam generator (HRSG). The CTGs and DBs are fueled with pipeline quality natural gas. The CTGs will operate in simple cycle and combined cycle modes. The gas turbines will be one of four options. |  | Simple cycle turbines greater than 25 megawatts (MW) firing natural gas | 15.11 | natural gas | 359 | MW | 4 options: General Electric (GE) 7HA 359 MW GE 7FA â€“ 215 MW Siemens SF5 (SF5) â€“ 225 MW Mitsubishi 501G (MHI510G) â€“ 263 MW | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 1232 | LB /MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 40 Code of Federal Regulations, Part 60 (40 CFR Part 60), Subpart TTTT
TX-0762 | CEDAR BAYOU ELECTRIC GENERATING STATION | NRG TEXAS POWER | CHAMBERS | TX |  | USA | CRAIG ECKBERT | (713) 795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, (512) 239-5220 Ruth.Alvirez@tceq.texas.gov | GHGPSDTX102, 105810, PSDTX1308 | 4911 | 221112 | 110015743301 | 03/06/2015 &nbsp;ACT | 09/15/2015 &nbsp;ACT | 2015-08-25 | 2016-07-06 | B |  | Electric Generating Utility: The project will consist of two gas fired combustion turbines (CTGs) each equipped with a supplementary fired [duct burners (DBs)] heat recovery steam generator (HRSG). The CTGs and DBs are fueled with pipeline quality natural gas. The CTGs will operate in simple cycle and combined cycle modes. The gas turbines will be one of four options. |  | Simple cycle turbines greater than 25 megawatts (MW) | 15.11 | natural gas | 359 | MW | 4 turbine options General Electric 7HA â€“ 359 MW GE 7FA â€“ 215 MW Siemens SF5 (SF5) â€“ 225 MW Mitsubishi 501G (MHI510G) â€“ 263 MW | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 1232 | LB CO2/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 40 Code of Federal Regulations , Part 60 (40 CFR Part 60), Subpart TTTT
TX-0780 | VAN ALSTYNE ENERGY CENTER | NAVASOTA NORTH PEAKERS OPERATING COMPANY I, LLC. | GRAYSON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | GHGPSDTX119, 121051, PSDTX1418 | 4911 | 221112 | UNKNOWN | 08/12/2015 &nbsp;ACT | 01/13/2016 &nbsp;ACT | 2016-01-07 | 2016-07-06 | A |  | Navasota North Peakers Operating Company I, LLC. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 megawatt (MW) each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | mw | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 1461 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
WV-0026 | WAVERLY FACILITY | PLEASANTS ENERGY, LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 304-665-4201 | GERALD.GATTI@GDFSUEZNA.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0034 | 4911 | 221112 | 110010376734 | 04/18/2016 &nbsp;ACT | 01/23/2017 &nbsp;ACT | 2017-03-21 | 2018-05-01 | D | http://www.dep.wv.gov/daq/Documents/January 2017 Permits and Evals/073-00022_PERM_R14-0034.pdf | 300 MW, natural gas fired, simple cycle peaking power facility | In this permitting action PSD only applies to the modified combustion turbines based on the relaxation of an original synthetic minor permit issued in 1999. Project also involves previous installation of turbo-charging. All BACT emission limits are given without turbocharging and startup/shutdown emissions are not included. Please contact above engineer for more information. There are two identical turbines but only one is listed. | GE Model 7FA Turbine | 15.11 | Natural Gas | 1571 | mmbtu/hr | There are two identical units at the facility. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | Use of Natural Gas, Selection of GE7FA | 1300 | LB/MW-HR | NATURAL GAS | BACT-PSD |  | U | 0 | U | 1900 | LB/MW-HR | FUEL OIL | 1300 | LB/MW-HR | NATURAL GAS | 0 | 0 | N |  | Additional emission limits are in the permit for use of turbocharging and startup/shutdown emissions. Please contact if need additional information.
CA-1223 | PIO PICO ENERGY CENTER | PIO PICO ENERGY CENTER, LLC | OTAY MESA | CA | 92154 | USA | GARY CHANDLER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SD 11-01 | 4911 | 221112 | 110045006943 | 06/14/2012 &nbsp;ACT | 11/19/2012 &nbsp;ACT | 2013-03-05 | 2014-01-28 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | CONSTRUCTION OF THREE GENERAL ELECTRIC (GE) LMS100 NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 100 MW EACH. THE PROJECT WILL HAVE AN ELECTRICAL OUTPUT OF 300 MW. | NOTE: PERMIT ISSUED 11/19/2012. ENVIRONMENTAL APPEALS BOARD REMANDED THE PM BACT ANALYSIS TO REGION 9 ON 8/2/2013. FINAL PERMIT ISSUED ON 2/28/2014. ONE PETITION FILED IN 9TH CIRCUIT FEDERAL COURT CHALLENGING THE FINAL PERMIT DECISION. THIS LAWSUIT WAS DISMISSED ON 6/17/2014 IN RESPONSE TO PETITIONERSâ€™ MOTION FOR VOLUNTARY DISMISSAL. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.11 | NATURAL GAS | 300 | MW | Three simple cycle combustion turbine generators (CTG). Each CTG rated at 100 MW (nominal net). | Carbon Dioxide Equivalent (CO2e) | Other - EPA METHOD 1-4, 3A | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1328 | LB/MW-H | GROSS OUTPUT | BACT-PSD |  | U | 0 | U | 720 | H | ROLLING OPERATING HOUR AVG | 0 |  |  | 0 | 0 | N
CO-0075 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO |  | USA | MARK LUX | 303-568-3241 | MARK.LUX@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 13PB2245 | 4911 | 221112 | 110058377830 | 09/10/2013 &nbsp;ACT | 05/30/2014 &nbsp;ACT | 2014-10-24 | 2016-02-19 | B |  | Power generation facility |  | Turbine - simple cycle gas | 15.11 | natural gas | 375 | MMBTU/H | One (1) General Electric, simple cycle, gas turbine electric generator, Unit 6 (CT08), model: LM6000, SN: N/A, rated at 375 MMBtu per hour. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Control | 1600 | LB/MW H GROSS | ROLLING 365-DAY AVE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 193555 | TONS PER YEAR | ROLLING 365-DAY AVE | 0 |  |  | 0 | 0 | N
FL-0355 | FORT MYERS PLANT | FLORIDA POWER & LIGHT (FPL) | LEE | FL | 33905 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0710002-022-AC | 4911 | 221112 | 110000365248 | 05/12/2015 &nbsp;ACT | 09/10/2015 &nbsp;ACT | 2016-03-10 | 2016-07-06 | D | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.80831.1]&[profile=Permitting_Authorization] | Electric power plant, consists of a 6-on-2 combined-cycle unit (Units 2A through 2F) and two modern simple-cycle combustion turbines. Primary fuel is natural gas. Also includes 12 gas turbines (63 MW each) for peaking, introduced into service in 1974. This project entails decommissioning 10 of the 12 peaking turbines. They will be replaced with two new GE 7F.05 turbines, each with nominal capacity of 200 MW | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0710002.022.AC.D.ZIP | Combustion Turbines | 15.11 | Natural gas | 2262.4 | MMBtu/hr gas | Two GE 7F.05 turbines, approximately 200 MW each. Natural-gas is primary fuel. Permitted 3390 hr/yr of operation, of which no more than 500 hr may be on fuel oil. Dry Low-NOx, with wet injection for oil firing. | Carbon Dioxide Equivalent (CO2e) | Other - Fuel-use monitoring, or CO2 CEMS | (Greenhouse Gasses (GHG)) | CO2e | P | Use of low-emitting fuel and efficient turbine | 1374 | LB CO2E / MWH | FOR NATURAL GAS OPERATION | BACT-PSD | NSPS | U | 0 | U | 1874 | LB CO2E / MWH | FOR ULSD OPERATION | 0 |  |  | 0 | 0 | N |  | GHG standard is a weighted average of standards for natural gas operation and fuel oil operation. Turbines grouped together for first 36 months, 12-month rolling average. After 36 months, each individual turbine is subject to limit on a 36-month rolling average.
IL-0121 | INVENERGY NELSON EXPANSION LLC | INVENERGY | LEE | IL | 61058 | USA | GORDON GRAY | 312-582-1290 | GGRAY@INVENERGY.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Bob Smet; 217-785-9250; robert.smet@illinois.gov | 15060042 | 4911 | 221112 | Not Found | 07/28/2016 &nbsp;ACT | 09/27/2016 &nbsp;ACT | 2017-01-27 | 2017-04-28 | B | https://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/9dbc452815081576862580b2006897b4/$FILE/ATT4AK5N.pdf/15060042.pdf | Peaking facility at an existing major source. The expansion will consist of two simple cycle combustion turbines and a fuel heater. |  | Two Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 190 | MW | Two simple cycle combustion turbines used for peaking purposes and fired primarily on natural gas with ULSD as a secondary fuel. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Turbine-generator design and proper operation | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The GHG emissions of each affected turbine, as carbon dioxide equivalents (CO2e), as an annual average of 12 consecutive operating months, rolled monthly, shall not exceed a limit that is calculated as follows. Compliance with this limit shall be determined using the relevant procedures for quantification of GHG emissions in 40 CFR Part 98 Subpart D. E = {(Gng x Rng) + (Gulsd x Rulsd} Ã· (Gng + Gulsd) Where E = Limit on GHG emissions, as CO2e, pounds/MW-hr gross electrical output, annual average, rolled monthly. Gng = Gross electrical output of the affected turbine-generator from natural gas, in MW-hr, including output in hours when ultra-low-sulfur diesel provides less than 50 percent of the heat input of the turbine. Gulsd = Gross electrical output, of the affected turbine generator from ultra-low-sulfur diesel, in MW-hr, including output in hours when ultra-low-sulfur diesel provides 50 percent or more of the heat input of the turbine. Rng = 1367 lb/MW-hr gross output (allowable rate for natural gas). Rulsd = 1934 lb/MW-hr gross output (allowable rate for ultra-low-sulfur diesel).
KY-0104 | CASH CREEK GENERATING STATION | CASH CREEK GENERATION, L.L.C | HENDERSON | KY | 41047 | USA | MIKE MCINNUS | 502 357 9907 | MMCINNIS@ERORA.COM | 4 | KY001 | KENTUCKY DEP, DIV FOR AIR QUALITY | MR. RICK SHEWEKAH, MGR | (502)564-3999 | Sreenivas.Kesaraju@ky.gov |  | V-14-011 | 4911 | 221112 | 110042328479 | 06/18/2014 &nbsp;ACT | 06/10/2015 &nbsp;ACT | 2017-02-28 | 2017-04-28 | A |  | natural gas fired combined cycle power plant |  | Combined cycle combustion turnbine with HRSG and duct firing | 15.11 | Natural gas pipeline quality | 849 | MW | Two CT with HRSGs with duct burner Max fuel input for CTs and HRSGs 6,714 mmBtu/hr HHV Max Gross output 849 MW at 0F | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Combust only pipeline quality natural gas | 884 | LB/MWH | 12 MONTH ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Refrigeration Compressor Turbines (16) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion/operating practices and fueled by natural gas - use GE LM2500+G4 turbines | 4872107 | TONS/YR | ANNUAL MAXIMUM FROM THE FACILITYWIDE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO2(e)
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Generation Turbines (2) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion/operating practices and fueled by natural gas - use GE LM2500+G4 turbines | 4872107 | TONS/YR | ANNUAL MAXIMUM FROM THE FACILITYWIDE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO2(e)
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Gas Turbines (8 units) | 15.11 | natural gas | 333 | mm btu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion/operating/maintenance practices and fueled by natural gas; use intake air chiller | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110029511883 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices and fueled by natural gas; Use high thermal efficiency turbines | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0043 | PERRYMAN GENERATING STATION | CONSTELLATION POWER SOURCE GENERATION, INC. | HARFORD | MD | 21130 | USA | BILL LEEDY | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9136 | 4911 | 221119 | 110000499559 | 07/01/2014 &nbsp;ACT | 07/01/2014 &nbsp;ACT | 2015-07-31 | 2016-07-25 | B |  | 120 MEGAWATT SIMPLE CYCLE NATURAL GAS FIRED POWER PLANTPERRYMAN 6 PROJECT-WIDE EMISSION LIMITS: PM10 = 43.0 TONS/YR PM2.5 = 43.0 TONS/YR NOX = 58.5 TONS/YR CO2E = 430,210 TONS/YR | PERRYMAN 6 PROJECT-WIDE EMISSION LIMITS: PM10 = 43.0 TONS/YR PM2.5 = 43.0 TONS/YR NOX = 58.5 TONS/YR CO2E = 430,210 TONS/YR | (2) 60-MW SIMPLE CYCLE COMBUSTION TURBINES, FIRING NATURAL GAS | 15.11 | NATURAL GAS | 120 | MW | (2) 60-MEGAWATT PRATT & WHITNEY GAS TURBINE GENERATOR PACKAGE | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | USE OF NATURAL GAS. ENERGY EFFICIENCY DESIGN - USE OF INLET FOGGING/WET COMPRESSION, INSULATION BLANKETS TO REDUCE HEAT LOSS, AND FUEL GAS PREHEATING. | 1394 | LB CO2E/MWH | 12-MONTH ROLLING, EXCLUDING SU/SD | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 2 COMBUSTION TURBINES | 15.11 | NATURAL GAS | 130 | MW | TWO GENERAL ELECTRIC (GE) FRAME 7EA COMBUSTION TURBINES (CTS) WITH A NOMINAL NET 87.2 MEGAWATT (MW) RATED CAPACITY, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), EQUIPPED WITH DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION SYSTEM (SCR), AND OXIDATION CATALYST | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | HIGH EFFICIENCY GE 7EA CTS WITH HRSGS EQUIPPED WITH DLN1 COMBUSTORS AND EXCLUSIVE USE OF FACILITY PROCESS FUEL GAS OR PIPELINE QUALITY NATURAL GAS | 117 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 117 LB/MMBTU EMISSION LIMIT IS PER TURBINE
ND-0028 | R.M. HESKETT STATION | MONTANA-DAKOTA UTILITIES CO. | MORTON | ND | 58554 | USA | ABBIE KREBSBACH | (701) 222-7844 | ABBIE.KREBSBACH@MDU.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Primary contact is Tom Bachman at (701) 328-5188. | PTC13016 | 4911 | 221112 | 110022356591 | 11/07/2012 &nbsp;ACT | 02/22/2013 &nbsp;ACT | 2013-04-01 | 2017-04-28 | B |  | Addition of a natural gas-fired turbine (Unit 3) to an exisiting coal-fired power plant. The turbine will be used for supplying peak power and is rated at 986 MMBtu/hr and 88 MWe at average site conditions. |  | Combustion Turbine | 15.11 | Natural gas | 986 | MMBTU/H | Turbine is a GE Model PG 7121 (7EA) used as a peaking unit. | Carbon Dioxide Equivalent (CO2e) | Other - Methods in 40 CFR 75.10(a)(3) | (Greenhouse Gasses (GHG)) | CO2e | N |  | 413198 | TONS/12 MONTH | 12 MONTH ROLLING TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ND-0029 | PIONEER GENERATING STATION | BASIN ELECTRIC POWER COOPERATIVE | WILLIAMS | ND |  | USA | JERRY MENGE | 7012230441 | JMENGE@BEPC.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact. | PTC 13037 | 4911 | 221112 | 110058380238 | 02/19/2013 &nbsp;ACT | 05/14/2013 &nbsp;ACT | 2013-06-19 | 2016-11-03 | B |  | Three GE LM6000 PC SPRINT natural gas fired turbines used to generate electricity for peak periods. | The permit was for the addition of 2 turbines to the station. Since a synthetic minor limit was relaxed for the first unit, BACT was required for all three turbines. | Natural gas-fired turbines | 15.11 | Natural gas | 451 | MMBTU/H | Rating is for each turbine. | Carbon Dioxide Equivalent (CO2e) | Other - Methods in 40 CFR 75.10(a)(3) | (Greenhouse Gasses (GHG)) | CO2e | N |  | 243147 | T/12 MON ROLL TOTAL | 12 MONTH ROLLING TOTAL/EACH UNIT | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Turbines are GE LM6000 PC SPRINT units that burn natural gas with a HHV of 1200 Btu/scf. RBLC Staff: Original Emis Limit 1 Units were Numeric Limit - &lsquo;&lsquo;TONS&lsquo;&lsquo; and Avg Time/Condition - &lsquo;&lsquo;12 MONTH ROLLING TOTAL/EACH UNIT&lsquo;&lsquo; The Emission Units are usually &lsquo;&lsquo;mass unit PER time unit&lsquo;&lsquo;. Separating them out makes understanding limit difficult for the users. The units were combined. The corrected entry is: Numeric Limit - &lsquo;&lsquo;T/12 MON ROLL TOTAL&lsquo;&lsquo; Avg Time/Condition - &lsquo;&lsquo;12 MONTH ROLLING TOTAL/EACH UNIT&lsquo;&lsquo;
ND-0030 | LONESOME CREEK GENERATING STATION | BASIN ELECTRIC POWER COOP. | MCKENZIE | ND | 58831 | USA | JERRY MENGE | (701)223-0441 |  | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact at (701) 328-5188. | PTC 13049 | 4911 | 221112 | 110057111003 | 04/05/2013 &nbsp;EST | 09/16/2013 &nbsp;ACT | 2013-09-24 | 2017-06-28 | B |  | Three natural gas fired simple cycle turbines used to generate electricity for peak power demand. The turbines are GE LM6000 PF Sprint units with a nominal capacity of 45 MW each. |  | Natural Gas Fired Simple Cycle Turbines | 15.11 | Natural gas | 412 | MMBTU/H | The heat input is for a single unit. | Carbon Dioxide Equivalent (CO2e) | Other - methods in 40 CFR 75.10(a)(3) | (Greenhouse Gasses (GHG)) | CO2e | P | High efficiency turbines | 220122 | TONS | 12 MONTH ROLLING TOTAL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is for each unit.
NY-0103 | CRICKET VALLEY ENERGY CENTER | CRICKET VALLEY ENERGY CENTER LLC | USA | NY | 12522-0407 | USA |  | 845-877-0596 | INFO@CRICKETVALLEY.COM | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-1326-00275/00009 | 4911 | 221112 | 110043340364 | 02/03/2016 &nbsp;ACT | 02/03/2016 &nbsp;ACT | 2017-08-24 | 2017-09-28 | A | http://www.dec.ny.gov/chemical/32249.html | Cricket Valley Energy Center LLC (CVEC) constructed the Cricket Valley Energy Center (the Facility), a nominal net 1,000-megawatt (MW) combined-cycle gas turbine electric generating facility, on a site located in Dover, Dutchess County, New York. The Facility consists of three General Electric (GE) Model 7FA.05 combustion turbine generators (CTGs) operating in combined-cycle mode with supplemental firing of the heat recovery steam generators (HRSGs); natural gas will be the sole fuel fired in the CTGs and duct burners. The Facility will include a natural gas-fired auxiliary boiler, four ultra-low sulfur distillate (ULSD) fired black-start generator engines and a ULSD-fired emergency fire pump engine. In addition to the air emitting equipment, the Facility will include three steam turbine generators (STGs), an air cooled condenser (ACC) and associated auxiliary equipment and systems. Each combined cycle generating unit consisting of the CTG, HRSG and STG will be exhausted through its own stack. Air emissions from the proposed Facility primarily consist of products of combustion from the CTGs, HRSG duct burners, and ancillary combustion sources. Dutchess County is designated as in attainment with respect to the National Ambient Air Quality Standards (NAAQS) for all criteria pollutants with the exception of ozone. Based upon the potential to emit (PTE) estimates, the Facility is subject to Prevention of Significant Deterioration (PSD) requirements for emissions of carbon monoxide (CO); nitrogen oxides (NOx); particulate matter (PM) with a diameter equal to or less than 10 microns (PM10), PM with a diameter equal to or less than 2.5 microns (PM2.5); greenhouse gases (GHG); sulfuric acid mist (H2SO4); and volatile organic compounds (VOC). In accordance with the NYSDECâ€™s Nonattainment New Source Review (NNSR) permitting program, the Facility is also subject to NNSR for emissions of NOx and VOC. |  | Turbines and duct burners | 15.11 | natural gas | 228 | mw |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | max heat rate 7,604 btu/kw-h HHV without duct firing good combustion practice and burning natural gas | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | EPA approved method
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | GE LMS-100 combustion turbines, simple cycle with water injection | 15.11 | natural gas | 1690 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Thermal efficiency Clean fuels | 1707 | LB OF CO2 /GROSS MWH | 365-DAY ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0305 | SHELL CHEM APPALACHIA/PETROCHEMICALS COMPLEX | SHELL CHEMICAL APPALACHIA | BEAVER | PA | 15061-2210 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 04-00740A | 2821 | 325110 | 110060029115 | 05/01/2014 &nbsp;ACT | 06/18/2015 &nbsp;ACT | 2017-06-05 | 2017-07-12 | A |  | The plan approval will allow the construction and temporary operation of seven (7) 620 MMBtu/hr ethane cracking furnaces fired primarily by tail gas and natural gas for the production of approximately 1.5 million metric tons/year of polyethylene. Byproducts from the ethylene production include coke residue/tar, light gasoline, pyrolysis fuel oil, and a C3+ mixture and will be remove from the site for disposal or use as appropriate. Additional facilities include an electric and steam cogeneration from three (3) combustion turbines with duct burners and heat recovery steam generators with a plant capacity of 250.4 MW, four (4) emergency generators, three (3) diesel-fired fire pump engines, cooling towers, flares, and storage tanks. | (7) 620.000 MMBtu/hr Ethane cracking furnaces, (3) 664.000 combustion turbines with duct burners. Shell intends to convert ethane in to ethylene for manufacturing of various grades of low density and high density polyethylene as a final product. | Combustion turbine wih duct burner and heat recovery steam generator | 15.11 | Natural Gas | 0 | Three 40.6 MW turbines | Three (3) General Electric Frame 6B NG fired turbine with duct burners and heat recovery steam generators. Total electric generating capacity will be 250.4 MW from cogeneration three turbines at 40.6 MW and two HRSG at 64.3 MW. Excess electricity generated will be sold to the grid in quantities sufficient to classify the facility as an electric utility. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1030 | CO2E/MWH | 30 DAY ROLLING AVG* | BACT-PSD |  | U | 0 | U | 340558 | TONS | ANY CONSECUTIVE 12 MONTH PERIOD | 0 |  |  | 0 | 0 | N
*TX-0638 | MONT BELVIEU COMPLEX | ENTERPRISE PRODUCTS OPERATING LLC | CHAMBERS | TX | 77580 | USA | TERRY HURLBURT | 713-381-6595 | SNOLAN@EPROD.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | PSD-TX-1286-GHG | 1321 | 325110 |  | 06/06/2012 &nbsp;ACT | 10/12/2012 &nbsp;ACT | 2013-10-25 | 2015-03-16 | D |  | the facility will add two new natural gas liquids (NGL) fractionation (Eagleford Fractionation) units and a deisobutanizer (DIB) unit at the Enterprise Mont Belvieu Complex in Mont Belvieu, Texas. The Eagleford Fractionation units will be capable of separating an NGL feed into separate ethane, propane, butane, and gasoline fractions. Each fractionation unit will have a nominal feed capacity of 110,000 barrels per day. The DIB unit will be capable of separating isobutene and normal butane from mixed butane streams. The Eagleford Fractionation and DIB unit will consist of two fractionation unit deethanizer distillation columns, two fractionation unit debutanizer distillation columns, two depropanizer colwnns, two hot oil heaters, two regenerant gas heaters, one flare, one deisobutanizer distillation column, and supporting equipment. |  | 2 Regenerant Heaters | 15.11 |  | 28.8 |  | 2 Regenerant Heaters (Combustion Units). Each unit has a maximum design beat input rate of28.5 MMBTU/HR and fired with natural gas, tired with natural gas. HR15.002A and HR15.002B. | Carbon Dioxide Equivalent (CO2e) | Other - Part 98, Subpart A, Table A-1 | (Greenhouse Gasses (GHG)) | CO2e | N |  | 14872 | T/PY | 12-MONTH ROLLING BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission rate is for each of the two regenerant heaters.
TX-0679 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | GHGPSDTX123 | 4925 | 221210 | 110057188626 | 12/12/2014 &nbsp;ACT | 02/27/2015 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. The LNG terminal will operate three trains continuously (8,760 hours per year) using eighteen (18) GE LM2500+G4 (with dry low NOx emissions) gas-fired refrigeration compressor turbines, six on each train. There are two methane, two ethylene, and two propane refrigeration turbines per train. |  | Refrigeration Compressor Turbines | 15.11 | natural gas | 40000 | hp | There are three LNG trains with a total of (12) GE LM2500+ DLE turbines that drive the propane and methane refrigeration compressors. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | install efficient turbines, follow the turbine manufacturerâ€™s emission-related written instructions for maintenance activities including prescribed maintenance intervals to assure good combustion and efficient operation. Compressors shall be inspected and maintained according to a written maintenance plan to maintain efficiency. | 146754 | TPY | ROLLING 12-MONTH BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is for each turbine.
TX-0735 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JOLLY HAYDEN | 806-349-5250 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, (512)239-2175, laura.gibson@tceq.texas.gov | GHGPSDTX41M1 | 4911 | 221112 | 110043432737 | 04/02/2015 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2015-05-14 | 2018-04-18 | B |  | Golden Spread Electric Cooperative, Inc. (GSEC) is requesting authorization for three additional simple cycle electric generating plants at an existing site to meet increased energy demand in the area. The generating equipment consists of three new GE 7F5-Series natural gas-fired combustion turbines (CTG). Each turbine has a maximum electric output of 202 MW. |  | Simple Cycle Turbine &amp; Generator | 15.11 | natural gas | 202 | MW | 3 additional GE 7F 5-Series Combustion Turbine Generators | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency, good design & combustion practices | 1304 | LB CO2/MWHR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of each turbine is limited to 4,572 hours per year
TX-0753 | GUADALUPE GENERATING STATION | GUADALUPE POWER PARTNERS, L.P. | GUADALUPE | TX | 78124 | USA | BILL SKINNER | 281-252-5221 | BSKINNER@NAVASOTAENERGY.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Melanie Magee, EPA Region 6, Air Permits Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | PSD-TX-1310-GHG | 4911 | 221112 | 110021360329 | 10/24/2014 &nbsp;ACT | 12/02/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | B | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | GPP proposes to add two (2) new gas-fired simple-cycle combustion turbines of 227 MW (nominal) electric generating capacity each to the 1,000 MW (nominal) existing major stationary source, Guadalupe Generating Station (GGS), located in Marion, Texas. The proposed project will provide peaking capacity at an existing natural gas fired combined cycle electric generating station. The two new natural gas-fired simple-cycle turbines are proposed to provide a fast ramp up for additional peaking capacity during peak electricity demand periods. In addition, the project also includes the installation of a firewater pump engine, circuit breakers and associated fugitive emissions. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. See CN600132120 and RN100225820 | Simple Cycle Combustion Turbine Generator | 15.11 | Pipeline Natural Gas | 10673 | Btu/kWh | Natural gas-fired simple cycle combustion turbine generators (CTG) will be General Electric 7FA.05 (GE 7FA.05), each with a maximum base-load electric power output of 227 megawatts (MW, nominal). Combined gross heat rate limit of 10,279,456 MMBtu/yr. | Carbon Dioxide Equivalent (CO2e) | Other - 40 CFR 60.8; Method 3a or 3b | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1293.3 | LB CO2/MWHR (GROSS) | 12-MONTH ROLLING AVERAGE (NORMAL OPER) | BACT-PSD |  | U | 0 | U | 20.8 | TONS CO2/HR | 12-MONTH ROLLING AVERAGE BASIS (MSS OPER | 0 |  |  | 0 | 0 | N |  | BACT limits above are for each CT. The two new turbines have a combined limit of 5,000 hours of operation (including MSS) on a 12-month rolling total basis. Both CT are limited to 300 combined hours of start and 300 combined hours of shutdown on a 12-month rolling total basis. Stack Testing Requirements: initial compliance with the CO2 emission limits. Shall be conducted in accordance with 40 CFR 60.8 and Method 3a or 3b. Emission testing for the CT shall be performed every 5 years, plus or minus 6 months to verify continued performance at permitted emission limits.
TX-0753 | GUADALUPE GENERATING STATION | GUADALUPE POWER PARTNERS, L.P. | GUADALUPE | TX | 78124 | USA | BILL SKINNER | 281-252-5221 | BSKINNER@NAVASOTAENERGY.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Melanie Magee, EPA Region 6, Air Permits Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | PSD-TX-1310-GHG | 4911 | 221112 | 110021360329 | 10/24/2014 &nbsp;ACT | 12/02/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | B | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | GPP proposes to add two (2) new gas-fired simple-cycle combustion turbines of 227 MW (nominal) electric generating capacity each to the 1,000 MW (nominal) existing major stationary source, Guadalupe Generating Station (GGS), located in Marion, Texas. The proposed project will provide peaking capacity at an existing natural gas fired combined cycle electric generating station. The two new natural gas-fired simple-cycle turbines are proposed to provide a fast ramp up for additional peaking capacity during peak electricity demand periods. In addition, the project also includes the installation of a firewater pump engine, circuit breakers and associated fugitive emissions. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. See CN600132120 and RN100225820 | Simple Cycle Combustion Turbine Generator | 15.11 | Pipeline Natural Gas | 10673 | Btu/kWh | Natural gas-fired simple cycle combustion turbine generators (CTG) will be General Electric 7FA.05 (GE 7FA.05), each with a maximum base-load electric power output of 227 megawatts (MW, nominal). Combined gross heat rate limit of 10,279,456 MMBtu/yr. | Carbon Dioxide Equivalent (CO2e) | Other - 40 CFR 60.8; Method 3a or 3b | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1293.3 | LB CO2/MWHR (GROSS) | 12-MONTH ROLLING AVERAGE (NORMAL OPER) | BACT-PSD |  | U | 0 | U | 20.8 | TONS CO2/HR | 12-MONTH ROLLING AVERAGE BASIS (MSS OPER | 0 |  |  | 0 | 0 | N |  | BACT limits above are for each CT. The two new turbines have a combined limit of 5,000 hours of operation (including MSS) on a 12-month rolling total basis. Both CT are limited to 300 combined hours of start and 300 combined hours of shutdown on a 12-month rolling total basis. Stack Testing Requirements: initial compliance with the CO2 emission limits. Shall be conducted in accordance with 40 CFR 60.8 and Method 3a or 3b. Emission testing for the CT shall be performed every 5 years, plus or minus 6 months to verify continued performance at permitted emission limits.
TX-0757 | INDECK WHARTON ENERGY CENTER | INDECK WHARTON, LLC | WHARTON | TX | 77432 | USA | JAMES SCHNEIDER | 847-520-3212 | JSCHNEIDER@INDECKENERGY.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Jennifer Huser, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | PSD-TX-1374-GHG | 4911 | 221112 | Not Assigned | 04/05/2014 &nbsp;ACT | 05/12/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | A | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | Indeck proposes to construct a peaking power plant, the Indeck Wharton Energy Center, generally located south of Danevang, Texas. To meet the anticipated demand for peak power, Indeck proposes to construct three identical natural gas-fired F-class simple cycle combustion turbines with associated support equipment. Indeck proposes that the three new combustion turbine generators (CTGs) will be either General Electric (GE) 7FA.05 or Siemens SGT6-5000F(5). The GE 7FA.05 has a base-load electric power output of approximately 213 megawatts (MW, net nominal), and the Siemens SGT6-5000F(5) has a base-load electric power output of approximately 225 MW (net nominal). This project also proposes to install one emergency diesel generator, one diesel fire water pump, one natural gas pipeline heater, and other auxiliary equipment. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. | Simple Cycle Combustion Turbine, GE 7FA.05 | 15.11 | Pipeline Natural Gas | 0 |  | Indeck proposes to construct three identical natural gas-fired F-class simple cycle combustion turbines with associated support equipment. Indeck proposes that the three new combustion turbine generators (CTGs) will be either General Electric (GE) 7FA.05 or Siemens SGT6-5000F(5). The GE 7FA.05 has a base-load electric power output of approximately 213 megawatts (MW, net nominal), and the Siemens SGT6-5000F(5) has a base-load electric power output of approximately 225 MW (net nominal). | Carbon Dioxide Equivalent (CO2e) | Other - 40 CFR 60.8; Method 3A or 3B | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1276 | LB CO2/MWHR (GROSS) | 2,500 OPERATIONAL HR ROLLING DAILY/CT | BACT-PSD |  | U | 0 | U | 321028 | TPY CO2E | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N |  | GHG BACT for Indeck is the use of modern natural gas-fired, thermally efficient simple cycle combustion turbines combined with evaporative cooling and good combustion and maintenance practices to maintain optimum efficiency. The GE FA7.05 or Siemens SGT6-5000F(5) turbines are consistent with the BACT requirement and the specific goal of this project. EPA is proposing an emission limit of 1,276 lb CO2/MWhr gross output on a 2,500 operational hour rolling basis for the GE 7FA.05 combustion turbine. Each combustion turbine is limited to 2,500 hours of operation, plus 300 startup and shutdown events on a 12-month rolling basis. To account for the additional hours of operation associated with the startup and shutdowns, each turbine is limited by fuel use associated with the 2,500 hours of operation per year. Limiting the fuel use achieves the same objective as limiting the number of hours of operation of each turbine to 2,500 hours. The fuel use limit for each combustion turbine that corresponds to the 2,500 hour of operation on a 12-month rolling basis is 5,394,500 MMBtu (HHV) on a 12-month rolling basis for the GE 7FA.05 combustion turbine. An initial stack test demonstration will be required for CO2 emissions from each emission unit. An initial stack test demonstration for CH4 and N2O emissions are not required because the CH4 and N2O emissions are less than 0.01% of the total CO2e emissions from the CTGs.
TX-0757 | INDECK WHARTON ENERGY CENTER | INDECK WHARTON, LLC | WHARTON | TX | 77432 | USA | JAMES SCHNEIDER | 847-520-3212 | JSCHNEIDER@INDECKENERGY.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Jennifer Huser, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | PSD-TX-1374-GHG | 4911 | 221112 | Not Assigned | 04/05/2014 &nbsp;ACT | 05/12/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | A | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | Indeck proposes to construct a peaking power plant, the Indeck Wharton Energy Center, generally located south of Danevang, Texas. To meet the anticipated demand for peak power, Indeck proposes to construct three identical natural gas-fired F-class simple cycle combustion turbines with associated support equipment. Indeck proposes that the three new combustion turbine generators (CTGs) will be either General Electric (GE) 7FA.05 or Siemens SGT6-5000F(5). The GE 7FA.05 has a base-load electric power output of approximately 213 megawatts (MW, net nominal), and the Siemens SGT6-5000F(5) has a base-load electric power output of approximately 225 MW (net nominal). This project also proposes to install one emergency diesel generator, one diesel fire water pump, one natural gas pipeline heater, and other auxiliary equipment. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. | Simple Cycle Combustion Turbine, SGT-5000F(5) | 15.11 | Pipeline Natural Gas | 0 |  | Indeck proposes to construct three identical natural gas-fired F-class simple cycle combustion turbines with associated support equipment. Indeck proposes that the three new combustion turbine generators (CTGs) will be either General Electric (GE) 7FA.05 or Siemens SGT6-5000F(5). The GE 7FA.05 has a base-load electric power output of approximately 213 megawatts (MW, net nominal), and the Siemens SGT6-5000F(5) has a base-load electric power output of approximately 225 MW (net nominal). | Carbon Dioxide Equivalent (CO2e) | Other - 40 CFR 60.8, Method 3A or 3B | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1337 | LB CO2/MWHR (GROSS) | 2500 OPERATIONAL HR ROLLING DAILY/CT | BACT-PSD |  | U | 0 | U | 358529 | TPY CO2E | 12-MONTH ROLLING | 0 |  |  | 0 | 0 | N |  | GHG BACT for Indeck is the use of modern natural gas-fired, thermally efficient simple cycle combustion turbines combined with evaporative cooling and good combustion and maintenance practices to maintain optimum efficiency. The GE FA7.05 or Siemens SGT6-5000F(5) turbines are consistent with the BACT requirement and the specific goal of this project. EPA is proposing an emission limit of 1,337 lb CO2/MWhr gross output for the Siemens SGT6-5000F(5) combustion turbine on a 2,500 operational hour rolling basis. Each combustion turbine is limited to 2,500 hours of operation, plus 300 startup and shutdown events on a 12-month rolling basis. To account for the additional hours of operation associated with the startup and shutdowns, each turbine is limited by fuel use associated with the 2,500 hours of operation per year. Limiting the fuel use achieves the same objective as limiting the number of hours of operation of each turbine to 2,500 hours. The fuel use limit for each combustion turbine that corresponds to the 2,500 hour of operation on a 12-month rolling basis is 5,394,500 MMBtu (HHV) on a 12-month rolling basis for the GE 7FA.05 combustion turbine, or 6,024,650 MMBtu (HHV) on a 12-month rolling basis for the Siemens SGT6-5000F(5). An initial stack test demonstration will be required for CO2 emissions from each emission unit. An initial stack test demonstration for CH4 and N2O emissions are not required because the CH4 and N2O emissions are less than 0.01% of the total CO2e emissions from the CTGs.
TX-0758 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX | 79741 | USA | MATTHEW THORNTON | 312-582-1527 | MTHORNTON@INVENERGYLLC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | EPA Region 6 Permit Writer: Anna Milburn, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | GHGPSDTX1366 | 4911 | 221112 | Not Assigned | 04/18/2014 &nbsp;ACT | 08/01/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | A | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | Invenergy proposes to construct a 330 MW peak power plant (known as the Ector County Energy Center Plant (ECEC)), located in Goldsmith, Ector County, Texas. With this proposed project, Invenergy plans to construct two natural gas-fired simple-cycle turbines, General Electric (GE) Model 7FA.03, and associated equipment, a fire water pump engine, a natural gas-fired dew-point heater, and two circuit breakers. For the purposes of this proposed permitting action, GHG emissions are permitted for the two turbines, the fire water pump engine, the natural gas-fired dew-point heater, and the circuit breakers, as well as for fugitive emissions, and maintenance, startup and shutdown emissions. | Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. | Simple Cycle Combustion Turbine, GE 7FA.03 | 15.11 | Natural Gas | 11707 | Btu/kWh (HHV) |  | Carbon Dioxide Equivalent (CO2e) | Other - 40 CFR 60.8; Method 3A or 3B | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1393 | LB CO2/MWHR (GROSS) | 2500 OPERATIONAL HR ROLLING DAILY/CT | BACT-PSD |  | U | 0 | U | 239649 | TPY CO2E | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | an emission limit of 1,393 lb CO2/MWhr gross output for the GE7FA.03 combustion turbine to be utilized for this project. Each combustion turbine is limited to 2,500 operational hours on a rolling basis, plus 500 startup and shutdown events on a 12â€“month rolling average. Until the 2,500 operational hour basis has been established, Invenergy should utilize the performance testing data to establish a plan whereby Invenergy may operate the emission unit in a manner that will not exceed the permitted CO2e emissions limits. To account for the additional hours of operation associated with the startup and shutdowns, each turbine is limited by fuel use associated with the 2,500 hours of operation per year. Limiting the fuel use achieves the same objective as limiting the number of hours of operation of each turbine to 2,500 hours. The fuel use limit for each combustion turbine that corresponds to the 2,500 hours of operation per 365 day basis is 4,028,700 MMBtu (HHV) on a 12-month rolling basis for the GE7FA.03 combustion turbine. An initial stack test demonstration will be required for CO2 emissions from each emission unit. An initial stack test demonstration for CH4 and N2O emissions are not required because the CH4 and N2O emission are less than 0.01% of the total CO2e emissions from the CTGs
TX-0758 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX | 79741 | USA | MATTHEW THORNTON | 312-582-1527 | MTHORNTON@INVENERGYLLC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | EPA Region 6 Permit Writer: Anna Milburn, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | GHGPSDTX1366 | 4911 | 221112 | Not Assigned | 04/18/2014 &nbsp;ACT | 08/01/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | A | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | Invenergy proposes to construct a 330 MW peak power plant (known as the Ector County Energy Center Plant (ECEC)), located in Goldsmith, Ector County, Texas. With this proposed project, Invenergy plans to construct two natural gas-fired simple-cycle turbines, General Electric (GE) Model 7FA.03, and associated equipment, a fire water pump engine, a natural gas-fired dew-point heater, and two circuit breakers. For the purposes of this proposed permitting action, GHG emissions are permitted for the two turbines, the fire water pump engine, the natural gas-fired dew-point heater, and the circuit breakers, as well as for fugitive emissions, and maintenance, startup and shutdown emissions. | Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. | Simple Cycle Combustion Turbine-MSS | 15.11 | Natural Gas | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 21 | TON CO2E/EVENT | EACH MSS EVENT | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT applies during all periods of turbine operation, including startup and shutdown. MSS emissions are limited to 10,502 CO2e per year and each start up and shut down event is limited to 21 tons of CO2e. The number of startups and shutdowns is based on the number of operational hours per year (2,500 service hours per year per turbine). All startups and shutdowns are limited to 60 minutes in duration per event. A startup of each turbine is defined as the period that begins when there is measureable fuel flow to the turbine and ends when the turbine load reaches 60 percent. A shutdown of each turbine is defined as the time period that begins when the combustion turbine drops out of the normal operating low-NOx combustion mode (which equates to approximately 60% combustion turbine load) following an instruction to shut down, and ends when flame is no longer detected in the combustion turbine combustors. The proposed ECEC project is proposing 500 startups/shutdowns in addition to 2,500 operational hours per year per turbine. BACT for startup/shutdown is the work practice standard to utilize good pollution control practices, safe operating practices, and protection of the facility. â€¢ Startups and shutdowns are limited to no more than 60 minutes per event. Each start up and shutdown shall not exceed 21 tons of CO2e per event. â€¢ No more than 500 startup and shutdown events per turbine on a 12-month rolling basis. â€¢ The maximum heat input during startup shall be limited to 1,320 MMBtu/hr. â€¢ No more than one of the two simple-cycle turbines will undergo a startup and/or shutdown in any 30 minute period, except that simultaneous startups of multiple turbines within a 30 minute period may occur 52 times on a 12-month rolling basis.
TX-0771 | SHAWNEE ENERGY CENTER | SHAWNEE ENERGY CENTER, LLC | HILL | TX |  | USA | NEIL O'DONOVAN | 312-422-1608 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, P.E., 512-239-1353, joseph.janecka@tceq.texas.gov | GHGPSDTX126, PSDTX1442, 125963 | 4911 | 221112 | UNKNOWN | 09/16/2015 &nbsp;ACT | 11/10/2015 &nbsp;ACT | 2015-11-03 | 2016-07-06 | A |  | Electric Generating Utility: The project will consist of four gas fired combustion turbines (CTGs). The CTGs are fueled with pipeline quality natural gas and will operate in simple cycle mode. The gas turbines will be one of two options. |  | Simple cycle turbines greater than 25 megawatts (MW) | 15.11 | natural gas | 230 | MW | Siemens Model SGT6-5000 F5ee â€“ 230 MW or Second turbine option: General Electric Model 7FA.05TP â€“ 227 MW | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1398 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,920 hours on a 12-month rolling average.
TX-0775 | CLEAR SPRINGS ENERGY CENTER (CSEC) | NAVASOTA SOUTH PEAKERS OPERATING COMPANY II, LLC. | GUADALUPE | TX |  | USA | BILL SKINNER | 281-252-5221 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jack Coleman, 512-239-1255, jack.coleman@tceq.texas.gov | GHGPSDTX120, 120849, AND PSDTX | 4911 | 221112 | UNKNOWN | 07/03/2015 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-11-10 | 2016-07-06 | A |  | Navasota South Peakers Operating Company II LLC proposes to install three new natural gas fired combustion turbine generators (CTGs). Each CTG will be a General Electric 7FA.04 model that can produce approximately 183 Megawatts (MW) each based upon the manufacturerâ€™s projected output at baseload operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Low carbon fuel, good combustion, efficient combined cycle design | 1461 | LB/MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT, CTGs will operate at 2500 hours of operation per year at baseload.
TX-0778 | UNION VALLEY ENERGY CENTER | NAVASOTA SOUTH PEAKERS OPERATING COMPANY II, LLC. | NIXON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | GHGPSDTX117 | 4911 | 221112 | UNKNOWN | 08/10/2015 &nbsp;ACT | 12/16/2015 &nbsp;ACT | 2015-12-11 | 2016-07-06 | A |  | three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 megawatt (MW) each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1461 | LB/MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT, SIMPLE CYCLE PEAKING TURBINE
TX-0786 | NACOGDOCHES POWER ELECTRIC GENERATING PLANT | NACOGDOCHES POWER | NACOGDOCHES | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joel Lunsford, 512-239-1513, joel.lunsford@tceq.texas.gov | GHGPSDTX116, 77679, PSDTX1061M | 4911 | 221112 | UNKNOWN | 12/10/2015 &nbsp;ACT | 03/01/2016 &nbsp;ACT | 2016-02-19 | 2016-07-06 | B |  | Electric Generation |  | Combined Cycle &amp; Cogeneration | 15.11 | natural gas | 232 | MW |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 1316 | LB/MW HR |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Large Combustion Turbines &gt; 25 MW | 15.11 | natural gas | 232 | MW | 4 Simple cycle CTGs, 2,500 hr/yr operational limitation. Facility will consist of either 232 MW (Siemens) or 220 MW (GE) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practiceS | 1341 | LB/MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK AND TTTT
TX-0794 | HILL COUNTY GENERATING FACILITY | BRAZOS ELECTRIC COOPERATIVE | HILL | TX |  | USA | MIKE MEYERS | (254)750-6228 | MMEYERS@BRAZOSELECTRIC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512)239-1512, randy.hamilton@tceq.texas.gov | 130051,PSDTX1450, GHGPSDTX131 | 4911 | 221112 | UNKNOWN | 12/18/2015 &nbsp;ACT | 04/07/2016 &nbsp;ACT | 2016-04-05 | 2016-07-29 | A |  | Four simple cycle combustion turbine electric generators are proposed. Natural gas or ultra-low sulfur diesel fuel oil are the fuels. Turbine model options are: General Electric (GE) 7FA.03, GE 7FA.04, GE 7FA.05, and Siemes SGT6-5000(5)ee. Electric output is between 684 and 928 megawatts (MW). |  | Simple cycle turbine | 15.11 | natural gas | 171 | MW | Each combustion turbine is limited to 2,920 hours of annual operation, including startup and shutdown hours. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1434 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
TX-0816 | CORPUS CHRISTI LIQUEFACTION | CORPUS CHRISTI LIQUEFACTION STAGE III, LLC | SAN PATRICIO | TX |  | USA | KEITH LITTLE | (713) 375-5204 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 139479, PSDTX1496, GHGPSDTX157 | 4925 | 221210 | Not Found | 11/16/2016 &nbsp;ACT | 02/14/2017 &nbsp;ACT | 2017-02-07 | 2018-04-18 | B |  | Trains 4 and 5 will consist of 12 natural gas compressor turbines, 2 thermal oxidizers, 2 sets of flares each comprised of one wet gas flare and one dry gas flare, 2 amine surge tanks (maintenance, startup, and shutdown [MSS] only), 3 diesel generators, 3 fire-water pump diesel engines, 6 fixed roof diesel storage tanks, and piping components. |  | Refrigeration compressor turbines | 15.11 | NATURAL GAS | 40000 | HP | 2 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane, ethylene, and methane section compressors. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1793574 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit is a cap for all eight turbines.
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Simple Cycle Turbine | 15.11 | natural gas | 227.5 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Pipeline quality natural gas; limited hours; good combustion practices | 1300 | LB/MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
TX-0824 | JACKSON COUNTY GENERATING FACILITY | SOUTHERN POWER | JACKSON | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Marc Sturdivant, (512)239-1313, marc.sturdivant@tceq.texas.gov | GHGPSDTX118 | 4911 | 221112 | Not Found | 08/15/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-07-20 | 2017-11-16 | A |  | simple cycle electric generation |  | Simple Cycle Turbines | 15.11 | natural gas | 920 | MW | The facility will consist of four Siemens F5 model (~230 megawatts (MW) each for a total of 920 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | energy efficiency designs, practices, and procedures, CT inlet air cooling, periodic CT burner maintenance and tuning, reduction in heat loss, i.e., insulation of the CT, instrumentation and controls | 1316 | LB/MW HR |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
TX-0826 | MUSTANG STATION | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | YOAKUM | TX |  | USA | JEFF PIPPIN | 806-418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | 72579, PSDTX1080M1, GHGPSDTX13 | 4911 | 221112 | 110041502433 | 06/12/2017 &nbsp;ACT | 08/16/2017 &nbsp;ACT | 2017-07-24 | 2018-04-18 | C |  | GE7FA combustion turbine (Unit 6) to increase the hours of operation to 3000 hours per year. The turbine construction was completed the first quarter of 2013 and initial firing began on April 1, 2013. |  | Simple Cycle Turbine | 15.11 | NATURAL GAS | 162.8 | MW | Unit 6 Turbine is limited to 3000 hours per year. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Pipeline quality natural gas and good combustion practices | 120 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*WV-0028 | WAVERLY POWER PLANT | PLEASANTS ENERGY LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 3046654201 | GERALD.GATTI@DYNEGY.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Steve Pursley, PE Engineer West Virginia Division of Air Quality 601-57th St., SE Charleston, WV 25304 Phone: (304) 926-0499 x1218 Fax: (304) 926-0478 steve.r.pursley@wv.gov | R14-0034A | 4911 | 221112 | 110063231042 | 11/30/2017 &nbsp;ACT | 03/13/2018 &nbsp;ACT | 2018-05-29 | 2018-05-29 | U | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/073-00022_PERM_R14-0034A.pdf | 300 MW Sinple-Cycle Peaking Plant | Modification to existing PSD Permit (R14-0034, RBLC Number WV-0027) to add &lsquo;&lsquo;advanced gas path&lsquo;&lsquo; technology to the turbines that was defined as a &lsquo;&lsquo;change in the method of operation&lsquo;&lsquo; that resulted a major modification to the turbines. | GE 7FA.004 Turbine | 15.11 | Natural Gas | 167.8 | MW | This one entry is for both turbines as they are the same. Each turbine, after this modification, is a nominal 167.8 MW GE Model 7FA.004. Has oil-fire backup. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of natural gas & use of GE 7FA.004 | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 1300 | LB/MW-HR | 12 MONTH ROLLING AVERAGE | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055426409 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Three simple cycle combustion turbines | 15.11 | natural gas | 799.7 | MMBTU/H | Three GE, LMS100PA, natural gas-fired, simple cycle CTG rated at 799.7 MMBtu per hour each,based on HHV. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Good Combustion Control and Catalytic Oxidation (CatOx) | 10 | PPMVD AT 15% O2 | 1-HR AVE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 19.8 | LB/H | 30-DAY ROLLING AVE | 0 |  |  | 0 | 0 | N |  | Startup limit: 28.0 lb per event Shutdown limit: 36.0 lb per event compliance with BACT limits monitored via continuous emissions monitors.
CO-0076 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110058377830 | 06/16/2014 &nbsp;ACT | 12/11/2014 &nbsp;ACT | 2014-12-31 | 2016-02-19 | C |  | Electric generation | Permit modification to convert startup and shutdown BACT limits to an hourly basis (from event based). | Turbines - two simple cycle gas | 15.11 | natural gas | 799.7 | MMBTU/H each | GE LMS100PA, natural gas fired, simple cycle, combustion turbine. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | Catalytic Oxidation. | 55 | LB/H | 1-HR AVE / STARTUP AND SHUTDOWN | BACT-PSD | OPERATING PERMIT , NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The CO limit was converted to an equivalent hourly based limit (the original permit included an event based limit) for periods of startup and shutdown.
FL-0305 | OUC CURTIS H. STANTON ENERGY CENTER | ORLANDO UTILITIES COMMISSION (OUC) | ORLANDO | FL | 32831 | USA | DENISE M. STALLS | 4077374236 | DSTALLS@OUC.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | ALVARO LINERO, P.E. SPECIAL PROJECT ADMINISTRATOR BUREAU OF AIR REGULATION | PSD-FL-373A AND 0950137-020-AC | 4911 | 221112 | UNKNOWN | 03/04/2008 &nbsp;ACT | 05/12/2008 &nbsp;ACT | 2009-02-20 | 2009-08-31 | B |  | THE EXISTING FACILITY CONSISTS OF TWO 468 MW FOSSIL FUEL FIRED STEAM ELECTRIC GENERATING UNITS (UNITS 1 AND 2), AND ONE 640 MW NGCC UNIT (UNIT A). THERE ARE STORAGE AND HANDLING FACILITIES FOR SOLID FUELS, FLY ASH, LIMESTONE, GYPSUM, SLAG, AND BOTTOM ASH. NEW PROJECT ADDS UNIT B, A 300 MW COMBINED CYCLE COMBUSTION TURBINE AND ASSOCIATED EQUIPMENT. | THE NEW PROJECT IS TO CONSTRUCT A Â¿ONE-ON-ONEÂ¿ F-CLASS NGCC UNIT (STANTON UNIT B) AND ASSOCIATED AUXILIARY EQUIPMENT. UNIT B WILL CONSIST OF: ONE NOMINAL 150 MEGAWATTS (MW) GENERAL ELECTRIC 7241 FA COMBUSTION TURBINE-ELECTRICAL GENERATOR (CTG); A SUPPLEMENTARY FIRED HEAT RECOVERY STEAM GENERATOR (HRSG) WITH NATURAL GAS FUELED DUCT BURNERS; AND A NOMINAL 150 MW STEAM TURBINE GENERATOR (STG) FOR AN OVERALL NOMINAL RATING OF 300 MW. THE PROJECT INCLUDES HIGHLY AUTOMATED CONTROLS, DESCRIBED AS THE GE MARK VI GAS TURBINE CONTROL SYSTEM TO FULFILL ALL OF THE GAS TURBINE CONTROL REQUIREMENTS. UNIT B WILL FIRE NATURAL GAS AS THE PRIMARY FUEL, AND ULTRALOW SULFUR DIESEL (ULSD) FUEL OIL SERVING AS A BACKUP FUEL. | 300 MW COMBINED CYCLE COMBUSTION TURBINE | 15.11 | NATURAL GAS | 1765 | MMBTU/H | FOR ULTRA LOW SULFUR (0.0015% SULFUR BY WEIGHT) FUEL OIL IS 1935 MMBTU/H. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION | 8 | PPMVD @15% | 24-HR | BACT-PSD |  | U | 0 | U | 14 | PPMVD @15% | 24-HR DURING PA WITH OR W/O DB | 6 | PPMVD @15% | 12-MONTH OIL/GAS ALL MODES | 0 | 0 | N |  | CONTINUOUS COMPLIANCE WITH THE 24-HOUR CO STANDARDS SHALL BE DEMONSTRATED BASED ON DATA COLLECTED BY THE REQUIRED CEMS. THE INITIAL AND ANNUAL EPA METHOD 10 TESTS ASSOCIATED WITH THE CERTIFICATION OF THE CEMS INSTRUMENTS SHALL ALSO BE USED TO DEMONSTRATE COMPLIANCE WITH THE INDIVIDUAL STANDARDS FOR NATURAL GAS, FUEL OIL, AND BASIC DUCT BURNER MODE. COMPLIANCE WITH THE 24-HOUR CO CEMS STANDARDS SHALL BE DETERMINED SEPARATELY FOR THE POWER AUGMENTATION (PA) MODE AND ALL OTHER MODES BASED ON THE HOURS OF OPERATION FOR EACH MODE. DB = DUCT BURNER
FL-0310 | SHADY HILLS GENERATING STATION | SHADY HILLS POWER COMPANY | PASCO | FL | 6927 | USA | ROY S. BELDEN | 2033576820 | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | SYED ARIF, PROJECT ENGINEER PHONE 850/ 921-9528 SYED.ARIF@DEP.STATE.FL.US TERESA HERON PHONE 850/921-9529 TERESA.HERON@DEP.STATE.FL.US | PSD-FL-402 | 4911 | 221122 | 1210100373 | 05/13/2008 &nbsp;ACT | 01/12/2009 &nbsp;ACT | 2009-07-29 | 2010-01-26 | B |  | THIS FACILITY CONSISTS OF THREE, DUAL-FUEL, NOMINAL 170 MW GENERAL ELECTRIC MODEL PG7241FA (GE 7FA) SIMPLE CYCLE COMBUSTION TURBINES-ELECTRICAL GENERATORS, THREE EXHAUST STACKS THAT ARE 18 FEET IN DIAMETER AND 75 FEET TALL, AND ONE 2.8-MILLION GALLON DISTILLATE FUEL OIL STORAGE TANK. THE COMBUSTION TURBINE UNITS CAN OPERATE IN SIMPLE-CYCLE MODE AND INTERMITTENT DUTY MODE. THE UNITS ARE EQUIPPED WITH DRY LOW-NITROGEN OXIDES (NOX) COMBUSTORS AND WATER INJECTION CAPABILITY. THE THREE COMBUSTION TURBINES ARE REGULATED UNDER PHASE II OF THE FEDERAL ACID RAIN PROGRAM. THIS FACILITY OPERATES DURING PEAK HOURS OF ELECTRICAL USE. |  | TWO SIMPLE CYCLE COMBUSTION TURBINE - MODEL 7FA | 15.11 | NATURAL GAS | 170 | MW | BACKUP FUEL: ULTRA LOW SULFUR DIESEL WITH A MAXIMUM SULFUR CONTENT OF 0.0015%, BY WEIGHT | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P |  | 6.5 | PPMVD @ 15% O2 NG |  | BACT-PSD |  | U | 0 | U | 21.5 | LB/H NATURAL GAS | 3 ONE HR TEST RUNS BY EPA METHOD 10 | 0 |  |  | 0 | 0 | N |  | EMISSIONS BURNING FUEL OIL: 13.5 PPMVD @ 15% O2 44.7 LB/H METHOD 10
FL-0319 | GREENLAND ENERGY CENTER | JACKSONVILLE ELECTRIC AUTHORITY (JEA) | DUVAL | FL | 32258 | USA | N. BERT GIANAZZA | 904-665-6247 | GIANNB@JEA.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Syed Arif Project Manager 850-921-9580 Jeff Koerner, P.E. Administrator Phone 850-921-9536 | PSD-FL-401 | 4911 | 221112 | UNKNOWN | 04/21/2008 &nbsp;ACT | 03/10/2009 &nbsp;ACT | 2010-09-23 | 2011-12-01 | A |  | The proposed facility is a new electric-generating facility referred to as Greenfield Energy Center (GEC). GEC will be built in two phases. The initial phase will be the construction of two natural gas-fired simple cycle combustion turbine (CT) units that are proposed to be operational June 2011. The second phase will convert these simple cycle units to a combined cycle combustion turbine (â€œ2-on 1â€ configuration). Heat recovery equipment will be installed on the two simple cycle combustion turbines to capture enough heat energy to run a steam turbine (ST). This phase is proposed to be operational by June 2013. | Each combustion turbine shall not operate more than 3,500 hours during any consecutive 12 months of which 500 hours may be on ULSFO. Each combustion turbine shall not operate more than 17 hours exclusively on ULSFO per calendar day, or with a combination of ULSFO burning of 12 hours with 12 hours of natural gas for compliance with regional haze impact thresholds. | 190 MW Combustion Turbine | 15.11 | ULSO | 30213 | GAL/YR | Capacity: 1806 MMBtu/H, natural gas Capacity: 1994 MMBtu/H, fuel oil Authorized Fuels (Pre-onsite natural gas availability): Each combustion turbine shall fire ULSFO which shall contain no more than 0.0015% sulfur by weight as the primary fuel until natural gas is available at the facility. If natural gas is not available by June 1, 2011, the permittee shall submit to the Department and EQD semi-annual status reports on the availability of natural gas to the facility. The first status report shall be submitted by June 1, 2011. The status reports shall be submitted until natural gas is available at the facility. Authorized Fuels (Post-onsite natural gas availability): Each combustion turbine shall fire natural gas as the primary fuel, which shall contain no more than 2 grains of sulfur per 100 standard cubic feet of natural gas. As a restricted alternate fuel, the combustion turbine may fire ULSFO containing no more than 0.0015% sulfur by weight. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Good Combustion | 4.1 | PPMVD @ 15% O2 (GAS) | 24-HR BLOCK/CEMS | BACT-PSD |  | U | 0 | U | 16.2 | LB/H (GAS) | (3) 1-HR RUNS/STACK TEST | 0 |  |  | 0 | 0 | N |  | Emission Limit firing oil (ULSFO with 0.0015% S): 1) 8.0 ppmvd @ 15% O2 24-hr rolling average/CEMS 2) 38.2 lb/hr - three 1-hr runs/stack test. Continuous compliance with the 24-hour CO standards shall be demonstrated based on data collected by the required CEMS. The initial and annual EPA Method 10 tests associated with the certification of the CEMS instruments may also be used to demonstrate compliance with the individual standards for natural gas and ULSFO. CO mass emission rates are at ISO conditions.
FL-0346 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-011-AC | 4911 | 221112 | 110002044065 | 11/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-01-08 | 2016-05-05 | D | http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | In this project, 24 peaking turbines from the Lauderdale facility are being replaced with five 200 MW combustion turbines at Lauderdale. The turbines will fire primarily natural gas, but may also fire ULSD fuel oil. Triggers PSD for NOx, PM, CO, VOC, and GHG. GHG permit issued by US EPA Region 4. Technical evaluation available at http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2000 | MMBtu/hr (approx) | Throughput could vary slightly (+/- 120 MMBtu/hr) depending on final selection of turbine model and firing of natural gas or oil. Primary fuel is expected to be gas. Each turbine limited to 3300 hrs per rolling 12-month period. Of these 3300 hrs, no more than 500 may use ULSD fuel oil. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 4 | PPMVD @ 15% O2 |  | BACT-PSD |  | U | 0 | U | 21 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Natural gas: 4.0 ppmvd @ 15% O2, and 21.0 lb/hr. ULSD: 9.0 ppmvd@15%O2, and 49.0 lb/hr. lb/hr limits are per turbine.
FL-0354 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-013-AC | 4911 | 221112 | 110002044065 | 04/20/2015 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2016-02-17 | 2016-07-06 | D | https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | Re-affirmed BACT determinations in Permit No. 0110037-011-AC. Also, new GHG BACT determination. Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2100 | MMBtu/hr (approx) | Five simple cycle GE 7F.05 turbines. Max of 3390 hours per year per turbine. Of the 3390 hours per year, up to 500 hour may be on ULSD fuel oil. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Good combustion minimizes CO formation | 4 | PPMVD@15%O2 | NAT GAS, THREE 1-HR RUNS | BACT-PSD | SIP | U | 0 | U | 9 | PPMVD@15%O2 | ULSD, THREE 1-HR RUNS | 0 |  |  | 0 | 0 | N |  | Initial and annual stack test. Also subject to 20 lb/hr CO on gas and 49.6 lb/hr on ULSD.
GA-0139 | DAHLBERG COMBUSDTION TURBINE ELECTRIC GENERATING FACILITY (P | SOUTHERN POWER COMPANY | JACKSON | GA | 30565 | USA | MR. E.S. (SCOTT) DIAL | 704 278-6601 | ESDIAL@SOUTHERNCO.COM | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-157-0034-V-04-1 | 4911 | 221112 | UNKNOWN | 07/10/2008 &nbsp;ACT | 05/14/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | C |  | PLANT DAHLBERG HAS PROPOSED TO CONSTRUCT AND OPERATE FOUR ADDITIONAL SIMPLE-CYCLE COMBUSTION TURBINES (SOURCE CODES: CT11-CT14) AND ONE FUEL OIL STORAGE TANK. THE PROPOSED PROJECT WILL HAVE A NOMINAL GENERATING CAPACITY OF 760 MW. THE FACILITY IS CURRENTLY PERMITTED TO OPERATE 10 DUAL-FUELED SIMPLE-CYCLE CTG's. AFTER THE EXPANSION, THE FACILITY WILL HAVE A TOTAL NOMINAL GENERATING CAPACITY OF 1530 MW. |  | SIMPLE CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.11 | NATURAL GASE | 1530 | MW | THE PROCESS USES FUEL OIL FOR BACKUP AT THE RATE OF 2129 MMBUT/H | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 9 | PPM@15%02 | 3-HOUR AVERAGE/CONDITION 3.3.24 | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | N | 30 | PPM@15%02 | 3-HOUR AVERAGE/CONDITION 3.3.28 | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER | 15.11 | NATURAL GAS | 92.5 | MMBTU/H | NATURAL GAS USAGE SHALL NOT EXCEED 18.14 MMCF/YEAR. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN, USE NATURAL GAS | 37.23 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER | 15.11 | NATURAL GAS | 92.5 | MMBTU/H | NATURAL GAS USAGE SHALL NOT EXCEED 18.14 MMCF/YEAR. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN, USE NATURAL GAS | 37.23 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0261 | VERMILLION GENERATING STATION | DUKE ENERGY INDIANA, LLC VERMILLION GENERATING STA | VERMILLION | IN | 47928 | USA | PATRICK COUGHLIN | 3178382108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIP SINHA PH.D. 317-234-4907 | 165-36956-00022 | 4911 | 221112 | 110006010921 | 03/16/2016 &nbsp;ACT | 02/28/2017 &nbsp;ACT | 2017-07-07 | 2017-08-09 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36956F.PDF | ELECTRIC UTILITY SERVICES |  | SIMPLE CYCLE, NATURAL GAS FIRED COMBUSTION TURBINES | 15.11 | NATURAL GAS | 80 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 525 | LB/H | EACH TURBINE | BACT-PSD |  | N | 0 |  | 52.5 | TON/12 CONSEC. MONTH | COMPLIANCE DETERMINED END OF EACH MONTH | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: ONLY TWO TURBINES WILL OPERATE DURING LOW LOAD OPERATION
IN-0264 | MONTPELIER GENERATING STATION | AES OHIO GENERATION, LLC | WELLS | IN | 46781 | USA | DREW PARKER | 9373314993 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: MADHURIMA MOULIK 317-233-6663 MMOULIK@IDEM.IN.GOV SECTION CHIEF: JASON KRAWCZYK 317-234-5174 | 179-37209-00026 | 4911 | 221112 | 110021089061 | 05/23/2016 &nbsp;ACT | 01/06/2017 &nbsp;ACT | 2017-07-07 | 2017-11-17 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/37209F.PDF | COMBUSTION TURBINES |  | PRATT &amp; TWIN-PAC SIMPLE CYCLE TURBINES | 15.11 | NATURAL GAS | 270.9 | MMBTU/H | NO. 2 DIESEL OIL BACKUP FUEL | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | NATURAL GAS AS PRIMARY FUEL; GOOD COMBUSTION PRACTICES | 0.2 | LB/MMBTU | NATURAL GAS | BACT-PSD |  | U | 0 | U | 0.3 | LB/MMBTU | FUEL OIL | 0 |  |  | 0 | 0 | N |  | EACH TURBINE LIMITED TO 4555 HOURS OF OPERATION PER 12 MONTH PERIOD; EACH TURBINE LIMITED TO 500 HOURS OF FUEL OIL COMBUSTION PER 12 MONTH PERIOD
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE LM6000PC SPRINT Simple cycle combustion turbine | 15.11 | Pipeline quality natural gas | 405.3 | MMBTU/hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | utilize efficient combustion/design technology | 63.8 | LB/HR | FULL LOAD, AMBIENT TEMP < OR = TO 54 F | BACT-PSD |  | U | 0 | U | 36 | LB/HR | FULL LOAD, AMBIENT TEMP > 54 F | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE 7FA Simple Cycle Combustion Turbine | 15.11 | Pipeline quality natural gas | 1780 | MMBTU/HR |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | utilize efficient combustion/design technology | 39 | LB/HR | AT FULL LOAD | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KY-0104 | CASH CREEK GENERATING STATION | CASH CREEK GENERATION, L.L.C | HENDERSON | KY | 41047 | USA | MIKE MCINNUS | 502 357 9907 | MMCINNIS@ERORA.COM | 4 | KY001 | KENTUCKY DEP, DIV FOR AIR QUALITY | MR. RICK SHEWEKAH, MGR | (502)564-3999 | Sreenivas.Kesaraju@ky.gov |  | V-14-011 | 4911 | 221112 | 110042328479 | 06/18/2014 &nbsp;ACT | 06/10/2015 &nbsp;ACT | 2017-02-28 | 2017-04-28 | A |  | natural gas fired combined cycle power plant |  | Combined cycle combustion turnbine with HRSG and duct firing | 15.11 | Natural gas pipeline quality | 849 | MW | Two CT with HRSGs with duct burner Max fuel input for CTs and HRSGs 6,714 mmBtu/hr HHV Max Gross output 849 MW at 0F | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Catalytic Oxidation | 2 | PPMVD | @15%O2 BASED ON 3-HOUR ROLLING AVERAGE | BACT-PSD | NSPS | U | 90 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0224 | ARSENAL HILL POWER PLANT | SOUTHWEST ELECTRIC POWER COMPANY (SWEPCO) | CADDO | LA | 71101 | USA | KRIS GAUS | 2147771113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-726 | 4911 | 221112 | 110001270847 | 01/07/2008 &nbsp;ACT | 03/20/2008 &nbsp;ACT | 2008-04-18 | 2012-05-18 | B |  | NATURAL GAS FIRED ELECTRICAL GENERATION PLANT. |  | SCN-3 COLD STARTUP CTG-1 SCN-7 COLD STARTUP CTG-2 | 15.11 | NATURAL GAS | 2110 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N | COMPLETE EVENTS AS QUICKLY AS POSSIBLE ACCORDING TO MANUFACTUREÂ¿S RECOMMENDED PROCEDURES. | 1508.15 | LB/H | MAX | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0224 | ARSENAL HILL POWER PLANT | SOUTHWEST ELECTRIC POWER COMPANY (SWEPCO) | CADDO | LA | 71101 | USA | KRIS GAUS | 2147771113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-726 | 4911 | 221112 | 110001270847 | 01/07/2008 &nbsp;ACT | 03/20/2008 &nbsp;ACT | 2008-04-18 | 2012-05-18 | B |  | NATURAL GAS FIRED ELECTRICAL GENERATION PLANT. |  | SCN-5 SHUTDOWN CTG-1 / SCN-9 SHUTDOWN CTG-2 | 15.11 | NATURAL GAS | 2110 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N | COMPLETE EVENTS AS QUICKLY AS POSSIBLE ACCORDING TO MANUFACTUREÂ¿S RECOMMENDED PROCEDURES. | 964.57 | LB/H | MAX | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Refrigeration Compressor Turbines (16) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices and fueled by natural gas | 43.6 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 58.4 | PPMV | AT 15% OXYGEN | 0 | 0 | N
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Generation Turbines (2) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices and fueled by natural gas | 17.46 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 25 | PPMV | AT 15% O2 | 0 | 0 | N
LA-0258 | CALCASIEU PLANT | ENTERGY GULF STATES LA LLC | CALCASIEU | LA | 70665 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: TEGAN TREADAWAY, (225) 219-3408 | PSD-LA-746 | 4911 | 221112 | 110007042565 | 11/10/2009 &nbsp;ACT | 12/21/2011 &nbsp;ACT | 2012-02-01 | 2012-04-03 | C |  | 320 MW POWER PLANT COMPRISED OF 2 NATURAL GAS-FIRED SIMPLE CYCLE COMBUSTION TURBINES. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS PSD TRIGGERED DUE TO RELAXATION OF A FEDERALLY-ENFORCEABLE CONDITION LIMITING POTENTIAL EMISSIONS BELOW MAJOR STATIONARY SOURCE THRESHOLDS. | TURBINE EXHAUST STACK NO. 1 &amp; NO. 2 | 15.11 | NATURAL GAS | 1900 | MM BTU/H EACH |  | Carbon Monoxide | Other - CEMS | (InOrganic Compounds) | 630-08-0 | P | DRY LOW NOX COMBUSTORS | 781 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 5745.6 | LB/H | HOURLY MAXIMUM / STARTUP & SHUTDOWN ONLY | 15 | PPMVD @ 15% O2 |  | 0 | 0 | N |  | LIMITS ARE PER TURBINE EXHAUST STACK. AGGREGATE CO EMISSIONS FROM BOTH TURBINE EXHAUST STACKS ARE LIMITED TO 1344.53 TONS PER YEAR. STARTUP & SHUTDOWN OPERATIONS ARE LIMITED TO 520 HOURS PER YEAR.
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Gas Turbines (8 units) | 15.11 | natural gas | 333 | mm btu/hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion practices and fueled by natural gas | 0.062 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110029511883 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion practices and fueled by natural gas | 15 | PPMVD | @15%O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | COMBUSTION TURBINES (2) | 15.11 | NATURAL GAS |  |  | GENERAL ELECTRIC 207FA COMBUSTION TURBINE WITH HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT FIRING CAPABILIY (DUCT BURNER EQUIPPED WITH LNB). EACH CT IS CAPABLE OF GENERATING A NOMINAL 176 MW OF ELECTRICITY. THE STEAM TURBINE IS CAPABLE OF GENERATING 304 MW OF ELECTRICITY. OVERALL FACILITY NOMINAL GENERATION CAPACITY OF 640 MW | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 2 | PPMVD @ 15% O2 | 3-HR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | APPLICABLE TO OPERATING WITH OR WITHOUT DUCT BURNING
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 2 COMBUSTION TURBINES | 15.11 | NATURAL GAS | 130 | MW | TWO GENERAL ELECTRIC (GE) FRAME 7EA COMBUSTION TURBINES (CTS) WITH A NOMINAL NET 87.2 MEGAWATT (MW) RATED CAPACITY, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), EQUIPPED WITH DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION SYSTEM (SCR), AND OXIDATION CATALYST | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | EXCLUSIVE USE OF FACILITY PROCESS FUEL GAS OR PIPELINE QUALITY NATURAL GAS, USE OF AN OXIDATION CATALYST AND EFFICIENT COMBUSTION | 1.5 | PPMVD @ 15% O2 | 3-HOUR BLOCK AVERAGE, EXLUDING SU/SD | BACT-PSD |  |  | 0 |  | 562.4 | LB/EVENT | FOR ALL STARTUPS | 0 |  |  | 0 | 0 | N |  | 59.2 LB/SHUTDOWN EVENT. LIMITS ARE TOTAL FOR BOTH FRAME 7 CTS PER STARTUP OR SHUTDOWN EVENT
MN-0075 | GREAT RIVER ENERGY - ELK RIVER STATION | GREAT RIVER ENERGY | SHERBURNE | MN | 55330 | USA | MARK STROHFUS | 7634455210 | MSTROHFU@GRENERGY.COM | 5 | MN001 | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | MR. RICHARD CORDES | (651)757-2291 | RICHARD.CORDES@STATE.MN.US | TONI VOLKMEIER, TONI.VOLKMEIER@PCA.STATE.MN.US | 14100003-004 | 4911 | 221119 | UNKNOWN | 03/31/2008 &nbsp;EST | 07/01/2008 &nbsp;ACT | 2008-12-01 | 2009-01-26 | B |  | THE FACILITY IS AN ELECTRIC POWER GENERATING STATION BURNING REFUSE DERIVED FUEL (RDF). THE RDF BURNED AT THIS FACILITY IS PROCESSED FROM MUNICIPAL SOLID WASTE. THE FACILITY PRODUCES APPROXIMATELY 40 MEGAWATTS OF ELECTRICITY. THERE IS ALSO A SINGLE CYCLE COMBUSTION TURBINE GENERATOR (CTG) |  | COMBUSTION TURBINE GENERATOR | 15.11 | NATURAL GAS | 2169 | MMBTU/H | GENERATOR IS A SIMPLE CYCLE COMBUSTION TURBINE, WHICH WILL BE OPERATED AS A PEAK-SHAVING UNIT. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 4 | PPM | 4 HR ROLLING AVG, NG, >/= 70% LOAD | BACT-PSD | NSPS , OTHER | Y | 0 | U | 10 | PPM | 4 HR ROLLING AVG, NG, 60% - 70% LOAD | 0.9 | LB/MW-H |  | 0 | 0 | N
MN-0075 | GREAT RIVER ENERGY - ELK RIVER STATION | GREAT RIVER ENERGY | SHERBURNE | MN | 55330 | USA | MARK STROHFUS | 7634455210 | MSTROHFU@GRENERGY.COM | 5 | MN001 | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | MR. RICHARD CORDES | (651)757-2291 | RICHARD.CORDES@STATE.MN.US | TONI VOLKMEIER, TONI.VOLKMEIER@PCA.STATE.MN.US | 14100003-004 | 4911 | 221119 | UNKNOWN | 03/31/2008 &nbsp;EST | 07/01/2008 &nbsp;ACT | 2008-12-01 | 2009-01-26 | B |  | THE FACILITY IS AN ELECTRIC POWER GENERATING STATION BURNING REFUSE DERIVED FUEL (RDF). THE RDF BURNED AT THIS FACILITY IS PROCESSED FROM MUNICIPAL SOLID WASTE. THE FACILITY PRODUCES APPROXIMATELY 40 MEGAWATTS OF ELECTRICITY. THERE IS ALSO A SINGLE CYCLE COMBUSTION TURBINE GENERATOR (CTG) |  | COMBUSTION TURBINE GENERATOR | 15.11 | NATURAL GAS | 2169 | MMBTU/H | GENERATOR IS A SIMPLE CYCLE COMBUSTION TURBINE, WHICH WILL BE OPERATED AS A PEAK-SHAVING UNIT. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION CONTROL | 250 | PPM | 4 HR ROLLING AVG, FO, 60% - 70% LOAD | BACT-PSD | NSPS , OTHER | Y | 0 | U | 600 | PPM | 4 HR ROLLING AVG, FO, <60% LOAD | 0 |  |  | 0 | 0 | N |  | SEPARATE LIMITS FOR NATURAL GAS OR FUEL OIL COMBUSTION, AND FOR DIFFERING LOADS
ND-0028 | R.M. HESKETT STATION | MONTANA-DAKOTA UTILITIES CO. | MORTON | ND | 58554 | USA | ABBIE KREBSBACH | (701) 222-7844 | ABBIE.KREBSBACH@MDU.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Primary contact is Tom Bachman at (701) 328-5188. | PTC13016 | 4911 | 221112 | 110022356591 | 11/07/2012 &nbsp;ACT | 02/22/2013 &nbsp;ACT | 2013-04-01 | 2017-04-28 | B |  | Addition of a natural gas-fired turbine (Unit 3) to an exisiting coal-fired power plant. The turbine will be used for supplying peak power and is rated at 986 MMBtu/hr and 88 MWe at average site conditions. |  | Combustion Turbine | 15.11 | Natural gas | 986 | MMBTU/H | Turbine is a GE Model PG 7121 (7EA) used as a peaking unit. | Carbon Monoxide | Other - CEMS | (InOrganic Compounds) | 630-08-0 | P | Good Combustion | 25 | PPMVD @ 15% OXYGEN | 4 H.R.A./WHEN > 50 MWE | BACT-PSD |  | Y | 0 | U | 27 | TONS/30 DAY | 30 DAY ROLLING TOTAL / WHEN < 50 MWE | 0 |  |  | 0 | 0 | N
ND-0029 | PIONEER GENERATING STATION | BASIN ELECTRIC POWER COOPERATIVE | WILLIAMS | ND |  | USA | JERRY MENGE | 7012230441 | JMENGE@BEPC.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact. | PTC 13037 | 4911 | 221112 | 110058380238 | 02/19/2013 &nbsp;ACT | 05/14/2013 &nbsp;ACT | 2013-06-19 | 2016-11-03 | B |  | Three GE LM6000 PC SPRINT natural gas fired turbines used to generate electricity for peak periods. | The permit was for the addition of 2 turbines to the station. Since a synthetic minor limit was relaxed for the first unit, BACT was required for all three turbines. | Natural gas-fired turbines | 15.11 | Natural gas | 451 | MMBTU/H | Rating is for each turbine. | Carbon Monoxide | Other - CEM | (InOrganic Compounds) | 630-08-0 | A | Catalytic oxidation system | 6 | PPMVD | 8 HR. ROLLING AVERAGE/EXCEPT STARTUP | BACT-PSD |  | U | 95.2 | N | 57.2 | LB/H | DURING STARTUP | 0 |  |  | 0 | 0 | N |  | RBLC Staff: Original Emis Limit 2 Units were Numeric Limit - &lsquo;&lsquo;LB&lsquo;&lsquo; and Avg Time/Condition - &lsquo;&lsquo;1 HR/DURING STARTUP&lsquo;&lsquo; The Emission Units are usually &lsquo;&lsquo;mass unit PER time unit&lsquo;&lsquo;. Separating them out makes understanding limit difficult for the users. The units were combined. The corrected entry is: Numeric Limit - &lsquo;&lsquo;LB/H&lsquo;&lsquo; Avg Time/Condition - &lsquo;&lsquo;During Startup&lsquo;&lsquo;
ND-0030 | LONESOME CREEK GENERATING STATION | BASIN ELECTRIC POWER COOP. | MCKENZIE | ND | 58831 | USA | JERRY MENGE | (701)223-0441 |  | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact at (701) 328-5188. | PTC 13049 | 4911 | 221112 | 110057111003 | 04/05/2013 &nbsp;EST | 09/16/2013 &nbsp;ACT | 2013-09-24 | 2017-06-28 | B |  | Three natural gas fired simple cycle turbines used to generate electricity for peak power demand. The turbines are GE LM6000 PF Sprint units with a nominal capacity of 45 MW each. |  | Natural Gas Fired Simple Cycle Turbines | 15.11 | Natural gas | 412 | MMBTU/H | The heat input is for a single unit. | Carbon Monoxide | Other - CEM | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 6 | PPMVD | 8-HOUR ROLLING AVERAGE EXCEPT STARTUP | BACT-PSD |  | N | 90 | N | 31.5 | LB | 30 MINUTE TOTAL FOR STARTUP | 0 |  |  | 0 | 0 | N |  | The startup limit is for each unit. The three units are limited to a total combined emission rate of 54.2 pounds per hour (1-hour average) at all times.
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110000801614 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine with Duct Burner firing natural gas | 15.11 | Natural Gas | 0 |  |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation Catalyst and good combustion practices | 2 | PPMVD@15%O2 | 3 H ROLLING AV BASED ON ONE H BLOCK | BACT-PSD | OPERATING PERMIT | N | 74 | N | 18.7 | LB/H | AV OF THREE ONE H STACK TESTS | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110000801614 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine without Duct Burner Firing Natural Gas | 15.11 | Natural Gas | 28169501 | MMBTU/YR | Natural Gas Usage: <=28,169,501 MMBtu/year which includes maximum ultra low sulfur distillate oil usage of =2,371,943 MMBTU/year | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST AND GOOD COMBUSTION PRACTICES | 2 | PPMVD@15%O2 | 3 H ROLLING AV BASED ON ONE H BLOCK | BACT-PSD | OPERATING PERMIT | N | 74 | N | 15.4 | LB/H | AV OF THREE ONE H STACK TESTS | 0 |  |  | 0 | 0 | N
NM-0051 | CUNNINGHAM POWER PLANT | SOUTHWESTERN PUBLIC SERVICE CO. | LEA | NM | 88241-1650 | USA | KEVIN WORLEY | 806 378 2185 | KEVIN.WORLEY@XCELENERGY.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Cember Hardison is permit writer. 505 476 4346. cember.hardison@state.nm.us | PSD-NM-622-M3 | 4911 | 221122 | 110010571639 | 03/08/2011 &nbsp;ACT | 05/02/2011 &nbsp;ACT | 2011-08-02 | 2012-01-05 | C |  | Electric steam generating facility providing commercial electric power using natural gas fired boilers and turbines. | Simple Cycle Combustion Turbines. Permit revises the NOx BACT ppmvd limit for turbines established in permit PSD-NM-622-M2 issued 2-10-97 because turbines have not been able to meet NOx BACT limits. No modification or change to mass emissions. Former NOx BACT was at 15 ppmvd w/out power augmentation (normal mode) and 25 ppmvd w/ power augmentation (see RBLC ID NM-0028). Entry also clarifies the existing CO, SOx, and PM BACT. | Normal Mode (without Power Augmentation) | 15.11 | natural gas | 0 |  |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good Combustion Practices as defined in the permit. | 77.2 | LB/H | HOURLY | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO BACT established in PSD-NM-622-M2 issued 2-10-97.
NM-0051 | CUNNINGHAM POWER PLANT | SOUTHWESTERN PUBLIC SERVICE CO. | LEA | NM | 88241-1650 | USA | KEVIN WORLEY | 806 378 2185 | KEVIN.WORLEY@XCELENERGY.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Cember Hardison is permit writer. 505 476 4346. cember.hardison@state.nm.us | PSD-NM-622-M3 | 4911 | 221122 | 110010571639 | 03/08/2011 &nbsp;ACT | 05/02/2011 &nbsp;ACT | 2011-08-02 | 2012-01-05 | C |  | Electric steam generating facility providing commercial electric power using natural gas fired boilers and turbines. | Simple Cycle Combustion Turbines. Permit revises the NOx BACT ppmvd limit for turbines established in permit PSD-NM-622-M2 issued 2-10-97 because turbines have not been able to meet NOx BACT limits. No modification or change to mass emissions. Former NOx BACT was at 15 ppmvd w/out power augmentation (normal mode) and 25 ppmvd w/ power augmentation (see RBLC ID NM-0028). Entry also clarifies the existing CO, SOx, and PM BACT. | Power Augmentation | 15.11 | natural gas | 0 |  | Increase power output by lowering the outlet air temperatur through water inejctinos into the compressor. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices as defined in the permit. | 138.9 | LB/H | HOURLY | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO BACT established in PSD-NM-622-M2 issued 2-10-97.
NY-0103 | CRICKET VALLEY ENERGY CENTER | CRICKET VALLEY ENERGY CENTER LLC | USA | NY | 12522-0407 | USA |  | 845-877-0596 | INFO@CRICKETVALLEY.COM | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-1326-00275/00009 | 4911 | 221112 | 110043340364 | 02/03/2016 &nbsp;ACT | 02/03/2016 &nbsp;ACT | 2017-08-24 | 2017-09-28 | A | http://www.dec.ny.gov/chemical/32249.html | Cricket Valley Energy Center LLC (CVEC) constructed the Cricket Valley Energy Center (the Facility), a nominal net 1,000-megawatt (MW) combined-cycle gas turbine electric generating facility, on a site located in Dover, Dutchess County, New York. The Facility consists of three General Electric (GE) Model 7FA.05 combustion turbine generators (CTGs) operating in combined-cycle mode with supplemental firing of the heat recovery steam generators (HRSGs); natural gas will be the sole fuel fired in the CTGs and duct burners. The Facility will include a natural gas-fired auxiliary boiler, four ultra-low sulfur distillate (ULSD) fired black-start generator engines and a ULSD-fired emergency fire pump engine. In addition to the air emitting equipment, the Facility will include three steam turbine generators (STGs), an air cooled condenser (ACC) and associated auxiliary equipment and systems. Each combined cycle generating unit consisting of the CTG, HRSG and STG will be exhausted through its own stack. Air emissions from the proposed Facility primarily consist of products of combustion from the CTGs, HRSG duct burners, and ancillary combustion sources. Dutchess County is designated as in attainment with respect to the National Ambient Air Quality Standards (NAAQS) for all criteria pollutants with the exception of ozone. Based upon the potential to emit (PTE) estimates, the Facility is subject to Prevention of Significant Deterioration (PSD) requirements for emissions of carbon monoxide (CO); nitrogen oxides (NOx); particulate matter (PM) with a diameter equal to or less than 10 microns (PM10), PM with a diameter equal to or less than 2.5 microns (PM2.5); greenhouse gases (GHG); sulfuric acid mist (H2SO4); and volatile organic compounds (VOC). In accordance with the NYSDECâ€™s Nonattainment New Source Review (NNSR) permitting program, the Facility is also subject to NNSR for emissions of NOx and VOC. |  | Turbines and duct burners | 15.11 | natural gas | 228 | mw |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | good combustion practice and oxidation catalyst | 2 | PPMVD @ 15% O2 | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Applies to all operating loads, except during startup and shutdown.
NY-0106 | GREENIDGE STATION | GREENIDGE GENERATION LLC | YATES | NY | 14441-0187 | USA |  | 315-536-2359 |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov |  | 8-5736-00004/00017 | 4911 | 221112 | 110000327619 | 09/07/2016 &nbsp;ACT | 09/07/2016 &nbsp;ACT | 2017-08-30 | 2017-09-28 | C | http://www.dec.ny.gov/chemical/32249.html | Greenidge Generation LLC has submitted a revised application for a Title V Air Permit in accordance with the requirements of Title 6 of the New York compilation of Codes, Rules, and Regulations, Part 201-6 (6 NYCRR Part 201-6). The application is for conversion of the Greenidge Electricity Generating Station, located in the Town of Torrey, Yates County to operate primarily on natural gas with up to 19% biomass co-firing. Greenidge Station is comprised of Unit 4, which includes a Combustion Engineering, tangentially-fired dry bottom boiler (Boiler No. 6) with a maximum heat input rating of 1,117 MMBtu/hr, and a steam generating turbine with a maximum rated output of 107 Megawatts (MW) of electricity. The facility is equipped with a suite of air pollution control (both pre-combustion and post-combustion) systems to control pollutant nitrogen oxides, carbon monoxide, and particulate matter (PM, PM10 and PM2.5) emissions from facility operations. Greenhouse gases will be reduced substantially primarily by the use of cleaner fuels. Under the proposal, Unit 4 will not burn coal or fuel oil any longer. | Also NAICS 221117 - biomass with wood | Turbine - natural gas | 15.11 | natural gas | 107 | MW |  | Carbon Monoxide | Other - 40 CFR 60 App A | (InOrganic Compounds) | 630-08-0 | N |  | 0.095 | LB/MMBTU | 12 MO | BACT-PSD |  | U | 0 | U | 0.037 | LB/MMBTU | 24 H | 0 |  |  | 0 | 0 | N |  | Includes startups, shutdowns, malfunctions, and upsets.
OH-0333 | DAYTON POWER & LIGHT ENERGY LLC | DAYTON POWER & LIGHT COMPANY | MONTGOMERY | OH | 45439 | USA | CARRIE BURKS | 937-331-3042 |  | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104867 | 4911 | 221112 | 110000394145 | 04/30/2009 &nbsp;ACT | 12/03/2009 &nbsp;ACT | 2010-05-13 | 2010-05-20 | C |  | Seven simple cycle stationary combustion turbines all with rating of 80 MW and nominal heat input of 1115.2 mmBtu/hr using natural gas or No. 2 fuel oil and all with water injection control and last 5 also with low NOx burners. | Simple cycle stationary combution turbines issed in 2 different permits. Four turbines in this permit with dry low NOx combustion and water injection controls. Administrative Modification to original PTI #08-04153 issued 8/7/01, to incorporate low mass emissions methodology as allowed per 40 CFR 75.19 in lieu of methods under Appendix D or E to Part 75, by meeting the requirements of having mass emissions of less than 25 T/YR SO2 and less than 100 T/YR NOx (per turbine) based on 3 years of operation. Modification also reduced permitted formaldehyde emissions by 8.7 tons, recalculated based on the restriction on hours of operation. | Turbines (4), simple cycle, natural gas | 15.11 | NATURAL GAS | 15020 | H/YR | Hours per year for all 4 turbines | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | efficient combution technology | 301 | LB/H | EACH TURBINE | BACT-PSD | SIP | U | 0 | Y | 724 | T/YR | PER ROLLING 12-MO. FOR 4 UNITS &ALL FUEL | 20 | PPMV | AT 15% OXYGEN ON A DRY BASIS AS 3HR AVG. | 0 | 0 | N |  | T/YR limit is for both fuels and for the 4 turbines combined. Limit during startup-shutdown shall not exceed 413 LB/H for each unit when burning natural gas.
OK-0127 | WESTERN FARMERS ELECTRIC ANADARKO | WESTERN FARMERS ELECTRIC COOPERATIVE | CADDO | OK | 73005 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2005-037-C(M-2) PSD | 4911 | 221112 | 110001631440 | 02/01/2008 &nbsp;ACT | 06/13/2008 &nbsp;ACT | 2008-12-31 | 2009-04-20 | B |  | THE FACILITY GENERATES WHOLESALE ELECTRICITY WHICH IS TRANSMITTED OVER WFECÂ¿S ELECTRICAL DISTRIBUTION SYSTEM. THE ELECTRICITY IS SOLD IN RURAL AREAS OF APPROXIMATELY 3/4 OF THE STATE OF OKLAHOMA. THE CURRENT FACILITY CONSISTS OF TWO NATURAL GAS FIRED HIGH PRESSURE BOILERS, A GAS/OIL FIRED HIGH PRESSURE BOILER, THREE GAS/OIL FIRED COMBINED CYCLE GAS TURBINES, A FIRE PUMP DIESEL ENGINE FOR EMERGENCY BACKUP, AND OTHER SOURCES WHICH ARE CONSIDERED INSIGNIFICANT OR TRIVIAL. THE THREE BOILERS ARE BACKUP UNITS THAT ONLY OPERATE WHEN IT IS FEASIBLE, SUCH AS DURING PEAK DEMAND. TWO OF THE BOILERS HAVE BEEN IDLE SINCE 1984. ONE BOILER WAS REPLACED IN 1997, AND ANOTHER WAS REPLACED IN 1998. | WESTERN FARMERS ELEC COOP PROPOSES TO CONSTRUCT AND OPERATE THREE NATURAL GAS-FIRED PEAKING ELECTRIC GENERATING UNITS AT THE FACILITY TO MEET ANTICIPATED FUTURE ENERGY DEMAND. EACH UNIT CAPACITY OF +/- 50 MW. | COMBUSTION TURBINE PEAKING UNIT(S) | 15.11 | NATURAL GAS | 462.7 | MMBTU/H | THE INSTALLATION WILL CONSIST OF THREE GENERAL ELECTRIC LM6000 SPRINT SIMPLE CYCLE AERODERIVATIVE COMBUSTION TURBINE GENERATORS. EACH OF THE TURBINES WILL HAVE A MAXIMUM PEAK HEAT INPUT RATE OF 462.7 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTUH). THE NEW COMBUSTION TURBINES WILL FIRE ONLY PIPELINE-QUALITY NATURAL GAS AND WILL BE EQUIPPED WITH WATER INJECTION. THE PROPOSED NEW UNITS WILL EACH HAVE A NOMINAL ELECTRICAL GENERATING CAPACITY OF 50 MW. ACTUAL UNIT CAPACITY WILL BE DETERMINED DURING DETAILED DESIGN OF THE PLANT AND MAY BE 5 TO 10-MW HIGHER OR LOWER THAN THE NOMINAL VALUE OF 50 MW, DEPENDING ON AMBIENT CONDITION RATINGS AND FINAL DESIGN. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N | NO CONTROLS FEASIBLE. | 63 | PPM | CORRECTED TO 15% O2 | BACT-PSD |  | U | 0 | U | 65.5 | LB/H | 2,500 HR/YEAR | 0 |  |  | 0 | 0 | N |  | GOOD COMBUSTION PRACTICES AND DESIGN TO 63 PPMVD CORRECTED TO 15% O2 IS DETERMINED ACCEPTABLE AS BACT.
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | GE LMS-100 combustion turbines, simple cycle with water injection | 15.11 | natural gas | 1690 | MMBTU/H |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | B | Oxidation catalyst; Limit the time in startup or shutdown. | 6 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON NG | BACT-PSD |  | U | 0 | U | 6 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON ULSD | 0 |  |  | 0 | 0 | N
*PA-0305 | SHELL CHEM APPALACHIA/PETROCHEMICALS COMPLEX | SHELL CHEMICAL APPALACHIA | BEAVER | PA | 15061-2210 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 04-00740A | 2821 | 325110 | 110060029115 | 05/01/2014 &nbsp;ACT | 06/18/2015 &nbsp;ACT | 2017-06-05 | 2017-07-12 | A |  | The plan approval will allow the construction and temporary operation of seven (7) 620 MMBtu/hr ethane cracking furnaces fired primarily by tail gas and natural gas for the production of approximately 1.5 million metric tons/year of polyethylene. Byproducts from the ethylene production include coke residue/tar, light gasoline, pyrolysis fuel oil, and a C3+ mixture and will be remove from the site for disposal or use as appropriate. Additional facilities include an electric and steam cogeneration from three (3) combustion turbines with duct burners and heat recovery steam generators with a plant capacity of 250.4 MW, four (4) emergency generators, three (3) diesel-fired fire pump engines, cooling towers, flares, and storage tanks. | (7) 620.000 MMBtu/hr Ethane cracking furnaces, (3) 664.000 combustion turbines with duct burners. Shell intends to convert ethane in to ethylene for manufacturing of various grades of low density and high density polyethylene as a final product. | Combustion turbine wih duct burner and heat recovery steam generator | 15.11 | Natural Gas | 0 | Three 40.6 MW turbines | Three (3) General Electric Frame 6B NG fired turbine with duct burners and heat recovery steam generators. Total electric generating capacity will be 250.4 MW from cogeneration three turbines at 40.6 MW and two HRSG at 64.3 MW. Excess electricity generated will be sold to the grid in quantities sufficient to classify the facility as an electric utility. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 2 | PPMDV @ 15% O2 | 1 HR AVG EX DURING STARTUP AND SHUTDOWN | BACT-PSD |  | U | 0 | U | 276 | LB/HR | DURING STARTUP AND SHUTDOWN | 0 |  |  | 0 | 0 | N
SC-0161 | DUKE ENERGY CAROLINAS LLC, W.S. LEE STEAM STATION |  | ANDERSON | SC | 29627 | USA |  | SYSNULL |  | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MR. DENNIS CAMIT | (803)898-4284 | camitdr@dhec.sc.gov | SHEILA WATTS (803) 898-4123 | 0200-0004-CG | 4911 | 221112 | 110004937864 | 01/16/2013 &nbsp;ACT | 02/19/2014 &nbsp;ACT | 2015-08-25 | 2017-07-24 | B |  |  |  | COMBINED CYCLE COMBUSTION TURBINES (SIEMENS) | 15.11 |  | 0 |  | THE FACILITY PLANS TO INSTALL EITHER TWO GE 7FA.05 OR TWO SIEMENS SGT-5000F(5) NATURAL GAS FIRED COMBUSTION TURBINE GENERATORS, EACH EQUIPPED WITH A DUCT-FIRED HEAT RECOVERY STEAM GENERATOR. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | A | OXIDATION CATALYST | 4.7 | LB/H | CONT. OPERATION WITHOUT DUCT BURNERS | BACT-PSD |  |  | 0 |  | 1804 | LB/H | AVG. PER STARTUP AND SHUTDOWN EVENT | 0.9 | PPMVD @ 15% O2 | CONT. OPERATION WITHOUT DUCT BURNERS | 0 | 0 | N |  | THERE ARE ALSO CO EMISSON LIMITS ASSOCIATED WITH DUCT BURNERS (CONTINUOUS OPERATION) WHICH ARE 1.7 PPMVD @15% O2 AND 11.4 LB/HR.
TX-0540 | BOSQUE COUNTY POWER PLANT | BOSQUE POWER COMPANY LLC | BOSQUE | TX | 76644 | USA | MS KATHY FRENCH | 6365322200 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | MS. BRIDGET MALONE (512) 239-4286 | 40620 | 4911 | 221112 | 4803500002 | 10/26/2007 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | PSDTX931M1 | ELECTRICAL GENERATION | 15.11 | NATURAL GAS | 170 | MW | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | BACT IS THE USE OF GOOD COMBUSTION PRACTICES TO MINIMIZE THE PRODUCTS OF INCOMPLETE COMBUSTION AND ACHIEVE 9 PPMVD AT 15% O2 IN THE TURBINE EXHAUST OVER A ROLLING 3-HOUR PERIOD. | 9 | PPMVD | 3 HOUR @ 15% O2 | BACT-PSD |  |  | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057188626 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.11 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane and methane section compressors. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | dry low emission combustors | 29 | PPMVD | @15% O2, 4 HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0686 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JEFF PIPPIN | 806-418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, 512-239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358 | 4911 | 221112 | 110043432737 | 04/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-03-18 | 2016-05-09 | B |  | GSEC is proposing to build three additional new CTGs at the existing Antelope Elk Energy Center. The new facility will provide primarily peaking and intermediate power needs. The new units will be GE 7F5-Series gas turbines in simple cycle application, rated at 202 MW. Each turbine will operate a maximum of 4,572 hours per year. |  | Combustion Turbine-Generator(CTG) | 15.11 | Natural Gas | 202 | MW | Simple Cycle | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices; limited hours | 9 | PPMVD | 15% O2, 3HR AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0688 | SR BERTRON ELECTRIC GENERATION STATION | NRG TEXAS POWER | HARRIS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 102731, PSDTX1294 | 4911 | 221112 | 110034988413 | 05/10/2012 &nbsp;ACT | 12/19/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power generation station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the simple cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The new units will produce between 215-263 MW each. |  | Simple cycle natural gas turbines | 15.11 | Natural Gas | 225 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good Combustion Practices | 9 | PPM | 1HR ROLLING AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0690 | CEDAR BAYOU ELECTRIC GERNERATION STATION | NRG TEXAS POWER | CHAMBERS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 105810, PSDTX1308 | 4911 | 221112 | 110015743301 | 08/29/2014 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power generation station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the simple cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The units will produce between 215-263 MW each. |  | Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 225 | MW | The gas turbines will be one of three options: (1) Two Siemens Model F5 (SF5) CTGs each rated at nominal capability of 225 megawatts (MW). (2) Two General Electric Model 7FA (GE7FA) CTGs each rated at nominal capability of 215 MW. (3) Two Mitsubishi Heavy Industry G Frame (MHI501G) CTGs each rated at a nominal electric output of 263 MW. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good Combustion Practices | 9 | PPM | 1HR ROLLING AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0691 | PH ROBINSON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | GALVESTON | TX |  | USA | CRAIG ECKBERG | (832) 357-5291 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 erik.hendrickson@tceq.texas.gov | 108182 PSDTX1346 | 4911 | 221112 | 110002345515 | 02/06/2013 &nbsp;ACT | 05/20/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG proposes to construct six natural gas-fired simple cycle combustion turbine generators (CTG) for peaking, designed to operate during periods of high electric demand. The six CTGs selected by NRG are General Electric Frame 7E turbines have an ISO rating of 65 MW and a nominal maximum generating capacity of 80 MW. Each of the turbines will not exceed 20 percent annual capacity (equivalent to 1,752 full load hours) in any single year or 10 percent annual capacity factor (equivalent to 876 full load hours) averaged over any three year period. |  | (6) simple cycle turbines | 15.11 | natural gas | 65 | MW | General Electric Frame 7E turbines have an ISO rating of 65 MW and a nominal maximum generating capacity of 80 MW. The turbines were originally constructed as Frame 7B units that were remanufactured in 1999 and upgraded to 7E machines Each of the turbines will not exceed 20 percent annual capacity (equivalent to 1,752 full load hours) in any single year or 10 percent annual capacity factor (equivalent to 876 full load hours) averaged over any three year period, which qualifies each of the CTGs as Acid Rain Peaking Units under 40 CFR 72.2 | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | DLN combustors | 25 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | limited use
TX-0693 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE INC | HALE | TX |  | USA | JEFF PIPPIN | (806) 418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson 512-239-2175 laura.gibson@tceq.texas.gov | 109148 PSDTX1358 | 4911 | 221112 | 110043432737 | 04/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-03-19 | 2016-07-29 | B |  | Golden Spread Electric Cooperative (GSEC) currently owns and operates Antelope Station (now renamed Antelope Elk Energy Center), a 168 MW generating facility made up of 18 quick start WÃ¤rtsilÃ¤ engines. GSEC is proposing to build a new combustion turbine-generator (CTG) facility at Antelope Station, while the 18 WÃ¤rtsilÃ¤ engines will remain and continue to be authorized by TCEQ Standard Permit. The new turbine-generator will provide primarily peaking and intermediate power needs in a highly cyclical operation. The CTG will produce approximately 100 - 200 MW of electricity, depending on loading and ambient temperature. |  | combustion turbine | 15.11 | natural gas | 202 | MW | new GE 7FA 5-Series gas turbine in a simple cycle application, with a maximum electric output of 202 megawatts (MW) and a maximum design capacity of 1,941 million British thermal units per hour (MMBtu/hr). The turbine will operate a maximum of 4,572 hours per year. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | DLN combustors, good combustion practices | 9 | PPMVD | @15% O2. 3-HR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0694 | INDECK WHARTON ENERGY CENTER | INDECK WHARTON, L.L.C. | WHARTON | TX |  | USA | JAMES SCHNEIDER | (847) 520-3212 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 111724 PSDTX1374 | 4911 | 221112 | unknown | 06/18/2013 &nbsp;ACT | 02/02/2015 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | Indeck Wharton, L.L.C. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will either be the General Electric 7FA (~214 MW each) or the Siemens SGT6-5000F (~227 MW each), operating as peaking units in simple cycle mode. |  | (3) combustion turbines | 15.11 | natural gas | 220 | MW | The CTGs will either be the General Electric 7FA (~214 MW each) or the Siemens SGT6-5000F (~227 MW each), operating as peaking units in simple cycle mode | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | DLN combustors | 4 | PPMVD | @15% O2, 3-HR ROLLING AVG - SIEMENS | BACT-PSD |  | U | 0 | U | 9 | PPMVD | @15% O2, 3-HR ROLLING AVG - GE 7FA | 0 |  |  | 0 | 0 | N
TX-0695 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX |  | USA | JIM SHIELD | (312) 582-1440 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | 110423 PSDTX1366 | 4911 | 221112 | 110057112850 | 05/13/2013 &nbsp;ACT | 08/01/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | The proposed project is to construct and operate two natural gas-fired simple-cycle combustion turbine generators (CTGs) at the Ector County Energy Center (ECEC), located approximately 20 miles northwest of Odessa, Texas, in Ector County. |  | (2) combustion turbines | 15.11 | natural gas | 180 | MW | (2) GE 7FA.03, 2500 hours of operation per year each | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | DLN combustors | 9 | PPMVD | @15% O2, 3-HR ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 2500 hrs/yr operation
TX-0696 | ROANâ€™S PRAIRIE GENERATING STATION | TENASKA ROANâ€™S PRAIRIE PARTNERS (TRPP), LLC | GRIMES | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 erik.hendrickson@tceq.texas.gov | 114698 PSDTX1378 | 4911 | 221112 | 110028050141 | 10/25/2013 &nbsp;ACT | 09/22/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | The proposed project is to construct and operate the RPGS comprised of three new simple cycle combustion turbine generators (CTG), fueled by pipeline quality natural gas. The new CTGs will be peaking units, designed to operate during periods of high electric demand. The three CTGs will produce between 507 and 694 MW of electricity combined, depending on ambient temperature and the model of combustion turbine (CT) selected. The applicant is considering three models of CTs; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. |  | (2) simple cycle turbines | 15.11 | natural gas | 600 | MW | The three possible CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. will operate 2,920 hours per year at full load for each CT | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | DLN combustors | 9 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | will operate 2,920 hours per year at full load for each CT
TX-0701 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX |  | USA | JIM SHIELD | 312-582-1440 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Marc Sturdivant, 512-239-1313, Marc.Sturdivant@tceq.texas.gov | 110423, PSDTX1366 | 4911 | 221112 | 110013396379 | 08/01/2014 &nbsp;ACT | 05/13/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is for two natural gas fired simple cycle CTGs. The proposed models include GE7Fa.03 and GE7Fa.05. They have an output of 165-193 MW. The new CTGs will operate as peaking units and will be limited to 2500 hours per year of operation each. |  | Simple Cycle Combustion Turbines | 15.11 | natural gas | 180 | MW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 9 | PPMVD | 15%O2, 3HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0733 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JOLLY HAYDEN | 806-349-5250 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, (512)239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358M1 | 4911 | 221112 | 110043432737 | 03/20/2015 &nbsp;ACT | 05/12/2015 &nbsp;ACT | 2015-05-04 | 2016-06-08 | B |  | Golden Spread Electric Cooperative, Inc. (GSEC) is requesting authorization for three additional simple cycle electric generating plants at an existing site to meet increased energy demand in the area. The generating equipment consists of three new GE 7F5-Series natural gas-fired combustion turbine generators (CTGs). Each turbine has a maximum electric output of 202 MW. |  | Simple Cycle Turbine &amp; Generator | 15.11 | natural gas | 202 | MW | 3 additional GE 7F 5-Series Combustion Turbine Generators | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices; limited operating hours | 9 | PPMVD @ 15% O2 | 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of each turbine is limited to 4,572 hours per year
TX-0734 | CLEAR SPRINGS ENERGY CENTER (CSEC) | NAVASOTA SOUTH PEAKERS OPERATING COMPANY II, LLC. | GUADALUPE | TX | 78155 | USA | FRANK GIACALONE | (281) 252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jack Coleman, 512-239-1255, jack.coleman@tceq.texas.gov | 120849 AND PSDTX1414 | 4911 | 221112 | Not Found | 02/20/2015 &nbsp;ACT | 05/08/2015 &nbsp;ACT | 2015-05-08 | 2018-04-18 | A |  | Navasota South Peakers Operating Company II LLC. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 MW each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | DLN burners and good combustion practices | 9 | PPMVD @ 15% O2 | ALL LOADS | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK CTGs will operate at 2500 hours of operation per year at baseload.
TX-0764 | NACOGDOCHES POWER ELECTRIC GENERATING PLANT | NACOGDOCHES POWER, LLC | NACOGDOCHES | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem 512-239-1310 Tzvi.shalem@tceq.texas.gov | 77679, PSDTX1061M1 & O-3455 | 4911 | 221112 | 110043814744 | 06/25/2015 &nbsp;ACT | 10/14/2015 &nbsp;ACT | 2015-09-16 | 2016-07-06 | B |  | Nacogdoches Power, LLC is requesting authorization for one natural gas fired, simple cycle combustion turbine generator (CTG). The CTG will be a Siemens F5 and have a nominal electric output of 232 megawatts (MW). |  | Natural Gas Simple Cycle Turbine (&gt;25 MW) | 15.11 | natural gas | 232 | MW | One Siemens F5 simple cycle combustion turbine generator | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | dry low NOx burners, good combustion practices, limited operation | 9 | PPMVD @ 15% O2 |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,500 hours on a 12-month rolling average.
TX-0768 | SHAWNEE ENERGY CENTER | SHAWNEE ENERGY CENTER, LLC | HILL | TX |  | USA | NEIL O'DONOVAN | 312-422-1608 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, P.E., 512-239-1353, joseph.janecka@tceq.texas.gov | PSDTX1442, 125963 | 4911 | 221112 | UNKNOWN | 07/31/2015 &nbsp;ACT | 10/09/2015 &nbsp;ACT | 2015-10-05 | 2016-07-06 | A |  | Electric Generating Utility: The project will consist of four gas fired combustion turbines (CTGs). The CTGs are fueled with pipeline quality natural gas and will operate in simple cycle mode. The gas turbines will be one of two options. |  | Simple cycle turbines greater than 25 megawatts (MW) | 15.11 | natural gas | 230 | MW | Siemens Model SGT6-5000 F5ee â€“ 230 MW or Second turbine option: General Electric Model 7FA.05TP â€“ 227 MW | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | dry low NOx burners and lmiited operation, clean fuel | 9 | PPMVD @ 15% O2 |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0769 | VAN ALSTYNE ENERGY CENTER (VAEC) | NAVASOTA NORTH COUNTRY PEAKERS OPERATING COMPANY I | GRAYSON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 121051 AND PSDTX1418 | 4911 | 221112 | UNKNOWN | 12/22/2014 &nbsp;ACT | 10/27/2015 &nbsp;ACT | 2015-10-30 | 2016-07-06 | A |  | Navasota North Country Peakers Operating Company I LLC. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 MW each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | DLN burners and good combustion practices | 9 | PPMVD @ 15% O2 |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CTGs will operate at 2500 hours of operation per year at baseload. NSPS KKKK
TX-0777 | UNION VALLEY ENERGY CENTER | NAVASOTA SOUTH PEAKERS OPERATING COMPANY I, LLC. | NIXON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 120973 AND PSDTX1420 | 4911 | 221112 | UNKNOWN | 02/06/2015 &nbsp;ACT | 12/09/2015 &nbsp;ACT | 2015-12-03 | 2016-07-06 | A |  | three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 megawatt (MW) each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | dry low NOx burners and good combustion practices | 9 | PPMVD @ 15% O2 | ALL LOADS | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK CTGs will operate at 2500 hours of operation per year at baseload.
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Large Combustion Turbines &gt; 25 MW | 15.11 | natural gas | 232 | MW | 4 Simple cycle CTGs, 2,500 hr/yr operational limitation. Facility will consist of either 232 MW (Siemens) or 220 MW (GE) | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion practices | 9 | PPM |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Subparts KKKK and TTTT
TX-0794 | HILL COUNTY GENERATING FACILITY | BRAZOS ELECTRIC COOPERATIVE | HILL | TX |  | USA | MIKE MEYERS | (254)750-6228 | MMEYERS@BRAZOSELECTRIC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512)239-1512, randy.hamilton@tceq.texas.gov | 130051,PSDTX1450, GHGPSDTX131 | 4911 | 221112 | UNKNOWN | 12/18/2015 &nbsp;ACT | 04/07/2016 &nbsp;ACT | 2016-04-05 | 2016-07-29 | A |  | Four simple cycle combustion turbine electric generators are proposed. Natural gas or ultra-low sulfur diesel fuel oil are the fuels. Turbine model options are: General Electric (GE) 7FA.03, GE 7FA.04, GE 7FA.05, and Siemes SGT6-5000(5)ee. Electric output is between 684 and 928 megawatts (MW). |  | Simple cycle turbine | 15.11 | natural gas | 171 | MW | Each combustion turbine is limited to 2,920 hours of annual operation, including startup and shutdown hours. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Premixing of fuel and air enhances combustion efficiency and minimizes emissions. | 9 | PPMVD @ 15% O2 | 3-HR AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0816 | CORPUS CHRISTI LIQUEFACTION | CORPUS CHRISTI LIQUEFACTION STAGE III, LLC | SAN PATRICIO | TX |  | USA | KEITH LITTLE | (713) 375-5204 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 139479, PSDTX1496, GHGPSDTX157 | 4925 | 221210 | Not Found | 11/16/2016 &nbsp;ACT | 02/14/2017 &nbsp;ACT | 2017-02-07 | 2018-04-18 | B |  | Trains 4 and 5 will consist of 12 natural gas compressor turbines, 2 thermal oxidizers, 2 sets of flares each comprised of one wet gas flare and one dry gas flare, 2 amine surge tanks (maintenance, startup, and shutdown [MSS] only), 3 diesel generators, 3 fire-water pump diesel engines, 6 fixed roof diesel storage tanks, and piping components. |  | Refrigeration compressor turbines | 15.11 | NATURAL GAS | 40000 | HP | 2 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane, ethylene, and methane section compressors. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Dry low emission burners | 29 | PPMDV | @ 15% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Simple Cycle Turbine | 15.11 | natural gas | 227.5 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices; limited operating hours | 9 | PPMVD | 3% O2 3-H AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Dry low NOx burners | 9 | PPMVD |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines MSS | 15.11 | NATURAL GAS | 0 |  |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Minimizing duration of startup/shutdown, using good air pollution control practices and safe operating practices. | 0.01 | TON/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0026 | WAVERLY FACILITY | PLEASANTS ENERGY, LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 304-665-4201 | GERALD.GATTI@GDFSUEZNA.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0034 | 4911 | 221112 | 110010376734 | 04/18/2016 &nbsp;ACT | 01/23/2017 &nbsp;ACT | 2017-03-21 | 2018-05-01 | D | http://www.dep.wv.gov/daq/Documents/January 2017 Permits and Evals/073-00022_PERM_R14-0034.pdf | 300 MW, natural gas fired, simple cycle peaking power facility | In this permitting action PSD only applies to the modified combustion turbines based on the relaxation of an original synthetic minor permit issued in 1999. Project also involves previous installation of turbo-charging. All BACT emission limits are given without turbocharging and startup/shutdown emissions are not included. Please contact above engineer for more information. There are two identical turbines but only one is listed. | GE Model 7FA Turbine | 15.11 | Natural Gas | 1571 | mmbtu/hr | There are two identical units at the facility. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good Combustion Practices | 9 | PPM | NATURAL GAS | BACT-PSD |  | U | 0 | U | 20 | PPM | FUEL OIL | 9 | PPM | NATURAL GAS | 0 | 0 | N
*WV-0028 | WAVERLY POWER PLANT | PLEASANTS ENERGY LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 3046654201 | GERALD.GATTI@DYNEGY.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Steve Pursley, PE Engineer West Virginia Division of Air Quality 601-57th St., SE Charleston, WV 25304 Phone: (304) 926-0499 x1218 Fax: (304) 926-0478 steve.r.pursley@wv.gov | R14-0034A | 4911 | 221112 | 110063231042 | 11/30/2017 &nbsp;ACT | 03/13/2018 &nbsp;ACT | 2018-05-29 | 2018-05-29 | U | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/073-00022_PERM_R14-0034A.pdf | 300 MW Sinple-Cycle Peaking Plant | Modification to existing PSD Permit (R14-0034, RBLC Number WV-0027) to add &lsquo;&lsquo;advanced gas path&lsquo;&lsquo; technology to the turbines that was defined as a &lsquo;&lsquo;change in the method of operation&lsquo;&lsquo; that resulted a major modification to the turbines. | GE 7FA.004 Turbine | 15.11 | Natural Gas | 167.8 | MW | This one entry is for both turbines as they are the same. Each turbine, after this modification, is a nominal 167.8 MW GE Model 7FA.004. Has oil-fire backup. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Combustion Controls | 33.9 | LB/HR |  | BACT-PSD |  | U | 0 | U | 235.54 | TONS/YEAR |  | 9 | PPM |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP03) | 15.11 | Natural Gas | 40 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidiation Catalyst | 6 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD |  | N | 0 | U | 5.6 | LB/H | 30-DAY ROLLING AVERAGE | 32.9 | T/YR |  | 3251 | 3251 | N | 2011
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Trubine (EP04) | 15.11 | Natural Gas | 40 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 6 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD |  | N | 0 | U | 5.6 | LB/H | 30-DAY ROLLING AVERAGE | 32.9 | T/YR |  | 3251 | 3251 | N | 2011
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP05) | 15.11 | Natural Gas | 40 | MW |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 6 | PPMV AT 15% O2 | 1-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 5.6 | LB/H | 30-DAY ROLLING AVERAGE | 32.9 | T/YR |  | 3251 | 3251 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE LM6000PC SPRINT Simple cycle combustion turbine | 15.11 | Pipeline quality natural gas | 405.3 | MMBTU/hr |  | Nitrogen Dioxide (NO2) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx)) | 10102-44-0 | P | dry low NOx burners and fire only pipeline natural gas | 9 | PPMDV | 24-HR ROLLING AVE, CORRECTED TO 15% O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NM-0051 | CUNNINGHAM POWER PLANT | SOUTHWESTERN PUBLIC SERVICE CO. | LEA | NM | 88241-1650 | USA | KEVIN WORLEY | 806 378 2185 | KEVIN.WORLEY@XCELENERGY.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Cember Hardison is permit writer. 505 476 4346. cember.hardison@state.nm.us | PSD-NM-622-M3 | 4911 | 221122 | 110010571639 | 03/08/2011 &nbsp;ACT | 05/02/2011 &nbsp;ACT | 2011-08-02 | 2012-01-05 | C |  | Electric steam generating facility providing commercial electric power using natural gas fired boilers and turbines. | Simple Cycle Combustion Turbines. Permit revises the NOx BACT ppmvd limit for turbines established in permit PSD-NM-622-M2 issued 2-10-97 because turbines have not been able to meet NOx BACT limits. No modification or change to mass emissions. Former NOx BACT was at 15 ppmvd w/out power augmentation (normal mode) and 25 ppmvd w/ power augmentation (see RBLC ID NM-0028). Entry also clarifies the existing CO, SOx, and PM BACT. | Normal Mode (without Power Augmentation) | 15.11 | natural gas | 0 |  |  | Nitrogen Dioxide (NO2) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx)) | 10102-44-0 | P | Dry Low NOx Burners Type K & Good Combustion Practice | 21 | PPMVD | HOUR | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | Y |  | Limit is NOx ppmvd at 15% O2 at site conditions (not adjusted to standard conditions). Base case. No cost analysis was provided for dry low NOx burners. However, costs for other controls were evaluated.
NM-0051 | CUNNINGHAM POWER PLANT | SOUTHWESTERN PUBLIC SERVICE CO. | LEA | NM | 88241-1650 | USA | KEVIN WORLEY | 806 378 2185 | KEVIN.WORLEY@XCELENERGY.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Cember Hardison is permit writer. 505 476 4346. cember.hardison@state.nm.us | PSD-NM-622-M3 | 4911 | 221122 | 110010571639 | 03/08/2011 &nbsp;ACT | 05/02/2011 &nbsp;ACT | 2011-08-02 | 2012-01-05 | C |  | Electric steam generating facility providing commercial electric power using natural gas fired boilers and turbines. | Simple Cycle Combustion Turbines. Permit revises the NOx BACT ppmvd limit for turbines established in permit PSD-NM-622-M2 issued 2-10-97 because turbines have not been able to meet NOx BACT limits. No modification or change to mass emissions. Former NOx BACT was at 15 ppmvd w/out power augmentation (normal mode) and 25 ppmvd w/ power augmentation (see RBLC ID NM-0028). Entry also clarifies the existing CO, SOx, and PM BACT. | Power Augmentation | 15.11 | natural gas | 0 |  | Increase power output by lowering the outlet air temperatur through water inejctinos into the compressor. | Nitrogen Dioxide (NO2) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx)) | 10102-44-0 | P | Dry Low NOx burners, Type K. Good Combustion Practices as defined in the permit. | 30 | PPMVD | HOURLY | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NOx BACT during power augmentation is 30 ppmvd at 15 % O2 and site conditions (not adjusted to standard conditions).
CA-1174 | EL CAJON ENERGY LLC | EL CAJON ENERGY LLC | SAN DIEGO | CA | 92020 | USA | GENEVIEVE HUFFMAN |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Evariste Haury (858)-586-2745 Evariste.Haury@sdcounty.ca.gov | 987824 | 519 | 311999 | 110043330106 | 11/01/2008 &nbsp;ACT | 12/11/2009 &nbsp;ACT | 2010-09-20 | 2011-04-11 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 49.95 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Water injection and SCR | 2.5 | PPMV | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1175 | ESCONDIDO ENERGY CENTER LLC |  | SAN DIEGO | CA | 92029 | USA |  |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Arthur Carbonell (858)-586-2741 arthur.carbonell@sdcounty.ca.gov | 985693 | 491 | 221122 | UNKNOWN | &nbsp; | 07/02/2008 &nbsp;ACT | 2010-09-21 | 2011-06-27 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 46.5 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR water injection | 2.5 | PPMV@15% OXYGEN | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1176 | ORANGE GROVE PROJECT |  | SAN DIEGO | CA | 92059 | USA |  |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Camqui Nguyen (858)586-2747 camqui.nguyen@sdcounty.ca.gov | 985708 | 491 | 221122 | UNKNOWN | 11/03/2007 &nbsp;ACT | 12/04/2008 &nbsp;ACT | 2010-09-21 | 2011-06-27 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 49.8 | MW | Combustion turbine for peaking power plant | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR water injection | 2.5 | PPM | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1223 | PIO PICO ENERGY CENTER | PIO PICO ENERGY CENTER, LLC | OTAY MESA | CA | 92154 | USA | GARY CHANDLER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SD 11-01 | 4911 | 221112 | 110045006943 | 06/14/2012 &nbsp;ACT | 11/19/2012 &nbsp;ACT | 2013-03-05 | 2014-01-28 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | CONSTRUCTION OF THREE GENERAL ELECTRIC (GE) LMS100 NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 100 MW EACH. THE PROJECT WILL HAVE AN ELECTRICAL OUTPUT OF 300 MW. | NOTE: PERMIT ISSUED 11/19/2012. ENVIRONMENTAL APPEALS BOARD REMANDED THE PM BACT ANALYSIS TO REGION 9 ON 8/2/2013. FINAL PERMIT ISSUED ON 2/28/2014. ONE PETITION FILED IN 9TH CIRCUIT FEDERAL COURT CHALLENGING THE FINAL PERMIT DECISION. THIS LAWSUIT WAS DISMISSED ON 6/17/2014 IN RESPONSE TO PETITIONERSâ€™ MOTION FOR VOLUNTARY DISMISSAL. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.11 | NATURAL GAS | 300 | MW | Three simple cycle combustion turbine generators (CTG). Each CTG rated at 100 MW (nominal net). | Nitrogen Oxides (NOx) | Other - EPA mETHOD 7E, OR METHOD 7E & 19 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | WATER INJECTION, SCR | 2.5 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 8.18 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N
CA-1223 | PIO PICO ENERGY CENTER | PIO PICO ENERGY CENTER, LLC | OTAY MESA | CA | 92154 | USA | GARY CHANDLER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SD 11-01 | 4911 | 221112 | 110045006943 | 06/14/2012 &nbsp;ACT | 11/19/2012 &nbsp;ACT | 2013-03-05 | 2014-01-28 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | CONSTRUCTION OF THREE GENERAL ELECTRIC (GE) LMS100 NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 100 MW EACH. THE PROJECT WILL HAVE AN ELECTRICAL OUTPUT OF 300 MW. | NOTE: PERMIT ISSUED 11/19/2012. ENVIRONMENTAL APPEALS BOARD REMANDED THE PM BACT ANALYSIS TO REGION 9 ON 8/2/2013. FINAL PERMIT ISSUED ON 2/28/2014. ONE PETITION FILED IN 9TH CIRCUIT FEDERAL COURT CHALLENGING THE FINAL PERMIT DECISION. THIS LAWSUIT WAS DISMISSED ON 6/17/2014 IN RESPONSE TO PETITIONERSâ€™ MOTION FOR VOLUNTARY DISMISSAL. | COMBUSTION TURBINES (STARTUP &amp; SHUTDOWN PERIODS) | 15.11 | NATURAL GAS | 300 | MW | Three simple cycle combustion turbine generators (CTG). Each CTG rated at 100 MW (nominal net). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | water injection and SCR system | 22.5 | LB/H | STARTUP EVENTS | BACT-PSD |  | U | 0 | U | 6 | LB/H | SHUTDOWN EVENTS | 0 |  |  | 0 | 0 | N |  | Third emission limit incorrectly entered into the Standard Limit field. RBLC SysOp moved the information into this Notes field. Here is the information: 26.60 LB/H 1-HR AVG, STARTUP & SHUTDOWN EVENTS 1) DURATION OF STARTUPS OF EACH CTG SHALL NOT EXCEED 30 MINUTES PER EVENT; 2) DURATION OF SHUTDOWNS OF EACH CTG SHALL NOT EXCEED 11 MINUTES EVENT; 3) TOTAL NUMBER OF STARTUPS SHALL NOT EXCEED 500 PER TURBINE, PER CALENDAR YEAR.
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055426409 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Three simple cycle combustion turbines | 15.11 | natural gas | 799.7 | MMBTU/H | Three GE, LMS100PA, natural gas-fired, simple cycle CTG rated at 799.7 MMBtu per hour each,based on HHV. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Good combustor design, Water Injection and Selective Catalytic Reduction (SCR) | 5 | PPMVD AT 15% O2 | 1-HR AVE | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 0 | U | 15.5 | LB/H | 30-DAY ROLLING AVE | 0 |  |  | 0 | 0 | N |  | startup limit = 12.0 lb per event shutdown limit = 18.0 lb per event compliance with BACT limits monitored via continuous emissions monitors.
CO-0076 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110058377830 | 06/16/2014 &nbsp;ACT | 12/11/2014 &nbsp;ACT | 2014-12-31 | 2016-02-19 | C |  | Electric generation | Permit modification to convert startup and shutdown BACT limits to an hourly basis (from event based). | Turbines - two simple cycle gas | 15.11 | natural gas | 799.7 | MMBTU/H each | GE LMS100PA, natural gas fired, simple cycle, combustion turbine. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR and dry low NOx burners | 23 | LB/H | 1-HR AVE / STARTUP AND SHUTDOWN | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The NOx limit was converted to an equivalent hourly based limit (the original permit included an event based limit) for periods of startup and shutdown.
FL-0305 | OUC CURTIS H. STANTON ENERGY CENTER | ORLANDO UTILITIES COMMISSION (OUC) | ORLANDO | FL | 32831 | USA | DENISE M. STALLS | 4077374236 | DSTALLS@OUC.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | ALVARO LINERO, P.E. SPECIAL PROJECT ADMINISTRATOR BUREAU OF AIR REGULATION | PSD-FL-373A AND 0950137-020-AC | 4911 | 221112 | UNKNOWN | 03/04/2008 &nbsp;ACT | 05/12/2008 &nbsp;ACT | 2009-02-20 | 2009-08-31 | B |  | THE EXISTING FACILITY CONSISTS OF TWO 468 MW FOSSIL FUEL FIRED STEAM ELECTRIC GENERATING UNITS (UNITS 1 AND 2), AND ONE 640 MW NGCC UNIT (UNIT A). THERE ARE STORAGE AND HANDLING FACILITIES FOR SOLID FUELS, FLY ASH, LIMESTONE, GYPSUM, SLAG, AND BOTTOM ASH. NEW PROJECT ADDS UNIT B, A 300 MW COMBINED CYCLE COMBUSTION TURBINE AND ASSOCIATED EQUIPMENT. | THE NEW PROJECT IS TO CONSTRUCT A Â¿ONE-ON-ONEÂ¿ F-CLASS NGCC UNIT (STANTON UNIT B) AND ASSOCIATED AUXILIARY EQUIPMENT. UNIT B WILL CONSIST OF: ONE NOMINAL 150 MEGAWATTS (MW) GENERAL ELECTRIC 7241 FA COMBUSTION TURBINE-ELECTRICAL GENERATOR (CTG); A SUPPLEMENTARY FIRED HEAT RECOVERY STEAM GENERATOR (HRSG) WITH NATURAL GAS FUELED DUCT BURNERS; AND A NOMINAL 150 MW STEAM TURBINE GENERATOR (STG) FOR AN OVERALL NOMINAL RATING OF 300 MW. THE PROJECT INCLUDES HIGHLY AUTOMATED CONTROLS, DESCRIBED AS THE GE MARK VI GAS TURBINE CONTROL SYSTEM TO FULFILL ALL OF THE GAS TURBINE CONTROL REQUIREMENTS. UNIT B WILL FIRE NATURAL GAS AS THE PRIMARY FUEL, AND ULTRALOW SULFUR DIESEL (ULSD) FUEL OIL SERVING AS A BACKUP FUEL. | 300 MW COMBINED CYCLE COMBUSTION TURBINE | 15.11 | NATURAL GAS | 1765 | MMBTU/H | FOR ULTRA LOW SULFUR (0.0015% SULFUR BY WEIGHT) FUEL OIL IS 1935 MMBTU/H. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS AND SCR WATER INJECTION | 8 | PPMVD @15% O2 | 24-HR ( OIL) | BACT-PSD | NSPS | U | 0 | U | 2 | PPMVD @15% O2 | 24-HR (GAS) | 0 |  |  | 0 | 0 | N |  | CONTINUOUS COMPLIANCE WITH THE 24-HR NOX STANDARDS SHALL BE DEMONSTRATED BASED ON DATA COLLECTED BY THE REQUIRED CEMS. THE INITIAL AND ANNUAL EPA METHOD 7E OR METHOD 20 TESTS ASSOCIATED WITH DEMONSTRATION OF COMPLIANCE WITH 40 CFR 60, SUBPART KKKK OR CERTIFICATION OF THE CEMS INSTRUMENTS SHALL ALSO BE USED TO DEMONSTRATE COMPLIANCE WITH THE INDIVIDUAL STANDARDS FOR NATURAL GAS, FUEL OIL, AND DUCT BURNER MODES DURING THE TIME OF THOSE TESTS. NOX MASS EMISSION RATES ARE DEFINED AS OXIDES OF NITROGEN EXPRESSED AS NITROGEN DIOXIDE (NO2).
FL-0310 | SHADY HILLS GENERATING STATION | SHADY HILLS POWER COMPANY | PASCO | FL | 6927 | USA | ROY S. BELDEN | 2033576820 | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | SYED ARIF, PROJECT ENGINEER PHONE 850/ 921-9528 SYED.ARIF@DEP.STATE.FL.US TERESA HERON PHONE 850/921-9529 TERESA.HERON@DEP.STATE.FL.US | PSD-FL-402 | 4911 | 221122 | 1210100373 | 05/13/2008 &nbsp;ACT | 01/12/2009 &nbsp;ACT | 2009-07-29 | 2010-01-26 | B |  | THIS FACILITY CONSISTS OF THREE, DUAL-FUEL, NOMINAL 170 MW GENERAL ELECTRIC MODEL PG7241FA (GE 7FA) SIMPLE CYCLE COMBUSTION TURBINES-ELECTRICAL GENERATORS, THREE EXHAUST STACKS THAT ARE 18 FEET IN DIAMETER AND 75 FEET TALL, AND ONE 2.8-MILLION GALLON DISTILLATE FUEL OIL STORAGE TANK. THE COMBUSTION TURBINE UNITS CAN OPERATE IN SIMPLE-CYCLE MODE AND INTERMITTENT DUTY MODE. THE UNITS ARE EQUIPPED WITH DRY LOW-NITROGEN OXIDES (NOX) COMBUSTORS AND WATER INJECTION CAPABILITY. THE THREE COMBUSTION TURBINES ARE REGULATED UNDER PHASE II OF THE FEDERAL ACID RAIN PROGRAM. THIS FACILITY OPERATES DURING PEAK HOURS OF ELECTRICAL USE. |  | TWO SIMPLE CYCLE COMBUSTION TURBINE - MODEL 7FA | 15.11 | NATURAL GAS | 170 | MW | BACKUP FUEL: ULTRA LOW SULFUR DIESEL WITH A MAXIMUM SULFUR CONTENT OF 0.0015%, BY WEIGHT | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | FIRING NATURAL GAS AND USING DLN 2.6 COMBUSTORS TO MINIMIZE NOX EMISSSIONS. | 9 | PPMVD @ 15% O2 | 24-HR BLOCK AVG BY CEMS | BACT-PSD |  | Y | 0 | U | 59 | LB/H | 3 ONE HOUR RUN BY 7E OR 20 | 9 | PPMVD @ 15% O2 | 24-HR BLOCK AVG BY CEMS | 0 | 0 | N
FL-0319 | GREENLAND ENERGY CENTER | JACKSONVILLE ELECTRIC AUTHORITY (JEA) | DUVAL | FL | 32258 | USA | N. BERT GIANAZZA | 904-665-6247 | GIANNB@JEA.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Syed Arif Project Manager 850-921-9580 Jeff Koerner, P.E. Administrator Phone 850-921-9536 | PSD-FL-401 | 4911 | 221112 | UNKNOWN | 04/21/2008 &nbsp;ACT | 03/10/2009 &nbsp;ACT | 2010-09-23 | 2011-12-01 | A |  | The proposed facility is a new electric-generating facility referred to as Greenfield Energy Center (GEC). GEC will be built in two phases. The initial phase will be the construction of two natural gas-fired simple cycle combustion turbine (CT) units that are proposed to be operational June 2011. The second phase will convert these simple cycle units to a combined cycle combustion turbine (â€œ2-on 1â€ configuration). Heat recovery equipment will be installed on the two simple cycle combustion turbines to capture enough heat energy to run a steam turbine (ST). This phase is proposed to be operational by June 2013. | Each combustion turbine shall not operate more than 3,500 hours during any consecutive 12 months of which 500 hours may be on ULSFO. Each combustion turbine shall not operate more than 17 hours exclusively on ULSFO per calendar day, or with a combination of ULSFO burning of 12 hours with 12 hours of natural gas for compliance with regional haze impact thresholds. | 190 MW Combustion Turbine | 15.11 | ULSO | 30213 | GAL/YR | Capacity: 1806 MMBtu/H, natural gas Capacity: 1994 MMBtu/H, fuel oil Authorized Fuels (Pre-onsite natural gas availability): Each combustion turbine shall fire ULSFO which shall contain no more than 0.0015% sulfur by weight as the primary fuel until natural gas is available at the facility. If natural gas is not available by June 1, 2011, the permittee shall submit to the Department and EQD semi-annual status reports on the availability of natural gas to the facility. The first status report shall be submitted by June 1, 2011. The status reports shall be submitted until natural gas is available at the facility. Authorized Fuels (Post-onsite natural gas availability): Each combustion turbine shall fire natural gas as the primary fuel, which shall contain no more than 2 grains of sulfur per 100 standard cubic feet of natural gas. As a restricted alternate fuel, the combustion turbine may fire ULSFO containing no more than 0.0015% sulfur by weight. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DLN Combustion System when firing natural gas and water injection system when firing fuel oil. | 9 | PPMVD @15% O2 (GAS) | 24-HR BLOCK/CEMS | BACT-PSD | NSPS | U | 0 | U | 58.5 | LB/H (GAS) | (3) 1-HR RUNS/STACK TEST | 0 |  |  | 0 | 0 | N |  | Water injection system 80-90 % efficiency. Emission Limit firing oil (ULSFO with 0.0015% S): 1) 42.0 ppmvd @ 15% O2 4-hr rolling average/CEMS 2) 329.4 lb/hr - three 1-hr runs/stack test. Continuous compliance with the 24-hour block and 4-hour rolling average NOX standards shall be demonstrated based on data collected by the required Continuous Emissions Monitoring System (CEMS). The initial and annual EPA Method 7E or Method 20 tests associated with demonstration of compliance with 40 CFR 60, Subpart KKKK or certification of the CEMS instruments may also be used to demonstrate compliance with the individual standards for natural gas and ULSFO during the time of those tests. NOX mass emission rates are at International Organization for Standardization (ISO) conditions and are defined as oxides of nitrogen expressed as NO2.
FL-0346 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-011-AC | 4911 | 221112 | 110002044065 | 11/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-01-08 | 2016-05-05 | D | http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | In this project, 24 peaking turbines from the Lauderdale facility are being replaced with five 200 MW combustion turbines at Lauderdale. The turbines will fire primarily natural gas, but may also fire ULSD fuel oil. Triggers PSD for NOx, PM, CO, VOC, and GHG. GHG permit issued by US EPA Region 4. Technical evaluation available at http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2000 | MMBtu/hr (approx) | Throughput could vary slightly (+/- 120 MMBtu/hr) depending on final selection of turbine model and firing of natural gas or oil. Primary fuel is expected to be gas. Each turbine limited to 3300 hrs per rolling 12-month period. Of these 3300 hrs, no more than 500 may use ULSD fuel oil. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Required to employ dry low-NOx technology and wet injection. Water injection must be used when firing ULSD. | 9 | PPMVD @ 15% 02 | 24-HR BLOCK AVG, BY CEMS (NAT GAS) | BACT-PSD | NSPS | U | 0 | U | 77 | LB/H | 24-HR BLOCK, BY CEMS (NAT GAS) | 0 |  |  | 0 | 0 | N |  | NOx CEMS required -- employing EPA Method 7E. For natural gas, 9.0 ppmvd@15% O2 and 77 lb/hr. For oil, 42.0 ppmvd@15% O2 and 378.0 lb/hr.
FL-0354 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-013-AC | 4911 | 221112 | 110002044065 | 04/20/2015 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2016-02-17 | 2016-07-06 | D | https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | Re-affirmed BACT determinations in Permit No. 0110037-011-AC. Also, new GHG BACT determination. Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2100 | MMBtu/hr (approx) | Five simple cycle GE 7F.05 turbines. Max of 3390 hours per year per turbine. Of the 3390 hours per year, up to 500 hour may be on ULSD fuel oil. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry-low-NOx combustion system. Wet injection when firing ULSD. | 9 | PPMVD@15%O2 | 24-HR BLOCK AVERAGE | BACT-PSD | NSPS | U | 0 | U | 42 | PPMVD@15%O2 | 4-HR ROLLING | 0 |  |  | 0 | 0 | N |  | Compliance by NOx CEMS. Also subject to NSPS Subpart KKKK.
FL-0355 | FORT MYERS PLANT | FLORIDA POWER & LIGHT (FPL) | LEE | FL | 33905 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0710002-022-AC | 4911 | 221112 | 110000365248 | 05/12/2015 &nbsp;ACT | 09/10/2015 &nbsp;ACT | 2016-03-10 | 2016-07-06 | D | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.80831.1]&[profile=Permitting_Authorization] | Electric power plant, consists of a 6-on-2 combined-cycle unit (Units 2A through 2F) and two modern simple-cycle combustion turbines. Primary fuel is natural gas. Also includes 12 gas turbines (63 MW each) for peaking, introduced into service in 1974. This project entails decommissioning 10 of the 12 peaking turbines. They will be replaced with two new GE 7F.05 turbines, each with nominal capacity of 200 MW | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0710002.022.AC.D.ZIP | Combustion Turbines | 15.11 | Natural gas | 2262.4 | MMBtu/hr gas | Two GE 7F.05 turbines, approximately 200 MW each. Natural-gas is primary fuel. Permitted 3390 hr/yr of operation, of which no more than 500 hr may be on fuel oil. Dry Low-NOx, with wet injection for oil firing. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DLN and wet injection (for ULSD operation) | 9 | PPMVD@15% O2 | GAS FIRING, 24-HR BLOCK AVG | BACT-PSD | NSPS | U | 0 | U | 42 | PPMVD@15% O2 | ULSD FIRING, 4-HR ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Compliance by NOx CEMS. Also subject to low-load (<75%) Subpart KKKK NOx limit.
GA-0139 | DAHLBERG COMBUSDTION TURBINE ELECTRIC GENERATING FACILITY (P | SOUTHERN POWER COMPANY | JACKSON | GA | 30565 | USA | MR. E.S. (SCOTT) DIAL | 704 278-6601 | ESDIAL@SOUTHERNCO.COM | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-157-0034-V-04-1 | 4911 | 221112 | UNKNOWN | 07/10/2008 &nbsp;ACT | 05/14/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | C |  | PLANT DAHLBERG HAS PROPOSED TO CONSTRUCT AND OPERATE FOUR ADDITIONAL SIMPLE-CYCLE COMBUSTION TURBINES (SOURCE CODES: CT11-CT14) AND ONE FUEL OIL STORAGE TANK. THE PROPOSED PROJECT WILL HAVE A NOMINAL GENERATING CAPACITY OF 760 MW. THE FACILITY IS CURRENTLY PERMITTED TO OPERATE 10 DUAL-FUELED SIMPLE-CYCLE CTG's. AFTER THE EXPANSION, THE FACILITY WILL HAVE A TOTAL NOMINAL GENERATING CAPACITY OF 1530 MW. |  | SIMPLE CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.11 | NATURAL GASE | 1530 | MW | THE PROCESS USES FUEL OIL FOR BACKUP AT THE RATE OF 2129 MMBUT/H | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DRY LOW NOX BURNERS (FIRING NATURAL GAS). WATER INJECTION (FIRING FUEL OIL). | 9 | PPM@15%02 | 3 HOUR AVERAGE/CONDITION 3.3.23 | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 42 | PPM@15%02 | 3 HOUR AVERAGE/CONTIION 3.3.27 | 0 |  |  | 0 | 0 | N
GA-0139 | DAHLBERG COMBUSDTION TURBINE ELECTRIC GENERATING FACILITY (P | SOUTHERN POWER COMPANY | JACKSON | GA | 30565 | USA | MR. E.S. (SCOTT) DIAL | 704 278-6601 | ESDIAL@SOUTHERNCO.COM | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-157-0034-V-04-1 | 4911 | 221112 | UNKNOWN | 07/10/2008 &nbsp;ACT | 05/14/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | C |  | PLANT DAHLBERG HAS PROPOSED TO CONSTRUCT AND OPERATE FOUR ADDITIONAL SIMPLE-CYCLE COMBUSTION TURBINES (SOURCE CODES: CT11-CT14) AND ONE FUEL OIL STORAGE TANK. THE PROPOSED PROJECT WILL HAVE A NOMINAL GENERATING CAPACITY OF 760 MW. THE FACILITY IS CURRENTLY PERMITTED TO OPERATE 10 DUAL-FUELED SIMPLE-CYCLE CTG's. AFTER THE EXPANSION, THE FACILITY WILL HAVE A TOTAL NOMINAL GENERATING CAPACITY OF 1530 MW. |  | SIMPLE CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.11 | NATURAL GASE | 1530 | MW | THE PROCESS USES FUEL OIL FOR BACKUP AT THE RATE OF 2129 MMBUT/H | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DRY LOW NOx BURNERS (FIRING NATURAL GAS), WATER INJECTION (FIRING FUEL OIL). | 297 | T/YR | 12 CONSECUTIVE MONTH AVERAGE /CONDITION | BACT-PSD | OPERATING PERMIT | U | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NUMERIC LIMIT CONSIST OF NG AND FO.
IL-0121 | INVENERGY NELSON EXPANSION LLC | INVENERGY | LEE | IL | 61058 | USA | GORDON GRAY | 312-582-1290 | GGRAY@INVENERGY.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Bob Smet; 217-785-9250; robert.smet@illinois.gov | 15060042 | 4911 | 221112 | Not Found | 07/28/2016 &nbsp;ACT | 09/27/2016 &nbsp;ACT | 2017-01-27 | 2017-04-28 | B | https://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/9dbc452815081576862580b2006897b4/$FILE/ATT4AK5N.pdf/15060042.pdf | Peaking facility at an existing major source. The expansion will consist of two simple cycle combustion turbines and a fuel heater. |  | Two Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 190 | MW | Two simple cycle combustion turbines used for peaking purposes and fired primarily on natural gas with ULSD as a secondary fuel. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low-NOx combustion technology for natural gas and low-NOx combustion technology and water injection for ULSD. | 0.033 | LB/MMBTU |  | BACT-PSD | NSPS | N | 0 | U | 0.164 | LB/MMBTU |  | 0 |  |  | 0 | 0 | Y |  | Natural Gas: 9 ppmv at 15 percent O2 (equivalent to 0.033 lb/mmBtu, HHV). ULSD: 42 ppmv at 15 percent O2 (equivalent to 0.164 lb/mmBtu, HHV). During commissioning, NOx shall not exceed: Natural gas: 110 lb/hr, 110 lb/cycle ULSD: 349 lb/hr, 275 lb/cycle
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER | 15.11 | NATURAL GAS | 92.5 | MMBTU/H | NATURAL GAS USAGE SHALL NOT EXCEED 18.14 MMCF/YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | GOOD COMBUSTION PRACTICES AND PROPER DESIGN, USE NATURAL GAS | 183.7 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER | 15.11 | NATURAL GAS | 92.5 | MMBTU/H | NATURAL GAS USAGE SHALL NOT EXCEED 18.14 MMCF/YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | GOOD COMBUSTION PRACTICES AND PROPER DESIGN, USE NATURAL GAS | 183.7 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0261 | VERMILLION GENERATING STATION | DUKE ENERGY INDIANA, LLC VERMILLION GENERATING STA | VERMILLION | IN | 47928 | USA | PATRICK COUGHLIN | 3178382108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIP SINHA PH.D. 317-234-4907 | 165-36956-00022 | 4911 | 221112 | 110006010921 | 03/16/2016 &nbsp;ACT | 02/28/2017 &nbsp;ACT | 2017-07-07 | 2017-08-09 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36956F.PDF | ELECTRIC UTILITY SERVICES |  | SIMPLE CYCLE, NATURAL GAS FIRED COMBUSTION TURBINES | 15.11 | NATURAL GAS | 80 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES | 250 | LB/H | EACH TURBINE | BACT-PSD |  | N | 0 |  | 25 | TON/12 CONSEC. MONTH | COMPLIANCE DETERMINED END OF EACH MONTH | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: ONLY TWO (2) TURBINES WILL OPERATE DURING LOW LOAD OPERATION
IN-0264 | MONTPELIER GENERATING STATION | AES OHIO GENERATION, LLC | WELLS | IN | 46781 | USA | DREW PARKER | 9373314993 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: MADHURIMA MOULIK 317-233-6663 MMOULIK@IDEM.IN.GOV SECTION CHIEF: JASON KRAWCZYK 317-234-5174 | 179-37209-00026 | 4911 | 221112 | 110021089061 | 05/23/2016 &nbsp;ACT | 01/06/2017 &nbsp;ACT | 2017-07-07 | 2017-11-17 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/37209F.PDF | COMBUSTION TURBINES |  | PRATT &amp; TWIN-PAC SIMPLE CYCLE TURBINES | 15.11 | NATURAL GAS | 270.9 | MMBTU/H | NO. 2 DIESEL OIL BACKUP FUEL | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | WATER INJECTION | 25 | PPMV | AT 15% O2 FOR NATURAL GAS | BACT-PSD |  |  | 0 |  | 42 | PPMV | AT 15% O2 FOR FUEL OIL | 0 |  |  | 0 | 0 | N |  | 0.14 LB/MMBTU FOR NATURAL GAS AND 0.24 LB/MMBTU FOR FUEL OIL; EACH TURBINE LIMITED TO 4555 HOURS OF OPERATION PER 12 MONTH PERIOD
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE LM6000PC SPRINT Simple cycle combustion turbine | 15.11 | Pipeline quality natural gas | 405.3 | MMBTU/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | water injection | 25 | PPMDV | 24-HR ROLLING AVE; CORRECTED TO 15% O | BACT-PSD |  | U | 0 | U | 269.3 | TONS | 12 MO CALENDAR BASIS, FOR ALL 4 UNITS | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE 7FA Simple Cycle Combustion Turbine | 15.11 | Pipeline quality natural gas | 1780 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low NOx burners and fire only pipeline natural gas | 9 | PPMDV | 24-HR ROLLING AVE, CORRECTED TO 15% O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KY-0104 | CASH CREEK GENERATING STATION | CASH CREEK GENERATION, L.L.C | HENDERSON | KY | 41047 | USA | MIKE MCINNUS | 502 357 9907 | MMCINNIS@ERORA.COM | 4 | KY001 | KENTUCKY DEP, DIV FOR AIR QUALITY | MR. RICK SHEWEKAH, MGR | (502)564-3999 | Sreenivas.Kesaraju@ky.gov |  | V-14-011 | 4911 | 221112 | 110042328479 | 06/18/2014 &nbsp;ACT | 06/10/2015 &nbsp;ACT | 2017-02-28 | 2017-04-28 | A |  | natural gas fired combined cycle power plant |  | Combined cycle combustion turnbine with HRSG and duct firing | 15.11 | Natural gas pipeline quality | 849 | MW | Two CT with HRSGs with duct burner Max fuel input for CTs and HRSGs 6,714 mmBtu/hr HHV Max Gross output 849 MW at 0F | Nitrogen Oxides (NOx) | EPA/OAR Mthd 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR, low NOx burners | 2 | PPMVD | @15% O2 THREE HOUR ROLLING AVERAGE | BACT-PSD | NSPS | U | 90 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0224 | ARSENAL HILL POWER PLANT | SOUTHWEST ELECTRIC POWER COMPANY (SWEPCO) | CADDO | LA | 71101 | USA | KRIS GAUS | 2147771113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-726 | 4911 | 221112 | 110001270847 | 01/07/2008 &nbsp;ACT | 03/20/2008 &nbsp;ACT | 2008-04-18 | 2012-05-18 | B |  | NATURAL GAS FIRED ELECTRICAL GENERATION PLANT. |  | SCN-3 COLD STARTUP CTG-1 SCN-7 COLD STARTUP CTG-2 | 15.11 | NATURAL GAS | 2110 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N | COMPLETE EVENTS AS QUICKLY AS POSSIBLE ACCORDING TO MANUFACTUREÂ¿S RECOMMENDED PROCEDURES. | 400 | LB/H | MAX | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0224 | ARSENAL HILL POWER PLANT | SOUTHWEST ELECTRIC POWER COMPANY (SWEPCO) | CADDO | LA | 71101 | USA | KRIS GAUS | 2147771113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-726 | 4911 | 221112 | 110001270847 | 01/07/2008 &nbsp;ACT | 03/20/2008 &nbsp;ACT | 2008-04-18 | 2012-05-18 | B |  | NATURAL GAS FIRED ELECTRICAL GENERATION PLANT. |  | SCN-5 SHUTDOWN CTG-1 / SCN-9 SHUTDOWN CTG-2 | 15.11 | NATURAL GAS | 2110 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N | COMPLETE EVENTS AS QUICKLY AS POSSIBLE ACCORDING TO MANUFACTUREÂ¿S RECOMMENDED PROCEDURES. | 400 | LB/H | MAX | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Refrigeration Compressor Turbines (16) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Nitrogen Oxides (NOx) | EPA/OAR Mthd 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | water injection | 22.94 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 20 | PPMV | AT 15% O2 | 0 | 0 | N
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Generation Turbines (2) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Nitrogen Oxides (NOx) | EPA/OAR Mthd 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | water injection | 28.68 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 25 | PPMV | AT 15% O2 | 0 | 0 | N
LA-0258 | CALCASIEU PLANT | ENTERGY GULF STATES LA LLC | CALCASIEU | LA | 70665 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: TEGAN TREADAWAY, (225) 219-3408 | PSD-LA-746 | 4911 | 221112 | 110007042565 | 11/10/2009 &nbsp;ACT | 12/21/2011 &nbsp;ACT | 2012-02-01 | 2012-04-03 | C |  | 320 MW POWER PLANT COMPRISED OF 2 NATURAL GAS-FIRED SIMPLE CYCLE COMBUSTION TURBINES. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS PSD TRIGGERED DUE TO RELAXATION OF A FEDERALLY-ENFORCEABLE CONDITION LIMITING POTENTIAL EMISSIONS BELOW MAJOR STATIONARY SOURCE THRESHOLDS. | TURBINE EXHAUST STACK NO. 1 &amp; NO. 2 | 15.11 | NATURAL GAS | 1900 | MM BTU/H EACH |  | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DRY LOW NOX COMBUSTORS | 240 | LB/H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 798 | LB/H | HOURLY MAXIMUM / STARTUP & SHUTDOWN ONLY | 17.5 | PPMVD @ 15% O2 |  | 0 | 0 | N |  | LIMITS ARE PER TURBINE EXHAUST STACK. AGGREGATE NOX EMISSIONS FROM BOTH TURBINE EXHAUST STACKS ARE LIMITED TO 391.30 TONS PER YEAR. STARTUP & SHUTDOWN OPERATIONS ARE LIMITED TO 520 HOURS PER YEAR.
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Gas Turbines (8 units) | 15.11 | natural gas | 333 | mm btu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry Low NOX burners and good combustion practices | 25 | PPMVD | @15 %O2 | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110029511883 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | good combustion practices and dry low nox burners | 15 | PPMVD | @15%O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | COMBUSTION TURBINES (2) | 15.11 | NATURAL GAS |  |  | GENERAL ELECTRIC 207FA COMBUSTION TURBINE WITH HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT FIRING CAPABILIY (DUCT BURNER EQUIPPED WITH LNB). EACH CT IS CAPABLE OF GENERATING A NOMINAL 176 MW OF ELECTRICITY. THE STEAM TURBINE IS CAPABLE OF GENERATING 304 MW OF ELECTRICITY. OVERALL FACILITY NOMINAL GENERATION CAPACITY OF 640 MW | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DRY LOW NOX BURNER AND SCR | 2 | PPMVD @ 15% O2 | 3-HR ROLLING AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | APPLICABLE TO OPERATING WITH OR WITHOUT DUCT BURNING, LAER
MN-0075 | GREAT RIVER ENERGY - ELK RIVER STATION | GREAT RIVER ENERGY | SHERBURNE | MN | 55330 | USA | MARK STROHFUS | 7634455210 | MSTROHFU@GRENERGY.COM | 5 | MN001 | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | MR. RICHARD CORDES | (651)757-2291 | RICHARD.CORDES@STATE.MN.US | TONI VOLKMEIER, TONI.VOLKMEIER@PCA.STATE.MN.US | 14100003-004 | 4911 | 221119 | UNKNOWN | 03/31/2008 &nbsp;EST | 07/01/2008 &nbsp;ACT | 2008-12-01 | 2009-01-26 | B |  | THE FACILITY IS AN ELECTRIC POWER GENERATING STATION BURNING REFUSE DERIVED FUEL (RDF). THE RDF BURNED AT THIS FACILITY IS PROCESSED FROM MUNICIPAL SOLID WASTE. THE FACILITY PRODUCES APPROXIMATELY 40 MEGAWATTS OF ELECTRICITY. THERE IS ALSO A SINGLE CYCLE COMBUSTION TURBINE GENERATOR (CTG) |  | COMBUSTION TURBINE GENERATOR | 15.11 | NATURAL GAS | 2169 | MMBTU/H | GENERATOR IS A SIMPLE CYCLE COMBUSTION TURBINE, WHICH WILL BE OPERATED AS A PEAK-SHAVING UNIT. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DRY LOW-NOX COMBUSTION WHEN COMBUSTING NATURAL GAS | 9 | PPM | 4 HR ROLLING AVG, NG, >/= 60% LOAD | BACT-PSD | OTHER , NSPS | Y | 0 | U | 25 | PPM | 4 HR ROLLING AVG, NG, <60% LOAD | 96 | PPM | 4 HR ROLLING AVG, <75% LOAD | 0 | 0 | N |  | SEPARATE LIMIT DEVELOPED FOR NOX WHEN COMBUSTION NATURAL GAS OR FUEL OIL, AT DIFFERING LOADS
MN-0075 | GREAT RIVER ENERGY - ELK RIVER STATION | GREAT RIVER ENERGY | SHERBURNE | MN | 55330 | USA | MARK STROHFUS | 7634455210 | MSTROHFU@GRENERGY.COM | 5 | MN001 | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | MR. RICHARD CORDES | (651)757-2291 | RICHARD.CORDES@STATE.MN.US | TONI VOLKMEIER, TONI.VOLKMEIER@PCA.STATE.MN.US | 14100003-004 | 4911 | 221119 | UNKNOWN | 03/31/2008 &nbsp;EST | 07/01/2008 &nbsp;ACT | 2008-12-01 | 2009-01-26 | B |  | THE FACILITY IS AN ELECTRIC POWER GENERATING STATION BURNING REFUSE DERIVED FUEL (RDF). THE RDF BURNED AT THIS FACILITY IS PROCESSED FROM MUNICIPAL SOLID WASTE. THE FACILITY PRODUCES APPROXIMATELY 40 MEGAWATTS OF ELECTRICITY. THERE IS ALSO A SINGLE CYCLE COMBUSTION TURBINE GENERATOR (CTG) |  | COMBUSTION TURBINE GENERATOR | 15.11 | NATURAL GAS | 2169 | MMBTU/H | GENERATOR IS A SIMPLE CYCLE COMBUSTION TURBINE, WHICH WILL BE OPERATED AS A PEAK-SHAVING UNIT. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | WATER INJECTION WHEN COMBUSTING FUEL OIL | 42 | PPM | 4 HR ROLLING AVG, FO, >/= 70% LOAD | BACT-PSD | NSPS , OTHER | Y | 0 | U | 50 | PPM | 4 HR ROLLING AVG, FO, <70% LOAD | 96 | PPM | 4 HR ROLLING AVG, FO, <75% LOAD | 0 | 0 | N |  | SEPARATE NOX LIMITS FOR NATURAL GAS AND FUEL OIL COMBUSTION, AND AT DIFFERING LOADS.
ND-0028 | R.M. HESKETT STATION | MONTANA-DAKOTA UTILITIES CO. | MORTON | ND | 58554 | USA | ABBIE KREBSBACH | (701) 222-7844 | ABBIE.KREBSBACH@MDU.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Primary contact is Tom Bachman at (701) 328-5188. | PTC13016 | 4911 | 221112 | 110022356591 | 11/07/2012 &nbsp;ACT | 02/22/2013 &nbsp;ACT | 2013-04-01 | 2017-04-28 | B |  | Addition of a natural gas-fired turbine (Unit 3) to an exisiting coal-fired power plant. The turbine will be used for supplying peak power and is rated at 986 MMBtu/hr and 88 MWe at average site conditions. |  | Combustion Turbine | 15.11 | Natural gas | 986 | MMBTU/H | Turbine is a GE Model PG 7121 (7EA) used as a peaking unit. | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low-NOx combustion (DLN) | 9 | PPMVD @15% OYYGEN | 4 H.R.A. WHEN > 50MWE AND > 0 DEGREES F | BACT-PSD | NSPS | Y | 0 | U | 96 | PPMVD @15% OXYGEN | 4 H.R.A. WHEN < 50 MWE OR < 0 DEGREES F | 399 | LB/H | 1 HOUR AVG./ANY TIME | 0 | 0 | N | 2012
ND-0029 | PIONEER GENERATING STATION | BASIN ELECTRIC POWER COOPERATIVE | WILLIAMS | ND |  | USA | JERRY MENGE | 7012230441 | JMENGE@BEPC.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact. | PTC 13037 | 4911 | 221112 | 110058380238 | 02/19/2013 &nbsp;ACT | 05/14/2013 &nbsp;ACT | 2013-06-19 | 2016-11-03 | B |  | Three GE LM6000 PC SPRINT natural gas fired turbines used to generate electricity for peak periods. | The permit was for the addition of 2 turbines to the station. Since a synthetic minor limit was relaxed for the first unit, BACT was required for all three turbines. | Natural gas-fired turbines | 15.11 | Natural gas | 451 | MMBTU/H | Rating is for each turbine. | Nitrogen Oxides (NOx) | Other - CEM | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Water injection plus SCR | 5 | PPPMVD | 4 HR. ROLLING AVERAGE EXCEPT FOR STARTUP | BACT-PSD | NSPS | U | 80 | N | 19 | LB/H | DURING STARTUP | 0 |  |  | 0 | 0 | N |  | RBLC Staff: Original Emis Limit 2 Units were Numeric Limit - &lsquo;&lsquo;LB&lsquo;&lsquo; and Avg Time/Condition - &lsquo;&lsquo;PER HOUR DURING STARTUP&lsquo;&lsquo; The Emission Units are usually &lsquo;&lsquo;mass unit PER time unit&lsquo;&lsquo;. Separating them out makes understanding limit difficult for the users. The units were combined. The corrected entry is: Numeric Limit - &lsquo;&lsquo;LB/H&lsquo;&lsquo; Avg Time/Condition - &lsquo;&lsquo;During Startup&lsquo;&lsquo;
ND-0030 | LONESOME CREEK GENERATING STATION | BASIN ELECTRIC POWER COOP. | MCKENZIE | ND | 58831 | USA | JERRY MENGE | (701)223-0441 |  | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact at (701) 328-5188. | PTC 13049 | 4911 | 221112 | 110057111003 | 04/05/2013 &nbsp;EST | 09/16/2013 &nbsp;ACT | 2013-09-24 | 2017-06-28 | B |  | Three natural gas fired simple cycle turbines used to generate electricity for peak power demand. The turbines are GE LM6000 PF Sprint units with a nominal capacity of 45 MW each. |  | Natural Gas Fired Simple Cycle Turbines | 15.11 | Natural gas | 412 | MMBTU/H | The heat input is for a single unit. | Nitrogen Oxides (NOx) | Other - CEM | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 5 | PPMVD | 4 HOUR ROLLING AVERAGE EXCEPT STARTUP | BACT-PSD | NSPS | N | 90 | N | 18.5 | LB | TOTAL FOR 30 MINUTES DURING STARTUP | 0 |  |  | 0 | 0 | N |  | The startup limit is for each unit. The three units are limited to a total combined emission rate of 42.9 pounds per hour (1-hour average) at all times.
OH-0333 | DAYTON POWER & LIGHT ENERGY LLC | DAYTON POWER & LIGHT COMPANY | MONTGOMERY | OH | 45439 | USA | CARRIE BURKS | 937-331-3042 |  | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104867 | 4911 | 221112 | 110000394145 | 04/30/2009 &nbsp;ACT | 12/03/2009 &nbsp;ACT | 2010-05-13 | 2010-05-20 | C |  | Seven simple cycle stationary combustion turbines all with rating of 80 MW and nominal heat input of 1115.2 mmBtu/hr using natural gas or No. 2 fuel oil and all with water injection control and last 5 also with low NOx burners. | Simple cycle stationary combution turbines issed in 2 different permits. Four turbines in this permit with dry low NOx combustion and water injection controls. Administrative Modification to original PTI #08-04153 issued 8/7/01, to incorporate low mass emissions methodology as allowed per 40 CFR 75.19 in lieu of methods under Appendix D or E to Part 75, by meeting the requirements of having mass emissions of less than 25 T/YR SO2 and less than 100 T/YR NOx (per turbine) based on 3 years of operation. Modification also reduced permitted formaldehyde emissions by 8.7 tons, recalculated based on the restriction on hours of operation. | Turbines (4), simple cycle, natural gas | 15.11 | NATURAL GAS | 15020 | H/YR | Hours per year for all 4 turbines | Nitrogen Oxides (NOx) | Other - Method 7 or 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low NOx burners | 161 | LB/H | EACH TURBINE | BACT-PSD | SIP | U | 0 | Y | 1373.32 | T/YR | PER ROLLING 12-MO. FOR 4 UNITS &ALL FUEL | 15 | PPMV | AT 15% OXYGEN ON A DRY BASIS AS 1HR AVG. | 0 | 0 | N |  | T/YR limit is for both fuels and for the 4 turbines combined.
OK-0127 | WESTERN FARMERS ELECTRIC ANADARKO | WESTERN FARMERS ELECTRIC COOPERATIVE | CADDO | OK | 73005 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2005-037-C(M-2) PSD | 4911 | 221112 | 110001631440 | 02/01/2008 &nbsp;ACT | 06/13/2008 &nbsp;ACT | 2008-12-31 | 2009-04-20 | B |  | THE FACILITY GENERATES WHOLESALE ELECTRICITY WHICH IS TRANSMITTED OVER WFECÂ¿S ELECTRICAL DISTRIBUTION SYSTEM. THE ELECTRICITY IS SOLD IN RURAL AREAS OF APPROXIMATELY 3/4 OF THE STATE OF OKLAHOMA. THE CURRENT FACILITY CONSISTS OF TWO NATURAL GAS FIRED HIGH PRESSURE BOILERS, A GAS/OIL FIRED HIGH PRESSURE BOILER, THREE GAS/OIL FIRED COMBINED CYCLE GAS TURBINES, A FIRE PUMP DIESEL ENGINE FOR EMERGENCY BACKUP, AND OTHER SOURCES WHICH ARE CONSIDERED INSIGNIFICANT OR TRIVIAL. THE THREE BOILERS ARE BACKUP UNITS THAT ONLY OPERATE WHEN IT IS FEASIBLE, SUCH AS DURING PEAK DEMAND. TWO OF THE BOILERS HAVE BEEN IDLE SINCE 1984. ONE BOILER WAS REPLACED IN 1997, AND ANOTHER WAS REPLACED IN 1998. | WESTERN FARMERS ELEC COOP PROPOSES TO CONSTRUCT AND OPERATE THREE NATURAL GAS-FIRED PEAKING ELECTRIC GENERATING UNITS AT THE FACILITY TO MEET ANTICIPATED FUTURE ENERGY DEMAND. EACH UNIT CAPACITY OF +/- 50 MW. | COMBUSTION TURBINE PEAKING UNIT(S) | 15.11 | NATURAL GAS | 462.7 | MMBTU/H | THE INSTALLATION WILL CONSIST OF THREE GENERAL ELECTRIC LM6000 SPRINT SIMPLE CYCLE AERODERIVATIVE COMBUSTION TURBINE GENERATORS. EACH OF THE TURBINES WILL HAVE A MAXIMUM PEAK HEAT INPUT RATE OF 462.7 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTUH). THE NEW COMBUSTION TURBINES WILL FIRE ONLY PIPELINE-QUALITY NATURAL GAS AND WILL BE EQUIPPED WITH WATER INJECTION. THE PROPOSED NEW UNITS WILL EACH HAVE A NOMINAL ELECTRICAL GENERATING CAPACITY OF 50 MW. ACTUAL UNIT CAPACITY WILL BE DETERMINED DURING DETAILED DESIGN OF THE PLANT AND MAY BE 5 TO 10-MW HIGHER OR LOWER THAN THE NOMINAL VALUE OF 50 MW, DEPENDING ON AMBIENT CONDITION RATINGS AND FINAL DESIGN. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | WATER INJECTION | 25 | PPM | ADJUSTED 15% O2 | BACT-PSD | NSPS | U | 0 | U | 42 | LB/H | 2,500 HR/YEAR | 0 |  |  | 0 | 0 | N |  | WATER INJECTION THAT ACHIEVES 25 PPMVD OR LESS CORRECTED TO 15% O2 IS DETERMINED ACCEPTABLE AS BACT.
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | GE LMS-100 combustion turbines, simple cycle with water injection | 15.11 | natural gas | 1690 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Utilize water injection when combusting natural gas or ULSD; Utilize selective catalytic reduction (SCR) with aqueous ammonia injection at all times except during startup and shutdown; Limit the time in startup or shutdown. | 2.5 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON NG | BACT-PSD |  | U | 0 | U | 3.8 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON ULSD | 0 |  |  | 0 | 0 | N
TX-0540 | BOSQUE COUNTY POWER PLANT | BOSQUE POWER COMPANY LLC | BOSQUE | TX | 76644 | USA | MS KATHY FRENCH | 6365322200 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | MS. BRIDGET MALONE (512) 239-4286 | 40620 | 4911 | 221112 | 4803500002 | 10/26/2007 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | PSDTX931M1 | ELECTRICAL GENERATION | 15.11 | NATURAL GAS | 170 | MW | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | BACT IS 9 PPMVD AT 15% O2 THROUGH THE USE OF DRY LOW-NOX (DLN) COMBUSTERS WHEN THE COMBUSTION TURBINE IS OPERATING IN THE SIMPLE CYCLE MODE. | 2 | PPMVD | 24-HOUR 15% O2 | BACT-PSD |  |  | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057188626 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.11 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane and methane section compressors. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low emission combustors | 25 | PPMVD | @ 15% O2, 4 HOUR ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0686 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JEFF PIPPIN | 806-418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, 512-239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358 | 4911 | 221112 | 110043432737 | 04/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-03-18 | 2016-05-09 | B |  | GSEC is proposing to build three additional new CTGs at the existing Antelope Elk Energy Center. The new facility will provide primarily peaking and intermediate power needs. The new units will be GE 7F5-Series gas turbines in simple cycle application, rated at 202 MW. Each turbine will operate a maximum of 4,572 hours per year. |  | Combustion Turbine-Generator(CTG) | 15.11 | Natural Gas | 202 | MW | Simple Cycle | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DLN | 9 | PPM | 15% O2, 3 HR. ROLLING AVG. | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0688 | SR BERTRON ELECTRIC GENERATION STATION | NRG TEXAS POWER | HARRIS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 102731, PSDTX1294 | 4911 | 221112 | 110034988413 | 05/10/2012 &nbsp;ACT | 12/19/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power generation station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the simple cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The new units will produce between 215-263 MW each. |  | Simple cycle natural gas turbines | 15.11 | Natural Gas | 225 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DLN | 9 | PPM | 3HR ROLLING AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0690 | CEDAR BAYOU ELECTRIC GERNERATION STATION | NRG TEXAS POWER | CHAMBERS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 105810, PSDTX1308 | 4911 | 221112 | 110015743301 | 08/29/2014 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power generation station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the simple cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The units will produce between 215-263 MW each. |  | Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 225 | MW | The gas turbines will be one of three options: (1) Two Siemens Model F5 (SF5) CTGs each rated at nominal capability of 225 megawatts (MW). (2) Two General Electric Model 7FA (GE7FA) CTGs each rated at nominal capability of 215 MW. (3) Two Mitsubishi Heavy Industry G Frame (MHI501G) CTGs each rated at a nominal electric output of 263 MW. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DLN | 9 | PPM | 3HR. ROLLING AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0691 | PH ROBINSON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | GALVESTON | TX |  | USA | CRAIG ECKBERG | (832) 357-5291 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 erik.hendrickson@tceq.texas.gov | 108182 PSDTX1346 | 4911 | 221112 | 110002345515 | 02/06/2013 &nbsp;ACT | 05/20/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG proposes to construct six natural gas-fired simple cycle combustion turbine generators (CTG) for peaking, designed to operate during periods of high electric demand. The six CTGs selected by NRG are General Electric Frame 7E turbines have an ISO rating of 65 MW and a nominal maximum generating capacity of 80 MW. Each of the turbines will not exceed 20 percent annual capacity (equivalent to 1,752 full load hours) in any single year or 10 percent annual capacity factor (equivalent to 876 full load hours) averaged over any three year period. |  | (6) simple cycle turbines | 15.11 | natural gas | 65 | MW | General Electric Frame 7E turbines have an ISO rating of 65 MW and a nominal maximum generating capacity of 80 MW. The turbines were originally constructed as Frame 7B units that were remanufactured in 1999 and upgraded to 7E machines Each of the turbines will not exceed 20 percent annual capacity (equivalent to 1,752 full load hours) in any single year or 10 percent annual capacity factor (equivalent to 876 full load hours) averaged over any three year period, which qualifies each of the CTGs as Acid Rain Peaking Units under 40 CFR 72.2 | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 15 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | limited use
TX-0693 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE INC | HALE | TX |  | USA | JEFF PIPPIN | (806) 418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson 512-239-2175 laura.gibson@tceq.texas.gov | 109148 PSDTX1358 | 4911 | 221112 | 110043432737 | 04/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-03-19 | 2016-07-29 | B |  | Golden Spread Electric Cooperative (GSEC) currently owns and operates Antelope Station (now renamed Antelope Elk Energy Center), a 168 MW generating facility made up of 18 quick start WÃ¤rtsilÃ¤ engines. GSEC is proposing to build a new combustion turbine-generator (CTG) facility at Antelope Station, while the 18 WÃ¤rtsilÃ¤ engines will remain and continue to be authorized by TCEQ Standard Permit. The new turbine-generator will provide primarily peaking and intermediate power needs in a highly cyclical operation. The CTG will produce approximately 100 - 200 MW of electricity, depending on loading and ambient temperature. |  | combustion turbine | 15.11 | natural gas | 202 | MW | new GE 7FA 5-Series gas turbine in a simple cycle application, with a maximum electric output of 202 megawatts (MW) and a maximum design capacity of 1,941 million British thermal units per hour (MMBtu/hr). The turbine will operate a maximum of 4,572 hours per year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 9 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0694 | INDECK WHARTON ENERGY CENTER | INDECK WHARTON, L.L.C. | WHARTON | TX |  | USA | JAMES SCHNEIDER | (847) 520-3212 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 111724 PSDTX1374 | 4911 | 221112 | unknown | 06/18/2013 &nbsp;ACT | 02/02/2015 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | Indeck Wharton, L.L.C. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will either be the General Electric 7FA (~214 MW each) or the Siemens SGT6-5000F (~227 MW each), operating as peaking units in simple cycle mode. |  | (3) combustion turbines | 15.11 | natural gas | 220 | MW | The CTGs will either be the General Electric 7FA (~214 MW each) or the Siemens SGT6-5000F (~227 MW each), operating as peaking units in simple cycle mode | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 9 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0695 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX |  | USA | JIM SHIELD | (312) 582-1440 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | 110423 PSDTX1366 | 4911 | 221112 | 110057112850 | 05/13/2013 &nbsp;ACT | 08/01/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | The proposed project is to construct and operate two natural gas-fired simple-cycle combustion turbine generators (CTGs) at the Ector County Energy Center (ECEC), located approximately 20 miles northwest of Odessa, Texas, in Ector County. |  | (2) combustion turbines | 15.11 | natural gas | 180 | MW | (2) GE 7FA.03, 2500 hours of operation per year each | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 9 | PPMVD | @15% O2, 3-HR ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 2500 hr/yr operation
TX-0696 | ROANâ€™S PRAIRIE GENERATING STATION | TENASKA ROANâ€™S PRAIRIE PARTNERS (TRPP), LLC | GRIMES | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 erik.hendrickson@tceq.texas.gov | 114698 PSDTX1378 | 4911 | 221112 | 110028050141 | 10/25/2013 &nbsp;ACT | 09/22/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | The proposed project is to construct and operate the RPGS comprised of three new simple cycle combustion turbine generators (CTG), fueled by pipeline quality natural gas. The new CTGs will be peaking units, designed to operate during periods of high electric demand. The three CTGs will produce between 507 and 694 MW of electricity combined, depending on ambient temperature and the model of combustion turbine (CT) selected. The applicant is considering three models of CTs; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. |  | (2) simple cycle turbines | 15.11 | natural gas | 600 | MW | The three possible CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. will operate 2,920 hours per year at full load for each CT | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 9 | PPMVD | @15% O2, 3-HR ROLLING AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | will operate 2,920 hours per year at full load for each CT
TX-0701 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX |  | USA | JIM SHIELD | 312-582-1440 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Marc Sturdivant, 512-239-1313, Marc.Sturdivant@tceq.texas.gov | 110423, PSDTX1366 | 4911 | 221112 | 110013396379 | 08/01/2014 &nbsp;ACT | 05/13/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is for two natural gas fired simple cycle CTGs. The proposed models include GE7Fa.03 and GE7Fa.05. They have an output of 165-193 MW. The new CTGs will operate as peaking units and will be limited to 2500 hours per year of operation each. |  | Simple Cycle Combustion Turbines | 15.11 | natural gas | 180 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry low NOx combustor | 9 | PPMVD | 15%O2, 3HR ROLLING BASIS | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0733 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JOLLY HAYDEN | 806-349-5250 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, (512)239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358M1 | 4911 | 221112 | 110043432737 | 03/20/2015 &nbsp;ACT | 05/12/2015 &nbsp;ACT | 2015-05-04 | 2016-06-08 | B |  | Golden Spread Electric Cooperative, Inc. (GSEC) is requesting authorization for three additional simple cycle electric generating plants at an existing site to meet increased energy demand in the area. The generating equipment consists of three new GE 7F5-Series natural gas-fired combustion turbine generators (CTGs). Each turbine has a maximum electric output of 202 MW. |  | Simple Cycle Turbine &amp; Generator | 15.11 | natural gas | 202 | MW | 3 additional GE 7F 5-Series Combustion Turbine Generators | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx burners | 9 | PPMVD AT 15% O2 |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | operation of each turbine is limited to 4,572 hours per year
TX-0734 | CLEAR SPRINGS ENERGY CENTER (CSEC) | NAVASOTA SOUTH PEAKERS OPERATING COMPANY II, LLC. | GUADALUPE | TX | 78155 | USA | FRANK GIACALONE | (281) 252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jack Coleman, 512-239-1255, jack.coleman@tceq.texas.gov | 120849 AND PSDTX1414 | 4911 | 221112 | Not Found | 02/20/2015 &nbsp;ACT | 05/08/2015 &nbsp;ACT | 2015-05-08 | 2018-04-18 | A |  | Navasota South Peakers Operating Company II LLC. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 MW each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low-NOx (DLN) burners | 9 | PPMVD @ 15% O2 | 3-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & IIII CTGs will operate at 2500 hours of operation per year at baseload.
TX-0764 | NACOGDOCHES POWER ELECTRIC GENERATING PLANT | NACOGDOCHES POWER, LLC | NACOGDOCHES | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem 512-239-1310 Tzvi.shalem@tceq.texas.gov | 77679, PSDTX1061M1 & O-3455 | 4911 | 221112 | 110043814744 | 06/25/2015 &nbsp;ACT | 10/14/2015 &nbsp;ACT | 2015-09-16 | 2016-07-06 | B |  | Nacogdoches Power, LLC is requesting authorization for one natural gas fired, simple cycle combustion turbine generator (CTG). The CTG will be a Siemens F5 and have a nominal electric output of 232 megawatts (MW). |  | Natural Gas Simple Cycle Turbine (&gt;25 MW) | 15.11 | natural gas | 232 | MW | One Siemens F5 simple cycle combustion turbine generator | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx burners, good combustion practices, limited operations | 9 | PPMVD @ 15% O2 |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,500 hours on a 12-month rolling average.
TX-0768 | SHAWNEE ENERGY CENTER | SHAWNEE ENERGY CENTER, LLC | HILL | TX |  | USA | NEIL O'DONOVAN | 312-422-1608 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, P.E., 512-239-1353, joseph.janecka@tceq.texas.gov | PSDTX1442, 125963 | 4911 | 221112 | UNKNOWN | 07/31/2015 &nbsp;ACT | 10/09/2015 &nbsp;ACT | 2015-10-05 | 2016-07-06 | A |  | Electric Generating Utility: The project will consist of four gas fired combustion turbines (CTGs). The CTGs are fueled with pipeline quality natural gas and will operate in simple cycle mode. The gas turbines will be one of two options. |  | Simple cycle turbines greater than 25 megawatts (MW) | 15.11 | natural gas | 230 | MW | Siemens Model SGT6-5000 F5ee â€“ 230 MW or Second turbine option: General Electric Model 7FA.05TP â€“ 227 MW | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx burners | 9 | PPMVD @ 15% O2 |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,920 hours on a 12-month rolling average.
TX-0769 | VAN ALSTYNE ENERGY CENTER (VAEC) | NAVASOTA NORTH COUNTRY PEAKERS OPERATING COMPANY I | GRAYSON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 121051 AND PSDTX1418 | 4911 | 221112 | UNKNOWN | 12/22/2014 &nbsp;ACT | 10/27/2015 &nbsp;ACT | 2015-10-30 | 2016-07-06 | A |  | Navasota North Country Peakers Operating Company I LLC. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 MW each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN burners | 9 | PPMVD @ 15% O2 | 3-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and IIII CTGs will operate at 2500 hours of operation per year at baseload.
TX-0777 | UNION VALLEY ENERGY CENTER | NAVASOTA SOUTH PEAKERS OPERATING COMPANY I, LLC. | NIXON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 120973 AND PSDTX1420 | 4911 | 221112 | UNKNOWN | 02/06/2015 &nbsp;ACT | 12/09/2015 &nbsp;ACT | 2015-12-03 | 2016-07-06 | A |  | three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 megawatt (MW) each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low NOX burners | 9 | PPMVD @ 15% O2 | 3-HR ROLLING AVERAGE PEAK | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & IIII
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Large Combustion Turbines &gt; 25 MW | 15.11 | natural gas | 232 | MW | 4 Simple cycle CTGs, 2,500 hr/yr operational limitation. Facility will consist of either 232 MW (Siemens) or 220 MW (GE) | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low-NOx burners (DLN), good combustion practices | 9 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Subparts KKKK and TTTT
TX-0794 | HILL COUNTY GENERATING FACILITY | BRAZOS ELECTRIC COOPERATIVE | HILL | TX |  | USA | MIKE MEYERS | (254)750-6228 | MMEYERS@BRAZOSELECTRIC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512)239-1512, randy.hamilton@tceq.texas.gov | 130051,PSDTX1450, GHGPSDTX131 | 4911 | 221112 | UNKNOWN | 12/18/2015 &nbsp;ACT | 04/07/2016 &nbsp;ACT | 2016-04-05 | 2016-07-29 | A |  | Four simple cycle combustion turbine electric generators are proposed. Natural gas or ultra-low sulfur diesel fuel oil are the fuels. Turbine model options are: General Electric (GE) 7FA.03, GE 7FA.04, GE 7FA.05, and Siemes SGT6-5000(5)ee. Electric output is between 684 and 928 megawatts (MW). |  | Simple cycle turbine | 15.11 | natural gas | 171 | MW | Each combustion turbine is limited to 2,920 hours of annual operation, including startup and shutdown hours. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Emission controls consist of dry low-NOx combustors (DLN). DLN combustors use two stages of combustion, transitioning from initial startup with fuel and flame in the primary nozzles only, through a lean lean stage with fuel and flame in the primary and secondary nozzles, to fuel in the secondary stage only, extinguishing the primary flame, and in full operation, premix mode, with fuel to both nozzles, but flame only in the second stage. When natural gas and air are well-mixed before combustion, the flame temperature and resulting NOx emissions are greatly reduced compared to conventional diffusion flame combustion. | 9 | PPMVD @ 15% O2 | 3-HR ROLLING AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0816 | CORPUS CHRISTI LIQUEFACTION | CORPUS CHRISTI LIQUEFACTION STAGE III, LLC | SAN PATRICIO | TX |  | USA | KEITH LITTLE | (713) 375-5204 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 139479, PSDTX1496, GHGPSDTX157 | 4925 | 221210 | Not Found | 11/16/2016 &nbsp;ACT | 02/14/2017 &nbsp;ACT | 2017-02-07 | 2018-04-18 | B |  | Trains 4 and 5 will consist of 12 natural gas compressor turbines, 2 thermal oxidizers, 2 sets of flares each comprised of one wet gas flare and one dry gas flare, 2 amine surge tanks (maintenance, startup, and shutdown [MSS] only), 3 diesel generators, 3 fire-water pump diesel engines, 6 fixed roof diesel storage tanks, and piping components. |  | Refrigeration compressor turbines | 15.11 | NATURAL GAS | 40000 | HP | 2 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane, ethylene, and methane section compressors. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low emission burners | 25 | PPMDV | @ 15% O2 | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Subpart KKKK
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Simple Cycle Turbine | 15.11 | natural gas | 227.5 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx burners (control), natural gas, good combustion practices, limited operating hours (prevention) | 9 | PPMV | 15% O2 3-H AVG | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Economic reasonableness, operation of each turbine is limited to 2000 hours per year.
TX-0826 | MUSTANG STATION | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | YOAKUM | TX |  | USA | JEFF PIPPIN | 806-418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | 72579, PSDTX1080M1, GHGPSDTX13 | 4911 | 221112 | 110041502433 | 06/12/2017 &nbsp;ACT | 08/16/2017 &nbsp;ACT | 2017-07-24 | 2018-04-18 | C |  | GE7FA combustion turbine (Unit 6) to increase the hours of operation to 3000 hours per year. The turbine construction was completed the first quarter of 2013 and initial firing began on April 1, 2013. |  | Simple Cycle Turbine | 15.11 | NATURAL GAS | 162.8 | MW | Unit 6 Turbine is limited to 3000 hours per year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low-NOx burners | 9 | PPMVD |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK MACT YYYY
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry low NOx burners | 9 | PPMVD |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines MSS | 15.11 | NATURAL GAS | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Minimizing duration of startup/shutdown, using good air pollution control practices and safe operating practices. | 0.01 | TON/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0026 | WAVERLY FACILITY | PLEASANTS ENERGY, LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 304-665-4201 | GERALD.GATTI@GDFSUEZNA.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0034 | 4911 | 221112 | 110010376734 | 04/18/2016 &nbsp;ACT | 01/23/2017 &nbsp;ACT | 2017-03-21 | 2018-05-01 | D | http://www.dep.wv.gov/daq/Documents/January 2017 Permits and Evals/073-00022_PERM_R14-0034.pdf | 300 MW, natural gas fired, simple cycle peaking power facility | In this permitting action PSD only applies to the modified combustion turbines based on the relaxation of an original synthetic minor permit issued in 1999. Project also involves previous installation of turbo-charging. All BACT emission limits are given without turbocharging and startup/shutdown emissions are not included. Please contact above engineer for more information. There are two identical turbines but only one is listed. | GE Model 7FA Turbine | 15.11 | Natural Gas | 1571 | mmbtu/hr | There are two identical units at the facility. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry Low-NOx Combustion System (DLNB), Water Injection | 9 | PPM | NATURAL GAS | BACT-PSD | NSPS | U | 0 | U | 49 | PPM | FUEL OIL | 9 | PPM | NATURAL GAS | 0 | 0 | N |  | Additional emission limits are in the permit for use of turbocharging and startup/shutdown emissions. Please contact if need additional information.
*WV-0028 | WAVERLY POWER PLANT | PLEASANTS ENERGY LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 3046654201 | GERALD.GATTI@DYNEGY.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Steve Pursley, PE Engineer West Virginia Division of Air Quality 601-57th St., SE Charleston, WV 25304 Phone: (304) 926-0499 x1218 Fax: (304) 926-0478 steve.r.pursley@wv.gov | R14-0034A | 4911 | 221112 | 110063231042 | 11/30/2017 &nbsp;ACT | 03/13/2018 &nbsp;ACT | 2018-05-29 | 2018-05-29 | U | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/073-00022_PERM_R14-0034A.pdf | 300 MW Sinple-Cycle Peaking Plant | Modification to existing PSD Permit (R14-0034, RBLC Number WV-0027) to add &lsquo;&lsquo;advanced gas path&lsquo;&lsquo; technology to the turbines that was defined as a &lsquo;&lsquo;change in the method of operation&lsquo;&lsquo; that resulted a major modification to the turbines. | GE 7FA.004 Turbine | 15.11 | Natural Gas | 167.8 | MW | This one entry is for both turbines as they are the same. Each turbine, after this modification, is a nominal 167.8 MW GE Model 7FA.004. Has oil-fire backup. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry LNB | 69 | LB/HR |  | BACT-PSD | NSPS | U | 0 | U | 232.3 | TONS/YEAR |  | 9 | PPM |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP03) | 15.11 | Natural Gas | 40 | MW |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 5 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD | NSPS | N | 0 | U | 7.7 | LB/H | 30-DAY ROLLING AVERAGE | 36 | T/YR |  | 8308 | 8308 | N | 2011
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Trubine (EP04) | 15.11 | Natural Gas | 40 | MW |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 5 | PPMV AT 15% O2 | 1-HOUR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 7.7 | LB/H | 30-DAY ROLLING AVERAGE | 36 | T/YR |  | 8308 | 8308 | N | 2011
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP05) | 15.11 | Natural Gas | 40 | MW |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 5 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD | NSPS | N | 0 | U | 7.7 | LB/H | 30-DAY ROLLING AVERAGE | 36 | T/YR |  | 8308 | 8308 | N | 2011
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | COMBUSTION TURBINES (2) | 15.11 | NATURAL GAS |  |  | GENERAL ELECTRIC 207FA COMBUSTION TURBINE WITH HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT FIRING CAPABILIY (DUCT BURNER EQUIPPED WITH LNB). EACH CT IS CAPABLE OF GENERATING A NOMINAL 176 MW OF ELECTRICITY. THE STEAM TURBINE IS CAPABLE OF GENERATING 304 MW OF ELECTRICITY. OVERALL FACILITY NOMINAL GENERATION CAPACITY OF 640 MW | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.012 | LB/MMBTU @ 15% O2 | 3-HR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | APPLICABLE TO OPERATING WITH OR WITHOUT DUCT BURNING
MN-0075 | GREAT RIVER ENERGY - ELK RIVER STATION | GREAT RIVER ENERGY | SHERBURNE | MN | 55330 | USA | MARK STROHFUS | 7634455210 | MSTROHFU@GRENERGY.COM | 5 | MN001 | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | MR. RICHARD CORDES | (651)757-2291 | RICHARD.CORDES@STATE.MN.US | TONI VOLKMEIER, TONI.VOLKMEIER@PCA.STATE.MN.US | 14100003-004 | 4911 | 221119 | UNKNOWN | 03/31/2008 &nbsp;EST | 07/01/2008 &nbsp;ACT | 2008-12-01 | 2009-01-26 | B |  | THE FACILITY IS AN ELECTRIC POWER GENERATING STATION BURNING REFUSE DERIVED FUEL (RDF). THE RDF BURNED AT THIS FACILITY IS PROCESSED FROM MUNICIPAL SOLID WASTE. THE FACILITY PRODUCES APPROXIMATELY 40 MEGAWATTS OF ELECTRICITY. THERE IS ALSO A SINGLE CYCLE COMBUSTION TURBINE GENERATOR (CTG) |  | COMBUSTION TURBINE GENERATOR | 15.11 | NATURAL GAS | 2169 | MMBTU/H | GENERATOR IS A SIMPLE CYCLE COMBUSTION TURBINE, WHICH WILL BE OPERATED AS A PEAK-SHAVING UNIT. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | P | FUEL LIMITED TO NATURAL GAS AND ULTRA-LOW SULFUR FUEL OIL | 0 |  | SEE NOTE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS
TX-0540 | BOSQUE COUNTY POWER PLANT | BOSQUE POWER COMPANY LLC | BOSQUE | TX | 76644 | USA | MS KATHY FRENCH | 6365322200 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | MS. BRIDGET MALONE (512) 239-4286 | 40620 | 4911 | 221112 | 4803500002 | 10/26/2007 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | PSDTX931M1 | ELECTRICAL GENERATION | 15.11 | NATURAL GAS | 170 | MW | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | P | BACT IS THE USE OF PIPELINE-QUALITY NATURAL GAS AND THE APPLICATION OF GOOD COMBUSTION CONTROLS. WITH THIS METHOD OF CONTROL, PM/PM10 EMISSIONS SHOULD NOT EXCEED 0.01 LB/MMBTU FOR A 3-HOUR ROLLING PERIOD. | 0.01 | LB/MMBTU | 3 HR ROLLING PERIOD | BACT-PSD |  |  | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0261 | VERMILLION GENERATING STATION | DUKE ENERGY INDIANA, LLC VERMILLION GENERATING STA | VERMILLION | IN | 47928 | USA | PATRICK COUGHLIN | 3178382108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIP SINHA PH.D. 317-234-4907 | 165-36956-00022 | 4911 | 221112 | 110006010921 | 03/16/2016 &nbsp;ACT | 02/28/2017 &nbsp;ACT | 2017-07-07 | 2017-08-09 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36956F.PDF | ELECTRIC UTILITY SERVICES |  | SIMPLE CYCLE, NATURAL GAS FIRED COMBUSTION TURBINES | 15.11 | NATURAL GAS | 80 | MW |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 5 | LB/H | EACH TURBINE | BACT-PSD |  | N | 0 |  | 0.5 | TON/12 CONSEC. MONTH | COMPLIANCE DETERMINED END OF EACH MONTH | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: ONLY TWO TURBINES WILL OPERATE DURING LOW LOAD OPERATION.
IN-0264 | MONTPELIER GENERATING STATION | AES OHIO GENERATION, LLC | WELLS | IN | 46781 | USA | DREW PARKER | 9373314993 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: MADHURIMA MOULIK 317-233-6663 MMOULIK@IDEM.IN.GOV SECTION CHIEF: JASON KRAWCZYK 317-234-5174 | 179-37209-00026 | 4911 | 221112 | 110021089061 | 05/23/2016 &nbsp;ACT | 01/06/2017 &nbsp;ACT | 2017-07-07 | 2017-11-17 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/37209F.PDF | COMBUSTION TURBINES |  | PRATT &amp; TWIN-PAC SIMPLE CYCLE TURBINES | 15.11 | NATURAL GAS | 270.9 | MMBTU/H | NO. 2 DIESEL OIL BACKUP FUEL | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS AS PRIMARY FUEL; GOOD COMBUSTION PRACTICES | 0.0066 | LB/MMBTU | 3-HR AVG FOR NATURAL GAS | BACT-PSD |  |  | 0 |  | 0.012 | LB/MMBTU | 3-HR AVG FOR FUEL OIL | 0 |  |  | 0 | 0 | N |  | EACH OF 8 TURBINES LIMITED TO 500 HOURS OF FUEL OIL COMBUSTION PER 12 MONTH PERIOD
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | COMBUSTION TURBINES (2) | 15.11 | NATURAL GAS |  |  | GENERAL ELECTRIC 207FA COMBUSTION TURBINE WITH HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT FIRING CAPABILIY (DUCT BURNER EQUIPPED WITH LNB). EACH CT IS CAPABLE OF GENERATING A NOMINAL 176 MW OF ELECTRICITY. THE STEAM TURBINE IS CAPABLE OF GENERATING 304 MW OF ELECTRICITY. OVERALL FACILITY NOMINAL GENERATION CAPACITY OF 640 MW | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.012 | LB/MMBTU @ 15% O2 | 3-HR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | APPLICABLE TO OPERATING WITH OR WITHOUT DUCT BURNING
MN-0075 | GREAT RIVER ENERGY - ELK RIVER STATION | GREAT RIVER ENERGY | SHERBURNE | MN | 55330 | USA | MARK STROHFUS | 7634455210 | MSTROHFU@GRENERGY.COM | 5 | MN001 | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | MR. RICHARD CORDES | (651)757-2291 | RICHARD.CORDES@STATE.MN.US | TONI VOLKMEIER, TONI.VOLKMEIER@PCA.STATE.MN.US | 14100003-004 | 4911 | 221119 | UNKNOWN | 03/31/2008 &nbsp;EST | 07/01/2008 &nbsp;ACT | 2008-12-01 | 2009-01-26 | B |  | THE FACILITY IS AN ELECTRIC POWER GENERATING STATION BURNING REFUSE DERIVED FUEL (RDF). THE RDF BURNED AT THIS FACILITY IS PROCESSED FROM MUNICIPAL SOLID WASTE. THE FACILITY PRODUCES APPROXIMATELY 40 MEGAWATTS OF ELECTRICITY. THERE IS ALSO A SINGLE CYCLE COMBUSTION TURBINE GENERATOR (CTG) |  | COMBUSTION TURBINE GENERATOR | 15.11 | NATURAL GAS | 2169 | MMBTU/H | GENERATOR IS A SIMPLE CYCLE COMBUSTION TURBINE, WHICH WILL BE OPERATED AS A PEAK-SHAVING UNIT. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | FUEL LIMITED TO NATURAL GAS AND ULTRA-LOW SULFUR FUEL OIL | 0 |  | SEE NOTE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS
MN-0075 | GREAT RIVER ENERGY - ELK RIVER STATION | GREAT RIVER ENERGY | SHERBURNE | MN | 55330 | USA | MARK STROHFUS | 7634455210 | MSTROHFU@GRENERGY.COM | 5 | MN001 | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | MR. RICHARD CORDES | (651)757-2291 | RICHARD.CORDES@STATE.MN.US | TONI VOLKMEIER, TONI.VOLKMEIER@PCA.STATE.MN.US | 14100003-004 | 4911 | 221119 | UNKNOWN | 03/31/2008 &nbsp;EST | 07/01/2008 &nbsp;ACT | 2008-12-01 | 2009-01-26 | B |  | THE FACILITY IS AN ELECTRIC POWER GENERATING STATION BURNING REFUSE DERIVED FUEL (RDF). THE RDF BURNED AT THIS FACILITY IS PROCESSED FROM MUNICIPAL SOLID WASTE. THE FACILITY PRODUCES APPROXIMATELY 40 MEGAWATTS OF ELECTRICITY. THERE IS ALSO A SINGLE CYCLE COMBUSTION TURBINE GENERATOR (CTG) |  | COMBUSTION TURBINE GENERATOR | 15.11 | NATURAL GAS | 2169 | MMBTU/H | GENERATOR IS A SIMPLE CYCLE COMBUSTION TURBINE, WHICH WILL BE OPERATED AS A PEAK-SHAVING UNIT. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | FUEL LIMITED TO NATURAL GAS AND ULTRA-LOW SULFUR FUEL OIL | 0 |  | SEE NOTE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS
NJ-0077 | HOWARD DOWN STATION | VINELAND MUNICIPAL ELECTRIC UTILITY (VMEU) | CUMBERLAND | NJ | 8360 | USA |  | SYSNULL |  | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | MICHAEL HOGAN, PERMIT EVALUATOR, MICHAEL.HOGAN@DEP.STATE.NJ.US YOGESH DOSHI, SUPERVISOR, YOGESH.DOSHI@DEP.STATE.NJ.US | 75507-BOP090003 | 4911 | 221112 | 110021327492 | 10/28/2009 &nbsp;ACT | 09/16/2010 &nbsp;ACT | 2011-08-23 | 2012-01-05 | A |  |  |  | SIMPLE CYCLE (NO WASTE HEAT RECOVERY)(&gt;25 MW) | 15.11 | NATURAL GAS | 5000 | MMFT3/YR | THE PROCESS CONSISTS OF ONE NEW TRENT 60 SIMPLE CYCLE COMBUSTION TURBINE. THE TURBINE WILL GENERATE 64 MW OF ELECTRICITY USING NATURAL GAS AS A PRIMARY FUEL (UP TO 8760 HOURS PER YEAR), WITH A BACKUP FUEL OF ULTRA LOW SULFUR DIESEL FUEL (ULSD) WHICH CAN ONLY BE COMBUSTED FOR A MAXIMUM OF 500 HOURS PER YEAR AND ONLY DURING NATURAL GAS CURTAILMENT. THE MAXIMUM HEAT INPUT RATE WHILE COMBUSTING NATURAL GAS IS 590 MMBTU/HR AND THE MAXIMUM HEAT INPUT RATE WHILE COMBUSTING ULSD IS 568 MMBTU/HR. THE TURBINE WILL UTILIZE WATER INJECTION AND SELECTIVE CATALYTIC REDUCTION TO CONTROL NOX EMISSION AND A CATALYTIC OXIDIZER TO CONTROL CO AND VOC EMISSION. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Other - TEST METHODS M201A AND M202 | (Particulate Matter (PM)) | PM | N | USE OF CLEAN BURNING FUELS; NATURAL GAS AS PRIMARY FUEL AND ULTRA LOW SULFUR DISTILLATE OIL WITH 15 PPMSULFUR BY WEIGHT AS BACKUP FUEL | 5 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NM-0051 | CUNNINGHAM POWER PLANT | SOUTHWESTERN PUBLIC SERVICE CO. | LEA | NM | 88241-1650 | USA | KEVIN WORLEY | 806 378 2185 | KEVIN.WORLEY@XCELENERGY.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Cember Hardison is permit writer. 505 476 4346. cember.hardison@state.nm.us | PSD-NM-622-M3 | 4911 | 221122 | 110010571639 | 03/08/2011 &nbsp;ACT | 05/02/2011 &nbsp;ACT | 2011-08-02 | 2012-01-05 | C |  | Electric steam generating facility providing commercial electric power using natural gas fired boilers and turbines. | Simple Cycle Combustion Turbines. Permit revises the NOx BACT ppmvd limit for turbines established in permit PSD-NM-622-M2 issued 2-10-97 because turbines have not been able to meet NOx BACT limits. No modification or change to mass emissions. Former NOx BACT was at 15 ppmvd w/out power augmentation (normal mode) and 25 ppmvd w/ power augmentation (see RBLC ID NM-0028). Entry also clarifies the existing CO, SOx, and PM BACT. | Normal Mode (without Power Augmentation) | 15.11 | natural gas | 0 |  |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | Good Combustion Practices as described in the permit. | 5.4 | LB/H | HOURLY | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | PM10 BACT as established in PSD-NM-622-M3 issued 2-10-97.
NM-0051 | CUNNINGHAM POWER PLANT | SOUTHWESTERN PUBLIC SERVICE CO. | LEA | NM | 88241-1650 | USA | KEVIN WORLEY | 806 378 2185 | KEVIN.WORLEY@XCELENERGY.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Cember Hardison is permit writer. 505 476 4346. cember.hardison@state.nm.us | PSD-NM-622-M3 | 4911 | 221122 | 110010571639 | 03/08/2011 &nbsp;ACT | 05/02/2011 &nbsp;ACT | 2011-08-02 | 2012-01-05 | C |  | Electric steam generating facility providing commercial electric power using natural gas fired boilers and turbines. | Simple Cycle Combustion Turbines. Permit revises the NOx BACT ppmvd limit for turbines established in permit PSD-NM-622-M2 issued 2-10-97 because turbines have not been able to meet NOx BACT limits. No modification or change to mass emissions. Former NOx BACT was at 15 ppmvd w/out power augmentation (normal mode) and 25 ppmvd w/ power augmentation (see RBLC ID NM-0028). Entry also clarifies the existing CO, SOx, and PM BACT. | Power Augmentation | 15.11 | natural gas | 0 |  | Increase power output by lowering the outlet air temperatur through water inejctinos into the compressor. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | Good combustion practices as defined in the permit. | 5.4 | LB/H | HOURLY | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | PM10 BACT established in PSD-NM-622-M2 issued 2-10-97.
NY-0106 | GREENIDGE STATION | GREENIDGE GENERATION LLC | YATES | NY | 14441-0187 | USA |  | 315-536-2359 |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov |  | 8-5736-00004/00017 | 4911 | 221112 | 110000327619 | 09/07/2016 &nbsp;ACT | 09/07/2016 &nbsp;ACT | 2017-08-30 | 2017-09-28 | C | http://www.dec.ny.gov/chemical/32249.html | Greenidge Generation LLC has submitted a revised application for a Title V Air Permit in accordance with the requirements of Title 6 of the New York compilation of Codes, Rules, and Regulations, Part 201-6 (6 NYCRR Part 201-6). The application is for conversion of the Greenidge Electricity Generating Station, located in the Town of Torrey, Yates County to operate primarily on natural gas with up to 19% biomass co-firing. Greenidge Station is comprised of Unit 4, which includes a Combustion Engineering, tangentially-fired dry bottom boiler (Boiler No. 6) with a maximum heat input rating of 1,117 MMBtu/hr, and a steam generating turbine with a maximum rated output of 107 Megawatts (MW) of electricity. The facility is equipped with a suite of air pollution control (both pre-combustion and post-combustion) systems to control pollutant nitrogen oxides, carbon monoxide, and particulate matter (PM, PM10 and PM2.5) emissions from facility operations. Greenhouse gases will be reduced substantially primarily by the use of cleaner fuels. Under the proposal, Unit 4 will not burn coal or fuel oil any longer. | Also NAICS 221117 - biomass with wood | Turbine - natural gas | 15.11 | natural gas | 107 | MW |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Other - 40 CFR 60 App A M-5 and 40 CFR 51 App M M-202 | (Particulate Matter (PM)) | PM | A | Baghouse with leak detection system. | 8.25 | E-3 LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0333 | DAYTON POWER & LIGHT ENERGY LLC | DAYTON POWER & LIGHT COMPANY | MONTGOMERY | OH | 45439 | USA | CARRIE BURKS | 937-331-3042 |  | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104867 | 4911 | 221112 | 110000394145 | 04/30/2009 &nbsp;ACT | 12/03/2009 &nbsp;ACT | 2010-05-13 | 2010-05-20 | C |  | Seven simple cycle stationary combustion turbines all with rating of 80 MW and nominal heat input of 1115.2 mmBtu/hr using natural gas or No. 2 fuel oil and all with water injection control and last 5 also with low NOx burners. | Simple cycle stationary combution turbines issed in 2 different permits. Four turbines in this permit with dry low NOx combustion and water injection controls. Administrative Modification to original PTI #08-04153 issued 8/7/01, to incorporate low mass emissions methodology as allowed per 40 CFR 75.19 in lieu of methods under Appendix D or E to Part 75, by meeting the requirements of having mass emissions of less than 25 T/YR SO2 and less than 100 T/YR NOx (per turbine) based on 3 years of operation. Modification also reduced permitted formaldehyde emissions by 8.7 tons, recalculated based on the restriction on hours of operation. | Turbines (4), simple cycle, natural gas | 15.11 | NATURAL GAS | 15020 | H/YR | Hours per year for all 4 turbines | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Other - Method 201 or 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 0.013 | LB/MMBTU | ACTUAL HEAT INPUT | BACT-PSD | SIP | U | 0 | Y | 46.12 | T/YR | PER ROLLING 12-MO. FOR 4 UNITS &ALL FUEL | 0.013 | LB/MMBTU | ACTUAL HEAT INPUT | 0 | 0 | N |  | The emission factor for PM was used as a surrogate for PM10 and PM2.5 where there were no other emission factors available. T/YR limit is for both fuels and for the 4 turbines combined. BACT: using only clean fuels, natural gas or #2 fuel oil.
OK-0127 | WESTERN FARMERS ELECTRIC ANADARKO | WESTERN FARMERS ELECTRIC COOPERATIVE | CADDO | OK | 73005 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2005-037-C(M-2) PSD | 4911 | 221112 | 110001631440 | 02/01/2008 &nbsp;ACT | 06/13/2008 &nbsp;ACT | 2008-12-31 | 2009-04-20 | B |  | THE FACILITY GENERATES WHOLESALE ELECTRICITY WHICH IS TRANSMITTED OVER WFECÂ¿S ELECTRICAL DISTRIBUTION SYSTEM. THE ELECTRICITY IS SOLD IN RURAL AREAS OF APPROXIMATELY 3/4 OF THE STATE OF OKLAHOMA. THE CURRENT FACILITY CONSISTS OF TWO NATURAL GAS FIRED HIGH PRESSURE BOILERS, A GAS/OIL FIRED HIGH PRESSURE BOILER, THREE GAS/OIL FIRED COMBINED CYCLE GAS TURBINES, A FIRE PUMP DIESEL ENGINE FOR EMERGENCY BACKUP, AND OTHER SOURCES WHICH ARE CONSIDERED INSIGNIFICANT OR TRIVIAL. THE THREE BOILERS ARE BACKUP UNITS THAT ONLY OPERATE WHEN IT IS FEASIBLE, SUCH AS DURING PEAK DEMAND. TWO OF THE BOILERS HAVE BEEN IDLE SINCE 1984. ONE BOILER WAS REPLACED IN 1997, AND ANOTHER WAS REPLACED IN 1998. | WESTERN FARMERS ELEC COOP PROPOSES TO CONSTRUCT AND OPERATE THREE NATURAL GAS-FIRED PEAKING ELECTRIC GENERATING UNITS AT THE FACILITY TO MEET ANTICIPATED FUTURE ENERGY DEMAND. EACH UNIT CAPACITY OF +/- 50 MW. | COMBUSTION TURBINE PEAKING UNIT(S) | 15.11 | NATURAL GAS | 462.7 | MMBTU/H | THE INSTALLATION WILL CONSIST OF THREE GENERAL ELECTRIC LM6000 SPRINT SIMPLE CYCLE AERODERIVATIVE COMBUSTION TURBINE GENERATORS. EACH OF THE TURBINES WILL HAVE A MAXIMUM PEAK HEAT INPUT RATE OF 462.7 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTUH). THE NEW COMBUSTION TURBINES WILL FIRE ONLY PIPELINE-QUALITY NATURAL GAS AND WILL BE EQUIPPED WITH WATER INJECTION. THE PROPOSED NEW UNITS WILL EACH HAVE A NOMINAL ELECTRICAL GENERATING CAPACITY OF 50 MW. ACTUAL UNIT CAPACITY WILL BE DETERMINED DURING DETAILED DESIGN OF THE PLANT AND MAY BE 5 TO 10-MW HIGHER OR LOWER THAN THE NOMINAL VALUE OF 50 MW, DEPENDING ON AMBIENT CONDITION RATINGS AND FINAL DESIGN. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | NO CONTROLS FEASIBLE. | 4 | LB/H | 2,500 HR/YEAR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | GOOD COMBUSTION PRACTICES IN COMBINATION WITH USE OF NATURAL GAS IS DETERMINED ACCEPTABLE AS BACT.
CA-1223 | PIO PICO ENERGY CENTER | PIO PICO ENERGY CENTER, LLC | OTAY MESA | CA | 92154 | USA | GARY CHANDLER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SD 11-01 | 4911 | 221112 | 110045006943 | 06/14/2012 &nbsp;ACT | 11/19/2012 &nbsp;ACT | 2013-03-05 | 2014-01-28 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | CONSTRUCTION OF THREE GENERAL ELECTRIC (GE) LMS100 NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 100 MW EACH. THE PROJECT WILL HAVE AN ELECTRICAL OUTPUT OF 300 MW. | NOTE: PERMIT ISSUED 11/19/2012. ENVIRONMENTAL APPEALS BOARD REMANDED THE PM BACT ANALYSIS TO REGION 9 ON 8/2/2013. FINAL PERMIT ISSUED ON 2/28/2014. ONE PETITION FILED IN 9TH CIRCUIT FEDERAL COURT CHALLENGING THE FINAL PERMIT DECISION. THIS LAWSUIT WAS DISMISSED ON 6/17/2014 IN RESPONSE TO PETITIONERSâ€™ MOTION FOR VOLUNTARY DISMISSAL. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.11 | NATURAL GAS | 300 | MW | Three simple cycle combustion turbine generators (CTG). Each CTG rated at 100 MW (nominal net). | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Other - EPA METHOD 5 & 202, OR CTM 039 | (Particulate Matter (PM)) | PM | P | PUC-QUALITY NATURAL GAS | 0.0065 | LB/MMBTU (HHV) | AT LOADS OF 80% OR HIGHER | BACT-PSD |  | U | 0 | U | 5.5 | LB/H |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Gas Turbines (8 units) | 15.11 | natural gas | 333 | mm btu/hr |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and fueled by natural gas | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0077 | HOWARD DOWN STATION | VINELAND MUNICIPAL ELECTRIC UTILITY (VMEU) | CUMBERLAND | NJ | 8360 | USA |  | SYSNULL |  | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | MICHAEL HOGAN, PERMIT EVALUATOR, MICHAEL.HOGAN@DEP.STATE.NJ.US YOGESH DOSHI, SUPERVISOR, YOGESH.DOSHI@DEP.STATE.NJ.US | 75507-BOP090003 | 4911 | 221112 | 110021327492 | 10/28/2009 &nbsp;ACT | 09/16/2010 &nbsp;ACT | 2011-08-23 | 2012-01-05 | A |  |  |  | SIMPLE CYCLE (NO WASTE HEAT RECOVERY)(&gt;25 MW) | 15.11 | NATURAL GAS | 5000 | MMFT3/YR | THE PROCESS CONSISTS OF ONE NEW TRENT 60 SIMPLE CYCLE COMBUSTION TURBINE. THE TURBINE WILL GENERATE 64 MW OF ELECTRICITY USING NATURAL GAS AS A PRIMARY FUEL (UP TO 8760 HOURS PER YEAR), WITH A BACKUP FUEL OF ULTRA LOW SULFUR DIESEL FUEL (ULSD) WHICH CAN ONLY BE COMBUSTED FOR A MAXIMUM OF 500 HOURS PER YEAR AND ONLY DURING NATURAL GAS CURTAILMENT. THE MAXIMUM HEAT INPUT RATE WHILE COMBUSTING NATURAL GAS IS 590 MMBTU/HR AND THE MAXIMUM HEAT INPUT RATE WHILE COMBUSTING ULSD IS 568 MMBTU/HR. THE TURBINE WILL UTILIZE WATER INJECTION AND SELECTIVE CATALYTIC REDUCTION TO CONTROL NOX EMISSION AND A CATALYTIC OXIDIZER TO CONTROL CO AND VOC EMISSION. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Other - TEST METHODS M201A AND M202 | (Particulate Matter (PM)) | PM | N | USE OF CLEAN BURNING FUELS; NATURAL GAS AS PRIMARY FUEL AND ULTRA LOW SULFUR DISTILLATE OIL WITH 15 PPMSULFUR BY WEIGHT AS BACKUP FUEL | 5 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0106 | GREENIDGE STATION | GREENIDGE GENERATION LLC | YATES | NY | 14441-0187 | USA |  | 315-536-2359 |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov |  | 8-5736-00004/00017 | 4911 | 221112 | 110000327619 | 09/07/2016 &nbsp;ACT | 09/07/2016 &nbsp;ACT | 2017-08-30 | 2017-09-28 | C | http://www.dec.ny.gov/chemical/32249.html | Greenidge Generation LLC has submitted a revised application for a Title V Air Permit in accordance with the requirements of Title 6 of the New York compilation of Codes, Rules, and Regulations, Part 201-6 (6 NYCRR Part 201-6). The application is for conversion of the Greenidge Electricity Generating Station, located in the Town of Torrey, Yates County to operate primarily on natural gas with up to 19% biomass co-firing. Greenidge Station is comprised of Unit 4, which includes a Combustion Engineering, tangentially-fired dry bottom boiler (Boiler No. 6) with a maximum heat input rating of 1,117 MMBtu/hr, and a steam generating turbine with a maximum rated output of 107 Megawatts (MW) of electricity. The facility is equipped with a suite of air pollution control (both pre-combustion and post-combustion) systems to control pollutant nitrogen oxides, carbon monoxide, and particulate matter (PM, PM10 and PM2.5) emissions from facility operations. Greenhouse gases will be reduced substantially primarily by the use of cleaner fuels. Under the proposal, Unit 4 will not burn coal or fuel oil any longer. | Also NAICS 221117 - biomass with wood | Turbine - natural gas | 15.11 | natural gas | 107 | MW |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Other - 40 CFR 60 App A M-5 and 40 CFR 51 App M M-202 | (Particulate Matter (PM)) | PM | A | Baghouse with leak detection system. | 8.25 | E-3 LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0686 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JEFF PIPPIN | 806-418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, 512-239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358 | 4911 | 221112 | 110043432737 | 04/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-03-18 | 2016-05-09 | B |  | GSEC is proposing to build three additional new CTGs at the existing Antelope Elk Energy Center. The new facility will provide primarily peaking and intermediate power needs. The new units will be GE 7F5-Series gas turbines in simple cycle application, rated at 202 MW. Each turbine will operate a maximum of 4,572 hours per year. |  | Combustion Turbine-Generator(CTG) | 15.11 | Natural Gas | 202 | MW | Simple Cycle | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; Good combustion practices | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Includes PM and PM10
TX-0688 | SR BERTRON ELECTRIC GENERATION STATION | NRG TEXAS POWER | HARRIS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 102731, PSDTX1294 | 4911 | 221112 | 110034988413 | 05/10/2012 &nbsp;ACT | 12/19/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power generation station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the simple cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The new units will produce between 215-263 MW each. |  | Simple cycle natural gas turbines | 15.11 | Natural Gas | 225 | MW |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices, natural gas | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Includes PM and PM10
TX-0690 | CEDAR BAYOU ELECTRIC GERNERATION STATION | NRG TEXAS POWER | CHAMBERS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 105810, PSDTX1308 | 4911 | 221112 | 110015743301 | 08/29/2014 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power generation station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the simple cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The units will produce between 215-263 MW each. |  | Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 225 | MW | The gas turbines will be one of three options: (1) Two Siemens Model F5 (SF5) CTGs each rated at nominal capability of 225 megawatts (MW). (2) Two General Electric Model 7FA (GE7FA) CTGs each rated at nominal capability of 215 MW. (3) Two Mitsubishi Heavy Industry G Frame (MHI501G) CTGs each rated at a nominal electric output of 263 MW. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices, Natural Gas | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Includes PM and PM10
IL-0121 | INVENERGY NELSON EXPANSION LLC | INVENERGY | LEE | IL | 61058 | USA | GORDON GRAY | 312-582-1290 | GGRAY@INVENERGY.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Bob Smet; 217-785-9250; robert.smet@illinois.gov | 15060042 | 4911 | 221112 | Not Found | 07/28/2016 &nbsp;ACT | 09/27/2016 &nbsp;ACT | 2017-01-27 | 2017-04-28 | B | https://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/9dbc452815081576862580b2006897b4/$FILE/ATT4AK5N.pdf/15060042.pdf | Peaking facility at an existing major source. The expansion will consist of two simple cycle combustion turbines and a fuel heater. |  | Two Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 190 | MW | Two simple cycle combustion turbines used for peaking purposes and fired primarily on natural gas with ULSD as a secondary fuel. | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | turbine design and good combustion practices | 0.0038 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0.015 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission 1 (natural gas): 0.0038 lb/mmbtu* Emission 2 (ULSD): 0.0150 lb/mmbtu* *During an hour that includes a startup, the particulate emissions of the turbine shall not exceed 7.5 lb/hr (natural gas) and 32.2 lb/hr (ULSD).
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER | 15.11 | NATURAL GAS | 92.5 | MMBTU/H | NATURAL GAS USAGE SHALL NOT EXCEED 18.14 MMCF/YEAR. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN, USE NATURAL GAS | 1.9 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER | 15.11 | NATURAL GAS | 92.5 | MMBTU/H | NATURAL GAS USAGE SHALL NOT EXCEED 18.14 MMCF/YEAR. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN, USE NATURAL GAS | 1.9 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0261 | VERMILLION GENERATING STATION | DUKE ENERGY INDIANA, LLC VERMILLION GENERATING STA | VERMILLION | IN | 47928 | USA | PATRICK COUGHLIN | 3178382108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIP SINHA PH.D. 317-234-4907 | 165-36956-00022 | 4911 | 221112 | 110006010921 | 03/16/2016 &nbsp;ACT | 02/28/2017 &nbsp;ACT | 2017-07-07 | 2017-08-09 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36956F.PDF | ELECTRIC UTILITY SERVICES |  | SIMPLE CYCLE, NATURAL GAS FIRED COMBUSTION TURBINES | 15.11 | NATURAL GAS | 80 | MW |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 5 | LB/H | EACH TURBINE | BACT-PSD |  | N | 0 |  | 0.5 | TON/12 CONSEC. MONTH | COMPLIANCE DETERMINED END OF EACH MONTH | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: ONLY TWO TURBINES WILL OPERATE DURING LOW LOAD OPERATION.
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 2 COMBUSTION TURBINES | 15.11 | NATURAL GAS | 130 | MW | TWO GENERAL ELECTRIC (GE) FRAME 7EA COMBUSTION TURBINES (CTS) WITH A NOMINAL NET 87.2 MEGAWATT (MW) RATED CAPACITY, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), EQUIPPED WITH DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION SYSTEM (SCR), AND OXIDATION CATALYST | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF FACILITY PROCESS FUEL GAS OR PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.0033 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0076 | PSEG FOSSIL LLC KEARNY GENERATING STATION | PSEG FOSSIL LLC | HUDSON | NJ | 7032 | USA |  |  |  | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | a. Aliya Khan, Permit evaluator, Aliya.Khan@dep.state.nj.us b. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS - yogesh.doshi@dep.state.nj.us- Phone Number 609-633-7249 | 12200-BOP100002 | 4911 | 221112 | 110043394396 | 08/03/2010 &nbsp;ACT | 10/27/2010 &nbsp;ACT | 2011-08-08 | 2011-09-07 | B |  | PSEG FOSSIL LLC KEARNY GENERATING STATION IS AN EXISTING ELECTRICITY GENERATING STATION. | This project consists of six new identical General Electric LM6000 sprint simple cycle combustion turbines burning natural gas. Each turbine will have a heat input rate of 485 million British thermal units per hour (MMBtu/hr) based on the high heating value of fuel (HHV). The combined maximum electricity generated by the six turbines will be 294 MW based on 2,978 hours of operation per turbine per year. All six new turbines will have water injection along with Selective Catalytic Reduction (SCR) systems to reduce Nitrogen Oxide (NOx) emissions and an oxidation catalyst to reduce Carbon Monoxide (CO) emissions | SIMPLE CYCLE TURBINE | 15.11 | Natural Gas | 8940000 | MMBtu/year (HHV) | Throughput <= 8.94xE6 MMBtu/year (HHV) combined for all six gas turbines. The 6 turbines are identical LM6000 simple cycle combustion turbines. | Particulate matter, filterable (FPM) | Other - New Jersey Air test method 1 | (Particulate Matter (PM)) | PM | P | Good combustion practice, Use of Clean Burning Fuel: Natural gas | 6 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110000801614 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine with Duct Burner firing natural gas | 15.11 | Natural Gas | 0 |  |  | Particulate matter, filterable (FPM) | Other - NJ Test Method | (Particulate Matter (PM)) | PM | P | Use of clean burning fuel like natural gas | 12 | LB/H | AV OF THREE ONE H STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110000801614 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine without Duct Burner Firing Natural Gas | 15.11 | Natural Gas | 28169501 | MMBTU/YR | Natural Gas Usage: <=28,169,501 MMBtu/year which includes maximum ultra low sulfur distillate oil usage of =2,371,943 MMBTU/year | Particulate matter, filterable (FPM) | Other - NJ TEST METHOD | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 4.7 | LB/H | AV OF THREE ONE H STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0103 | CRICKET VALLEY ENERGY CENTER | CRICKET VALLEY ENERGY CENTER LLC | USA | NY | 12522-0407 | USA |  | 845-877-0596 | INFO@CRICKETVALLEY.COM | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-1326-00275/00009 | 4911 | 221112 | 110043340364 | 02/03/2016 &nbsp;ACT | 02/03/2016 &nbsp;ACT | 2017-08-24 | 2017-09-28 | A | http://www.dec.ny.gov/chemical/32249.html | Cricket Valley Energy Center LLC (CVEC) constructed the Cricket Valley Energy Center (the Facility), a nominal net 1,000-megawatt (MW) combined-cycle gas turbine electric generating facility, on a site located in Dover, Dutchess County, New York. The Facility consists of three General Electric (GE) Model 7FA.05 combustion turbine generators (CTGs) operating in combined-cycle mode with supplemental firing of the heat recovery steam generators (HRSGs); natural gas will be the sole fuel fired in the CTGs and duct burners. The Facility will include a natural gas-fired auxiliary boiler, four ultra-low sulfur distillate (ULSD) fired black-start generator engines and a ULSD-fired emergency fire pump engine. In addition to the air emitting equipment, the Facility will include three steam turbine generators (STGs), an air cooled condenser (ACC) and associated auxiliary equipment and systems. Each combined cycle generating unit consisting of the CTG, HRSG and STG will be exhausted through its own stack. Air emissions from the proposed Facility primarily consist of products of combustion from the CTGs, HRSG duct burners, and ancillary combustion sources. Dutchess County is designated as in attainment with respect to the National Ambient Air Quality Standards (NAAQS) for all criteria pollutants with the exception of ozone. Based upon the potential to emit (PTE) estimates, the Facility is subject to Prevention of Significant Deterioration (PSD) requirements for emissions of carbon monoxide (CO); nitrogen oxides (NOx); particulate matter (PM) with a diameter equal to or less than 10 microns (PM10), PM with a diameter equal to or less than 2.5 microns (PM2.5); greenhouse gases (GHG); sulfuric acid mist (H2SO4); and volatile organic compounds (VOC). In accordance with the NYSDECâ€™s Nonattainment New Source Review (NNSR) permitting program, the Facility is also subject to NNSR for emissions of NOx and VOC. |  | Turbines and duct burners | 15.11 | natural gas | 228 | mw |  | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | good combustion practiced and pipeline quality natural gas | 0.005 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Also for PM-10 EPA Method 201/201A or 202 0.005 lb/mmBtu without duct firing 0.006 lb/mmBtu with duct firing Applies to all operating loads, except during startup and shutdown.
NY-0106 | GREENIDGE STATION | GREENIDGE GENERATION LLC | YATES | NY | 14441-0187 | USA |  | 315-536-2359 |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov |  | 8-5736-00004/00017 | 4911 | 221112 | 110000327619 | 09/07/2016 &nbsp;ACT | 09/07/2016 &nbsp;ACT | 2017-08-30 | 2017-09-28 | C | http://www.dec.ny.gov/chemical/32249.html | Greenidge Generation LLC has submitted a revised application for a Title V Air Permit in accordance with the requirements of Title 6 of the New York compilation of Codes, Rules, and Regulations, Part 201-6 (6 NYCRR Part 201-6). The application is for conversion of the Greenidge Electricity Generating Station, located in the Town of Torrey, Yates County to operate primarily on natural gas with up to 19% biomass co-firing. Greenidge Station is comprised of Unit 4, which includes a Combustion Engineering, tangentially-fired dry bottom boiler (Boiler No. 6) with a maximum heat input rating of 1,117 MMBtu/hr, and a steam generating turbine with a maximum rated output of 107 Megawatts (MW) of electricity. The facility is equipped with a suite of air pollution control (both pre-combustion and post-combustion) systems to control pollutant nitrogen oxides, carbon monoxide, and particulate matter (PM, PM10 and PM2.5) emissions from facility operations. Greenhouse gases will be reduced substantially primarily by the use of cleaner fuels. Under the proposal, Unit 4 will not burn coal or fuel oil any longer. | Also NAICS 221117 - biomass with wood | Turbine - natural gas | 15.11 | natural gas | 107 | MW |  | Particulate matter, filterable (FPM) | Other - 40 CFR 60 App A M-5 | (Particulate Matter (PM)) | PM | A | Baghouse with leak detection system. | 0.002 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0113 | EDGEWOOD ENERGY LLC | EDGEWOOD ENERGY LLC | SUFFOLK | NY | 11717 | USA |  | 631-643-1560 |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 1 631-444-0200 | 1-4728-03244/00005 | 4911 | 221112 | 110038105993 | 07/09/2013 &nbsp;ACT | 07/09/2013 &nbsp;ACT | 2017-09-14 | 2017-09-28 | C | http://www.dec.ny.gov/chemical/32249.html | Edgewood Energy LLC is a power is a simple cycle combustion turbine plant located in Edgewood, Suffolk County, New York that contains two GE LM6000 combustion turbines that fire only natural gas. The facility has an optimum electrical output of 95 megawatts (MW) firing only natural gas. This electrical output represents an increase from the 79.9 MW limit. This increase was allowed through a declaratory ruling that the Department of Public Service issued. The facility is subject to PSD for greenhouse gases (GHGs) and PM-10 emissions. The facility is not subject to non-attainment NSR for any non-attainment contaminant. |  | Turbines - NG | 15.11 | natural gas | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0112 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0333 | DAYTON POWER & LIGHT ENERGY LLC | DAYTON POWER & LIGHT COMPANY | MONTGOMERY | OH | 45439 | USA | CARRIE BURKS | 937-331-3042 |  | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104867 | 4911 | 221112 | 110000394145 | 04/30/2009 &nbsp;ACT | 12/03/2009 &nbsp;ACT | 2010-05-13 | 2010-05-20 | C |  | Seven simple cycle stationary combustion turbines all with rating of 80 MW and nominal heat input of 1115.2 mmBtu/hr using natural gas or No. 2 fuel oil and all with water injection control and last 5 also with low NOx burners. | Simple cycle stationary combution turbines issed in 2 different permits. Four turbines in this permit with dry low NOx combustion and water injection controls. Administrative Modification to original PTI #08-04153 issued 8/7/01, to incorporate low mass emissions methodology as allowed per 40 CFR 75.19 in lieu of methods under Appendix D or E to Part 75, by meeting the requirements of having mass emissions of less than 25 T/YR SO2 and less than 100 T/YR NOx (per turbine) based on 3 years of operation. Modification also reduced permitted formaldehyde emissions by 8.7 tons, recalculated based on the restriction on hours of operation. | Turbines (4), simple cycle, natural gas | 15.11 | NATURAL GAS | 15020 | H/YR | Hours per year for all 4 turbines | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | N |  | 0.013 | LB/MMBTU | ACTUAL HEAT INPUT | BACT-PSD | SIP | U | 0 | Y | 46.12 | T/YR | PER ROLLING 12-MO. FOR 4 UNITS &ALL FUEL | 0.013 | LB/MMBTU | ACTUAL HEAT INPUT | 0 | 0 | N |  | The emission factor for PM was used as a surrogate for PM10 and PM2.5 where there were no other emission factors available. T/YR limit is for both fuels and for the 4 turbines combined. BACT: using only clean fuels, natural gas or #2 fuel oil.
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustion practices. | 11.81 | TON/YR |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
CA-1223 | PIO PICO ENERGY CENTER | PIO PICO ENERGY CENTER, LLC | OTAY MESA | CA | 92154 | USA | GARY CHANDLER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SD 11-01 | 4911 | 221112 | 110045006943 | 06/14/2012 &nbsp;ACT | 11/19/2012 &nbsp;ACT | 2013-03-05 | 2014-01-28 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | CONSTRUCTION OF THREE GENERAL ELECTRIC (GE) LMS100 NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 100 MW EACH. THE PROJECT WILL HAVE AN ELECTRICAL OUTPUT OF 300 MW. | NOTE: PERMIT ISSUED 11/19/2012. ENVIRONMENTAL APPEALS BOARD REMANDED THE PM BACT ANALYSIS TO REGION 9 ON 8/2/2013. FINAL PERMIT ISSUED ON 2/28/2014. ONE PETITION FILED IN 9TH CIRCUIT FEDERAL COURT CHALLENGING THE FINAL PERMIT DECISION. THIS LAWSUIT WAS DISMISSED ON 6/17/2014 IN RESPONSE TO PETITIONERSâ€™ MOTION FOR VOLUNTARY DISMISSAL. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.11 | NATURAL GAS | 300 | MW | Three simple cycle combustion turbine generators (CTG). Each CTG rated at 100 MW (nominal net). | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA METHOD 5 & 202, OR CTM 039 | (Particulate Matter (PM)) | PM | P | PUC-QUALITY NATURAL GAS | 0.0065 | LB/MMBTU (HHV) | AT LOADS OF 80% OR HIGHER | BACT-PSD |  | U | 0 | U | 5.5 | LB/H |  | 0 |  |  | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055426409 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Three simple cycle combustion turbines | 15.11 | natural gas | 799.7 | MMBTU/H | Three GE, LMS100PA, natural gas-fired, simple cycle CTG rated at 799.7 MMBtu per hour each,based on HHV. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustor design | 6.6 | LB/H | AVE OVER STACK TEST LENGTH | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CO-0075 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO |  | USA | MARK LUX | 303-568-3241 | MARK.LUX@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 13PB2245 | 4911 | 221112 | 110058377830 | 09/10/2013 &nbsp;ACT | 05/30/2014 &nbsp;ACT | 2014-10-24 | 2016-02-19 | B |  | Power generation facility |  | Turbine - simple cycle gas | 15.11 | natural gas | 375 | MMBTU/H | One (1) General Electric, simple cycle, gas turbine electric generator, Unit 6 (CT08), model: LM6000, SN: N/A, rated at 375 MMBtu per hour. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Firing of pipeline quality natural gas as defined in 40 CFR Part 72. Specifically, the owner or the operator shall demonstrate that the natural gas burned has total sulfur content less than 0.5 grains/100 SCF. | 4.8 | LB/H | 3-HR AVE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0305 | OUC CURTIS H. STANTON ENERGY CENTER | ORLANDO UTILITIES COMMISSION (OUC) | ORLANDO | FL | 32831 | USA | DENISE M. STALLS | 4077374236 | DSTALLS@OUC.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | ALVARO LINERO, P.E. SPECIAL PROJECT ADMINISTRATOR BUREAU OF AIR REGULATION | PSD-FL-373A AND 0950137-020-AC | 4911 | 221112 | UNKNOWN | 03/04/2008 &nbsp;ACT | 05/12/2008 &nbsp;ACT | 2009-02-20 | 2009-08-31 | B |  | THE EXISTING FACILITY CONSISTS OF TWO 468 MW FOSSIL FUEL FIRED STEAM ELECTRIC GENERATING UNITS (UNITS 1 AND 2), AND ONE 640 MW NGCC UNIT (UNIT A). THERE ARE STORAGE AND HANDLING FACILITIES FOR SOLID FUELS, FLY ASH, LIMESTONE, GYPSUM, SLAG, AND BOTTOM ASH. NEW PROJECT ADDS UNIT B, A 300 MW COMBINED CYCLE COMBUSTION TURBINE AND ASSOCIATED EQUIPMENT. | THE NEW PROJECT IS TO CONSTRUCT A Â¿ONE-ON-ONEÂ¿ F-CLASS NGCC UNIT (STANTON UNIT B) AND ASSOCIATED AUXILIARY EQUIPMENT. UNIT B WILL CONSIST OF: ONE NOMINAL 150 MEGAWATTS (MW) GENERAL ELECTRIC 7241 FA COMBUSTION TURBINE-ELECTRICAL GENERATOR (CTG); A SUPPLEMENTARY FIRED HEAT RECOVERY STEAM GENERATOR (HRSG) WITH NATURAL GAS FUELED DUCT BURNERS; AND A NOMINAL 150 MW STEAM TURBINE GENERATOR (STG) FOR AN OVERALL NOMINAL RATING OF 300 MW. THE PROJECT INCLUDES HIGHLY AUTOMATED CONTROLS, DESCRIBED AS THE GE MARK VI GAS TURBINE CONTROL SYSTEM TO FULFILL ALL OF THE GAS TURBINE CONTROL REQUIREMENTS. UNIT B WILL FIRE NATURAL GAS AS THE PRIMARY FUEL, AND ULTRALOW SULFUR DIESEL (ULSD) FUEL OIL SERVING AS A BACKUP FUEL. | 300 MW COMBINED CYCLE COMBUSTION TURBINE | 15.11 | NATURAL GAS | 1765 | MMBTU/H | FOR ULTRA LOW SULFUR (0.0015% SULFUR BY WEIGHT) FUEL OIL IS 1935 MMBTU/H. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - Visible emissions Method 9 | (Particulate Matter (PM)) | PM | P | NATURAL GAS AN ULTRA LOW SULFUR FUEL OIL | 2 | GR S/100 DSCF OF GAS |  | BACT-PSD |  | U | 0 | U | 0.0015 | % SULFUR OIL |  | 0 |  |  | 0 | 0 | N |  | THE SULFUR FUEL SPECIFICATIONS COMBINED WITH THE EFFICIENT COMBUSTION DESIGN AND OPERATION OF THE GAS TURBINE REPRESENTS (BACT) FOR PM/PM10/PM2.5 EMISSIONS. COMPLIANCE WITH THE FUEL SPECIFICATIONS, CO STANDARDS, AND VISIBLE EMISSIONS STANDARDS SHALL SERVE AS INDICATORS OF GOOD COMBUSTION. COMPLIANCE WITH THE FUEL SPECIFICATIONS SHALL BE DEMONSTRATED BY KEEPING RECORDS OF THE FUEL SULFUR CONTENT AS DETAILED IN SPECIFIC CONDITION 30 OF PERMIT (PSD-FL-373A). COMPLIANCE WITH THE VISIBLE EMISSIONS STANDARD SHALL BE DEMONSTRATED BY CONDUCTING TESTS IN ACCORDANCE WITH EPA METHOD 9.
FL-0310 | SHADY HILLS GENERATING STATION | SHADY HILLS POWER COMPANY | PASCO | FL | 6927 | USA | ROY S. BELDEN | 2033576820 | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | SYED ARIF, PROJECT ENGINEER PHONE 850/ 921-9528 SYED.ARIF@DEP.STATE.FL.US TERESA HERON PHONE 850/921-9529 TERESA.HERON@DEP.STATE.FL.US | PSD-FL-402 | 4911 | 221122 | 1210100373 | 05/13/2008 &nbsp;ACT | 01/12/2009 &nbsp;ACT | 2009-07-29 | 2010-01-26 | B |  | THIS FACILITY CONSISTS OF THREE, DUAL-FUEL, NOMINAL 170 MW GENERAL ELECTRIC MODEL PG7241FA (GE 7FA) SIMPLE CYCLE COMBUSTION TURBINES-ELECTRICAL GENERATORS, THREE EXHAUST STACKS THAT ARE 18 FEET IN DIAMETER AND 75 FEET TALL, AND ONE 2.8-MILLION GALLON DISTILLATE FUEL OIL STORAGE TANK. THE COMBUSTION TURBINE UNITS CAN OPERATE IN SIMPLE-CYCLE MODE AND INTERMITTENT DUTY MODE. THE UNITS ARE EQUIPPED WITH DRY LOW-NITROGEN OXIDES (NOX) COMBUSTORS AND WATER INJECTION CAPABILITY. THE THREE COMBUSTION TURBINES ARE REGULATED UNDER PHASE II OF THE FEDERAL ACID RAIN PROGRAM. THIS FACILITY OPERATES DURING PEAK HOURS OF ELECTRICAL USE. |  | TWO SIMPLE CYCLE COMBUSTION TURBINE - MODEL 7FA | 15.11 | NATURAL GAS | 170 | MW | BACKUP FUEL: ULTRA LOW SULFUR DIESEL WITH A MAXIMUM SULFUR CONTENT OF 0.0015%, BY WEIGHT | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 10 | % OPACITY | 6-MINUTE BLOCK BY EPA METHOD 9 | BACT-PSD |  | U | 0 | U | 2 | GR S/100 SCF NG | NA/ RECORDING COMPLIANCE | 0.0015 | S BY WEIGHT | NA/ RECORDING COMPLIANCE | 0 | 0 | N |  | THE SULFUR FUEL SPECIFICTIONS COMBINED WITH THE EFFICIENT COMBUSTION DESIGN AND OPERATION OF THE CT WILL MINIMIZE PM/PM10 EMISSIONS. COMPLIANCE WITH THE FUEL SPECIFICATION, CO STANDARDS, AND VISIBLE EMISSIONS STANDARDS SHALL SERVE AS INDICATORS OF GOOD COMBUSTION.
FL-0319 | GREENLAND ENERGY CENTER | JACKSONVILLE ELECTRIC AUTHORITY (JEA) | DUVAL | FL | 32258 | USA | N. BERT GIANAZZA | 904-665-6247 | GIANNB@JEA.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Syed Arif Project Manager 850-921-9580 Jeff Koerner, P.E. Administrator Phone 850-921-9536 | PSD-FL-401 | 4911 | 221112 | UNKNOWN | 04/21/2008 &nbsp;ACT | 03/10/2009 &nbsp;ACT | 2010-09-23 | 2011-12-01 | A |  | The proposed facility is a new electric-generating facility referred to as Greenfield Energy Center (GEC). GEC will be built in two phases. The initial phase will be the construction of two natural gas-fired simple cycle combustion turbine (CT) units that are proposed to be operational June 2011. The second phase will convert these simple cycle units to a combined cycle combustion turbine (â€œ2-on 1â€ configuration). Heat recovery equipment will be installed on the two simple cycle combustion turbines to capture enough heat energy to run a steam turbine (ST). This phase is proposed to be operational by June 2013. | Each combustion turbine shall not operate more than 3,500 hours during any consecutive 12 months of which 500 hours may be on ULSFO. Each combustion turbine shall not operate more than 17 hours exclusively on ULSFO per calendar day, or with a combination of ULSFO burning of 12 hours with 12 hours of natural gas for compliance with regional haze impact thresholds. | 190 MW Combustion Turbine | 15.11 | ULSO | 30213 | GAL/YR | Capacity: 1806 MMBtu/H, natural gas Capacity: 1994 MMBtu/H, fuel oil Authorized Fuels (Pre-onsite natural gas availability): Each combustion turbine shall fire ULSFO which shall contain no more than 0.0015% sulfur by weight as the primary fuel until natural gas is available at the facility. If natural gas is not available by June 1, 2011, the permittee shall submit to the Department and EQD semi-annual status reports on the availability of natural gas to the facility. The first status report shall be submitted by June 1, 2011. The status reports shall be submitted until natural gas is available at the facility. Authorized Fuels (Post-onsite natural gas availability): Each combustion turbine shall fire natural gas as the primary fuel, which shall contain no more than 2 grains of sulfur per 100 standard cubic feet of natural gas. As a restricted alternate fuel, the combustion turbine may fire ULSFO containing no more than 0.0015% sulfur by weight. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - Fuel Analysis | (Particulate Matter (PM)) | PM | P | Use of low ash, low sulfur fuels, | 10 | OPACITY | 6 MINUTES BLOCK/VE TEST | BACT-PSD |  | U | 0 | U | 2 | GR S/100 SCF GAS | RECORD KEEPING | 0 |  |  | 0 | 0 | N |  | The sulfur fuel specification combined with the efficient combustion design and operation of the gas turbine represents BACT for PM/PM10 emissions. Compliance with the fuel specifications, CO standards, and visible emissions standards shall serve as indicators of good combustion. Compliance with the fuel specifications shall be demonstrated by keeping records of the fuel sulfur content. Compliance with the visible emissions standard shall be demonstrated by conducting tests in accordance with EPA Method 9.
FL-0354 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-013-AC | 4911 | 221112 | 110002044065 | 04/20/2015 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2016-02-17 | 2016-07-06 | D | https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | Re-affirmed BACT determinations in Permit No. 0110037-011-AC. Also, new GHG BACT determination. Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2100 | MMBtu/hr (approx) | Five simple cycle GE 7F.05 turbines. Max of 3390 hours per year per turbine. Of the 3390 hours per year, up to 500 hour may be on ULSD fuel oil. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - Use of low-S nat gas or ULSD | (Particulate Matter (PM)) | PM | P | Clean fuel prevents PM formation | 2 | GR. S / 100 SCF | FUEL RECORD KEEPING | BACT-PSD | SIP | U | 0 | U | 0.0015 | % S IN ULSD | FUEL RECORD KEEPING | 0 |  |  | 0 | 0 | N |  | Use of clean fuels prevents formation of particulate matter. Also, 10% VE limit with annual VE test is a proxy for PM.
FL-0355 | FORT MYERS PLANT | FLORIDA POWER & LIGHT (FPL) | LEE | FL | 33905 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0710002-022-AC | 4911 | 221112 | 110000365248 | 05/12/2015 &nbsp;ACT | 09/10/2015 &nbsp;ACT | 2016-03-10 | 2016-07-06 | D | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.80831.1]&[profile=Permitting_Authorization] | Electric power plant, consists of a 6-on-2 combined-cycle unit (Units 2A through 2F) and two modern simple-cycle combustion turbines. Primary fuel is natural gas. Also includes 12 gas turbines (63 MW each) for peaking, introduced into service in 1974. This project entails decommissioning 10 of the 12 peaking turbines. They will be replaced with two new GE 7F.05 turbines, each with nominal capacity of 200 MW | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0710002.022.AC.D.ZIP | Combustion Turbines | 15.11 | Natural gas | 2262.4 | MMBtu/hr gas | Two GE 7F.05 turbines, approximately 200 MW each. Natural-gas is primary fuel. Permitted 3390 hr/yr of operation, of which no more than 500 hr may be on fuel oil. Dry Low-NOx, with wet injection for oil firing. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - No test required | (Particulate Matter (PM)) | PM | P | Use of clean fuels | 2 | GR S / 100 SCF GAS | FOR NATURAL GAS | BACT-PSD |  | U | 0 | U | 0.0015 | % S IN ULSD | FOR ULSD | 0 |  |  | 0 | 0 | N |  | Clean fuels prevent PM formation. No PM testing required. Annual test for visible emissions.
GA-0139 | DAHLBERG COMBUSDTION TURBINE ELECTRIC GENERATING FACILITY (P | SOUTHERN POWER COMPANY | JACKSON | GA | 30565 | USA | MR. E.S. (SCOTT) DIAL | 704 278-6601 | ESDIAL@SOUTHERNCO.COM | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-157-0034-V-04-1 | 4911 | 221112 | UNKNOWN | 07/10/2008 &nbsp;ACT | 05/14/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | C |  | PLANT DAHLBERG HAS PROPOSED TO CONSTRUCT AND OPERATE FOUR ADDITIONAL SIMPLE-CYCLE COMBUSTION TURBINES (SOURCE CODES: CT11-CT14) AND ONE FUEL OIL STORAGE TANK. THE PROPOSED PROJECT WILL HAVE A NOMINAL GENERATING CAPACITY OF 760 MW. THE FACILITY IS CURRENTLY PERMITTED TO OPERATE 10 DUAL-FUELED SIMPLE-CYCLE CTG's. AFTER THE EXPANSION, THE FACILITY WILL HAVE A TOTAL NOMINAL GENERATING CAPACITY OF 1530 MW. |  | SIMPLE CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.11 | NATURAL GASE | 1530 | MW | THE PROCESS USES FUEL OIL FOR BACKUP AT THE RATE OF 2129 MMBUT/H | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | GOOD COMBUSTION PRACTICES PIPELINE QUALITY NATURAL GAS, ULTRA LOW SULFUR DISTILLATE FUEL | 9.1 | LB/H | 3 HOUR AVERAGE/CONDITION 3.3.23 | BACT-PSD | OPERATING PERMIT | U | 0 | N | 69 | LB/H | 3 HOUR AVERAGE/CONDITION 3.3.28 | 0 |  |  | 0 | 0 | N
IL-0121 | INVENERGY NELSON EXPANSION LLC | INVENERGY | LEE | IL | 61058 | USA | GORDON GRAY | 312-582-1290 | GGRAY@INVENERGY.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Bob Smet; 217-785-9250; robert.smet@illinois.gov | 15060042 | 4911 | 221112 | Not Found | 07/28/2016 &nbsp;ACT | 09/27/2016 &nbsp;ACT | 2017-01-27 | 2017-04-28 | B | https://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/9dbc452815081576862580b2006897b4/$FILE/ATT4AK5N.pdf/15060042.pdf | Peaking facility at an existing major source. The expansion will consist of two simple cycle combustion turbines and a fuel heater. |  | Two Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 190 | MW | Two simple cycle combustion turbines used for peaking purposes and fired primarily on natural gas with ULSD as a secondary fuel. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | turbine design and good combustion practices | 0.005 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0.02 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission 1 (natural gas): 0.0050 lb/mmbtu* Emission 2 (ULSD): 0.020 lb/mmbtu* *During an hour that includes a startup, the particulate emissions of the turbine shall not exceed 10.0 lb/hr (natural gas) and 42.7 lb/hr (ULSD).
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER | 15.11 | NATURAL GAS | 92.5 | MMBTU/H | NATURAL GAS USAGE SHALL NOT EXCEED 18.14 MMCF/YEAR. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN, USE NATURAL GAS | 7.6 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER | 15.11 | NATURAL GAS | 92.5 | MMBTU/H | NATURAL GAS USAGE SHALL NOT EXCEED 18.14 MMCF/YEAR. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN, USE NATURAL GAS | 7.6 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE LM6000PC SPRINT Simple cycle combustion turbine | 15.11 | Pipeline quality natural gas | 405.3 | MMBTU/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | fire only pipeline quality natural gas | 6 | LB/HR | AT FULL OAD | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE 7FA Simple Cycle Combustion Turbine | 15.11 | Pipeline quality natural gas | 1780 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | will fire only pipeline quality natural gas | 18 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KY-0104 | CASH CREEK GENERATING STATION | CASH CREEK GENERATION, L.L.C | HENDERSON | KY | 41047 | USA | MIKE MCINNUS | 502 357 9907 | MMCINNIS@ERORA.COM | 4 | KY001 | KENTUCKY DEP, DIV FOR AIR QUALITY | MR. RICK SHEWEKAH, MGR | (502)564-3999 | Sreenivas.Kesaraju@ky.gov |  | V-14-011 | 4911 | 221112 | 110042328479 | 06/18/2014 &nbsp;ACT | 06/10/2015 &nbsp;ACT | 2017-02-28 | 2017-04-28 | A |  | natural gas fired combined cycle power plant |  | Combined cycle combustion turnbine with HRSG and duct firing | 15.11 | Natural gas pipeline quality | 849 | MW | Two CT with HRSGs with duct burner Max fuel input for CTs and HRSGs 6,714 mmBtu/hr HHV Max Gross output 849 MW at 0F | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Combust only pipeline quality natural gas | 0.0088 | LB.MMBTU | THREE(3) HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0258 | CALCASIEU PLANT | ENTERGY GULF STATES LA LLC | CALCASIEU | LA | 70665 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: TEGAN TREADAWAY, (225) 219-3408 | PSD-LA-746 | 4911 | 221112 | 110007042565 | 11/10/2009 &nbsp;ACT | 12/21/2011 &nbsp;ACT | 2012-02-01 | 2012-04-03 | C |  | 320 MW POWER PLANT COMPRISED OF 2 NATURAL GAS-FIRED SIMPLE CYCLE COMBUSTION TURBINES. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS PSD TRIGGERED DUE TO RELAXATION OF A FEDERALLY-ENFORCEABLE CONDITION LIMITING POTENTIAL EMISSIONS BELOW MAJOR STATIONARY SOURCE THRESHOLDS. | TURBINE EXHAUST STACK NO. 1 &amp; NO. 2 | 15.11 | NATURAL GAS | 1900 | MM BTU/H EACH |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE NATURAL GAS | 17 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 17 | LB/H | HOURLY MAXIMUM / STARTUP & SHUTDOWN ONLY | 0 |  |  | 0 | 0 | N |  | LIMITS ARE PER TURBINE EXHAUST STACK. AGGREGATE PM10 EMISSIONS FROM BOTH TURBINE EXHAUST STACKS ARE LIMITED TO 30.94 TONS PER YEAR. STARTUP & SHUTDOWN OPERATIONS ARE LIMITED TO 520 HOURS PER YEAR.
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Gas Turbines (8 units) | 15.11 | natural gas | 333 | mm btu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and fueled by natural gas | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110029511883 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and fueled by natural gas | 0.0076 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0043 | PERRYMAN GENERATING STATION | CONSTELLATION POWER SOURCE GENERATION, INC. | HARFORD | MD | 21130 | USA | BILL LEEDY | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9136 | 4911 | 221119 | 110000499559 | 07/01/2014 &nbsp;ACT | 07/01/2014 &nbsp;ACT | 2015-07-31 | 2016-07-25 | B |  | 120 MEGAWATT SIMPLE CYCLE NATURAL GAS FIRED POWER PLANTPERRYMAN 6 PROJECT-WIDE EMISSION LIMITS: PM10 = 43.0 TONS/YR PM2.5 = 43.0 TONS/YR NOX = 58.5 TONS/YR CO2E = 430,210 TONS/YR | PERRYMAN 6 PROJECT-WIDE EMISSION LIMITS: PM10 = 43.0 TONS/YR PM2.5 = 43.0 TONS/YR NOX = 58.5 TONS/YR CO2E = 430,210 TONS/YR | (2) 60-MW SIMPLE CYCLE COMBUSTION TURBINES, FIRING NATURAL GAS | 15.11 | NATURAL GAS | 120 | MW | (2) 60-MEGAWATT PRATT & WHITNEY GAS TURBINE GENERATOR PACKAGE | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND USE OF NATURAL GAS | 5 | LB/H | 3 STACK TEST RUNS | BACT-PSD |  |  | 0 |  | 0.0079 | LB/MMBTU | HIGH HEAT VALUE (HHV) | 0 |  |  | 0 | 0 | N
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 2 COMBUSTION TURBINES | 15.11 | NATURAL GAS | 130 | MW | TWO GENERAL ELECTRIC (GE) FRAME 7EA COMBUSTION TURBINES (CTS) WITH A NOMINAL NET 87.2 MEGAWATT (MW) RATED CAPACITY, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), EQUIPPED WITH DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION SYSTEM (SCR), AND OXIDATION CATALYST | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF FACILITY PROCESS FUEL GAS OR PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.007 | LB/MMBTU | 3 STACK TEST RUN AVERAGE, EXCEPT SU/SD | BACT-PSD |  |  | 0 |  | 300.8 | LB/EVENT | FOR ALL STARTUPS | 0 |  |  | 0 | 0 | N |  | 5.6 LBS/SHUTDOWN EVENT. LIMITS ARE TOTAL FOR BOTH FRAME 7 CTS PER STARTUP OR SHUTDOWN EVENT.
ND-0028 | R.M. HESKETT STATION | MONTANA-DAKOTA UTILITIES CO. | MORTON | ND | 58554 | USA | ABBIE KREBSBACH | (701) 222-7844 | ABBIE.KREBSBACH@MDU.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Primary contact is Tom Bachman at (701) 328-5188. | PTC13016 | 4911 | 221112 | 110022356591 | 11/07/2012 &nbsp;ACT | 02/22/2013 &nbsp;ACT | 2013-04-01 | 2017-04-28 | B |  | Addition of a natural gas-fired turbine (Unit 3) to an exisiting coal-fired power plant. The turbine will be used for supplying peak power and is rated at 986 MMBtu/hr and 88 MWe at average site conditions. |  | Combustion Turbine | 15.11 | Natural gas | 986 | MMBTU/H | Turbine is a GE Model PG 7121 (7EA) used as a peaking unit. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 7.3 | LB/H | AVERAGE OF 3 TEST RUNS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0076 | PSEG FOSSIL LLC KEARNY GENERATING STATION | PSEG FOSSIL LLC | HUDSON | NJ | 7032 | USA |  |  |  | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | a. Aliya Khan, Permit evaluator, Aliya.Khan@dep.state.nj.us b. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS - yogesh.doshi@dep.state.nj.us- Phone Number 609-633-7249 | 12200-BOP100002 | 4911 | 221112 | 110043394396 | 08/03/2010 &nbsp;ACT | 10/27/2010 &nbsp;ACT | 2011-08-08 | 2011-09-07 | B |  | PSEG FOSSIL LLC KEARNY GENERATING STATION IS AN EXISTING ELECTRICITY GENERATING STATION. | This project consists of six new identical General Electric LM6000 sprint simple cycle combustion turbines burning natural gas. Each turbine will have a heat input rate of 485 million British thermal units per hour (MMBtu/hr) based on the high heating value of fuel (HHV). The combined maximum electricity generated by the six turbines will be 294 MW based on 2,978 hours of operation per turbine per year. All six new turbines will have water injection along with Selective Catalytic Reduction (SCR) systems to reduce Nitrogen Oxide (NOx) emissions and an oxidation catalyst to reduce Carbon Monoxide (CO) emissions | SIMPLE CYCLE TURBINE | 15.11 | Natural Gas | 8940000 | MMBtu/year (HHV) | Throughput <= 8.94xE6 MMBtu/year (HHV) combined for all six gas turbines. The 6 turbines are identical LM6000 simple cycle combustion turbines. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practice, Use of Clean Burning Fuel: Natural gas | 6 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110000801614 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine with Duct Burner firing natural gas | 15.11 | Natural Gas | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 22.6 | LB/H | AV OF THREE ONE H STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110000801614 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine without Duct Burner Firing Natural Gas | 15.11 | Natural Gas | 28169501 | MMBTU/YR | Natural Gas Usage: <=28,169,501 MMBtu/year which includes maximum ultra low sulfur distillate oil usage of =2,371,943 MMBTU/year | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 14.4 | LB/H | AV OF THREE ONE H STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | GE LMS-100 combustion turbines, simple cycle with water injection | 15.11 | natural gas | 1690 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Utilize only natural gas or ULSD fuel; Limit the time in startup or shutdown. | 9.1 | LB/H TOTAL PM | 6-HR AVERAGE ON NG | BACT-PSD |  | U | 0 | U | 22.7 | LB/H TOTAL PM | 6-HR AVERAGE ON ULSD | 0 |  |  | 0 | 0 | N
*PA-0305 | SHELL CHEM APPALACHIA/PETROCHEMICALS COMPLEX | SHELL CHEMICAL APPALACHIA | BEAVER | PA | 15061-2210 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 04-00740A | 2821 | 325110 | 110060029115 | 05/01/2014 &nbsp;ACT | 06/18/2015 &nbsp;ACT | 2017-06-05 | 2017-07-12 | A |  | The plan approval will allow the construction and temporary operation of seven (7) 620 MMBtu/hr ethane cracking furnaces fired primarily by tail gas and natural gas for the production of approximately 1.5 million metric tons/year of polyethylene. Byproducts from the ethylene production include coke residue/tar, light gasoline, pyrolysis fuel oil, and a C3+ mixture and will be remove from the site for disposal or use as appropriate. Additional facilities include an electric and steam cogeneration from three (3) combustion turbines with duct burners and heat recovery steam generators with a plant capacity of 250.4 MW, four (4) emergency generators, three (3) diesel-fired fire pump engines, cooling towers, flares, and storage tanks. | (7) 620.000 MMBtu/hr Ethane cracking furnaces, (3) 664.000 combustion turbines with duct burners. Shell intends to convert ethane in to ethylene for manufacturing of various grades of low density and high density polyethylene as a final product. | Combustion turbine wih duct burner and heat recovery steam generator | 15.11 | Natural Gas | 0 | Three 40.6 MW turbines | Three (3) General Electric Frame 6B NG fired turbine with duct burners and heat recovery steam generators. Total electric generating capacity will be 250.4 MW from cogeneration three turbines at 40.6 MW and two HRSG at 64.3 MW. Excess electricity generated will be sold to the grid in quantities sufficient to classify the facility as an electric utility. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0066 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0733 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JOLLY HAYDEN | 806-349-5250 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, (512)239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358M1 | 4911 | 221112 | 110043432737 | 03/20/2015 &nbsp;ACT | 05/12/2015 &nbsp;ACT | 2015-05-04 | 2016-06-08 | B |  | Golden Spread Electric Cooperative, Inc. (GSEC) is requesting authorization for three additional simple cycle electric generating plants at an existing site to meet increased energy demand in the area. The generating equipment consists of three new GE 7F5-Series natural gas-fired combustion turbine generators (CTGs). Each turbine has a maximum electric output of 202 MW. |  | Simple Cycle Turbine &amp; Generator | 15.11 | natural gas | 202 | MW | 3 additional GE 7F 5-Series Combustion Turbine Generators | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices. | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of each turbine is limited to 4,572 hours per year
TX-0764 | NACOGDOCHES POWER ELECTRIC GENERATING PLANT | NACOGDOCHES POWER, LLC | NACOGDOCHES | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem 512-239-1310 Tzvi.shalem@tceq.texas.gov | 77679, PSDTX1061M1 & O-3455 | 4911 | 221112 | 110043814744 | 06/25/2015 &nbsp;ACT | 10/14/2015 &nbsp;ACT | 2015-09-16 | 2016-07-06 | B |  | Nacogdoches Power, LLC is requesting authorization for one natural gas fired, simple cycle combustion turbine generator (CTG). The CTG will be a Siemens F5 and have a nominal electric output of 232 megawatts (MW). |  | Natural Gas Simple Cycle Turbine (&gt;25 MW) | 15.11 | natural gas | 232 | MW | One Siemens F5 simple cycle combustion turbine generator | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices. | 12.09 | LB/HR |  | BACT-PSD |  | N | 0 | U | 12.94 | TPY |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,500 hours on a 12-month rolling average.
TX-0768 | SHAWNEE ENERGY CENTER | SHAWNEE ENERGY CENTER, LLC | HILL | TX |  | USA | NEIL O'DONOVAN | 312-422-1608 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, P.E., 512-239-1353, joseph.janecka@tceq.texas.gov | PSDTX1442, 125963 | 4911 | 221112 | UNKNOWN | 07/31/2015 &nbsp;ACT | 10/09/2015 &nbsp;ACT | 2015-10-05 | 2016-07-06 | A |  | Electric Generating Utility: The project will consist of four gas fired combustion turbines (CTGs). The CTGs are fueled with pipeline quality natural gas and will operate in simple cycle mode. The gas turbines will be one of two options. |  | Simple cycle turbines greater than 25 megawatts (MW) | 15.11 | natural gas | 230 | MW | Siemens Model SGT6-5000 F5ee â€“ 230 MW or Second turbine option: General Electric Model 7FA.05TP â€“ 227 MW | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices. | 84.1 | LB/HR |  | BACT-PSD | NSPS | N | 0 | U | 152.96 | TPY |  | 0 |  |  | 0 | 0 | N
TX-0769 | VAN ALSTYNE ENERGY CENTER (VAEC) | NAVASOTA NORTH COUNTRY PEAKERS OPERATING COMPANY I | GRAYSON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 121051 AND PSDTX1418 | 4911 | 221112 | UNKNOWN | 12/22/2014 &nbsp;ACT | 10/27/2015 &nbsp;ACT | 2015-10-30 | 2016-07-06 | A |  | Navasota North Country Peakers Operating Company I LLC. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 MW each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline Quality Natural Gas | 8.6 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0777 | UNION VALLEY ENERGY CENTER | NAVASOTA SOUTH PEAKERS OPERATING COMPANY I, LLC. | NIXON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 120973 AND PSDTX1420 | 4911 | 221112 | UNKNOWN | 02/06/2015 &nbsp;ACT | 12/09/2015 &nbsp;ACT | 2015-12-03 | 2016-07-06 | A |  | three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 megawatt (MW) each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | pipeline quality natural gas, good combustion practices | 8.6 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Large Combustion Turbines &gt; 25 MW | 15.11 | natural gas | 232 | MW | 4 Simple cycle CTGs, 2,500 hr/yr operational limitation. Facility will consist of either 232 MW (Siemens) or 220 MW (GE) | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices, low sulfur fuel | 13.4 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK AND TTTT
TX-0794 | HILL COUNTY GENERATING FACILITY | BRAZOS ELECTRIC COOPERATIVE | HILL | TX |  | USA | MIKE MEYERS | (254)750-6228 | MMEYERS@BRAZOSELECTRIC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512)239-1512, randy.hamilton@tceq.texas.gov | 130051,PSDTX1450, GHGPSDTX131 | 4911 | 221112 | UNKNOWN | 12/18/2015 &nbsp;ACT | 04/07/2016 &nbsp;ACT | 2016-04-05 | 2016-07-29 | A |  | Four simple cycle combustion turbine electric generators are proposed. Natural gas or ultra-low sulfur diesel fuel oil are the fuels. Turbine model options are: General Electric (GE) 7FA.03, GE 7FA.04, GE 7FA.05, and Siemes SGT6-5000(5)ee. Electric output is between 684 and 928 megawatts (MW). |  | Simple cycle turbine | 15.11 | natural gas | 171 | MW | Each combustion turbine is limited to 2,920 hours of annual operation, including startup and shutdown hours. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - TM5 MODIFIED IMPINGER CATCH | (Particulate Matter (PM)) | PM | P | Premixing of fuel and air enhances combustion efficiency and minimizes emissions. | 14 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Simple Cycle Turbine | 15.11 | natural gas | 227.5 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices | 8.5 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0826 | MUSTANG STATION | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | YOAKUM | TX |  | USA | JEFF PIPPIN | 806-418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | 72579, PSDTX1080M1, GHGPSDTX13 | 4911 | 221112 | 110041502433 | 06/12/2017 &nbsp;ACT | 08/16/2017 &nbsp;ACT | 2017-07-24 | 2018-04-18 | C |  | GE7FA combustion turbine (Unit 6) to increase the hours of operation to 3000 hours per year. The turbine construction was completed the first quarter of 2013 and initial firing began on April 1, 2013. |  | Simple Cycle Turbine | 15.11 | NATURAL GAS | 162.8 | MW | Unit 6 Turbine is limited to 3000 hours per year. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas and good combustion practices | 27 | T/YR |  | BACT-PSD | MACT , NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK MACT YYYY
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustion practices. | 11.81 | TON/YR |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines MSS | 15.11 | NATURAL GAS | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Minimizing duration of startup/shutdown, using good air pollution control practices and safe operating practices. | 0.01 | TON/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CO-0075 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO |  | USA | MARK LUX | 303-568-3241 | MARK.LUX@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 13PB2245 | 4911 | 221112 | 110058377830 | 09/10/2013 &nbsp;ACT | 05/30/2014 &nbsp;ACT | 2014-10-24 | 2016-02-19 | B |  | Power generation facility |  | Turbine - simple cycle gas | 15.11 | natural gas | 375 | MMBTU/H | One (1) General Electric, simple cycle, gas turbine electric generator, Unit 6 (CT08), model: LM6000, SN: N/A, rated at 375 MMBtu per hour. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Firing of pipeline quality natural gas as defined in 40 CFR Part 72. Specifically, the owner or the operator shall demonstrate that the natural gas burned has total sulfur content less than 0.5 grains/100 SCF. | 4.8 | LB/H | 3-HR AVE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0346 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-011-AC | 4911 | 221112 | 110002044065 | 11/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-01-08 | 2016-05-05 | D | http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | In this project, 24 peaking turbines from the Lauderdale facility are being replaced with five 200 MW combustion turbines at Lauderdale. The turbines will fire primarily natural gas, but may also fire ULSD fuel oil. Triggers PSD for NOx, PM, CO, VOC, and GHG. GHG permit issued by US EPA Region 4. Technical evaluation available at http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2000 | MMBtu/hr (approx) | Throughput could vary slightly (+/- 120 MMBtu/hr) depending on final selection of turbine model and firing of natural gas or oil. Primary fuel is expected to be gas. Each turbine limited to 3300 hrs per rolling 12-month period. Of these 3300 hrs, no more than 500 may use ULSD fuel oil. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA Method 9 (VE) | (Particulate Matter (PM)) | PM | P | Good combustion practice and low-sulfur fuel | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The fuel specifications of 2.0 grains/100 standard cubic feet of natural gas and 0.0015% sulfur in the ULSD fuel together with a 10% opacity limits for visible emissions (VE) are proposed as BACT.
FL-0354 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-013-AC | 4911 | 221112 | 110002044065 | 04/20/2015 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2016-02-17 | 2016-07-06 | D | https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | Re-affirmed BACT determinations in Permit No. 0110037-011-AC. Also, new GHG BACT determination. Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2100 | MMBtu/hr (approx) | Five simple cycle GE 7F.05 turbines. Max of 3390 hours per year per turbine. Of the 3390 hours per year, up to 500 hour may be on ULSD fuel oil. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Use of low-S nat gas or ULSD | (Particulate Matter (PM)) | PM | P | Clean fuel prevents PM formation | 2 | GR. S / 100 SCF | FUEL RECORD KEEPING | BACT-PSD | SIP | U | 0 | U | 0.0015 | % S IN ULSD | FUEL RECORD KEEPING | 0 |  |  | 0 | 0 | N |  | Use of clean fuels prevents formation of particulate matter. Also, 10% VE limit with annual VE test is a proxy for PM.
FL-0355 | FORT MYERS PLANT | FLORIDA POWER & LIGHT (FPL) | LEE | FL | 33905 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0710002-022-AC | 4911 | 221112 | 110000365248 | 05/12/2015 &nbsp;ACT | 09/10/2015 &nbsp;ACT | 2016-03-10 | 2016-07-06 | D | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.80831.1]&[profile=Permitting_Authorization] | Electric power plant, consists of a 6-on-2 combined-cycle unit (Units 2A through 2F) and two modern simple-cycle combustion turbines. Primary fuel is natural gas. Also includes 12 gas turbines (63 MW each) for peaking, introduced into service in 1974. This project entails decommissioning 10 of the 12 peaking turbines. They will be replaced with two new GE 7F.05 turbines, each with nominal capacity of 200 MW | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0710002.022.AC.D.ZIP | Combustion Turbines | 15.11 | Natural gas | 2262.4 | MMBtu/hr gas | Two GE 7F.05 turbines, approximately 200 MW each. Natural-gas is primary fuel. Permitted 3390 hr/yr of operation, of which no more than 500 hr may be on fuel oil. Dry Low-NOx, with wet injection for oil firing. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - None required | (Particulate Matter (PM)) | PM | P | Use of clean fuels | 2 | GR S / 100 SCF GAS | FOR NATURAL GAS | BACT-PSD |  | U | 0 | U | 0.0015 | % S IN ULSD | FOR ULSD | 0 |  |  | 0 | 0 | N |  | Clean fuels prevent PM formation. No PM testing required. Annual test for visible emissions.
IL-0121 | INVENERGY NELSON EXPANSION LLC | INVENERGY | LEE | IL | 61058 | USA | GORDON GRAY | 312-582-1290 | GGRAY@INVENERGY.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Bob Smet; 217-785-9250; robert.smet@illinois.gov | 15060042 | 4911 | 221112 | Not Found | 07/28/2016 &nbsp;ACT | 09/27/2016 &nbsp;ACT | 2017-01-27 | 2017-04-28 | B | https://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/9dbc452815081576862580b2006897b4/$FILE/ATT4AK5N.pdf/15060042.pdf | Peaking facility at an existing major source. The expansion will consist of two simple cycle combustion turbines and a fuel heater. |  | Two Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 190 | MW | Two simple cycle combustion turbines used for peaking purposes and fired primarily on natural gas with ULSD as a secondary fuel. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - USEPA Method 201A & 202 | (Particulate Matter (PM)) | PM | P | turbine design and good combustion practices | 0.005 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0.02 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission 1 (natural gas): 0.0050 lb/mmbtu* Emission 2 (ULSD): 0.020 lb/mmbtu* *During an hour that includes a startup, the particulate emissions of the turbine shall not exceed 10.0 lb/hr (natural gas) and 42.7 lb/hr (ULSD).
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER | 15.11 | NATURAL GAS | 92.5 | MMBTU/H | NATURAL GAS USAGE SHALL NOT EXCEED 18.14 MMCF/YEAR. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN, USE NATURAL GAS | 7.6 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER | 15.11 | NATURAL GAS | 92.5 | MMBTU/H | NATURAL GAS USAGE SHALL NOT EXCEED 18.14 MMCF/YEAR. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN, USE NATURAL GAS | 7.6 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0261 | VERMILLION GENERATING STATION | DUKE ENERGY INDIANA, LLC VERMILLION GENERATING STA | VERMILLION | IN | 47928 | USA | PATRICK COUGHLIN | 3178382108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIP SINHA PH.D. 317-234-4907 | 165-36956-00022 | 4911 | 221112 | 110006010921 | 03/16/2016 &nbsp;ACT | 02/28/2017 &nbsp;ACT | 2017-07-07 | 2017-08-09 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36956F.PDF | ELECTRIC UTILITY SERVICES |  | SIMPLE CYCLE, NATURAL GAS FIRED COMBUSTION TURBINES | 15.11 | NATURAL GAS | 80 | MW |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 5 | LB/H | EACH TURBINE | BACT-PSD |  | N | 0 |  | 0.5 | TON/12 CONSEC. MONTH | COMPLIANCE DETERMINED END OF EACH MONTH | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: ONLY TWO TURBINES WILL OPERATE DURING LOW LOAD OPERATION
IN-0264 | MONTPELIER GENERATING STATION | AES OHIO GENERATION, LLC | WELLS | IN | 46781 | USA | DREW PARKER | 9373314993 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: MADHURIMA MOULIK 317-233-6663 MMOULIK@IDEM.IN.GOV SECTION CHIEF: JASON KRAWCZYK 317-234-5174 | 179-37209-00026 | 4911 | 221112 | 110021089061 | 05/23/2016 &nbsp;ACT | 01/06/2017 &nbsp;ACT | 2017-07-07 | 2017-11-17 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/37209F.PDF | COMBUSTION TURBINES |  | PRATT &amp; TWIN-PAC SIMPLE CYCLE TURBINES | 15.11 | NATURAL GAS | 270.9 | MMBTU/H | NO. 2 DIESEL OIL BACKUP FUEL | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS PRIMARY FUEL; GOOD COMBUSTION PRACTICES | 0.0066 | LB/MMBTU | 3-HR AVG FOR NATURAL GAS | BACT-PSD |  |  | 0 |  | 0.012 | LB/MMBTU | 3-HR AVG FOR FUEL OIL | 0 |  |  | 0 | 0 | N |  | EACH OF 8 TURBINES LIMITED TO 500 HOURS FUEL OIL USAGE PER 12 MONTH PERIOD
KY-0104 | CASH CREEK GENERATING STATION | CASH CREEK GENERATION, L.L.C | HENDERSON | KY | 41047 | USA | MIKE MCINNUS | 502 357 9907 | MMCINNIS@ERORA.COM | 4 | KY001 | KENTUCKY DEP, DIV FOR AIR QUALITY | MR. RICK SHEWEKAH, MGR | (502)564-3999 | Sreenivas.Kesaraju@ky.gov |  | V-14-011 | 4911 | 221112 | 110042328479 | 06/18/2014 &nbsp;ACT | 06/10/2015 &nbsp;ACT | 2017-02-28 | 2017-04-28 | A |  | natural gas fired combined cycle power plant |  | Combined cycle combustion turnbine with HRSG and duct firing | 15.11 | Natural gas pipeline quality | 849 | MW | Two CT with HRSGs with duct burner Max fuel input for CTs and HRSGs 6,714 mmBtu/hr HHV Max Gross output 849 MW at 0F | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Combust pipeline quality natural gas only | 0.0088 | LB/MMBTU | THREE HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0258 | CALCASIEU PLANT | ENTERGY GULF STATES LA LLC | CALCASIEU | LA | 70665 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: TEGAN TREADAWAY, (225) 219-3408 | PSD-LA-746 | 4911 | 221112 | 110007042565 | 11/10/2009 &nbsp;ACT | 12/21/2011 &nbsp;ACT | 2012-02-01 | 2012-04-03 | C |  | 320 MW POWER PLANT COMPRISED OF 2 NATURAL GAS-FIRED SIMPLE CYCLE COMBUSTION TURBINES. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS PSD TRIGGERED DUE TO RELAXATION OF A FEDERALLY-ENFORCEABLE CONDITION LIMITING POTENTIAL EMISSIONS BELOW MAJOR STATIONARY SOURCE THRESHOLDS. | TURBINE EXHAUST STACK NO. 1 &amp; NO. 2 | 15.11 | NATURAL GAS | 1900 | MM BTU/H EACH |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE NATURAL GAS | 17 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 17 | LB/H | HOURLY MAXIMUM / STARTUP & SHUTDOWN ONLY | 0 |  |  | 0 | 0 | N |  | LIMITS ARE PER TURBINE EXHAUST STACK. AGGREGATE PM2.5 EMISSIONS FROM BOTH TURBINE EXHAUST STACKS ARE LIMITED TO 30.94 TONS PER YEAR. STARTUP & SHUTDOWN OPERATIONS ARE LIMITED TO 520 HOURS PER YEAR.
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110029511883 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and fueled by natural gas | 0.0076 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 2 COMBUSTION TURBINES | 15.11 | NATURAL GAS | 130 | MW | TWO GENERAL ELECTRIC (GE) FRAME 7EA COMBUSTION TURBINES (CTS) WITH A NOMINAL NET 87.2 MEGAWATT (MW) RATED CAPACITY, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), EQUIPPED WITH DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION SYSTEM (SCR), AND OXIDATION CATALYST | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF FACILITY PROCESS FUEL GAS OR PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.007 | LB/MMBTU | 3 STACK TEST RUN AVERAGE, EXCEPT SU/SD | BACT-PSD |  |  | 0 |  | 300.8 | LB/EVENT | FOR ALL STARTUPS | 0 |  |  | 0 | 0 | N |  | 5.6 LBS/SHUTDOWN EVENT. LIMITS ARE TOTAL FOR BOTH FRAME 7 CTS PER STARTUP OR SHUTDOWN EVENT
ND-0028 | R.M. HESKETT STATION | MONTANA-DAKOTA UTILITIES CO. | MORTON | ND | 58554 | USA | ABBIE KREBSBACH | (701) 222-7844 | ABBIE.KREBSBACH@MDU.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Primary contact is Tom Bachman at (701) 328-5188. | PTC13016 | 4911 | 221112 | 110022356591 | 11/07/2012 &nbsp;ACT | 02/22/2013 &nbsp;ACT | 2013-04-01 | 2017-04-28 | B |  | Addition of a natural gas-fired turbine (Unit 3) to an exisiting coal-fired power plant. The turbine will be used for supplying peak power and is rated at 986 MMBtu/hr and 88 MWe at average site conditions. |  | Combustion Turbine | 15.11 | Natural gas | 986 | MMBTU/H | Turbine is a GE Model PG 7121 (7EA) used as a peaking unit. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 7.3 | LB/H | AVERAGE OF THREE TEST RUNS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ND-0029 | PIONEER GENERATING STATION | BASIN ELECTRIC POWER COOPERATIVE | WILLIAMS | ND |  | USA | JERRY MENGE | 7012230441 | JMENGE@BEPC.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact. | PTC 13037 | 4911 | 221112 | 110058380238 | 02/19/2013 &nbsp;ACT | 05/14/2013 &nbsp;ACT | 2013-06-19 | 2016-11-03 | B |  | Three GE LM6000 PC SPRINT natural gas fired turbines used to generate electricity for peak periods. | The permit was for the addition of 2 turbines to the station. Since a synthetic minor limit was relaxed for the first unit, BACT was required for all three turbines. | Natural gas-fired turbines | 15.11 | Natural gas | 451 | MMBTU/H | Rating is for each turbine. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - 1-4, 201a and 202 | (Particulate Matter (PM)) | PM | N |  | 5.4 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | RBLC Staff: Original Emis Limit 1 Units were Numeric Limit - &lsquo;&lsquo;LB&lsquo;&lsquo; and Avg Time/Condition - &lsquo;&lsquo;1 HOUR&lsquo;&lsquo; The Emission Units are usually &lsquo;&lsquo;mass unit PER time unit&lsquo;&lsquo;. Separating them out makes understanding limit difficult for the users. The units were combined. The corrected entry is: Numeric Limit - &lsquo;&lsquo;LB/H&lsquo;&lsquo; Avg Time/Condition - blank
ND-0030 | LONESOME CREEK GENERATING STATION | BASIN ELECTRIC POWER COOP. | MCKENZIE | ND | 58831 | USA | JERRY MENGE | (701)223-0441 |  | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact at (701) 328-5188. | PTC 13049 | 4911 | 221112 | 110057111003 | 04/05/2013 &nbsp;EST | 09/16/2013 &nbsp;ACT | 2013-09-24 | 2017-06-28 | B |  | Three natural gas fired simple cycle turbines used to generate electricity for peak power demand. The turbines are GE LM6000 PF Sprint units with a nominal capacity of 45 MW each. |  | Natural Gas Fired Simple Cycle Turbines | 15.11 | Natural gas | 412 | MMBTU/H | The heat input is for a single unit. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - 1-4, 201a, 202 | (Particulate Matter (PM)) | PM | N |  | 5 | LB/H | AVERAGE OF THREE TEST RUNS | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit is for each unit.
NJ-0076 | PSEG FOSSIL LLC KEARNY GENERATING STATION | PSEG FOSSIL LLC | HUDSON | NJ | 7032 | USA |  |  |  | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | a. Aliya Khan, Permit evaluator, Aliya.Khan@dep.state.nj.us b. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS - yogesh.doshi@dep.state.nj.us- Phone Number 609-633-7249 | 12200-BOP100002 | 4911 | 221112 | 110043394396 | 08/03/2010 &nbsp;ACT | 10/27/2010 &nbsp;ACT | 2011-08-08 | 2011-09-07 | B |  | PSEG FOSSIL LLC KEARNY GENERATING STATION IS AN EXISTING ELECTRICITY GENERATING STATION. | This project consists of six new identical General Electric LM6000 sprint simple cycle combustion turbines burning natural gas. Each turbine will have a heat input rate of 485 million British thermal units per hour (MMBtu/hr) based on the high heating value of fuel (HHV). The combined maximum electricity generated by the six turbines will be 294 MW based on 2,978 hours of operation per turbine per year. All six new turbines will have water injection along with Selective Catalytic Reduction (SCR) systems to reduce Nitrogen Oxide (NOx) emissions and an oxidation catalyst to reduce Carbon Monoxide (CO) emissions | SIMPLE CYCLE TURBINE | 15.11 | Natural Gas | 8940000 | MMBtu/year (HHV) | Throughput <= 8.94xE6 MMBtu/year (HHV) combined for all six gas turbines. The 6 turbines are identical LM6000 simple cycle combustion turbines. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - M201A and M202 | (Particulate Matter (PM)) | PM | P | Good combustion practice, Use of Clean Burning Fuel: Natural gas | 6 | LB/H | AVERGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110000801614 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine with Duct Burner firing natural gas | 15.11 | Natural Gas | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 22.6 | LB/H | AV OF THREE ONE H STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110000801614 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine without Duct Burner Firing Natural Gas | 15.11 | Natural Gas | 28169501 | MMBTU/YR | Natural Gas Usage: <=28,169,501 MMBtu/year which includes maximum ultra low sulfur distillate oil usage of =2,371,943 MMBTU/year | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 14.4 | LB/H | AV OF THREE ONE H STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057188626 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.11 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane and methane section compressors. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.72 | LB/H | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Natural gas is the fuel. PM and PM10 are equal to PM2.5.
TX-0691 | PH ROBINSON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | GALVESTON | TX |  | USA | CRAIG ECKBERG | (832) 357-5291 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 erik.hendrickson@tceq.texas.gov | 108182 PSDTX1346 | 4911 | 221112 | 110002345515 | 02/06/2013 &nbsp;ACT | 05/20/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG proposes to construct six natural gas-fired simple cycle combustion turbine generators (CTG) for peaking, designed to operate during periods of high electric demand. The six CTGs selected by NRG are General Electric Frame 7E turbines have an ISO rating of 65 MW and a nominal maximum generating capacity of 80 MW. Each of the turbines will not exceed 20 percent annual capacity (equivalent to 1,752 full load hours) in any single year or 10 percent annual capacity factor (equivalent to 876 full load hours) averaged over any three year period. |  | (6) simple cycle turbines | 15.11 | natural gas | 65 | MW | General Electric Frame 7E turbines have an ISO rating of 65 MW and a nominal maximum generating capacity of 80 MW. The turbines were originally constructed as Frame 7B units that were remanufactured in 1999 and upgraded to 7E machines Each of the turbines will not exceed 20 percent annual capacity (equivalent to 1,752 full load hours) in any single year or 10 percent annual capacity factor (equivalent to 876 full load hours) averaged over any three year period, which qualifies each of the CTGs as Acid Rain Peaking Units under 40 CFR 72.2 | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas fuel, includes PM and PM10
TX-0693 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE INC | HALE | TX |  | USA | JEFF PIPPIN | (806) 418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson 512-239-2175 laura.gibson@tceq.texas.gov | 109148 PSDTX1358 | 4911 | 221112 | 110043432737 | 04/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-03-19 | 2016-07-29 | B |  | Golden Spread Electric Cooperative (GSEC) currently owns and operates Antelope Station (now renamed Antelope Elk Energy Center), a 168 MW generating facility made up of 18 quick start WÃ¤rtsilÃ¤ engines. GSEC is proposing to build a new combustion turbine-generator (CTG) facility at Antelope Station, while the 18 WÃ¤rtsilÃ¤ engines will remain and continue to be authorized by TCEQ Standard Permit. The new turbine-generator will provide primarily peaking and intermediate power needs in a highly cyclical operation. The CTG will produce approximately 100 - 200 MW of electricity, depending on loading and ambient temperature. |  | combustion turbine | 15.11 | natural gas | 202 | MW | new GE 7FA 5-Series gas turbine in a simple cycle application, with a maximum electric output of 202 megawatts (MW) and a maximum design capacity of 1,941 million British thermal units per hour (MMBtu/hr). The turbine will operate a maximum of 4,572 hours per year. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas fuel, includes PM10
TX-0694 | INDECK WHARTON ENERGY CENTER | INDECK WHARTON, L.L.C. | WHARTON | TX |  | USA | JAMES SCHNEIDER | (847) 520-3212 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 111724 PSDTX1374 | 4911 | 221112 | unknown | 06/18/2013 &nbsp;ACT | 02/02/2015 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | Indeck Wharton, L.L.C. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will either be the General Electric 7FA (~214 MW each) or the Siemens SGT6-5000F (~227 MW each), operating as peaking units in simple cycle mode. |  | (3) combustion turbines | 15.11 | natural gas | 220 | MW | The CTGs will either be the General Electric 7FA (~214 MW each) or the Siemens SGT6-5000F (~227 MW each), operating as peaking units in simple cycle mode | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas fuel, includes PM and PM10
TX-0695 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX |  | USA | JIM SHIELD | (312) 582-1440 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | 110423 PSDTX1366 | 4911 | 221112 | 110057112850 | 05/13/2013 &nbsp;ACT | 08/01/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | The proposed project is to construct and operate two natural gas-fired simple-cycle combustion turbine generators (CTGs) at the Ector County Energy Center (ECEC), located approximately 20 miles northwest of Odessa, Texas, in Ector County. |  | (2) combustion turbines | 15.11 | natural gas | 180 | MW | (2) GE 7FA.03, 2500 hours of operation per year each | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas fuel, includes PM and PM10
TX-0696 | ROANâ€™S PRAIRIE GENERATING STATION | TENASKA ROANâ€™S PRAIRIE PARTNERS (TRPP), LLC | GRIMES | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 erik.hendrickson@tceq.texas.gov | 114698 PSDTX1378 | 4911 | 221112 | 110028050141 | 10/25/2013 &nbsp;ACT | 09/22/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | The proposed project is to construct and operate the RPGS comprised of three new simple cycle combustion turbine generators (CTG), fueled by pipeline quality natural gas. The new CTGs will be peaking units, designed to operate during periods of high electric demand. The three CTGs will produce between 507 and 694 MW of electricity combined, depending on ambient temperature and the model of combustion turbine (CT) selected. The applicant is considering three models of CTs; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. |  | (2) simple cycle turbines | 15.11 | natural gas | 600 | MW | The three possible CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. will operate 2,920 hours per year at full load for each CT | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas fuel, includes PM and PM10
TX-0701 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX |  | USA | JIM SHIELD | 312-582-1440 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Marc Sturdivant, 512-239-1313, Marc.Sturdivant@tceq.texas.gov | 110423, PSDTX1366 | 4911 | 221112 | 110013396379 | 08/01/2014 &nbsp;ACT | 05/13/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is for two natural gas fired simple cycle CTGs. The proposed models include GE7Fa.03 and GE7Fa.05. They have an output of 165-193 MW. The new CTGs will operate as peaking units and will be limited to 2500 hours per year of operation each. |  | Simple Cycle Combustion Turbines | 15.11 | natural gas | 180 | MW |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Firing pipeline quality natural gas and good combustion practices | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Includes PM and PM10
TX-0733 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JOLLY HAYDEN | 806-349-5250 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, (512)239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358M1 | 4911 | 221112 | 110043432737 | 03/20/2015 &nbsp;ACT | 05/12/2015 &nbsp;ACT | 2015-05-04 | 2016-06-08 | B |  | Golden Spread Electric Cooperative, Inc. (GSEC) is requesting authorization for three additional simple cycle electric generating plants at an existing site to meet increased energy demand in the area. The generating equipment consists of three new GE 7F5-Series natural gas-fired combustion turbine generators (CTGs). Each turbine has a maximum electric output of 202 MW. |  | Simple Cycle Turbine &amp; Generator | 15.11 | natural gas | 202 | MW | 3 additional GE 7F 5-Series Combustion Turbine Generators | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices. | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of each turbine is limited to 4,572 hours per year
TX-0764 | NACOGDOCHES POWER ELECTRIC GENERATING PLANT | NACOGDOCHES POWER, LLC | NACOGDOCHES | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem 512-239-1310 Tzvi.shalem@tceq.texas.gov | 77679, PSDTX1061M1 & O-3455 | 4911 | 221112 | 110043814744 | 06/25/2015 &nbsp;ACT | 10/14/2015 &nbsp;ACT | 2015-09-16 | 2016-07-06 | B |  | Nacogdoches Power, LLC is requesting authorization for one natural gas fired, simple cycle combustion turbine generator (CTG). The CTG will be a Siemens F5 and have a nominal electric output of 232 megawatts (MW). |  | Natural Gas Simple Cycle Turbine (&gt;25 MW) | 15.11 | natural gas | 232 | MW | One Siemens F5 simple cycle combustion turbine generator | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices. | 12.09 | LB/HR |  | BACT-PSD |  | N | 0 | U | 12.94 | TPY |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,500 hours on a 12-month rolling average.
TX-0768 | SHAWNEE ENERGY CENTER | SHAWNEE ENERGY CENTER, LLC | HILL | TX |  | USA | NEIL O'DONOVAN | 312-422-1608 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, P.E., 512-239-1353, joseph.janecka@tceq.texas.gov | PSDTX1442, 125963 | 4911 | 221112 | UNKNOWN | 07/31/2015 &nbsp;ACT | 10/09/2015 &nbsp;ACT | 2015-10-05 | 2016-07-06 | A |  | Electric Generating Utility: The project will consist of four gas fired combustion turbines (CTGs). The CTGs are fueled with pipeline quality natural gas and will operate in simple cycle mode. The gas turbines will be one of two options. |  | Simple cycle turbines greater than 25 megawatts (MW) | 15.11 | natural gas | 230 | MW | Siemens Model SGT6-5000 F5ee â€“ 230 MW or Second turbine option: General Electric Model 7FA.05TP â€“ 227 MW | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices. | 84.1 | LB/HR |  | BACT-PSD | NSPS | N | 0 | U | 152.96 | TPY |  | 0 |  |  | 0 | 0 | N
TX-0769 | VAN ALSTYNE ENERGY CENTER (VAEC) | NAVASOTA NORTH COUNTRY PEAKERS OPERATING COMPANY I | GRAYSON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 121051 AND PSDTX1418 | 4911 | 221112 | UNKNOWN | 12/22/2014 &nbsp;ACT | 10/27/2015 &nbsp;ACT | 2015-10-30 | 2016-07-06 | A |  | Navasota North Country Peakers Operating Company I LLC. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 MW each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline Quality Natural Gas | 8.6 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0777 | UNION VALLEY ENERGY CENTER | NAVASOTA SOUTH PEAKERS OPERATING COMPANY I, LLC. | NIXON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 120973 AND PSDTX1420 | 4911 | 221112 | UNKNOWN | 02/06/2015 &nbsp;ACT | 12/09/2015 &nbsp;ACT | 2015-12-03 | 2016-07-06 | A |  | three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 megawatt (MW) each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | pipeline quality natural gas, good combustion practices | 8.6 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Large Combustion Turbines &gt; 25 MW | 15.11 | natural gas | 232 | MW | 4 Simple cycle CTGs, 2,500 hr/yr operational limitation. Facility will consist of either 232 MW (Siemens) or 220 MW (GE) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices, low sulfur fuel | 13.4 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK AND TTTT
TX-0794 | HILL COUNTY GENERATING FACILITY | BRAZOS ELECTRIC COOPERATIVE | HILL | TX |  | USA | MIKE MEYERS | (254)750-6228 | MMEYERS@BRAZOSELECTRIC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512)239-1512, randy.hamilton@tceq.texas.gov | 130051,PSDTX1450, GHGPSDTX131 | 4911 | 221112 | UNKNOWN | 12/18/2015 &nbsp;ACT | 04/07/2016 &nbsp;ACT | 2016-04-05 | 2016-07-29 | A |  | Four simple cycle combustion turbine electric generators are proposed. Natural gas or ultra-low sulfur diesel fuel oil are the fuels. Turbine model options are: General Electric (GE) 7FA.03, GE 7FA.04, GE 7FA.05, and Siemes SGT6-5000(5)ee. Electric output is between 684 and 928 megawatts (MW). |  | Simple cycle turbine | 15.11 | natural gas | 171 | MW | Each combustion turbine is limited to 2,920 hours of annual operation, including startup and shutdown hours. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - TM5, MODIFY IMPINGER CATCH | (Particulate Matter (PM)) | PM | P | Premixing of fuel and air enhances combustion efficiency and minimizes emissions. | 14 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0816 | CORPUS CHRISTI LIQUEFACTION | CORPUS CHRISTI LIQUEFACTION STAGE III, LLC | SAN PATRICIO | TX |  | USA | KEITH LITTLE | (713) 375-5204 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 139479, PSDTX1496, GHGPSDTX157 | 4925 | 221210 | Not Found | 11/16/2016 &nbsp;ACT | 02/14/2017 &nbsp;ACT | 2017-02-07 | 2018-04-18 | B |  | Trains 4 and 5 will consist of 12 natural gas compressor turbines, 2 thermal oxidizers, 2 sets of flares each comprised of one wet gas flare and one dry gas flare, 2 amine surge tanks (maintenance, startup, and shutdown [MSS] only), 3 diesel generators, 3 fire-water pump diesel engines, 6 fixed roof diesel storage tanks, and piping components. |  | Refrigeration compressor turbines | 15.11 | NATURAL GAS | 40000 | HP | 2 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane, ethylene, and methane section compressors. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.75 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Simple Cycle Turbine | 15.11 | natural gas | 227.5 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices | 8.5 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0826 | MUSTANG STATION | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | YOAKUM | TX |  | USA | JEFF PIPPIN | 806-418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | 72579, PSDTX1080M1, GHGPSDTX13 | 4911 | 221112 | 110041502433 | 06/12/2017 &nbsp;ACT | 08/16/2017 &nbsp;ACT | 2017-07-24 | 2018-04-18 | C |  | GE7FA combustion turbine (Unit 6) to increase the hours of operation to 3000 hours per year. The turbine construction was completed the first quarter of 2013 and initial firing began on April 1, 2013. |  | Simple Cycle Turbine | 15.11 | NATURAL GAS | 162.8 | MW | Unit 6 Turbine is limited to 3000 hours per year. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas and good combustion practices | 27 | T/YR |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK MACT YYYY
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustion practices. | 11.81 | TON/YR |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines MSS | 15.11 | NATURAL GAS | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Minimizing duration of startup/shutdown, using good air pollution control practices and safe operating practices. | 0.01 | TON/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0026 | WAVERLY FACILITY | PLEASANTS ENERGY, LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 304-665-4201 | GERALD.GATTI@GDFSUEZNA.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0034 | 4911 | 221112 | 110010376734 | 04/18/2016 &nbsp;ACT | 01/23/2017 &nbsp;ACT | 2017-03-21 | 2018-05-01 | D | http://www.dep.wv.gov/daq/Documents/January 2017 Permits and Evals/073-00022_PERM_R14-0034.pdf | 300 MW, natural gas fired, simple cycle peaking power facility | In this permitting action PSD only applies to the modified combustion turbines based on the relaxation of an original synthetic minor permit issued in 1999. Project also involves previous installation of turbo-charging. All BACT emission limits are given without turbocharging and startup/shutdown emissions are not included. Please contact above engineer for more information. There are two identical turbines but only one is listed. | GE Model 7FA Turbine | 15.11 | Natural Gas | 1571 | mmbtu/hr | There are two identical units at the facility. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Inlet Air Filtration, Use of Natural Gas, Ultra-Low Sulfur Diesel | 15 | LB/HR | NATURAL GAS | BACT-PSD |  | U | 0 | U | 39 | LB/HR | FUEL OIL | 15 | LB/HR | NATURAL GAS | 0 | 0 | N |  | All PM emissions assumed to be PM2.5 or less. PM and PM10 emission limits are the same as above. Additional emission limits are in the permit for use of turbocharging and startup/shutdown emissions. Please contact if need additional information.
*WV-0028 | WAVERLY POWER PLANT | PLEASANTS ENERGY LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 3046654201 | GERALD.GATTI@DYNEGY.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Steve Pursley, PE Engineer West Virginia Division of Air Quality 601-57th St., SE Charleston, WV 25304 Phone: (304) 926-0499 x1218 Fax: (304) 926-0478 steve.r.pursley@wv.gov | R14-0034A | 4911 | 221112 | 110063231042 | 11/30/2017 &nbsp;ACT | 03/13/2018 &nbsp;ACT | 2018-05-29 | 2018-05-29 | U | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/073-00022_PERM_R14-0034A.pdf | 300 MW Sinple-Cycle Peaking Plant | Modification to existing PSD Permit (R14-0034, RBLC Number WV-0027) to add &lsquo;&lsquo;advanced gas path&lsquo;&lsquo; technology to the turbines that was defined as a &lsquo;&lsquo;change in the method of operation&lsquo;&lsquo; that resulted a major modification to the turbines. | GE 7FA.004 Turbine | 15.11 | Natural Gas | 167.8 | MW | This one entry is for both turbines as they are the same. Each turbine, after this modification, is a nominal 167.8 MW GE Model 7FA.004. Has oil-fire backup. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Inlet air filtration. | 15.09 | LB/HR |  | BACT-PSD |  | U | 0 | U | 41.65 | TONS/YEAR |  | 15.09 | LB/HR |  | 0 | 0 | N
CA-1223 | PIO PICO ENERGY CENTER | PIO PICO ENERGY CENTER, LLC | OTAY MESA | CA | 92154 | USA | GARY CHANDLER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SD 11-01 | 4911 | 221112 | 110045006943 | 06/14/2012 &nbsp;ACT | 11/19/2012 &nbsp;ACT | 2013-03-05 | 2014-01-28 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | CONSTRUCTION OF THREE GENERAL ELECTRIC (GE) LMS100 NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 100 MW EACH. THE PROJECT WILL HAVE AN ELECTRICAL OUTPUT OF 300 MW. | NOTE: PERMIT ISSUED 11/19/2012. ENVIRONMENTAL APPEALS BOARD REMANDED THE PM BACT ANALYSIS TO REGION 9 ON 8/2/2013. FINAL PERMIT ISSUED ON 2/28/2014. ONE PETITION FILED IN 9TH CIRCUIT FEDERAL COURT CHALLENGING THE FINAL PERMIT DECISION. THIS LAWSUIT WAS DISMISSED ON 6/17/2014 IN RESPONSE TO PETITIONERSâ€™ MOTION FOR VOLUNTARY DISMISSAL. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.11 | NATURAL GAS | 300 | MW | Three simple cycle combustion turbine generators (CTG). Each CTG rated at 100 MW (nominal net). | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | PUC-QUALITY NATURAL GAS | 0.0065 | LB/MMBTU (HHV) | AT LOADS OF 80% OR HIGHER | BACT-PSD |  | U | 0 | U | 5.5 | LB/H |  | 0 |  |  | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055426409 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Three simple cycle combustion turbines | 15.11 | natural gas | 799.7 | MMBTU/H | Three GE, LMS100PA, natural gas-fired, simple cycle CTG rated at 799.7 MMBtu per hour each,based on HHV. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustor design | 6.6 | LB/H | AVE OVER STACK TEST LENGTH | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0354 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-013-AC | 4911 | 221112 | 110002044065 | 04/20/2015 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2016-02-17 | 2016-07-06 | D | https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | Re-affirmed BACT determinations in Permit No. 0110037-011-AC. Also, new GHG BACT determination. Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2100 | MMBtu/hr (approx) | Five simple cycle GE 7F.05 turbines. Max of 3390 hours per year per turbine. Of the 3390 hours per year, up to 500 hour may be on ULSD fuel oil. | Particulate matter, total (TPM) | Other - Use of low-sulfur nat gas or ULSD | (Particulate Matter (PM)) | PM | P | Clean fuel prevents PM formation | 2 | GR. S / 100 SCF GAS | FUEL RECORD KEEPING | BACT-PSD | SIP | U | 0 | U | 0.0015 | % S IN FUEL OIL | FUEL RECORD KEEPING | 0 |  |  | 0 | 0 | N |  | Use of clean fuels prevents formation of particulate matter. Also, 10% VE limit with annual VE test is a proxy for PM.
FL-0355 | FORT MYERS PLANT | FLORIDA POWER & LIGHT (FPL) | LEE | FL | 33905 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0710002-022-AC | 4911 | 221112 | 110000365248 | 05/12/2015 &nbsp;ACT | 09/10/2015 &nbsp;ACT | 2016-03-10 | 2016-07-06 | D | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.80831.1]&[profile=Permitting_Authorization] | Electric power plant, consists of a 6-on-2 combined-cycle unit (Units 2A through 2F) and two modern simple-cycle combustion turbines. Primary fuel is natural gas. Also includes 12 gas turbines (63 MW each) for peaking, introduced into service in 1974. This project entails decommissioning 10 of the 12 peaking turbines. They will be replaced with two new GE 7F.05 turbines, each with nominal capacity of 200 MW | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0710002.022.AC.D.ZIP | Combustion Turbines | 15.11 | Natural gas | 2262.4 | MMBtu/hr gas | Two GE 7F.05 turbines, approximately 200 MW each. Natural-gas is primary fuel. Permitted 3390 hr/yr of operation, of which no more than 500 hr may be on fuel oil. Dry Low-NOx, with wet injection for oil firing. | Particulate matter, total (TPM) | Other - No PM tests required | (Particulate Matter (PM)) | PM | P | Use of clean fuels, and annual VE test | 2 | GR S / 100 SCF GAS | FOR NATURAL GAS | BACT-PSD |  | U | 0 | U | 0.0015 | % S IN ULSD | FOR ULSD | 0 |  |  | 0 | 0 | N |  | Clean fuels prevent PM formation. No PM testing required. Annual test for visible emissions.
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE LM6000PC SPRINT Simple cycle combustion turbine | 15.11 | Pipeline quality natural gas | 405.3 | MMBTU/hr |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | fire only pipeline quality natural gas | 6 | LB/HR | AT FULL LOAD | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE 7FA Simple Cycle Combustion Turbine | 15.11 | Pipeline quality natural gas | 1780 | MMBTU/HR |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | will fire only pipeline quality natural gas | 18 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KY-0104 | CASH CREEK GENERATING STATION | CASH CREEK GENERATION, L.L.C | HENDERSON | KY | 41047 | USA | MIKE MCINNUS | 502 357 9907 | MMCINNIS@ERORA.COM | 4 | KY001 | KENTUCKY DEP, DIV FOR AIR QUALITY | MR. RICK SHEWEKAH, MGR | (502)564-3999 | Sreenivas.Kesaraju@ky.gov |  | V-14-011 | 4911 | 221112 | 110042328479 | 06/18/2014 &nbsp;ACT | 06/10/2015 &nbsp;ACT | 2017-02-28 | 2017-04-28 | A |  | natural gas fired combined cycle power plant |  | Combined cycle combustion turnbine with HRSG and duct firing | 15.11 | Natural gas pipeline quality | 849 | MW | Two CT with HRSGs with duct burner Max fuel input for CTs and HRSGs 6,714 mmBtu/hr HHV Max Gross output 849 MW at 0F | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Combust only pipeline quality natural gas | 0.0088 | LB.MMBTU | THREE HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Refrigeration Compressor Turbines (16) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and fueled by natural gas | 2.08 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | also for PM10 and PM2.5
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Generation Turbines (2) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and fueled by natural gas | 2.08 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | also for PM10 and PM2.5
TX-0733 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JOLLY HAYDEN | 806-349-5250 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, (512)239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358M1 | 4911 | 221112 | 110043432737 | 03/20/2015 &nbsp;ACT | 05/12/2015 &nbsp;ACT | 2015-05-04 | 2016-06-08 | B |  | Golden Spread Electric Cooperative, Inc. (GSEC) is requesting authorization for three additional simple cycle electric generating plants at an existing site to meet increased energy demand in the area. The generating equipment consists of three new GE 7F5-Series natural gas-fired combustion turbine generators (CTGs). Each turbine has a maximum electric output of 202 MW. |  | Simple Cycle Turbine &amp; Generator | 15.11 | natural gas | 202 | MW | 3 additional GE 7F 5-Series Combustion Turbine Generators | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices. | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of each turbine is limited to 4,572 hours per year
TX-0764 | NACOGDOCHES POWER ELECTRIC GENERATING PLANT | NACOGDOCHES POWER, LLC | NACOGDOCHES | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem 512-239-1310 Tzvi.shalem@tceq.texas.gov | 77679, PSDTX1061M1 & O-3455 | 4911 | 221112 | 110043814744 | 06/25/2015 &nbsp;ACT | 10/14/2015 &nbsp;ACT | 2015-09-16 | 2016-07-06 | B |  | Nacogdoches Power, LLC is requesting authorization for one natural gas fired, simple cycle combustion turbine generator (CTG). The CTG will be a Siemens F5 and have a nominal electric output of 232 megawatts (MW). |  | Natural Gas Simple Cycle Turbine (&gt;25 MW) | 15.11 | natural gas | 232 | MW | One Siemens F5 simple cycle combustion turbine generator | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices. | 12.09 | LB/HR |  | BACT-PSD |  | N | 0 | U | 12.94 | TPY |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,500 hours on a 12-month rolling average.
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Simple Cycle Turbine | 15.11 | natural gas | 227.5 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices | 8.5 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines MSS | 15.11 | NATURAL GAS | 0 |  |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Minimizing duration of startup/shutdown, using good air pollution control practices and safe operating practices. | 0.01 | TON/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP03) | 15.11 | Natural Gas | 40 | MW |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 4 | LB/H | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 17.5 | TONS | CALENDAR YEAR | 0 |  |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Trubine (EP04) | 15.11 | Natural Gas | 40 | MW |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 4 | LB/H | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 17.5 | TONS | CALENDAR YEAR | 0 |  |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP05) | 15.11 | Natural Gas | 40 | MW |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 4 | LB/H | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 17.5 | TONS | CALENDAR YEAR | 0 |  |  | 0 | 0 | N
FL-0305 | OUC CURTIS H. STANTON ENERGY CENTER | ORLANDO UTILITIES COMMISSION (OUC) | ORLANDO | FL | 32831 | USA | DENISE M. STALLS | 4077374236 | DSTALLS@OUC.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | ALVARO LINERO, P.E. SPECIAL PROJECT ADMINISTRATOR BUREAU OF AIR REGULATION | PSD-FL-373A AND 0950137-020-AC | 4911 | 221112 | UNKNOWN | 03/04/2008 &nbsp;ACT | 05/12/2008 &nbsp;ACT | 2009-02-20 | 2009-08-31 | B |  | THE EXISTING FACILITY CONSISTS OF TWO 468 MW FOSSIL FUEL FIRED STEAM ELECTRIC GENERATING UNITS (UNITS 1 AND 2), AND ONE 640 MW NGCC UNIT (UNIT A). THERE ARE STORAGE AND HANDLING FACILITIES FOR SOLID FUELS, FLY ASH, LIMESTONE, GYPSUM, SLAG, AND BOTTOM ASH. NEW PROJECT ADDS UNIT B, A 300 MW COMBINED CYCLE COMBUSTION TURBINE AND ASSOCIATED EQUIPMENT. | THE NEW PROJECT IS TO CONSTRUCT A Â¿ONE-ON-ONEÂ¿ F-CLASS NGCC UNIT (STANTON UNIT B) AND ASSOCIATED AUXILIARY EQUIPMENT. UNIT B WILL CONSIST OF: ONE NOMINAL 150 MEGAWATTS (MW) GENERAL ELECTRIC 7241 FA COMBUSTION TURBINE-ELECTRICAL GENERATOR (CTG); A SUPPLEMENTARY FIRED HEAT RECOVERY STEAM GENERATOR (HRSG) WITH NATURAL GAS FUELED DUCT BURNERS; AND A NOMINAL 150 MW STEAM TURBINE GENERATOR (STG) FOR AN OVERALL NOMINAL RATING OF 300 MW. THE PROJECT INCLUDES HIGHLY AUTOMATED CONTROLS, DESCRIBED AS THE GE MARK VI GAS TURBINE CONTROL SYSTEM TO FULFILL ALL OF THE GAS TURBINE CONTROL REQUIREMENTS. UNIT B WILL FIRE NATURAL GAS AS THE PRIMARY FUEL, AND ULTRALOW SULFUR DIESEL (ULSD) FUEL OIL SERVING AS A BACKUP FUEL. | 300 MW COMBINED CYCLE COMBUSTION TURBINE | 15.11 | NATURAL GAS | 1765 | MMBTU/H | FOR ULTRA LOW SULFUR (0.0015% SULFUR BY WEIGHT) FUEL OIL IS 1935 MMBTU/H. | Sulfur Dioxide (SO2) | Other - Fuel records | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 2 | GR S/100 SCF GAS |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | THE FUEL SULFUR SPECIFICATIONS EFFECTIVELY LIMIT THE POTENTIAL EMISSIONS OF SAM AND SO2 FROM THE GAS TURBINES AND REPRESENT BACT FOR THESE POLLUTANTS. COMPLIANCE WITH THE FUEL SULFUR SPECIFICATIONS SHALL BE DETERMINED BY THE ASTM METHODS FOR DETERMINATION OF FUEL SULFUR AS DETAILED SPECIFIC CONDITION 30 OF PERMIT PSD-FL-373A.
FL-0310 | SHADY HILLS GENERATING STATION | SHADY HILLS POWER COMPANY | PASCO | FL | 6927 | USA | ROY S. BELDEN | 2033576820 | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | SYED ARIF, PROJECT ENGINEER PHONE 850/ 921-9528 SYED.ARIF@DEP.STATE.FL.US TERESA HERON PHONE 850/921-9529 TERESA.HERON@DEP.STATE.FL.US | PSD-FL-402 | 4911 | 221122 | 1210100373 | 05/13/2008 &nbsp;ACT | 01/12/2009 &nbsp;ACT | 2009-07-29 | 2010-01-26 | B |  | THIS FACILITY CONSISTS OF THREE, DUAL-FUEL, NOMINAL 170 MW GENERAL ELECTRIC MODEL PG7241FA (GE 7FA) SIMPLE CYCLE COMBUSTION TURBINES-ELECTRICAL GENERATORS, THREE EXHAUST STACKS THAT ARE 18 FEET IN DIAMETER AND 75 FEET TALL, AND ONE 2.8-MILLION GALLON DISTILLATE FUEL OIL STORAGE TANK. THE COMBUSTION TURBINE UNITS CAN OPERATE IN SIMPLE-CYCLE MODE AND INTERMITTENT DUTY MODE. THE UNITS ARE EQUIPPED WITH DRY LOW-NITROGEN OXIDES (NOX) COMBUSTORS AND WATER INJECTION CAPABILITY. THE THREE COMBUSTION TURBINES ARE REGULATED UNDER PHASE II OF THE FEDERAL ACID RAIN PROGRAM. THIS FACILITY OPERATES DURING PEAK HOURS OF ELECTRICAL USE. |  | TWO SIMPLE CYCLE COMBUSTION TURBINE - MODEL 7FA | 15.11 | NATURAL GAS | 170 | MW | BACKUP FUEL: ULTRA LOW SULFUR DIESEL WITH A MAXIMUM SULFUR CONTENT OF 0.0015%, BY WEIGHT | Sulfur Dioxide (SO2) | Other - Verification/delivery receipts | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | FIRING OF NATURAL GAS WITH A MAXIMUM S CONTENT AT 2GR/100 SCF AND ULTRA LOW SULFUR DIESEL FUEL OIL WITH A MAXIMUM S CONTENT AT 0.0015%, BY WEIGHT. | 2 | GR S/100 SCF NG | NA/RECORDING COMPLIANCE | BACT-PSD |  | U | 0 | U | 0.0015 | S BY WEIGHT FUEL OIL | NA/RECORDING COMPLIANCE | 0 |  |  | 0 | 0 | N
FL-0319 | GREENLAND ENERGY CENTER | JACKSONVILLE ELECTRIC AUTHORITY (JEA) | DUVAL | FL | 32258 | USA | N. BERT GIANAZZA | 904-665-6247 | GIANNB@JEA.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Syed Arif Project Manager 850-921-9580 Jeff Koerner, P.E. Administrator Phone 850-921-9536 | PSD-FL-401 | 4911 | 221112 | UNKNOWN | 04/21/2008 &nbsp;ACT | 03/10/2009 &nbsp;ACT | 2010-09-23 | 2011-12-01 | A |  | The proposed facility is a new electric-generating facility referred to as Greenfield Energy Center (GEC). GEC will be built in two phases. The initial phase will be the construction of two natural gas-fired simple cycle combustion turbine (CT) units that are proposed to be operational June 2011. The second phase will convert these simple cycle units to a combined cycle combustion turbine (â€œ2-on 1â€ configuration). Heat recovery equipment will be installed on the two simple cycle combustion turbines to capture enough heat energy to run a steam turbine (ST). This phase is proposed to be operational by June 2013. | Each combustion turbine shall not operate more than 3,500 hours during any consecutive 12 months of which 500 hours may be on ULSFO. Each combustion turbine shall not operate more than 17 hours exclusively on ULSFO per calendar day, or with a combination of ULSFO burning of 12 hours with 12 hours of natural gas for compliance with regional haze impact thresholds. | 190 MW Combustion Turbine | 15.11 | ULSO | 30213 | GAL/YR | Capacity: 1806 MMBtu/H, natural gas Capacity: 1994 MMBtu/H, fuel oil Authorized Fuels (Pre-onsite natural gas availability): Each combustion turbine shall fire ULSFO which shall contain no more than 0.0015% sulfur by weight as the primary fuel until natural gas is available at the facility. If natural gas is not available by June 1, 2011, the permittee shall submit to the Department and EQD semi-annual status reports on the availability of natural gas to the facility. The first status report shall be submitted by June 1, 2011. The status reports shall be submitted until natural gas is available at the facility. Authorized Fuels (Post-onsite natural gas availability): Each combustion turbine shall fire natural gas as the primary fuel, which shall contain no more than 2 grains of sulfur per 100 standard cubic feet of natural gas. As a restricted alternate fuel, the combustion turbine may fire ULSFO containing no more than 0.0015% sulfur by weight. | Sulfur Dioxide (SO2) | Other - Fuel Analysis | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Fuel/material sulfur limitation | 2 | GR S/100 SCF GAS | RECORD KEEPING | BACT-PSD |  | U | 0 | U | 0.0015 | % S FUEL OIL | RECORD KEEPING | 0 |  |  | 0 | 0 | N |  | The fuel sulfur specification effectively limits the potential emissions of SAM and SO2 from the gas turbines and represents BACT for these pollutants. Compliance with the fuel sulfur specifications shall be determined by the ASTM methods or a certified fuel sulfur analysis from the fuel vendor for determination of fuel sulfur as detailed in the permit.
FL-0354 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-013-AC | 4911 | 221112 | 110002044065 | 04/20/2015 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2016-02-17 | 2016-07-06 | D | https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | Re-affirmed BACT determinations in Permit No. 0110037-011-AC. Also, new GHG BACT determination. Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2100 | MMBtu/hr (approx) | Five simple cycle GE 7F.05 turbines. Max of 3390 hours per year per turbine. Of the 3390 hours per year, up to 500 hour may be on ULSD fuel oil. | Sulfur Dioxide (SO2) | Other - Use of low-S nat gas or ULSD | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Limitation on S in fuel | 2 | GR. S / 100 SCF | FUEL RECORD KEEPING | BACT-PSD | NSPS , SIP | U | 0 | U | 0.0015 | % S IN ULSD | FUEL RECORD KEEPING | 0 |  |  | 0 | 0 | N |  | Limitation on sulfur in fuel, compliance by recordkeeping. No testing required. Also subject to NSPS Subpart KKKK.
FL-0355 | FORT MYERS PLANT | FLORIDA POWER & LIGHT (FPL) | LEE | FL | 33905 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0710002-022-AC | 4911 | 221112 | 110000365248 | 05/12/2015 &nbsp;ACT | 09/10/2015 &nbsp;ACT | 2016-03-10 | 2016-07-06 | D | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.80831.1]&[profile=Permitting_Authorization] | Electric power plant, consists of a 6-on-2 combined-cycle unit (Units 2A through 2F) and two modern simple-cycle combustion turbines. Primary fuel is natural gas. Also includes 12 gas turbines (63 MW each) for peaking, introduced into service in 1974. This project entails decommissioning 10 of the 12 peaking turbines. They will be replaced with two new GE 7F.05 turbines, each with nominal capacity of 200 MW | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0710002.022.AC.D.ZIP | Combustion Turbines | 15.11 | Natural gas | 2262.4 | MMBtu/hr gas | Two GE 7F.05 turbines, approximately 200 MW each. Natural-gas is primary fuel. Permitted 3390 hr/yr of operation, of which no more than 500 hr may be on fuel oil. Dry Low-NOx, with wet injection for oil firing. | Sulfur Dioxide (SO2) | Other - Vendor cert for S content in fuel | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Use of clean fuels | 2 | GR S / 100 SCF GAS | FOR NATURAL GAS | BACT-PSD | NSPS | U | 0 | U | 0.0015 | % S IN ULSD | FOR ULSD | 0 |  |  | 0 | 0 | N |  | Clean fuels prevent SO2 emission. No SO2 testing required. Compliance via recordkeeping of sulfur content in fuels (similar to Subpart KKKK).
IN-0261 | VERMILLION GENERATING STATION | DUKE ENERGY INDIANA, LLC VERMILLION GENERATING STA | VERMILLION | IN | 47928 | USA | PATRICK COUGHLIN | 3178382108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIP SINHA PH.D. 317-234-4907 | 165-36956-00022 | 4911 | 221112 | 110006010921 | 03/16/2016 &nbsp;ACT | 02/28/2017 &nbsp;ACT | 2017-07-07 | 2017-08-09 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36956F.PDF | ELECTRIC UTILITY SERVICES |  | SIMPLE CYCLE, NATURAL GAS FIRED COMBUSTION TURBINES | 15.11 | NATURAL GAS | 80 | MW |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD COMBUSTION PRACTICES | 0.6 | LB/H | EACH TURBINE | BACT-PSD |  | N | 0 |  | 0.1 | TON/12 CONSEC. MONTH | COMPLIANCE DETERMINED END OF EACH MONTH | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: ONLY TWO TURBINES WILL OPERATE DURING LOW LOAD.
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE LM6000PC SPRINT Simple cycle combustion turbine | 15.11 | Pipeline quality natural gas | 405.3 | MMBTU/hr |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | fire only pipeline quality natural gas | 2 | GR S/100 SCF |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE 7FA Simple Cycle Combustion Turbine | 15.11 | Pipeline quality natural gas | 1780 | MMBTU/HR |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | fire only pipeline quality natural gas | 2 | GR S/100 SCF |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KY-0104 | CASH CREEK GENERATING STATION | CASH CREEK GENERATION, L.L.C | HENDERSON | KY | 41047 | USA | MIKE MCINNUS | 502 357 9907 | MMCINNIS@ERORA.COM | 4 | KY001 | KENTUCKY DEP, DIV FOR AIR QUALITY | MR. RICK SHEWEKAH, MGR | (502)564-3999 | Sreenivas.Kesaraju@ky.gov |  | V-14-011 | 4911 | 221112 | 110042328479 | 06/18/2014 &nbsp;ACT | 06/10/2015 &nbsp;ACT | 2017-02-28 | 2017-04-28 | A |  | natural gas fired combined cycle power plant |  | Combined cycle combustion turnbine with HRSG and duct firing | 15.11 | Natural gas pipeline quality | 849 | MW | Two CT with HRSGs with duct burner Max fuel input for CTs and HRSGs 6,714 mmBtu/hr HHV Max Gross output 849 MW at 0F | Sulfur Dioxide (SO2) | Other - EPA method 20 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | The use of pipeline quality natural gas with a sulfur content of less than or equal to 1.0 grain/100 dscf | 0.0027 | LB/MMBTU | THREE(3) HOUR ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NM-0051 | CUNNINGHAM POWER PLANT | SOUTHWESTERN PUBLIC SERVICE CO. | LEA | NM | 88241-1650 | USA | KEVIN WORLEY | 806 378 2185 | KEVIN.WORLEY@XCELENERGY.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Cember Hardison is permit writer. 505 476 4346. cember.hardison@state.nm.us | PSD-NM-622-M3 | 4911 | 221122 | 110010571639 | 03/08/2011 &nbsp;ACT | 05/02/2011 &nbsp;ACT | 2011-08-02 | 2012-01-05 | C |  | Electric steam generating facility providing commercial electric power using natural gas fired boilers and turbines. | Simple Cycle Combustion Turbines. Permit revises the NOx BACT ppmvd limit for turbines established in permit PSD-NM-622-M2 issued 2-10-97 because turbines have not been able to meet NOx BACT limits. No modification or change to mass emissions. Former NOx BACT was at 15 ppmvd w/out power augmentation (normal mode) and 25 ppmvd w/ power augmentation (see RBLC ID NM-0028). Entry also clarifies the existing CO, SOx, and PM BACT. | Normal Mode (without Power Augmentation) | 15.11 | natural gas | 0 |  |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | 5.25 gr/100 SCF total sulfur limit in fuel. | 22.1 | LB/H | HOURLY | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | SO2 BACT established in PSD-NM-622-M2 issued 2-10-97.
NM-0051 | CUNNINGHAM POWER PLANT | SOUTHWESTERN PUBLIC SERVICE CO. | LEA | NM | 88241-1650 | USA | KEVIN WORLEY | 806 378 2185 | KEVIN.WORLEY@XCELENERGY.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Cember Hardison is permit writer. 505 476 4346. cember.hardison@state.nm.us | PSD-NM-622-M3 | 4911 | 221122 | 110010571639 | 03/08/2011 &nbsp;ACT | 05/02/2011 &nbsp;ACT | 2011-08-02 | 2012-01-05 | C |  | Electric steam generating facility providing commercial electric power using natural gas fired boilers and turbines. | Simple Cycle Combustion Turbines. Permit revises the NOx BACT ppmvd limit for turbines established in permit PSD-NM-622-M2 issued 2-10-97 because turbines have not been able to meet NOx BACT limits. No modification or change to mass emissions. Former NOx BACT was at 15 ppmvd w/out power augmentation (normal mode) and 25 ppmvd w/ power augmentation (see RBLC ID NM-0028). Entry also clarifies the existing CO, SOx, and PM BACT. | Power Augmentation | 15.11 | natural gas | 0 |  | Increase power output by lowering the outlet air temperatur through water inejctinos into the compressor. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | 5.25 gr/scf total sulfur in fuel | 22.1 | LB/H | HOURLY | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | SO2 BACT established in PSD-NM-622-M2 issued 2-10-97.
OH-0333 | DAYTON POWER & LIGHT ENERGY LLC | DAYTON POWER & LIGHT COMPANY | MONTGOMERY | OH | 45439 | USA | CARRIE BURKS | 937-331-3042 |  | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104867 | 4911 | 221112 | 110000394145 | 04/30/2009 &nbsp;ACT | 12/03/2009 &nbsp;ACT | 2010-05-13 | 2010-05-20 | C |  | Seven simple cycle stationary combustion turbines all with rating of 80 MW and nominal heat input of 1115.2 mmBtu/hr using natural gas or No. 2 fuel oil and all with water injection control and last 5 also with low NOx burners. | Simple cycle stationary combution turbines issed in 2 different permits. Four turbines in this permit with dry low NOx combustion and water injection controls. Administrative Modification to original PTI #08-04153 issued 8/7/01, to incorporate low mass emissions methodology as allowed per 40 CFR 75.19 in lieu of methods under Appendix D or E to Part 75, by meeting the requirements of having mass emissions of less than 25 T/YR SO2 and less than 100 T/YR NOx (per turbine) based on 3 years of operation. Modification also reduced permitted formaldehyde emissions by 8.7 tons, recalculated based on the restriction on hours of operation. | Turbines (4), simple cycle, natural gas | 15.11 | NATURAL GAS | 15020 | H/YR | Hours per year for all 4 turbines | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Fuel oil with no more than 0.05% by weight sulfur | 0.0026 | LB/MMBTU | ACTUAL HEAT INPUT | BACT-PSD | SIP | U | 0 | Y | 138.6 | T/YR | PER ROLLING 12-MO. FOR 4 UNITS &ALL FUEL | 0.0026 | LB/MMBTU | ACTUAL HEAT INPUT | 0 | 0 | N |  | T/YR limit is for both fuels and for the 4 turbines combined. Compliance by monitoring quality of low sulfur fuel oil.
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057188626 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.11 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane and methane section compressors. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.31 | LB/H | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Fuel sulfur is very low for natural gas.
TX-0695 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX |  | USA | JIM SHIELD | (312) 582-1440 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | 110423 PSDTX1366 | 4911 | 221112 | 110057112850 | 05/13/2013 &nbsp;ACT | 08/01/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | The proposed project is to construct and operate two natural gas-fired simple-cycle combustion turbine generators (CTGs) at the Ector County Energy Center (ECEC), located approximately 20 miles northwest of Odessa, Texas, in Ector County. |  | (2) combustion turbines | 15.11 | natural gas | 180 | MW | (2) GE 7FA.03, 2500 hours of operation per year each | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 1 | GR/100 DSCF |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0701 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX |  | USA | JIM SHIELD | 312-582-1440 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Marc Sturdivant, 512-239-1313, Marc.Sturdivant@tceq.texas.gov | 110423, PSDTX1366 | 4911 | 221112 | 110013396379 | 08/01/2014 &nbsp;ACT | 05/13/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is for two natural gas fired simple cycle CTGs. The proposed models include GE7Fa.03 and GE7Fa.05. They have an output of 165-193 MW. The new CTGs will operate as peaking units and will be limited to 2500 hours per year of operation each. |  | Simple Cycle Combustion Turbines | 15.11 | natural gas | 180 | MW |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Firing pipeline quality natural gas and good combustion practices. | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Large Combustion Turbines &gt; 25 MW | 15.11 | natural gas | 232 | MW | 4 Simple cycle CTGs, 2,500 hr/yr operational limitation. Facility will consist of either 232 MW (Siemens) or 220 MW (GE) | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | good combustion practices, low sulfur fuel | 1 | GR/100 SCF | HOURLY | BACT-PSD | NSPS | N | 0 | U | 0.25 | GR/100 SCF | ANNUAL AVERAGE | 0 |  |  | 0 | 0 | N |  | NSPS KKKK AND TTTT
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Simple Cycle Turbine | 15.11 | natural gas | 227.5 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Pipeline quality natural gas; limited hours; good combustion practices | 1.54 | GR/100 DSCF |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | KKKK
CA-1174 | EL CAJON ENERGY LLC | EL CAJON ENERGY LLC | SAN DIEGO | CA | 92020 | USA | GENEVIEVE HUFFMAN |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Evariste Haury (858)-586-2745 Evariste.Haury@sdcounty.ca.gov | 987824 | 519 | 311999 | 110043330106 | 11/01/2008 &nbsp;ACT | 12/11/2009 &nbsp;ACT | 2010-09-20 | 2011-04-11 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 49.95 | MW |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxydation catalyst | 2 | PPMV | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1175 | ESCONDIDO ENERGY CENTER LLC |  | SAN DIEGO | CA | 92029 | USA |  |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Arthur Carbonell (858)-586-2741 arthur.carbonell@sdcounty.ca.gov | 985693 | 491 | 221122 | UNKNOWN | &nbsp; | 07/02/2008 &nbsp;ACT | 2010-09-21 | 2011-06-27 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 46.5 | MW |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxydation catalyst | 2 | PPMV@15% OXYGEN | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1176 | ORANGE GROVE PROJECT |  | SAN DIEGO | CA | 92059 | USA |  |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Camqui Nguyen (858)586-2747 camqui.nguyen@sdcounty.ca.gov | 985708 | 491 | 221122 | UNKNOWN | 11/03/2007 &nbsp;ACT | 12/04/2008 &nbsp;ACT | 2010-09-21 | 2011-06-27 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 49.8 | MW | Combustion turbine for peaking power plant | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation catalyst | 2 | PPM | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055426409 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Three simple cycle combustion turbines | 15.11 | natural gas | 799.7 | MMBTU/H | Three GE, LMS100PA, natural gas-fired, simple cycle CTG rated at 799.7 MMBtu per hour each,based on HHV. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Good Combustion Control and Catalytic Oxidation (CatOx) | 2.5 | PPMVD AT 15% O2 | AVE OVER STACK TEST LENGTH | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0346 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-011-AC | 4911 | 221112 | 110002044065 | 11/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-01-08 | 2016-05-05 | D | http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | In this project, 24 peaking turbines from the Lauderdale facility are being replaced with five 200 MW combustion turbines at Lauderdale. The turbines will fire primarily natural gas, but may also fire ULSD fuel oil. Triggers PSD for NOx, PM, CO, VOC, and GHG. GHG permit issued by US EPA Region 4. Technical evaluation available at http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2000 | MMBtu/hr (approx) | Throughput could vary slightly (+/- 120 MMBtu/hr) depending on final selection of turbine model and firing of natural gas or oil. Primary fuel is expected to be gas. Each turbine limited to 3300 hrs per rolling 12-month period. Of these 3300 hrs, no more than 500 may use ULSD fuel oil. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 320 | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practice | 3.77 | LB/H | THREE ONE-HR RUNS (NATURAL GAS) | BACT-PSD |  | U | 0 | U | 8 | LB/H | THREE ONE-HR RUNS (OIL) | 0 |  |  | 0 | 0 | N |  | Initial and annual stack tests required.
GA-0139 | DAHLBERG COMBUSDTION TURBINE ELECTRIC GENERATING FACILITY (P | SOUTHERN POWER COMPANY | JACKSON | GA | 30565 | USA | MR. E.S. (SCOTT) DIAL | 704 278-6601 | ESDIAL@SOUTHERNCO.COM | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-157-0034-V-04-1 | 4911 | 221112 | UNKNOWN | 07/10/2008 &nbsp;ACT | 05/14/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | C |  | PLANT DAHLBERG HAS PROPOSED TO CONSTRUCT AND OPERATE FOUR ADDITIONAL SIMPLE-CYCLE COMBUSTION TURBINES (SOURCE CODES: CT11-CT14) AND ONE FUEL OIL STORAGE TANK. THE PROPOSED PROJECT WILL HAVE A NOMINAL GENERATING CAPACITY OF 760 MW. THE FACILITY IS CURRENTLY PERMITTED TO OPERATE 10 DUAL-FUELED SIMPLE-CYCLE CTG's. AFTER THE EXPANSION, THE FACILITY WILL HAVE A TOTAL NOMINAL GENERATING CAPACITY OF 1530 MW. |  | SIMPLE CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.11 | NATURAL GASE | 1530 | MW | THE PROCESS USES FUEL OIL FOR BACKUP AT THE RATE OF 2129 MMBUT/H | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 5 | PPM@15%02 | 3 HOUR AVERAGE/CONTITION 3.3.24 | BACT-PSD | OPERATING PERMIT | U | 0 | N | 5 | PPM@15%02 | 3 HOUR AVERAGE/CONDITION 3.3.28 | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER | 15.11 | NATURAL GAS | 92.5 | MMBTU/H | NATURAL GAS USAGE SHALL NOT EXCEED 18.14 MMCF/YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | PROPER DESIGN AND GOOD COMBUSTION PRACTICES | 5.5 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER | 15.11 | NATURAL GAS | 92.5 | MMBTU/H | NATURAL GAS USAGE SHALL NOT EXCEED 18.14 MMCF/YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | PROPER DESIGN AND GOOD COMBUSTION PRACTICES | 5.5 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0261 | VERMILLION GENERATING STATION | DUKE ENERGY INDIANA, LLC VERMILLION GENERATING STA | VERMILLION | IN | 47928 | USA | PATRICK COUGHLIN | 3178382108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIP SINHA PH.D. 317-234-4907 | 165-36956-00022 | 4911 | 221112 | 110006010921 | 03/16/2016 &nbsp;ACT | 02/28/2017 &nbsp;ACT | 2017-07-07 | 2017-08-09 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36956F.PDF | ELECTRIC UTILITY SERVICES |  | SIMPLE CYCLE, NATURAL GAS FIRED COMBUSTION TURBINES | 15.11 | NATURAL GAS | 80 | MW |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 17.6 | LB/H | EACH TURBINE | BACT-PSD |  | N | 0 |  | 1.76 | TON/12 CONSEC. MONTH | COMPLIANCE DETERMINED END OF EACH MONTH | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: ONLY TWO TURBINES WILL OPERATE DURING LOW LOAD OPERATION
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE LM6000PC SPRINT Simple cycle combustion turbine | 15.11 | Pipeline quality natural gas | 405.3 | MMBTU/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | utilize efficient combustion/design technology | 5.8 | LB/HR | AT FULL LOAD | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE 7FA Simple Cycle Combustion Turbine | 15.11 | Pipeline quality natural gas | 1780 | MMBTU/HR |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | will utilize efficient combustion/design technology | 3.2 | LB/HR | AT FULL LOAD | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0224 | ARSENAL HILL POWER PLANT | SOUTHWEST ELECTRIC POWER COMPANY (SWEPCO) | CADDO | LA | 71101 | USA | KRIS GAUS | 2147771113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-726 | 4911 | 221112 | 110001270847 | 01/07/2008 &nbsp;ACT | 03/20/2008 &nbsp;ACT | 2008-04-18 | 2012-05-18 | B |  | NATURAL GAS FIRED ELECTRICAL GENERATION PLANT. |  | SCN-3 COLD STARTUP CTG-1 SCN-7 COLD STARTUP CTG-2 | 15.11 | NATURAL GAS | 2110 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N | COMPLETE EVENTS AS QUICKLY AS POSSIBLE ACCORDING TO MANUFACTUREÂ¿S RECOMMENDED PROCEDURES. | 214.07 | LB/H | MAX | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Refrigeration Compressor Turbines (16) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices and fueled by natural gas | 0.66 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110030770351 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Generation Turbines (2) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices and fueled by natural gas | 0.66 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0258 | CALCASIEU PLANT | ENTERGY GULF STATES LA LLC | CALCASIEU | LA | 70665 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: TEGAN TREADAWAY, (225) 219-3408 | PSD-LA-746 | 4911 | 221112 | 110007042565 | 11/10/2009 &nbsp;ACT | 12/21/2011 &nbsp;ACT | 2012-02-01 | 2012-04-03 | C |  | 320 MW POWER PLANT COMPRISED OF 2 NATURAL GAS-FIRED SIMPLE CYCLE COMBUSTION TURBINES. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS PSD TRIGGERED DUE TO RELAXATION OF A FEDERALLY-ENFORCEABLE CONDITION LIMITING POTENTIAL EMISSIONS BELOW MAJOR STATIONARY SOURCE THRESHOLDS. | TURBINE EXHAUST STACK NO. 1 &amp; NO. 2 | 15.11 | NATURAL GAS | 1900 | MM BTU/H EACH |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | DRY LOW NOX COMBUSTORS | 7 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 132 | LB/H | HOURLY MAXIMUM / STARTUP & SHUTDOWN ONLY | 3 | PPMVD @ 15% O2 |  | 0 | 0 | N |  | LIMITS ARE PER TURBINE EXHAUST STACK. AGGREGATE VOC EMISSIONS FROM BOTH TURBINE EXHAUST STACKS ARE LIMITED TO 45.24 TONS PER YEAR. STARTUP & SHUTDOWN OPERATIONS ARE LIMITED TO 520 HOURS PER YEAR.
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Gas Turbines (8 units) | 15.11 | natural gas | 333 | mm btu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices and fueled by natural gas | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110029511883 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices and fueled by natural gas | 1.6 | PPMVD | @15%O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0333 | DAYTON POWER & LIGHT ENERGY LLC | DAYTON POWER & LIGHT COMPANY | MONTGOMERY | OH | 45439 | USA | CARRIE BURKS | 937-331-3042 |  | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104867 | 4911 | 221112 | 110000394145 | 04/30/2009 &nbsp;ACT | 12/03/2009 &nbsp;ACT | 2010-05-13 | 2010-05-20 | C |  | Seven simple cycle stationary combustion turbines all with rating of 80 MW and nominal heat input of 1115.2 mmBtu/hr using natural gas or No. 2 fuel oil and all with water injection control and last 5 also with low NOx burners. | Simple cycle stationary combution turbines issed in 2 different permits. Four turbines in this permit with dry low NOx combustion and water injection controls. Administrative Modification to original PTI #08-04153 issued 8/7/01, to incorporate low mass emissions methodology as allowed per 40 CFR 75.19 in lieu of methods under Appendix D or E to Part 75, by meeting the requirements of having mass emissions of less than 25 T/YR SO2 and less than 100 T/YR NOx (per turbine) based on 3 years of operation. Modification also reduced permitted formaldehyde emissions by 8.7 tons, recalculated based on the restriction on hours of operation. | Turbines (4), simple cycle, natural gas | 15.11 | NATURAL GAS | 15020 | H/YR | Hours per year for all 4 turbines | Volatile Organic Compounds (VOC) | Other - Method 25 or 25A | (Volatile Organic Compounds (VOC)) | VOC | N |  | 4 | LB/H | EACH TURBINE | BACT-PSD | SIP | U | 0 | Y | 31.64 | T/YR | PER ROLLING 12-MO. FOR 4 UNITS &ALL FUEL | 0 |  |  | 0 | 0 | N |  | T/YR limit is for both fuels and for the 4 turbines combined.
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | GE LMS-100 combustion turbines, simple cycle with water injection | 15.11 | natural gas | 1690 | MMBTU/H |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation catalyst; Limit the time in startup or shutdown. | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
SC-0161 | DUKE ENERGY CAROLINAS LLC, W.S. LEE STEAM STATION |  | ANDERSON | SC | 29627 | USA |  | SYSNULL |  | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MR. DENNIS CAMIT | (803)898-4284 | camitdr@dhec.sc.gov | SHEILA WATTS (803) 898-4123 | 0200-0004-CG | 4911 | 221112 | 110004937864 | 01/16/2013 &nbsp;ACT | 02/19/2014 &nbsp;ACT | 2015-08-25 | 2017-07-24 | B |  |  |  | COMBINED CYCLE COMBUSTION TURBINES (SIEMENS) | 15.11 |  | 0 |  | THE FACILITY PLANS TO INSTALL EITHER TWO GE 7FA.05 OR TWO SIEMENS SGT-5000F(5) NATURAL GAS FIRED COMBUSTION TURBINE GENERATORS, EACH EQUIPPED WITH A DUCT-FIRED HEAT RECOVERY STEAM GENERATOR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDATION CATALYST | 3 | LB/H | CONTINUOUS OPERATION WITHOUT DUCT BURNER | BACT-PSD |  |  | 0 |  | 203 | LB/H | AVERAGE PER STARTUP AND SHUTDOWN EVENT | 1 | PPMVD @ 15% O2 | CONTINUOUS OPERATION WITHOUT DUCT BURNER | 0 | 0 | N |  | THERE ARE ALSO VOC EMISSON LIMITS ASSOCIATED WITH DUCT BURNERS (CONTINUOUS OPERATION) WHICH ARE 2.0 PPMVD @15% O2 AND 7.7 LB/HR.
SC-0161 | DUKE ENERGY CAROLINAS LLC, W.S. LEE STEAM STATION |  | ANDERSON | SC | 29627 | USA |  | SYSNULL |  | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MR. DENNIS CAMIT | (803)898-4284 | camitdr@dhec.sc.gov | SHEILA WATTS (803) 898-4123 | 0200-0004-CG | 4911 | 221112 | 110004937864 | 01/16/2013 &nbsp;ACT | 02/19/2014 &nbsp;ACT | 2015-08-25 | 2017-07-24 | B |  |  |  | COMBINED CYCLE COMBUSTION TURBINES (GE) | 15.11 |  | 0 |  | THE FACILITY PLANS TO INSTALL EITHER TWO GE 7FA.05 OR TWO SIEMENS SGT-5000F(5) NATURAL GAS FIRED COMBUSTION TURBINE GENERATORS, EACH EQUIPPED WITH A DUCT-FIRED HEAT RECOVERY STEAM GENERATOR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDATION CATALYST | 2.8 | LB/H | CONTINUOUS OPERATION WITHOUT DUCT BURNER | BACT-PSD |  |  | 0 |  | 133.3 | LB/H | AVERAGE PER STARTUP AND SHUTDOWN EVENT | 1 | PPMVD @ 15% O2 | CONTINUOUS OPERATION WITHOUT DUCT BURNER | 0 | 0 | N |  | THERE ARE ALSO VOC EMISSON LIMITS ASSOCIATED WITH DUCT BURNERS (CONTINUOUS OPERATION) WHICH ARE 2.0 PPMVD @15% O2 AND 7.1 LB/HR.
TX-0540 | BOSQUE COUNTY POWER PLANT | BOSQUE POWER COMPANY LLC | BOSQUE | TX | 76644 | USA | MS KATHY FRENCH | 6365322200 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | MS. BRIDGET MALONE (512) 239-4286 | 40620 | 4911 | 221112 | 4803500002 | 10/26/2007 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | PSDTX931M1 | ELECTRICAL GENERATION | 15.11 | NATURAL GAS | 170 | MW | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | BACT IS THE USE OF GOOD COMBUSTION PRACTICES TO MINIMIZE THE PRODUCTS OF INCOMPLETE COMBUSTION OF THE NATURAL GAS TO ACHIEVE LESS THAN 4 PPMV OVER A ROLLING 3-HOUR PERIOD. | 4 | PPMVD | 3 HOUR | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057188626 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.11 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane and methane section compressors. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0.6 | LB/H | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0696 | ROANâ€™S PRAIRIE GENERATING STATION | TENASKA ROANâ€™S PRAIRIE PARTNERS (TRPP), LLC | GRIMES | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 erik.hendrickson@tceq.texas.gov | 114698 PSDTX1378 | 4911 | 221112 | 110028050141 | 10/25/2013 &nbsp;ACT | 09/22/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | The proposed project is to construct and operate the RPGS comprised of three new simple cycle combustion turbine generators (CTG), fueled by pipeline quality natural gas. The new CTGs will be peaking units, designed to operate during periods of high electric demand. The three CTGs will produce between 507 and 694 MW of electricity combined, depending on ambient temperature and the model of combustion turbine (CT) selected. The applicant is considering three models of CTs; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. |  | (2) simple cycle turbines | 15.11 | natural gas | 600 | MW | The three possible CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. will operate 2,920 hours per year at full load for each CT | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion | 1.4 | PPMVD | @15% O2 GE OPTION | BACT-PSD |  | N | 0 | U | 1 | PPMVD | @15% O2 SIEMENS OPTION | 0 |  |  | 0 | 0 | N
TX-0733 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JOLLY HAYDEN | 806-349-5250 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, (512)239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358M1 | 4911 | 221112 | 110043432737 | 03/20/2015 &nbsp;ACT | 05/12/2015 &nbsp;ACT | 2015-05-04 | 2016-06-08 | B |  | Golden Spread Electric Cooperative, Inc. (GSEC) is requesting authorization for three additional simple cycle electric generating plants at an existing site to meet increased energy demand in the area. The generating equipment consists of three new GE 7F5-Series natural gas-fired combustion turbine generators (CTGs). Each turbine has a maximum electric output of 202 MW. |  | Simple Cycle Turbine &amp; Generator | 15.11 | natural gas | 202 | MW | 3 additional GE 7F 5-Series Combustion Turbine Generators | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 2 | PPMVD @ 15% O2 |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of each turbine is limited to 4,572 hours per year
TX-0764 | NACOGDOCHES POWER ELECTRIC GENERATING PLANT | NACOGDOCHES POWER, LLC | NACOGDOCHES | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem 512-239-1310 Tzvi.shalem@tceq.texas.gov | 77679, PSDTX1061M1 & O-3455 | 4911 | 221112 | 110043814744 | 06/25/2015 &nbsp;ACT | 10/14/2015 &nbsp;ACT | 2015-09-16 | 2016-07-06 | B |  | Nacogdoches Power, LLC is requesting authorization for one natural gas fired, simple cycle combustion turbine generator (CTG). The CTG will be a Siemens F5 and have a nominal electric output of 232 megawatts (MW). |  | Natural Gas Simple Cycle Turbine (&gt;25 MW) | 15.11 | natural gas | 232 | MW | One Siemens F5 simple cycle combustion turbine generator | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Pipeline quality natural gas; limited hours; good combustion practices. | 2 | PPMVD @ 15% O2 |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,500 hours on a 12-month rolling average.
TX-0768 | SHAWNEE ENERGY CENTER | SHAWNEE ENERGY CENTER, LLC | HILL | TX |  | USA | NEIL O'DONOVAN | 312-422-1608 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, P.E., 512-239-1353, joseph.janecka@tceq.texas.gov | PSDTX1442, 125963 | 4911 | 221112 | UNKNOWN | 07/31/2015 &nbsp;ACT | 10/09/2015 &nbsp;ACT | 2015-10-05 | 2016-07-06 | A |  | Electric Generating Utility: The project will consist of four gas fired combustion turbines (CTGs). The CTGs are fueled with pipeline quality natural gas and will operate in simple cycle mode. The gas turbines will be one of two options. |  | Simple cycle turbines greater than 25 megawatts (MW) | 15.11 | natural gas | 230 | MW | Siemens Model SGT6-5000 F5ee â€“ 230 MW or Second turbine option: General Electric Model 7FA.05TP â€“ 227 MW | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Pipeline quality natural gas; limited hours; good combustion practices. | 1.4 | PPMV |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,920 hours on a 12-month rolling average.
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110064514903 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Large Combustion Turbines &gt; 25 MW | 15.11 | natural gas | 232 | MW | 4 Simple cycle CTGs, 2,500 hr/yr operational limitation. Facility will consist of either 232 MW (Siemens) or 220 MW (GE) | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 2 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | SUBPARTS KKKK AND TTTT
TX-0794 | HILL COUNTY GENERATING FACILITY | BRAZOS ELECTRIC COOPERATIVE | HILL | TX |  | USA | MIKE MEYERS | (254)750-6228 | MMEYERS@BRAZOSELECTRIC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512)239-1512, randy.hamilton@tceq.texas.gov | 130051,PSDTX1450, GHGPSDTX131 | 4911 | 221112 | UNKNOWN | 12/18/2015 &nbsp;ACT | 04/07/2016 &nbsp;ACT | 2016-04-05 | 2016-07-29 | A |  | Four simple cycle combustion turbine electric generators are proposed. Natural gas or ultra-low sulfur diesel fuel oil are the fuels. Turbine model options are: General Electric (GE) 7FA.03, GE 7FA.04, GE 7FA.05, and Siemes SGT6-5000(5)ee. Electric output is between 684 and 928 megawatts (MW). |  | Simple cycle turbine | 15.11 | natural gas | 171 | MW | Each combustion turbine is limited to 2,920 hours of annual operation, including startup and shutdown hours. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | Premixing of fuel and air enhances combustion efficiency and minimizes emissions. | 5.4 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0816 | CORPUS CHRISTI LIQUEFACTION | CORPUS CHRISTI LIQUEFACTION STAGE III, LLC | SAN PATRICIO | TX |  | USA | KEITH LITTLE | (713) 375-5204 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 139479, PSDTX1496, GHGPSDTX157 | 4925 | 221210 | Not Found | 11/16/2016 &nbsp;ACT | 02/14/2017 &nbsp;ACT | 2017-02-07 | 2018-04-18 | B |  | Trains 4 and 5 will consist of 12 natural gas compressor turbines, 2 thermal oxidizers, 2 sets of flares each comprised of one wet gas flare and one dry gas flare, 2 amine surge tanks (maintenance, startup, and shutdown [MSS] only), 3 diesel generators, 3 fire-water pump diesel engines, 6 fixed roof diesel storage tanks, and piping components. |  | Refrigeration compressor turbines | 15.11 | NATURAL GAS | 40000 | HP | 2 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane, ethylene, and methane section compressors. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 0.68 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Simple Cycle Turbine | 15.11 | natural gas | 227.5 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Pipeline quality natural gas; limited hours; good combustion practices | 2 | PPMVD | 145% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 2 | PPMVD |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines MSS | 15.11 | NATURAL GAS | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Minimizing duration of startup/shutdown, using good air pollution control practices and safe operating practices. | 0.06 | TON/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP03) | 15.11 | Natural Gas | 40 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 3 | PPMV AT 15% O2 | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 3 | LB/H | 3-HOUR AVERAGE | 14 | T/YR |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Trubine (EP04) | 15.11 | Natural Gas | 40 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 3 | PPMV AT 15% O2 | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 3 | LB/H | 3-HOUR AVERAGE | 14 | T/YR |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP05) | 15.11 | Natural Gas | 40 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 3 | PPMV AT 15% O2 | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 3 | LB/H | 3-HOUR AVERAGE | 14 | T/YR |  | 0 | 0 | N