## CO2e_Large Simple Cycle Gas-Fir
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
TX-0735 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JOLLY HAYDEN | 806-349-5250 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, (512)239-2175, laura.gibson@tceq.texas.gov | GHGPSDTX41M1 | 4911 | 221112 | 110043000000 | 04/02/2015 &nbsp;ACT | 05/20/2015 &nbsp;ACT | 2015-05-14 | 2018-04-18 | B |  | Golden Spread Electric Cooperative, Inc. (GSEC) is requesting authorization for three additional simple cycle electric generating plants at an existing site to meet increased energy demand in the area. The generating equipment consists of three new GE 7F5-Series natural gas-fired combustion turbines (CTG). Each turbine has a maximum electric output of 202 MW. |  | Simple Cycle Turbine &amp; Generator | 15.11 | natural gas | 202 | MW | 3 additional GE 7F 5-Series Combustion Turbine Generators | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency, good design & combustion practices | 1304 | LB CO2/MWHR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of each turbine is limited to 4,572 hours per year
TX-0753 | GUADALUPE GENERATING STATION | GUADALUPE POWER PARTNERS, L.P. | GUADALUPE | TX | 78124 | USA | BILL SKINNER | 281-252-5221 | BSKINNER@NAVASOTAENERGY.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Melanie Magee, EPA Region 6, Air Permits Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | PSD-TX-1310-GHG | 4911 | 221112 | 110021000000 | 10/24/2014 &nbsp;ACT | 12/02/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | B | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | GPP proposes to add two (2) new gas-fired simple-cycle combustion turbines of 227 MW (nominal) electric generating capacity each to the 1,000 MW (nominal) existing major stationary source, Guadalupe Generating Station (GGS), located in Marion, Texas. The proposed project will provide peaking capacity at an existing natural gas fired combined cycle electric generating station. The two new natural gas-fired simple-cycle turbines are proposed to provide a fast ramp up for additional peaking capacity during peak electricity demand periods. In addition, the project also includes the installation of a firewater pump engine, circuit breakers and associated fugitive emissions. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. See CN600132120 and RN100225820 | Simple Cycle Combustion Turbine Generator | 15.11 | Pipeline Natural Gas | 10673 | Btu/kWh | Natural gas-fired simple cycle combustion turbine generators (CTG) will be General Electric 7FA.05 (GE 7FA.05), each with a maximum base-load electric power output of 227 megawatts (MW, nominal). Combined gross heat rate limit of 10,279,456 MMBtu/yr. | Carbon Dioxide Equivalent (CO2e) | Other - 40 CFR 60.8; Method 3a or 3b | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1293.3 | LB CO2/MWHR (GROSS) | 12-MONTH ROLLING AVERAGE (NORMAL OPER) | BACT-PSD |  | U | 0 | U | 20.8 | TONS CO2/HR | 12-MONTH ROLLING AVERAGE BASIS (MSS OPER | 0 |  |  | 0 | 0 | N |  | BACT limits above are for each CT. The two new turbines have a combined limit of 5,000 hours of operation (including MSS) on a 12-month rolling total basis. Both CT are limited to 300 combined hours of start and 300 combined hours of shutdown on a 12-month rolling total basis. Stack Testing Requirements: initial compliance with the CO2 emission limits. Shall be conducted in accordance with 40 CFR 60.8 and Method 3a or 3b. Emission testing for the CT shall be performed every 5 years, plus or minus 6 months to verify continued performance at permitted emission limits.
TX-0753 | GUADALUPE GENERATING STATION | GUADALUPE POWER PARTNERS, L.P. | GUADALUPE | TX | 78124 | USA | BILL SKINNER | 281-252-5221 | BSKINNER@NAVASOTAENERGY.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Melanie Magee, EPA Region 6, Air Permits Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | PSD-TX-1310-GHG | 4911 | 221112 | 110021000000 | 10/24/2014 &nbsp;ACT | 12/02/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | B | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | GPP proposes to add two (2) new gas-fired simple-cycle combustion turbines of 227 MW (nominal) electric generating capacity each to the 1,000 MW (nominal) existing major stationary source, Guadalupe Generating Station (GGS), located in Marion, Texas. The proposed project will provide peaking capacity at an existing natural gas fired combined cycle electric generating station. The two new natural gas-fired simple-cycle turbines are proposed to provide a fast ramp up for additional peaking capacity during peak electricity demand periods. In addition, the project also includes the installation of a firewater pump engine, circuit breakers and associated fugitive emissions. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. See CN600132120 and RN100225820 | Simple Cycle Combustion Turbine Generator | 15.11 | Pipeline Natural Gas | 10673 | Btu/kWh | Natural gas-fired simple cycle combustion turbine generators (CTG) will be General Electric 7FA.05 (GE 7FA.05), each with a maximum base-load electric power output of 227 megawatts (MW, nominal). Combined gross heat rate limit of 10,279,456 MMBtu/yr. | Carbon Dioxide Equivalent (CO2e) | Other - 40 CFR 60.8; Method 3a or 3b | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1293.3 | LB CO2/MWHR (GROSS) | 12-MONTH ROLLING AVERAGE (NORMAL OPER) | BACT-PSD |  | U | 0 | U | 20.8 | TONS CO2/HR | 12-MONTH ROLLING AVERAGE BASIS (MSS OPER | 0 |  |  | 0 | 0 | N |  | BACT limits above are for each CT. The two new turbines have a combined limit of 5,000 hours of operation (including MSS) on a 12-month rolling total basis. Both CT are limited to 300 combined hours of start and 300 combined hours of shutdown on a 12-month rolling total basis. Stack Testing Requirements: initial compliance with the CO2 emission limits. Shall be conducted in accordance with 40 CFR 60.8 and Method 3a or 3b. Emission testing for the CT shall be performed every 5 years, plus or minus 6 months to verify continued performance at permitted emission limits.
TX-0758 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX | 79741 | USA | MATTHEW THORNTON | 312-582-1527 | MTHORNTON@INVENERGYLLC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | EPA Region 6 Permit Writer: Anna Milburn, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | GHGPSDTX1366 | 4911 | 221112 | Not Assigned | 04/18/2014 &nbsp;ACT | 08/01/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | A | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | Invenergy proposes to construct a 330 MW peak power plant (known as the Ector County Energy Center Plant (ECEC)), located in Goldsmith, Ector County, Texas. With this proposed project, Invenergy plans to construct two natural gas-fired simple-cycle turbines, General Electric (GE) Model 7FA.03, and associated equipment, a fire water pump engine, a natural gas-fired dew-point heater, and two circuit breakers. For the purposes of this proposed permitting action, GHG emissions are permitted for the two turbines, the fire water pump engine, the natural gas-fired dew-point heater, and the circuit breakers, as well as for fugitive emissions, and maintenance, startup and shutdown emissions. | Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. | Simple Cycle Combustion Turbine, GE 7FA.03 | 15.11 | Natural Gas | 11707 | Btu/kWh (HHV) |  | Carbon Dioxide Equivalent (CO2e) | Other - 40 CFR 60.8; Method 3A or 3B | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1393 | LB CO2/MWHR (GROSS) | 2500 OPERATIONAL HR ROLLING DAILY/CT | BACT-PSD |  | U | 0 | U | 239649 | TPY CO2E | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | an emission limit of 1,393 lb CO2/MWhr gross output for the GE7FA.03 combustion turbine to be utilized for this project. Each combustion turbine is limited to 2,500 operational hours on a rolling basis, plus 500 startup and shutdown events on a 12â€“month rolling average. Until the 2,500 operational hour basis has been established, Invenergy should utilize the performance testing data to establish a plan whereby Invenergy may operate the emission unit in a manner that will not exceed the permitted CO2e emissions limits. To account for the additional hours of operation associated with the startup and shutdowns, each turbine is limited by fuel use associated with the 2,500 hours of operation per year. Limiting the fuel use achieves the same objective as limiting the number of hours of operation of each turbine to 2,500 hours. The fuel use limit for each combustion turbine that corresponds to the 2,500 hours of operation per 365 day basis is 4,028,700 MMBtu (HHV) on a 12-month rolling basis for the GE7FA.03 combustion turbine. An initial stack test demonstration will be required for CO2 emissions from each emission unit. An initial stack test demonstration for CH4 and N2O emissions are not required because the CH4 and N2O emission are less than 0.01% of the total CO2e emissions from the CTGs
TX-0757 | INDECK WHARTON ENERGY CENTER | INDECK WHARTON, LLC | WHARTON | TX | 77432 | USA | JAMES SCHNEIDER | 847-520-3212 | JSCHNEIDER@INDECKENERGY.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Jennifer Huser, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | PSD-TX-1374-GHG | 4911 | 221112 | Not Assigned | 04/05/2014 &nbsp;ACT | 05/12/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | A | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | Indeck proposes to construct a peaking power plant, the Indeck Wharton Energy Center, generally located south of Danevang, Texas. To meet the anticipated demand for peak power, Indeck proposes to construct three identical natural gas-fired F-class simple cycle combustion turbines with associated support equipment. Indeck proposes that the three new combustion turbine generators (CTGs) will be either General Electric (GE) 7FA.05 or Siemens SGT6-5000F(5). The GE 7FA.05 has a base-load electric power output of approximately 213 megawatts (MW, net nominal), and the Siemens SGT6-5000F(5) has a base-load electric power output of approximately 225 MW (net nominal). This project also proposes to install one emergency diesel generator, one diesel fire water pump, one natural gas pipeline heater, and other auxiliary equipment. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. | Simple Cycle Combustion Turbine, GE 7FA.05 | 15.11 | Pipeline Natural Gas | 0 |  | Indeck proposes to construct three identical natural gas-fired F-class simple cycle combustion turbines with associated support equipment. Indeck proposes that the three new combustion turbine generators (CTGs) will be either General Electric (GE) 7FA.05 or Siemens SGT6-5000F(5). The GE 7FA.05 has a base-load electric power output of approximately 213 megawatts (MW, net nominal), and the Siemens SGT6-5000F(5) has a base-load electric power output of approximately 225 MW (net nominal). | Carbon Dioxide Equivalent (CO2e) | Other - 40 CFR 60.8; Method 3A or 3B | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1276 | LB CO2/MWHR (GROSS) | 2,500 OPERATIONAL HR ROLLING DAILY/CT | BACT-PSD |  | U | 0 | U | 321028 | TPY CO2E | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N |  | GHG BACT for Indeck is the use of modern natural gas-fired, thermally efficient simple cycle combustion turbines combined with evaporative cooling and good combustion and maintenance practices to maintain optimum efficiency. The GE FA7.05 or Siemens SGT6-5000F(5) turbines are consistent with the BACT requirement and the specific goal of this project. EPA is proposing an emission limit of 1,276 lb CO2/MWhr gross output on a 2,500 operational hour rolling basis for the GE 7FA.05 combustion turbine. Each combustion turbine is limited to 2,500 hours of operation, plus 300 startup and shutdown events on a 12-month rolling basis. To account for the additional hours of operation associated with the startup and shutdowns, each turbine is limited by fuel use associated with the 2,500 hours of operation per year. Limiting the fuel use achieves the same objective as limiting the number of hours of operation of each turbine to 2,500 hours. The fuel use limit for each combustion turbine that corresponds to the 2,500 hour of operation on a 12-month rolling basis is 5,394,500 MMBtu (HHV) on a 12-month rolling basis for the GE 7FA.05 combustion turbine. An initial stack test demonstration will be required for CO2 emissions from each emission unit. An initial stack test demonstration for CH4 and N2O emissions are not required because the CH4 and N2O emissions are less than 0.01% of the total CO2e emissions from the CTGs.
TX-0757 | INDECK WHARTON ENERGY CENTER | INDECK WHARTON, LLC | WHARTON | TX | 77432 | USA | JAMES SCHNEIDER | 847-520-3212 | JSCHNEIDER@INDECKENERGY.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Jennifer Huser, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | PSD-TX-1374-GHG | 4911 | 221112 | Not Assigned | 04/05/2014 &nbsp;ACT | 05/12/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | A | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | Indeck proposes to construct a peaking power plant, the Indeck Wharton Energy Center, generally located south of Danevang, Texas. To meet the anticipated demand for peak power, Indeck proposes to construct three identical natural gas-fired F-class simple cycle combustion turbines with associated support equipment. Indeck proposes that the three new combustion turbine generators (CTGs) will be either General Electric (GE) 7FA.05 or Siemens SGT6-5000F(5). The GE 7FA.05 has a base-load electric power output of approximately 213 megawatts (MW, net nominal), and the Siemens SGT6-5000F(5) has a base-load electric power output of approximately 225 MW (net nominal). This project also proposes to install one emergency diesel generator, one diesel fire water pump, one natural gas pipeline heater, and other auxiliary equipment. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. | Simple Cycle Combustion Turbine, SGT-5000F(5) | 15.11 | Pipeline Natural Gas | 0 |  | Indeck proposes to construct three identical natural gas-fired F-class simple cycle combustion turbines with associated support equipment. Indeck proposes that the three new combustion turbine generators (CTGs) will be either General Electric (GE) 7FA.05 or Siemens SGT6-5000F(5). The GE 7FA.05 has a base-load electric power output of approximately 213 megawatts (MW, net nominal), and the Siemens SGT6-5000F(5) has a base-load electric power output of approximately 225 MW (net nominal). | Carbon Dioxide Equivalent (CO2e) | Other - 40 CFR 60.8, Method 3A or 3B | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1337 | LB CO2/MWHR (GROSS) | 2500 OPERATIONAL HR ROLLING DAILY/CT | BACT-PSD |  | U | 0 | U | 358529 | TPY CO2E | 12-MONTH ROLLING | 0 |  |  | 0 | 0 | N |  | GHG BACT for Indeck is the use of modern natural gas-fired, thermally efficient simple cycle combustion turbines combined with evaporative cooling and good combustion and maintenance practices to maintain optimum efficiency. The GE FA7.05 or Siemens SGT6-5000F(5) turbines are consistent with the BACT requirement and the specific goal of this project. EPA is proposing an emission limit of 1,337 lb CO2/MWhr gross output for the Siemens SGT6-5000F(5) combustion turbine on a 2,500 operational hour rolling basis. Each combustion turbine is limited to 2,500 hours of operation, plus 300 startup and shutdown events on a 12-month rolling basis. To account for the additional hours of operation associated with the startup and shutdowns, each turbine is limited by fuel use associated with the 2,500 hours of operation per year. Limiting the fuel use achieves the same objective as limiting the number of hours of operation of each turbine to 2,500 hours. The fuel use limit for each combustion turbine that corresponds to the 2,500 hour of operation on a 12-month rolling basis is 5,394,500 MMBtu (HHV) on a 12-month rolling basis for the GE 7FA.05 combustion turbine, or 6,024,650 MMBtu (HHV) on a 12-month rolling basis for the Siemens SGT6-5000F(5). An initial stack test demonstration will be required for CO2 emissions from each emission unit. An initial stack test demonstration for CH4 and N2O emissions are not required because the CH4 and N2O emissions are less than 0.01% of the total CO2e emissions from the CTGs.
FL-0355 | FORT MYERS PLANT | FLORIDA POWER & LIGHT (FPL) | LEE | FL | 33905 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0710002-022-AC | 4911 | 221112 | 110000000000 | 05/12/2015 &nbsp;ACT | 09/10/2015 &nbsp;ACT | 2016-03-10 | 2016-07-06 | D | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.80831.1]&[profile=Permitting_Authorization] | Electric power plant, consists of a 6-on-2 combined-cycle unit (Units 2A through 2F) and two modern simple-cycle combustion turbines. Primary fuel is natural gas. Also includes 12 gas turbines (63 MW each) for peaking, introduced into service in 1974. This project entails decommissioning 10 of the 12 peaking turbines. They will be replaced with two new GE 7F.05 turbines, each with nominal capacity of 200 MW | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0710002.022.AC.D.ZIP | Combustion Turbines | 15.11 | Natural gas | 2262.4 | MMBtu/hr gas | Two GE 7F.05 turbines, approximately 200 MW each. Natural-gas is primary fuel. Permitted 3390 hr/yr of operation, of which no more than 500 hr may be on fuel oil. Dry Low-NOx, with wet injection for oil firing. | Carbon Dioxide Equivalent (CO2e) | Other - Fuel-use monitoring, or CO2 CEMS | (Greenhouse Gasses (GHG)) | CO2e | P | Use of low-emitting fuel and efficient turbine | 1374 | LB CO2E / MWH | FOR NATURAL GAS OPERATION | BACT-PSD | NSPS | U | 0 | U | 1874 | LB CO2E / MWH | FOR ULSD OPERATION | 0 |  |  | 0 | 0 | N |  | GHG standard is a weighted average of standards for natural gas operation and fuel oil operation. Turbines grouped together for first 36 months, 12-month rolling average. After 36 months, each individual turbine is subject to limit on a 36-month rolling average.
MD-0043 | PERRYMAN GENERATING STATION | CONSTELLATION POWER SOURCE GENERATION, INC. | HARFORD | MD | 21130 | USA | BILL LEEDY | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9136 | 4911 | 221119 | 110000000000 | 07/01/2014 &nbsp;ACT | 07/01/2014 &nbsp;ACT | 2015-07-31 | 2016-07-25 | B |  | 120 MEGAWATT SIMPLE CYCLE NATURAL GAS FIRED POWER PLANTPERRYMAN 6 PROJECT-WIDE EMISSION LIMITS: PM10 = 43.0 TONS/YR PM2.5 = 43.0 TONS/YR NOX = 58.5 TONS/YR CO2E = 430,210 TONS/YR | PERRYMAN 6 PROJECT-WIDE EMISSION LIMITS: PM10 = 43.0 TONS/YR PM2.5 = 43.0 TONS/YR NOX = 58.5 TONS/YR CO2E = 430,210 TONS/YR | (2) 60-MW SIMPLE CYCLE COMBUSTION TURBINES, FIRING NATURAL GAS | 15.11 | NATURAL GAS | 120 | MW | (2) 60-MEGAWATT PRATT & WHITNEY GAS TURBINE GENERATOR PACKAGE | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | USE OF NATURAL GAS. ENERGY EFFICIENCY DESIGN - USE OF INLET FOGGING/WET COMPRESSION, INSULATION BLANKETS TO REDUCE HEAT LOSS, AND FUEL GAS PREHEATING. | 1394 | LB CO2E/MWH | 12-MONTH ROLLING, EXCLUDING SU/SD | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057000000 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | GE LMS-100 combustion turbines, simple cycle with water injection | 15.11 | natural gas | 1690 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Thermal efficiency Clean fuels | 1707 | LB OF CO2 /GROSS MWH | 365-DAY ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 2 COMBUSTION TURBINES | 15.11 | NATURAL GAS | 130 | MW | TWO GENERAL ELECTRIC (GE) FRAME 7EA COMBUSTION TURBINES (CTS) WITH A NOMINAL NET 87.2 MEGAWATT (MW) RATED CAPACITY, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), EQUIPPED WITH DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION SYSTEM (SCR), AND OXIDATION CATALYST | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | HIGH EFFICIENCY GE 7EA CTS WITH HRSGS EQUIPPED WITH DLN1 COMBUSTORS AND EXCLUSIVE USE OF FACILITY PROCESS FUEL GAS OR PIPELINE QUALITY NATURAL GAS | 117 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 117 LB/MMBTU EMISSION LIMIT IS PER TURBINE
TX-0826 | MUSTANG STATION | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | YOAKUM | TX |  | USA | JEFF PIPPIN | 806-418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | 72579, PSDTX1080M1, GHGPSDTX13 | 4911 | 221112 | 110042000000 | 06/12/2017 &nbsp;ACT | 08/16/2017 &nbsp;ACT | 2017-07-24 | 2018-04-18 | C |  | GE7FA combustion turbine (Unit 6) to increase the hours of operation to 3000 hours per year. The turbine construction was completed the first quarter of 2013 and initial firing began on April 1, 2013. |  | Simple Cycle Turbine | 15.11 | NATURAL GAS | 162.8 | MW | Unit 6 Turbine is limited to 3000 hours per year. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Pipeline quality natural gas and good combustion practices | 120 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110065000000 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Large Combustion Turbines &gt; 25 MW | 15.11 | natural gas | 232 | MW | 4 Simple cycle CTGs, 2,500 hr/yr operational limitation. Facility will consist of either 232 MW (Siemens) or 220 MW (GE) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practiceS | 1341 | LB/MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK AND TTTT
TX-0775 | CLEAR SPRINGS ENERGY CENTER (CSEC) | NAVASOTA SOUTH PEAKERS OPERATING COMPANY II, LLC. | GUADALUPE | TX |  | USA | BILL SKINNER | 281-252-5221 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jack Coleman, 512-239-1255, jack.coleman@tceq.texas.gov | GHGPSDTX120, 120849, AND PSDTX | 4911 | 221112 | UNKNOWN | 07/03/2015 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-11-10 | 2016-07-06 | A |  | Navasota South Peakers Operating Company II LLC proposes to install three new natural gas fired combustion turbine generators (CTGs). Each CTG will be a General Electric 7FA.04 model that can produce approximately 183 Megawatts (MW) each based upon the manufacturerâ€™s projected output at baseload operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Low carbon fuel, good combustion, efficient combined cycle design | 1461 | LB/MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT, CTGs will operate at 2500 hours of operation per year at baseload.
TX-0778 | UNION VALLEY ENERGY CENTER | NAVASOTA SOUTH PEAKERS OPERATING COMPANY II, LLC. | NIXON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | GHGPSDTX117 | 4911 | 221112 | UNKNOWN | 08/10/2015 &nbsp;ACT | 12/16/2015 &nbsp;ACT | 2015-12-11 | 2016-07-06 | A |  | three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 megawatt (MW) each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1461 | LB/MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT, SIMPLE CYCLE PEAKING TURBINE
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Simple Cycle Turbine | 15.11 | natural gas | 227.5 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Pipeline quality natural gas; limited hours; good combustion practices | 1300 | LB/MW H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
CO-0075 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO |  | USA | MARK LUX | 303-568-3241 | MARK.LUX@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 13PB2245 | 4911 | 221112 | 110058000000 | 09/10/2013 &nbsp;ACT | 05/30/2014 &nbsp;ACT | 2014-10-24 | 2016-02-19 | B |  | Power generation facility |  | Turbine - simple cycle gas | 15.11 | natural gas | 375 | MMBTU/H | One (1) General Electric, simple cycle, gas turbine electric generator, Unit 6 (CT08), model: LM6000, SN: N/A, rated at 375 MMBtu per hour. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Control | 1600 | LB/MW H GROSS | ROLLING 365-DAY AVE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 193555 | TONS PER YEAR | ROLLING 365-DAY AVE | 0 |  |  | 0 | 0 | N
TX-0824 | JACKSON COUNTY GENERATING FACILITY | SOUTHERN POWER | JACKSON | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Marc Sturdivant, (512)239-1313, marc.sturdivant@tceq.texas.gov | GHGPSDTX118 | 4911 | 221112 | Not Found | 08/15/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-07-20 | 2017-11-16 | A |  | simple cycle electric generation |  | Simple Cycle Turbines | 15.11 | natural gas | 920 | MW | The facility will consist of four Siemens F5 model (~230 megawatts (MW) each for a total of 920 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | energy efficiency designs, practices, and procedures, CT inlet air cooling, periodic CT burner maintenance and tuning, reduction in heat loss, i.e., insulation of the CT, instrumentation and controls | 1316 | LB/MW HR |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
TX-0794 | HILL COUNTY GENERATING FACILITY | BRAZOS ELECTRIC COOPERATIVE | HILL | TX |  | USA | MIKE MEYERS | (254)750-6228 | MMEYERS@BRAZOSELECTRIC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512)239-1512, randy.hamilton@tceq.texas.gov | 130051,PSDTX1450, GHGPSDTX131 | 4911 | 221112 | UNKNOWN | 12/18/2015 &nbsp;ACT | 04/07/2016 &nbsp;ACT | 2016-04-05 | 2016-07-29 | A |  | Four simple cycle combustion turbine electric generators are proposed. Natural gas or ultra-low sulfur diesel fuel oil are the fuels. Turbine model options are: General Electric (GE) 7FA.03, GE 7FA.04, GE 7FA.05, and Siemes SGT6-5000(5)ee. Electric output is between 684 and 928 megawatts (MW). |  | Simple cycle turbine | 15.11 | natural gas | 171 | MW | Each combustion turbine is limited to 2,920 hours of annual operation, including startup and shutdown hours. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1434 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS TTTT
TX-0771 | SHAWNEE ENERGY CENTER | SHAWNEE ENERGY CENTER, LLC | HILL | TX |  | USA | NEIL O'DONOVAN | 312-422-1608 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, P.E., 512-239-1353, joseph.janecka@tceq.texas.gov | GHGPSDTX126, PSDTX1442, 125963 | 4911 | 221112 | UNKNOWN | 09/16/2015 &nbsp;ACT | 11/10/2015 &nbsp;ACT | 2015-11-03 | 2016-07-06 | A |  | Electric Generating Utility: The project will consist of four gas fired combustion turbines (CTGs). The CTGs are fueled with pipeline quality natural gas and will operate in simple cycle mode. The gas turbines will be one of two options. |  | Simple cycle turbines greater than 25 megawatts (MW) | 15.11 | natural gas | 230 | MW | Siemens Model SGT6-5000 F5ee â€“ 230 MW or Second turbine option: General Electric Model 7FA.05TP â€“ 227 MW | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1398 | LB/MWH |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,920 hours on a 12-month rolling average.
CA-1223 | PIO PICO ENERGY CENTER | PIO PICO ENERGY CENTER, LLC | OTAY MESA | CA | 92154 | USA | GARY CHANDLER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SD 11-01 | 4911 | 221112 | 110045000000 | 06/14/2012 &nbsp;ACT | 11/19/2012 &nbsp;ACT | 2013-03-05 | 2014-01-28 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | CONSTRUCTION OF THREE GENERAL ELECTRIC (GE) LMS100 NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 100 MW EACH. THE PROJECT WILL HAVE AN ELECTRICAL OUTPUT OF 300 MW. | NOTE: PERMIT ISSUED 11/19/2012. ENVIRONMENTAL APPEALS BOARD REMANDED THE PM BACT ANALYSIS TO REGION 9 ON 8/2/2013. FINAL PERMIT ISSUED ON 2/28/2014. ONE PETITION FILED IN 9TH CIRCUIT FEDERAL COURT CHALLENGING THE FINAL PERMIT DECISION. THIS LAWSUIT WAS DISMISSED ON 6/17/2014 IN RESPONSE TO PETITIONERSâ€™ MOTION FOR VOLUNTARY DISMISSAL. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.11 | NATURAL GAS | 300 | MW | Three simple cycle combustion turbine generators (CTG). Each CTG rated at 100 MW (nominal net). | Carbon Dioxide Equivalent (CO2e) | Other - EPA METHOD 1-4, 3A | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1328 | LB/MW-H | GROSS OUTPUT | BACT-PSD |  | U | 0 | U | 720 | H | ROLLING OPERATING HOUR AVG | 0 |  |  | 0 | 0 | N
*WV-0028 | WAVERLY POWER PLANT | PLEASANTS ENERGY LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 3046654201 | GERALD.GATTI@DYNEGY.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Steve Pursley, PE Engineer West Virginia Division of Air Quality 601-57th St., SE Charleston, WV 25304 Phone: (304) 926-0499 x1218 Fax: (304) 926-0478 steve.r.pursley@wv.gov | R14-0034A | 4911 | 221112 | 110063000000 | 11/30/2017 &nbsp;ACT | 03/13/2018 &nbsp;ACT | 2018-05-29 | 2018-05-29 | U | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/073-00022_PERM_R14-0034A.pdf | 300 MW Sinple-Cycle Peaking Plant | Modification to existing PSD Permit (R14-0034, RBLC Number WV-0027) to add &lsquo;&lsquo;advanced gas path&lsquo;&lsquo; technology to the turbines that was defined as a &lsquo;&lsquo;change in the method of operation&lsquo;&lsquo; that resulted a major modification to the turbines. | GE 7FA.004 Turbine | 15.11 | Natural Gas | 167.8 | MW | This one entry is for both turbines as they are the same. Each turbine, after this modification, is a nominal 167.8 MW GE Model 7FA.004. Has oil-fire backup. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of natural gas & use of GE 7FA.004 | 1300 | LB/MW-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 1300 | LB/MW-HR | 12 MONTH ROLLING AVERAGE | 0 | 0 | N
ND-0029 | PIONEER GENERATING STATION | BASIN ELECTRIC POWER COOPERATIVE | WILLIAMS | ND |  | USA | JERRY MENGE | 7012230441 | JMENGE@BEPC.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact. | PTC 13037 | 4911 | 221112 | 110058000000 | 02/19/2013 &nbsp;ACT | 05/14/2013 &nbsp;ACT | 2013-06-19 | 2016-11-03 | B |  | Three GE LM6000 PC SPRINT natural gas fired turbines used to generate electricity for peak periods. | The permit was for the addition of 2 turbines to the station. Since a synthetic minor limit was relaxed for the first unit, BACT was required for all three turbines. | Natural gas-fired turbines | 15.11 | Natural gas | 451 | MMBTU/H | Rating is for each turbine. | Carbon Dioxide Equivalent (CO2e) | Other - Methods in 40 CFR 75.10(a)(3) | (Greenhouse Gasses (GHG)) | CO2e | N |  | 243147 | T/12 MON ROLL TOTAL | 12 MONTH ROLLING TOTAL/EACH UNIT | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Turbines are GE LM6000 PC SPRINT units that burn natural gas with a HHV of 1200 Btu/scf. RBLC Staff: Original Emis Limit 1 Units were Numeric Limit - &lsquo;&lsquo;TONS&lsquo;&lsquo; and Avg Time/Condition - &lsquo;&lsquo;12 MONTH ROLLING TOTAL/EACH UNIT&lsquo;&lsquo; The Emission Units are usually &lsquo;&lsquo;mass unit PER time unit&lsquo;&lsquo;. Separating them out makes understanding limit difficult for the users. The units were combined. The corrected entry is: Numeric Limit - &lsquo;&lsquo;T/12 MON ROLL TOTAL&lsquo;&lsquo; Avg Time/Condition - &lsquo;&lsquo;12 MONTH ROLLING TOTAL/EACH UNIT&lsquo;&lsquo;
TX-0816 | CORPUS CHRISTI LIQUEFACTION | CORPUS CHRISTI LIQUEFACTION STAGE III, LLC | SAN PATRICIO | TX |  | USA | KEITH LITTLE | (713) 375-5204 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 139479, PSDTX1496, GHGPSDTX157 | 4925 | 221210 | Not Found | 11/16/2016 &nbsp;ACT | 02/14/2017 &nbsp;ACT | 2017-02-07 | 2018-04-18 | B |  | Trains 4 and 5 will consist of 12 natural gas compressor turbines, 2 thermal oxidizers, 2 sets of flares each comprised of one wet gas flare and one dry gas flare, 2 amine surge tanks (maintenance, startup, and shutdown [MSS] only), 3 diesel generators, 3 fire-water pump diesel engines, 6 fixed roof diesel storage tanks, and piping components. |  | Refrigeration compressor turbines | 15.11 | NATURAL GAS | 40000 | HP | 2 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane, ethylene, and methane section compressors. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1793574 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This limit is a cap for all eight turbines.
TX-0758 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX | 79741 | USA | MATTHEW THORNTON | 312-582-1527 | MTHORNTON@INVENERGYLLC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | EPA Region 6 Permit Writer: Anna Milburn, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | GHGPSDTX1366 | 4911 | 221112 | Not Assigned | 04/18/2014 &nbsp;ACT | 08/01/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | A | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | Invenergy proposes to construct a 330 MW peak power plant (known as the Ector County Energy Center Plant (ECEC)), located in Goldsmith, Ector County, Texas. With this proposed project, Invenergy plans to construct two natural gas-fired simple-cycle turbines, General Electric (GE) Model 7FA.03, and associated equipment, a fire water pump engine, a natural gas-fired dew-point heater, and two circuit breakers. For the purposes of this proposed permitting action, GHG emissions are permitted for the two turbines, the fire water pump engine, the natural gas-fired dew-point heater, and the circuit breakers, as well as for fugitive emissions, and maintenance, startup and shutdown emissions. | Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. | Simple Cycle Combustion Turbine-MSS | 15.11 | Natural Gas | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 21 | TON CO2E/EVENT | EACH MSS EVENT | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT applies during all periods of turbine operation, including startup and shutdown. MSS emissions are limited to 10,502 CO2e per year and each start up and shut down event is limited to 21 tons of CO2e. The number of startups and shutdowns is based on the number of operational hours per year (2,500 service hours per year per turbine). All startups and shutdowns are limited to 60 minutes in duration per event. A startup of each turbine is defined as the period that begins when there is measureable fuel flow to the turbine and ends when the turbine load reaches 60 percent. A shutdown of each turbine is defined as the time period that begins when the combustion turbine drops out of the normal operating low-NOx combustion mode (which equates to approximately 60% combustion turbine load) following an instruction to shut down, and ends when flame is no longer detected in the combustion turbine combustors. The proposed ECEC project is proposing 500 startups/shutdowns in addition to 2,500 operational hours per year per turbine. BACT for startup/shutdown is the work practice standard to utilize good pollution control practices, safe operating practices, and protection of the facility. â€¢ Startups and shutdowns are limited to no more than 60 minutes per event. Each start up and shutdown shall not exceed 21 tons of CO2e per event. â€¢ No more than 500 startup and shutdown events per turbine on a 12-month rolling basis. â€¢ The maximum heat input during startup shall be limited to 1,320 MMBtu/hr. â€¢ No more than one of the two simple-cycle turbines will undergo a startup and/or shutdown in any 30 minute period, except that simultaneous startups of multiple turbines within a 30 minute period may occur 52 times on a 12-month rolling basis.
ND-0030 | LONESOME CREEK GENERATING STATION | BASIN ELECTRIC POWER COOP. | MCKENZIE | ND | 58831 | USA | JERRY MENGE | (701)223-0441 |  | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact at (701) 328-5188. | PTC 13049 | 4911 | 221112 | 110057000000 | 04/05/2013 &nbsp;EST | 09/16/2013 &nbsp;ACT | 2013-09-24 | 2017-06-28 | B |  | Three natural gas fired simple cycle turbines used to generate electricity for peak power demand. The turbines are GE LM6000 PF Sprint units with a nominal capacity of 45 MW each. |  | Natural Gas Fired Simple Cycle Turbines | 15.11 | Natural gas | 412 | MMBTU/H | The heat input is for a single unit. | Carbon Dioxide Equivalent (CO2e) | Other - methods in 40 CFR 75.10(a)(3) | (Greenhouse Gasses (GHG)) | CO2e | P | High efficiency turbines | 220122 | TONS | 12 MONTH ROLLING TOTAL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is for each unit.
ND-0028 | R.M. HESKETT STATION | MONTANA-DAKOTA UTILITIES CO. | MORTON | ND | 58554 | USA | ABBIE KREBSBACH | (701) 222-7844 | ABBIE.KREBSBACH@MDU.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Primary contact is Tom Bachman at (701) 328-5188. | PTC13016 | 4911 | 221112 | 110022000000 | 11/07/2012 &nbsp;ACT | 02/22/2013 &nbsp;ACT | 2013-04-01 | 2017-04-28 | B |  | Addition of a natural gas-fired turbine (Unit 3) to an exisiting coal-fired power plant. The turbine will be used for supplying peak power and is rated at 986 MMBtu/hr and 88 MWe at average site conditions. |  | Combustion Turbine | 15.11 | Natural gas | 986 | MMBTU/H | Turbine is a GE Model PG 7121 (7EA) used as a peaking unit. | Carbon Dioxide Equivalent (CO2e) | Other - Methods in 40 CFR 75.10(a)(3) | (Greenhouse Gasses (GHG)) | CO2e | N |  | 413198 | TONS/12 MONTH | 12 MONTH ROLLING TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110031000000 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Generation Turbines (2) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion/operating practices and fueled by natural gas - use GE LM2500+G4 turbines | 4872107 | TONS/YR | ANNUAL MAXIMUM FROM THE FACILITYWIDE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO2(e)
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110031000000 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Refrigeration Compressor Turbines (16) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion/operating practices and fueled by natural gas - use GE LM2500+G4 turbines | 4872107 | TONS/YR | ANNUAL MAXIMUM FROM THE FACILITYWIDE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CO2(e)
TX-0679 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | GHGPSDTX123 | 4925 | 221210 | 110057000000 | 12/12/2014 &nbsp;ACT | 02/27/2015 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. The LNG terminal will operate three trains continuously (8,760 hours per year) using eighteen (18) GE LM2500+G4 (with dry low NOx emissions) gas-fired refrigeration compressor turbines, six on each train. There are two methane, two ethylene, and two propane refrigeration turbines per train. |  | Refrigeration Compressor Turbines | 15.11 | natural gas | 40000 | hp | There are three LNG trains with a total of (12) GE LM2500+ DLE turbines that drive the propane and methane refrigeration compressors. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | install efficient turbines, follow the turbine manufacturerâ€™s emission-related written instructions for maintenance activities including prescribed maintenance intervals to assure good combustion and efficient operation. Compressors shall be inspected and maintained according to a written maintenance plan to maintain efficiency. | 146754 | TPY | ROLLING 12-MONTH BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is for each turbine.
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069000000 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Gas Turbines (8 units) | 15.11 | natural gas | 333 | mm btu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion/operating/maintenance practices and fueled by natural gas; use intake air chiller | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110030000000 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices and fueled by natural gas; Use high thermal efficiency turbines | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0121 | INVENERGY NELSON EXPANSION LLC | INVENERGY | LEE | IL | 61058 | USA | GORDON GRAY | 312-582-1290 | GGRAY@INVENERGY.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Bob Smet; 217-785-9250; robert.smet@illinois.gov | 15060042 | 4911 | 221112 | Not Found | 07/28/2016 &nbsp;ACT | 09/27/2016 &nbsp;ACT | 2017-01-27 | 2017-04-28 | B | https://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/9dbc452815081576862580b2006897b4/$FILE/ATT4AK5N.pdf/15060042.pdf | Peaking facility at an existing major source. The expansion will consist of two simple cycle combustion turbines and a fuel heater. |  | Two Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 190 | MW | Two simple cycle combustion turbines used for peaking purposes and fired primarily on natural gas with ULSD as a secondary fuel. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Turbine-generator design and proper operation | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The GHG emissions of each affected turbine, as carbon dioxide equivalents (CO2e), as an annual average of 12 consecutive operating months, rolled monthly, shall not exceed a limit that is calculated as follows. Compliance with this limit shall be determined using the relevant procedures for quantification of GHG emissions in 40 CFR Part 98 Subpart D. E = {(Gng x Rng) + (Gulsd x Rulsd} Ã· (Gng + Gulsd) Where E = Limit on GHG emissions, as CO2e, pounds/MW-hr gross electrical output, annual average, rolled monthly. Gng = Gross electrical output of the affected turbine-generator from natural gas, in MW-hr, including output in hours when ultra-low-sulfur diesel provides less than 50 percent of the heat input of the turbine. Gulsd = Gross electrical output, of the affected turbine generator from ultra-low-sulfur diesel, in MW-hr, including output in hours when ultra-low-sulfur diesel provides 50 percent or more of the heat input of the turbine. Rng = 1367 lb/MW-hr gross output (allowable rate for natural gas). Rulsd = 1934 lb/MW-hr gross output (allowable rate for ultra-low-sulfur diesel).