## All Control Groups
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
TX-0686 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JEFF PIPPIN | 806-418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, 512-239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358 | 4911 | 221112 | 110043000000 | 04/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-03-18 | 2016-05-09 | B |  | GSEC is proposing to build three additional new CTGs at the existing Antelope Elk Energy Center. The new facility will provide primarily peaking and intermediate power needs. The new units will be GE 7F5-Series gas turbines in simple cycle application, rated at 202 MW. Each turbine will operate a maximum of 4,572 hours per year. |  | Combustion Turbine-Generator(CTG) | 15.11 | Natural Gas | 202 | MW | Simple Cycle | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DLN | 9 | PPM | 15% O2, 3 HR. ROLLING AVG. | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0690 | CEDAR BAYOU ELECTRIC GERNERATION STATION | NRG TEXAS POWER | CHAMBERS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 105810, PSDTX1308 | 4911 | 221112 | 110016000000 | 08/29/2014 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power generation station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the simple cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The units will produce between 215-263 MW each. |  | Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 225 | MW | The gas turbines will be one of three options: (1) Two Siemens Model F5 (SF5) CTGs each rated at nominal capability of 225 megawatts (MW). (2) Two General Electric Model 7FA (GE7FA) CTGs each rated at nominal capability of 215 MW. (3) Two Mitsubishi Heavy Industry G Frame (MHI501G) CTGs each rated at a nominal electric output of 263 MW. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DLN | 9 | PPM | 3HR. ROLLING AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0688 | SR BERTRON ELECTRIC GENERATION STATION | NRG TEXAS POWER | HARRIS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 102731, PSDTX1294 | 4911 | 221112 | 110035000000 | 05/10/2012 &nbsp;ACT | 12/19/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power generation station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the simple cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The new units will produce between 215-263 MW each. |  | Simple cycle natural gas turbines | 15.11 | Natural Gas | 225 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DLN | 9 | PPM | 3HR ROLLING AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0355 | FORT MYERS PLANT | FLORIDA POWER & LIGHT (FPL) | LEE | FL | 33905 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0710002-022-AC | 4911 | 221112 | 110000000000 | 05/12/2015 &nbsp;ACT | 09/10/2015 &nbsp;ACT | 2016-03-10 | 2016-07-06 | D | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.80831.1]&[profile=Permitting_Authorization] | Electric power plant, consists of a 6-on-2 combined-cycle unit (Units 2A through 2F) and two modern simple-cycle combustion turbines. Primary fuel is natural gas. Also includes 12 gas turbines (63 MW each) for peaking, introduced into service in 1974. This project entails decommissioning 10 of the 12 peaking turbines. They will be replaced with two new GE 7F.05 turbines, each with nominal capacity of 200 MW | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0710002.022.AC.D.ZIP | Combustion Turbines | 15.11 | Natural gas | 2262.4 | MMBtu/hr gas | Two GE 7F.05 turbines, approximately 200 MW each. Natural-gas is primary fuel. Permitted 3390 hr/yr of operation, of which no more than 500 hr may be on fuel oil. Dry Low-NOx, with wet injection for oil firing. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DLN | 9 | PPMVD@15% O2 | GAS FIRING, 24-HR BLOCK AVG | BACT-PSD | NSPS | U | 0 | U | 42 | PPMVD@15% O2 | ULSD FIRING, 4-HR ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Compliance by NOx CEMS. Also subject to low-load (<75%) Subpart KKKK NOx limit.
FL-0310 | SHADY HILLS GENERATING STATION | SHADY HILLS POWER COMPANY | PASCO | FL | 6927 | USA | ROY S. BELDEN | 2033576820 | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | SYED ARIF, PROJECT ENGINEER PHONE 850/ 921-9528 SYED.ARIF@DEP.STATE.FL.US TERESA HERON PHONE 850/921-9529 TERESA.HERON@DEP.STATE.FL.US | PSD-FL-402 | 4911 | 221122 | 1210100373 | 05/13/2008 &nbsp;ACT | 01/12/2009 &nbsp;ACT | 2009-07-29 | 2010-01-26 | B |  | THIS FACILITY CONSISTS OF THREE, DUAL-FUEL, NOMINAL 170 MW GENERAL ELECTRIC MODEL PG7241FA (GE 7FA) SIMPLE CYCLE COMBUSTION TURBINES-ELECTRICAL GENERATORS, THREE EXHAUST STACKS THAT ARE 18 FEET IN DIAMETER AND 75 FEET TALL, AND ONE 2.8-MILLION GALLON DISTILLATE FUEL OIL STORAGE TANK. THE COMBUSTION TURBINE UNITS CAN OPERATE IN SIMPLE-CYCLE MODE AND INTERMITTENT DUTY MODE. THE UNITS ARE EQUIPPED WITH DRY LOW-NITROGEN OXIDES (NOX) COMBUSTORS AND WATER INJECTION CAPABILITY. THE THREE COMBUSTION TURBINES ARE REGULATED UNDER PHASE II OF THE FEDERAL ACID RAIN PROGRAM. THIS FACILITY OPERATES DURING PEAK HOURS OF ELECTRICAL USE. |  | TWO SIMPLE CYCLE COMBUSTION TURBINE - MODEL 7FA | 15.11 | NATURAL GAS | 170 | MW | BACKUP FUEL: ULTRA LOW SULFUR DIESEL WITH A MAXIMUM SULFUR CONTENT OF 0.0015%, BY WEIGHT | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DLN 2.6 COMBUSTORS TO MINIMIZE NOX EMISSSIONS. | 9 | PPMVD @ 15% O2 | 24-HR BLOCK AVG BY CEMS | BACT-PSD |  | Y | 0 | U | 59 | LB/H | 3 ONE HOUR RUN BY 7E OR 20 | 9 | PPMVD @ 15% O2 | 24-HR BLOCK AVG BY CEMS | 0 | 0 | N
TX-0769 | VAN ALSTYNE ENERGY CENTER (VAEC) | NAVASOTA NORTH COUNTRY PEAKERS OPERATING COMPANY I | GRAYSON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 121051 AND PSDTX1418 | 4911 | 221112 | UNKNOWN | 12/22/2014 &nbsp;ACT | 10/27/2015 &nbsp;ACT | 2015-10-30 | 2016-07-06 | A |  | Navasota North Country Peakers Operating Company I LLC. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 MW each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN burners | 9 | PPMVD @ 15% O2 | 3-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and IIII CTGs will operate at 2500 hours of operation per year at baseload.
TX-0695 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX |  | USA | JIM SHIELD | (312) 582-1440 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | 110423 PSDTX1366 | 4911 | 221112 | 110057000000 | 05/13/2013 &nbsp;ACT | 08/01/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | The proposed project is to construct and operate two natural gas-fired simple-cycle combustion turbine generators (CTGs) at the Ector County Energy Center (ECEC), located approximately 20 miles northwest of Odessa, Texas, in Ector County. |  | (2) combustion turbines | 15.11 | natural gas | 180 | MW | (2) GE 7FA.03, 2500 hours of operation per year each | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 9 | PPMVD | @15% O2, 3-HR ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 2500 hr/yr operation
TX-0696 | ROANâ€™S PRAIRIE GENERATING STATION | TENASKA ROANâ€™S PRAIRIE PARTNERS (TRPP), LLC | GRIMES | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 erik.hendrickson@tceq.texas.gov | 114698 PSDTX1378 | 4911 | 221112 | 110028000000 | 10/25/2013 &nbsp;ACT | 09/22/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | The proposed project is to construct and operate the RPGS comprised of three new simple cycle combustion turbine generators (CTG), fueled by pipeline quality natural gas. The new CTGs will be peaking units, designed to operate during periods of high electric demand. The three CTGs will produce between 507 and 694 MW of electricity combined, depending on ambient temperature and the model of combustion turbine (CT) selected. The applicant is considering three models of CTs; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. |  | (2) simple cycle turbines | 15.11 | natural gas | 600 | MW | The three possible CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. will operate 2,920 hours per year at full load for each CT | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 9 | PPMVD | @15% O2, 3-HR ROLLING AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | will operate 2,920 hours per year at full load for each CT
TX-0694 | INDECK WHARTON ENERGY CENTER | INDECK WHARTON, L.L.C. | WHARTON | TX |  | USA | JAMES SCHNEIDER | (847) 520-3212 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 111724 PSDTX1374 | 4911 | 221112 | unknown | 06/18/2013 &nbsp;ACT | 02/02/2015 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | Indeck Wharton, L.L.C. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will either be the General Electric 7FA (~214 MW each) or the Siemens SGT6-5000F (~227 MW each), operating as peaking units in simple cycle mode. |  | (3) combustion turbines | 15.11 | natural gas | 220 | MW | The CTGs will either be the General Electric 7FA (~214 MW each) or the Siemens SGT6-5000F (~227 MW each), operating as peaking units in simple cycle mode | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 9 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0691 | PH ROBINSON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | GALVESTON | TX |  | USA | CRAIG ECKBERG | (832) 357-5291 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 erik.hendrickson@tceq.texas.gov | 108182 PSDTX1346 | 4911 | 221112 | 110002000000 | 02/06/2013 &nbsp;ACT | 05/20/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG proposes to construct six natural gas-fired simple cycle combustion turbine generators (CTG) for peaking, designed to operate during periods of high electric demand. The six CTGs selected by NRG are General Electric Frame 7E turbines have an ISO rating of 65 MW and a nominal maximum generating capacity of 80 MW. Each of the turbines will not exceed 20 percent annual capacity (equivalent to 1,752 full load hours) in any single year or 10 percent annual capacity factor (equivalent to 876 full load hours) averaged over any three year period. |  | (6) simple cycle turbines | 15.11 | natural gas | 65 | MW | General Electric Frame 7E turbines have an ISO rating of 65 MW and a nominal maximum generating capacity of 80 MW. The turbines were originally constructed as Frame 7B units that were remanufactured in 1999 and upgraded to 7E machines Each of the turbines will not exceed 20 percent annual capacity (equivalent to 1,752 full load hours) in any single year or 10 percent annual capacity factor (equivalent to 876 full load hours) averaged over any three year period, which qualifies each of the CTGs as Acid Rain Peaking Units under 40 CFR 72.2 | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 15 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | limited use
TX-0693 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE INC | HALE | TX |  | USA | JEFF PIPPIN | (806) 418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson 512-239-2175 laura.gibson@tceq.texas.gov | 109148 PSDTX1358 | 4911 | 221112 | 110043000000 | 04/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-03-19 | 2016-07-29 | B |  | Golden Spread Electric Cooperative (GSEC) currently owns and operates Antelope Station (now renamed Antelope Elk Energy Center), a 168 MW generating facility made up of 18 quick start WÃ¤rtsilÃ¤ engines. GSEC is proposing to build a new combustion turbine-generator (CTG) facility at Antelope Station, while the 18 WÃ¤rtsilÃ¤ engines will remain and continue to be authorized by TCEQ Standard Permit. The new turbine-generator will provide primarily peaking and intermediate power needs in a highly cyclical operation. The CTG will produce approximately 100 - 200 MW of electricity, depending on loading and ambient temperature. |  | combustion turbine | 15.11 | natural gas | 202 | MW | new GE 7FA 5-Series gas turbine in a simple cycle application, with a maximum electric output of 202 megawatts (MW) and a maximum design capacity of 1,941 million British thermal units per hour (MMBtu/hr). The turbine will operate a maximum of 4,572 hours per year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 9 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*WV-0028 | WAVERLY POWER PLANT | PLEASANTS ENERGY LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 3046654201 | GERALD.GATTI@DYNEGY.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Steve Pursley, PE Engineer West Virginia Division of Air Quality 601-57th St., SE Charleston, WV 25304 Phone: (304) 926-0499 x1218 Fax: (304) 926-0478 steve.r.pursley@wv.gov | R14-0034A | 4911 | 221112 | 110063000000 | 11/30/2017 &nbsp;ACT | 03/13/2018 &nbsp;ACT | 2018-05-29 | 2018-05-29 | U | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/073-00022_PERM_R14-0034A.pdf | 300 MW Sinple-Cycle Peaking Plant | Modification to existing PSD Permit (R14-0034, RBLC Number WV-0027) to add &lsquo;&lsquo;advanced gas path&lsquo;&lsquo; technology to the turbines that was defined as a &lsquo;&lsquo;change in the method of operation&lsquo;&lsquo; that resulted a major modification to the turbines. | GE 7FA.004 Turbine | 15.11 | Natural Gas | 167.8 | MW | This one entry is for both turbines as they are the same. Each turbine, after this modification, is a nominal 167.8 MW GE Model 7FA.004. Has oil-fire backup. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry LNB | 9 | ppmv |  | BACT-PSD | NSPS | U | 0 | U | 232.3 | TONS/YEAR |  | 9 | PPM |  | 0 | 0 | N
TX-0816 | CORPUS CHRISTI LIQUEFACTION | CORPUS CHRISTI LIQUEFACTION STAGE III, LLC | SAN PATRICIO | TX |  | USA | KEITH LITTLE | (713) 375-5204 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 139479, PSDTX1496, GHGPSDTX157 | 4925 | 221210 | Not Found | 11/16/2016 &nbsp;ACT | 02/14/2017 &nbsp;ACT | 2017-02-07 | 2018-04-18 | B |  | Trains 4 and 5 will consist of 12 natural gas compressor turbines, 2 thermal oxidizers, 2 sets of flares each comprised of one wet gas flare and one dry gas flare, 2 amine surge tanks (maintenance, startup, and shutdown [MSS] only), 3 diesel generators, 3 fire-water pump diesel engines, 6 fixed roof diesel storage tanks, and piping components. |  | Refrigeration compressor turbines | 15.11 | NATURAL GAS | 40000 | HP | 2 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane, ethylene, and methane section compressors. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low emission burners | 25 | PPMDV | @ 15% O2 | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Subpart KKKK
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057000000 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.11 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane and methane section compressors. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low emission combustors | 25 | PPMVD | @ 15% O2, 4 HOUR ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0333 | DAYTON POWER & LIGHT ENERGY LLC | DAYTON POWER & LIGHT COMPANY | MONTGOMERY | OH | 45439 | USA | CARRIE BURKS | 937-331-3042 |  | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104867 | 4911 | 221112 | 110000000000 | 04/30/2009 &nbsp;ACT | 12/03/2009 &nbsp;ACT | 2010-05-13 | 2010-05-20 | C |  | Seven simple cycle stationary combustion turbines all with rating of 80 MW and nominal heat input of 1115.2 mmBtu/hr using natural gas or No. 2 fuel oil and all with water injection control and last 5 also with low NOx burners. | Simple cycle stationary combution turbines issed in 2 different permits. Four turbines in this permit with dry low NOx combustion and water injection controls. Administrative Modification to original PTI #08-04153 issued 8/7/01, to incorporate low mass emissions methodology as allowed per 40 CFR 75.19 in lieu of methods under Appendix D or E to Part 75, by meeting the requirements of having mass emissions of less than 25 T/YR SO2 and less than 100 T/YR NOx (per turbine) based on 3 years of operation. Modification also reduced permitted formaldehyde emissions by 8.7 tons, recalculated based on the restriction on hours of operation. | Turbines (4), simple cycle, natural gas | 15.11 | NATURAL GAS | 15020 | H/YR | Hours per year for all 4 turbines | Nitrogen Oxides (NOx) | Other - Method 7 or 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low NOx burners | 15 | ppmv | at 15% 02EACH TURBINE | BACT-PSD | SIP | U | 0 | Y | 1373.32 | T/YR | PER ROLLING 12-MO. FOR 4 UNITS &ALL FUEL | 15 | PPMV | AT 15% OXYGEN ON A DRY BASIS AS 1HR AVG. | 0 | 0 | N |  | T/YR limit is for both fuels and for the 4 turbines combined.
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry low NOx burners | 9 | PPMVD |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0777 | UNION VALLEY ENERGY CENTER | NAVASOTA SOUTH PEAKERS OPERATING COMPANY I, LLC. | NIXON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 120973 AND PSDTX1420 | 4911 | 221112 | UNKNOWN | 02/06/2015 &nbsp;ACT | 12/09/2015 &nbsp;ACT | 2015-12-03 | 2016-07-06 | A |  | three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 megawatt (MW) each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low NOX burners | 9 | PPMVD @ 15% O2 | 3-HR ROLLING AVERAGE PEAK | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & IIII
TX-0768 | SHAWNEE ENERGY CENTER | SHAWNEE ENERGY CENTER, LLC | HILL | TX |  | USA | NEIL O'DONOVAN | 312-422-1608 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, P.E., 512-239-1353, joseph.janecka@tceq.texas.gov | PSDTX1442, 125963 | 4911 | 221112 | UNKNOWN | 07/31/2015 &nbsp;ACT | 10/09/2015 &nbsp;ACT | 2015-10-05 | 2016-07-06 | A |  | Electric Generating Utility: The project will consist of four gas fired combustion turbines (CTGs). The CTGs are fueled with pipeline quality natural gas and will operate in simple cycle mode. The gas turbines will be one of two options. |  | Simple cycle turbines greater than 25 megawatts (MW) | 15.11 | natural gas | 230 | MW | Siemens Model SGT6-5000 F5ee â€“ 230 MW or Second turbine option: General Electric Model 7FA.05TP â€“ 227 MW | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx burners | 9 | PPMVD @ 15% O2 |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,920 hours on a 12-month rolling average.
TX-0733 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JOLLY HAYDEN | 806-349-5250 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, (512)239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358M1 | 4911 | 221112 | 110043000000 | 03/20/2015 &nbsp;ACT | 05/12/2015 &nbsp;ACT | 2015-05-04 | 2016-06-08 | B |  | Golden Spread Electric Cooperative, Inc. (GSEC) is requesting authorization for three additional simple cycle electric generating plants at an existing site to meet increased energy demand in the area. The generating equipment consists of three new GE 7F5-Series natural gas-fired combustion turbine generators (CTGs). Each turbine has a maximum electric output of 202 MW. |  | Simple Cycle Turbine &amp; Generator | 15.11 | natural gas | 202 | MW | 3 additional GE 7F 5-Series Combustion Turbine Generators | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx burners | 9 | PPMVD AT 15% O2 |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | operation of each turbine is limited to 4,572 hours per year
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110030000000 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low nox burners | 15 | PPMVD | @15%O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Simple Cycle Turbine | 15.11 | natural gas | 227.5 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx burners (control), natural gas, good combustion practices, limited operating hours (prevention) | 9 | PPMV | 15% O2 3-H AVG | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Economic reasonableness, operation of each turbine is limited to 2000 hours per year.
GA-0139 | DAHLBERG COMBUSDTION TURBINE ELECTRIC GENERATING FACILITY (P | SOUTHERN POWER COMPANY | JACKSON | GA | 30565 | USA | MR. E.S. (SCOTT) DIAL | 704 278-6601 | ESDIAL@SOUTHERNCO.COM | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-157-0034-V-04-1 | 4911 | 221112 | UNKNOWN | 07/10/2008 &nbsp;ACT | 05/14/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | C |  | PLANT DAHLBERG HAS PROPOSED TO CONSTRUCT AND OPERATE FOUR ADDITIONAL SIMPLE-CYCLE COMBUSTION TURBINES (SOURCE CODES: CT11-CT14) AND ONE FUEL OIL STORAGE TANK. THE PROPOSED PROJECT WILL HAVE A NOMINAL GENERATING CAPACITY OF 760 MW. THE FACILITY IS CURRENTLY PERMITTED TO OPERATE 10 DUAL-FUELED SIMPLE-CYCLE CTG's. AFTER THE EXPANSION, THE FACILITY WILL HAVE A TOTAL NOMINAL GENERATING CAPACITY OF 1530 MW. |  | SIMPLE CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.11 | NATURAL GASE | 1530 | MW | THE PROCESS USES FUEL OIL FOR BACKUP AT THE RATE OF 2129 MMBUT/H | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DRY LOW NOX BURNERS (FIRING NATURAL GAS). WATER INJECTION (FIRING FUEL OIL). | 9 | PPM@15%02 | 3 HOUR AVERAGE/CONDITION 3.3.23 | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 42 | PPM@15%02 | 3 HOUR AVERAGE/CONTIION 3.3.27 | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE 7FA Simple Cycle Combustion Turbine | 15.11 | Pipeline quality natural gas | 1780 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low NOx burners and fire only pipeline natural gas | 9 | PPMDV | 24-HR ROLLING AVE, CORRECTED TO 15% O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069000000 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Gas Turbines (8 units) | 15.11 | natural gas | 333 | mm btu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry Low NOX burners and good combustion practices | 25 | PPMVD | @15 %O2 | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0764 | NACOGDOCHES POWER ELECTRIC GENERATING PLANT | NACOGDOCHES POWER, LLC | NACOGDOCHES | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem 512-239-1310 Tzvi.shalem@tceq.texas.gov | 77679, PSDTX1061M1 & O-3455 | 4911 | 221112 | 110044000000 | 06/25/2015 &nbsp;ACT | 10/14/2015 &nbsp;ACT | 2015-09-16 | 2016-07-06 | B |  | Nacogdoches Power, LLC is requesting authorization for one natural gas fired, simple cycle combustion turbine generator (CTG). The CTG will be a Siemens F5 and have a nominal electric output of 232 megawatts (MW). |  | Natural Gas Simple Cycle Turbine (&gt;25 MW) | 15.11 | natural gas | 232 | MW | One Siemens F5 simple cycle combustion turbine generator | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx burners, good combustion practices, limited operations | 9 | PPMVD @ 15% O2 |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,500 hours on a 12-month rolling average.
TX-0701 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX |  | USA | JIM SHIELD | 312-582-1440 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Marc Sturdivant, 512-239-1313, Marc.Sturdivant@tceq.texas.gov | 110423, PSDTX1366 | 4911 | 221112 | 110013000000 | 08/01/2014 &nbsp;ACT | 05/13/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is for two natural gas fired simple cycle CTGs. The proposed models include GE7Fa.03 and GE7Fa.05. They have an output of 165-193 MW. The new CTGs will operate as peaking units and will be limited to 2500 hours per year of operation each. |  | Simple Cycle Combustion Turbines | 15.11 | natural gas | 180 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry low NOx combustor | 9 | PPMVD | 15%O2, 3HR ROLLING BASIS | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0258 | CALCASIEU PLANT | ENTERGY GULF STATES LA LLC | CALCASIEU | LA | 70665 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: TEGAN TREADAWAY, (225) 219-3408 | PSD-LA-746 | 4911 | 221112 | 110007000000 | 11/10/2009 &nbsp;ACT | 12/21/2011 &nbsp;ACT | 2012-02-01 | 2012-04-03 | C |  | 320 MW POWER PLANT COMPRISED OF 2 NATURAL GAS-FIRED SIMPLE CYCLE COMBUSTION TURBINES. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS PSD TRIGGERED DUE TO RELAXATION OF A FEDERALLY-ENFORCEABLE CONDITION LIMITING POTENTIAL EMISSIONS BELOW MAJOR STATIONARY SOURCE THRESHOLDS. | TURBINE EXHAUST STACK NO. 1 &amp; NO. 2 | 15.11 | NATURAL GAS | 1900 | MM BTU/H EACH |  | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DRY LOW NOX COMBUSTORS | 17.5 | ppmv | at 15% 02 HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 798 | LB/H | HOURLY MAXIMUM / STARTUP & SHUTDOWN ONLY | 17.5 | PPMVD @ 15% O2 |  | 0 | 0 | N |  | LIMITS ARE PER TURBINE EXHAUST STACK. AGGREGATE NOX EMISSIONS FROM BOTH TURBINE EXHAUST STACKS ARE LIMITED TO 391.30 TONS PER YEAR. STARTUP & SHUTDOWN OPERATIONS ARE LIMITED TO 520 HOURS PER YEAR.
TX-0734 | CLEAR SPRINGS ENERGY CENTER (CSEC) | NAVASOTA SOUTH PEAKERS OPERATING COMPANY II, LLC. | GUADALUPE | TX | 78155 | USA | FRANK GIACALONE | (281) 252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jack Coleman, 512-239-1255, jack.coleman@tceq.texas.gov | 120849 AND PSDTX1414 | 4911 | 221112 | Not Found | 02/20/2015 &nbsp;ACT | 05/08/2015 &nbsp;ACT | 2015-05-08 | 2018-04-18 | A |  | Navasota South Peakers Operating Company II LLC. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 MW each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low-NOx (DLN) burners | 9 | PPMVD @ 15% O2 | 3-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & IIII CTGs will operate at 2500 hours of operation per year at baseload.
TX-0540 | BOSQUE COUNTY POWER PLANT | BOSQUE POWER COMPANY LLC | BOSQUE | TX | 76644 | USA | MS KATHY FRENCH | 6365322200 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | MS. BRIDGET MALONE (512) 239-4286 | 40620 | 4911 | 221112 | 4803500002 | 10/26/2007 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | PSDTX931M1 | ELECTRICAL GENERATION | 15.11 | NATURAL GAS | 170 | MW | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DRY LOW-NOX (DLN) COMBUSTERS WHEN THE COMBUSTION TURBINE IS OPERATING IN THE SIMPLE CYCLE MODE. | 9 | PPMVD | 24-HOUR 15% O2 | BACT-PSD |  |  | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0826 | MUSTANG STATION | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | YOAKUM | TX |  | USA | JEFF PIPPIN | 806-418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | 72579, PSDTX1080M1, GHGPSDTX13 | 4911 | 221112 | 110042000000 | 06/12/2017 &nbsp;ACT | 08/16/2017 &nbsp;ACT | 2017-07-24 | 2018-04-18 | C |  | GE7FA combustion turbine (Unit 6) to increase the hours of operation to 3000 hours per year. The turbine construction was completed the first quarter of 2013 and initial firing began on April 1, 2013. |  | Simple Cycle Turbine | 15.11 | NATURAL GAS | 162.8 | MW | Unit 6 Turbine is limited to 3000 hours per year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low-NOx burners | 9 | PPMVD |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK MACT YYYY
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110065000000 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Large Combustion Turbines &gt; 25 MW | 15.11 | natural gas | 232 | MW | 4 Simple cycle CTGs, 2,500 hr/yr operational limitation. Facility will consist of either 232 MW (Siemens) or 220 MW (GE) | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low-NOx burners (DLN), good combustion practices | 9 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Subparts KKKK and TTTT
ND-0028 | R.M. HESKETT STATION | MONTANA-DAKOTA UTILITIES CO. | MORTON | ND | 58554 | USA | ABBIE KREBSBACH | (701) 222-7844 | ABBIE.KREBSBACH@MDU.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Primary contact is Tom Bachman at (701) 328-5188. | PTC13016 | 4911 | 221112 | 110022000000 | 11/07/2012 &nbsp;ACT | 02/22/2013 &nbsp;ACT | 2013-04-01 | 2017-04-28 | B |  | Addition of a natural gas-fired turbine (Unit 3) to an exisiting coal-fired power plant. The turbine will be used for supplying peak power and is rated at 986 MMBtu/hr and 88 MWe at average site conditions. |  | Combustion Turbine | 15.11 | Natural gas | 986 | MMBTU/H | Turbine is a GE Model PG 7121 (7EA) used as a peaking unit. | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low-NOx combustion (DLN) | 9 | PPMVD @15% OYYGEN | 4 H.R.A. WHEN > 50MWE AND > 0 DEGREES F | BACT-PSD | NSPS | Y | 0 | U | 96 | PPMVD @15% OXYGEN | 4 H.R.A. WHEN < 50 MWE OR < 0 DEGREES F | 399 | LB/H | 1 HOUR AVG./ANY TIME | 0 | 0 | N | 2012
WV-0026 | WAVERLY FACILITY | PLEASANTS ENERGY, LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 304-665-4201 | GERALD.GATTI@GDFSUEZNA.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0034 | 4911 | 221112 | 110010000000 | 04/18/2016 &nbsp;ACT | 01/23/2017 &nbsp;ACT | 2017-03-21 | 2018-05-01 | D | http://www.dep.wv.gov/daq/Documents/January 2017 Permits and Evals/073-00022_PERM_R14-0034.pdf | 300 MW, natural gas fired, simple cycle peaking power facility | In this permitting action PSD only applies to the modified combustion turbines based on the relaxation of an original synthetic minor permit issued in 1999. Project also involves previous installation of turbo-charging. All BACT emission limits are given without turbocharging and startup/shutdown emissions are not included. Please contact above engineer for more information. There are two identical turbines but only one is listed. | GE Model 7FA Turbine | 15.11 | Natural Gas | 1571 | mmbtu/hr | There are two identical units at the facility. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry Low-NOx Combustion System (DLNB), Water Injection | 9 | PPM | NATURAL GAS | BACT-PSD | NSPS | U | 0 | U | 49 | PPM | FUEL OIL | 9 | PPM | NATURAL GAS | 0 | 0 | N |  | Additional emission limits are in the permit for use of turbocharging and startup/shutdown emissions. Please contact if need additional information.
IL-0121 | INVENERGY NELSON EXPANSION LLC | INVENERGY | LEE | IL | 61058 | USA | GORDON GRAY | 312-582-1290 | GGRAY@INVENERGY.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Bob Smet; 217-785-9250; robert.smet@illinois.gov | 15060042 | 4911 | 221112 | Not Found | 07/28/2016 &nbsp;ACT | 09/27/2016 &nbsp;ACT | 2017-01-27 | 2017-04-28 | B | https://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/9dbc452815081576862580b2006897b4/$FILE/ATT4AK5N.pdf/15060042.pdf | Peaking facility at an existing major source. The expansion will consist of two simple cycle combustion turbines and a fuel heater. |  | Two Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 190 | MW | Two simple cycle combustion turbines used for peaking purposes and fired primarily on natural gas with ULSD as a secondary fuel. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low-NOx combustion technology for natural gas and low-NOx combustion technology and water injection for ULSD. | 9 | ppmv |  | BACT-PSD | NSPS | N | 0 | U | 0.164 | LB/MMBTU |  | 0 |  |  | 0 | 0 | Y |  | Natural Gas: 9 ppmv at 15 percent O2 (equivalent to 0.033 lb/mmBtu, HHV). ULSD: 42 ppmv at 15 percent O2 (equivalent to 0.164 lb/mmBtu, HHV). During commissioning, NOx shall not exceed: Natural gas: 110 lb/hr, 110 lb/cycle ULSD: 349 lb/hr, 275 lb/cycle
MN-0075 | GREAT RIVER ENERGY - ELK RIVER STATION | GREAT RIVER ENERGY | SHERBURNE | MN | 55330 | USA | MARK STROHFUS | 7634455210 | MSTROHFU@GRENERGY.COM | 5 | MN001 | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | MR. RICHARD CORDES | (651)757-2291 | RICHARD.CORDES@STATE.MN.US | TONI VOLKMEIER, TONI.VOLKMEIER@PCA.STATE.MN.US | 14100003-004 | 4911 | 221119 | UNKNOWN | 03/31/2008 &nbsp;EST | 07/01/2008 &nbsp;ACT | 2008-12-01 | 2009-01-26 | B |  | THE FACILITY IS AN ELECTRIC POWER GENERATING STATION BURNING REFUSE DERIVED FUEL (RDF). THE RDF BURNED AT THIS FACILITY IS PROCESSED FROM MUNICIPAL SOLID WASTE. THE FACILITY PRODUCES APPROXIMATELY 40 MEGAWATTS OF ELECTRICITY. THERE IS ALSO A SINGLE CYCLE COMBUSTION TURBINE GENERATOR (CTG) |  | COMBUSTION TURBINE GENERATOR | 15.11 | NATURAL GAS | 2169 | MMBTU/H | GENERATOR IS A SIMPLE CYCLE COMBUSTION TURBINE, WHICH WILL BE OPERATED AS A PEAK-SHAVING UNIT. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DRY LOW-NOX COMBUSTION WHEN COMBUSTING NATURAL GAS | 9 | PPM | 4 HR ROLLING AVG, NG, >/= 60% LOAD | BACT-PSD | OTHER , NSPS | Y | 0 | U | 25 | PPM | 4 HR ROLLING AVG, NG, <60% LOAD | 96 | PPM | 4 HR ROLLING AVG, <75% LOAD | 0 | 0 | N |  | SEPARATE LIMIT DEVELOPED FOR NOX WHEN COMBUSTION NATURAL GAS OR FUEL OIL, AT DIFFERING LOADS
TX-0794 | HILL COUNTY GENERATING FACILITY | BRAZOS ELECTRIC COOPERATIVE | HILL | TX |  | USA | MIKE MEYERS | (254)750-6228 | MMEYERS@BRAZOSELECTRIC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512)239-1512, randy.hamilton@tceq.texas.gov | 130051,PSDTX1450, GHGPSDTX131 | 4911 | 221112 | UNKNOWN | 12/18/2015 &nbsp;ACT | 04/07/2016 &nbsp;ACT | 2016-04-05 | 2016-07-29 | A |  | Four simple cycle combustion turbine electric generators are proposed. Natural gas or ultra-low sulfur diesel fuel oil are the fuels. Turbine model options are: General Electric (GE) 7FA.03, GE 7FA.04, GE 7FA.05, and Siemes SGT6-5000(5)ee. Electric output is between 684 and 928 megawatts (MW). |  | Simple cycle turbine | 15.11 | natural gas | 171 | MW | Each combustion turbine is limited to 2,920 hours of annual operation, including startup and shutdown hours. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low-NOx combustors (DLN). DLN combustors use two stages of combustion, transitioning from initial startup with fuel and flame in the primary nozzles only, through a lean lean stage with fuel and flame in the primary and secondary nozzles, to fuel in the secondary stage only, extinguishing the primary flame, and in full operation, premix mode, with fuel to both nozzles, but flame only in the second stage. When natural gas and air are well-mixed before combustion, the flame temperature and resulting NOx emissions are greatly reduced compared to conventional diffusion flame combustion. | 9 | PPMVD @ 15% O2 | 3-HR ROLLING AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
FL-0346 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-011-AC | 4911 | 221112 | 110002000000 | 11/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-01-08 | 2016-05-05 | D | http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | In this project, 24 peaking turbines from the Lauderdale facility are being replaced with five 200 MW combustion turbines at Lauderdale. The turbines will fire primarily natural gas, but may also fire ULSD fuel oil. Triggers PSD for NOx, PM, CO, VOC, and GHG. GHG permit issued by US EPA Region 4. Technical evaluation available at http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2000 | MMBtu/hr (approx) | Throughput could vary slightly (+/- 120 MMBtu/hr) depending on final selection of turbine model and firing of natural gas or oil. Primary fuel is expected to be gas. Each turbine limited to 3300 hrs per rolling 12-month period. Of these 3300 hrs, no more than 500 may use ULSD fuel oil. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | dry low-NOx technology and wet injection. Water injection must be used when firing ULSD. | 9 | PPMVD @ 15% 02 | 24-HR BLOCK AVG, BY CEMS (NAT GAS) | BACT-PSD | NSPS | U | 0 | U | 77 | LB/H | 24-HR BLOCK, BY CEMS (NAT GAS) | 0 |  |  | 0 | 0 | N |  | NOx CEMS required -- employing EPA Method 7E. For natural gas, 9.0 ppmvd@15% O2 and 77 lb/hr. For oil, 42.0 ppmvd@15% O2 and 378.0 lb/hr.
FL-0354 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-013-AC | 4911 | 221112 | 110002000000 | 04/20/2015 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2016-02-17 | 2016-07-06 | D | https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | Re-affirmed BACT determinations in Permit No. 0110037-011-AC. Also, new GHG BACT determination. Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2100 | MMBtu/hr (approx) | Five simple cycle GE 7F.05 turbines. Max of 3390 hours per year per turbine. Of the 3390 hours per year, up to 500 hour may be on ULSD fuel oil. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry-low-NOx combustion system. Wet injection when firing ULSD. | 9 | PPMVD@15%O2 | 24-HR BLOCK AVERAGE | BACT-PSD | NSPS | U | 0 | U | 42 | PPMVD@15%O2 | 4-HR ROLLING | 0 |  |  | 0 | 0 | N |  | Compliance by NOx CEMS. Also subject to NSPS Subpart KKKK.
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Trubine (EP04) | 15.11 | Natural Gas | 40 | MW |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 5 | PPMV AT 15% O2 | 1-HOUR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 7.7 | LB/H | 30-DAY ROLLING AVERAGE | 36 | T/YR |  | 8308 | 8308 | N | 2011
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP03) | 15.11 | Natural Gas | 40 | MW |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 5 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD | NSPS | N | 0 | U | 7.7 | LB/H | 30-DAY ROLLING AVERAGE | 36 | T/YR |  | 8308 | 8308 | N | 2011
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP05) | 15.11 | Natural Gas | 40 | MW |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 5 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD | NSPS | N | 0 | U | 7.7 | LB/H | 30-DAY ROLLING AVERAGE | 36 | T/YR |  | 8308 | 8308 | N | 2011
ND-0030 | LONESOME CREEK GENERATING STATION | BASIN ELECTRIC POWER COOP. | MCKENZIE | ND | 58831 | USA | JERRY MENGE | (701)223-0441 |  | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact at (701) 328-5188. | PTC 13049 | 4911 | 221112 | 110057000000 | 04/05/2013 &nbsp;EST | 09/16/2013 &nbsp;ACT | 2013-09-24 | 2017-06-28 | B |  | Three natural gas fired simple cycle turbines used to generate electricity for peak power demand. The turbines are GE LM6000 PF Sprint units with a nominal capacity of 45 MW each. |  | Natural Gas Fired Simple Cycle Turbines | 15.11 | Natural gas | 412 | MMBTU/H | The heat input is for a single unit. | Nitrogen Oxides (NOx) | Other - CEM | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 5 | PPMVD | 4 HOUR ROLLING AVERAGE EXCEPT STARTUP | BACT-PSD | NSPS | N | 90 | N | 18.5 | LB | TOTAL FOR 30 MINUTES DURING STARTUP | 0 |  |  | 0 | 0 | N |  | The startup limit is for each unit. The three units are limited to a total combined emission rate of 42.9 pounds per hour (1-hour average) at all times.
CA-1174 | EL CAJON ENERGY LLC | EL CAJON ENERGY LLC | SAN DIEGO | CA | 92020 | USA | GENEVIEVE HUFFMAN |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Evariste Haury (858)-586-2745 Evariste.Haury@sdcounty.ca.gov | 987824 | 519 | 311999 | 110043000000 | 11/01/2008 &nbsp;ACT | 12/11/2009 &nbsp;ACT | 2010-09-20 | 2011-04-11 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 49.95 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 2.5 | PPMV | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ND-0029 | PIONEER GENERATING STATION | BASIN ELECTRIC POWER COOPERATIVE | WILLIAMS | ND |  | USA | JERRY MENGE | 7012230441 | JMENGE@BEPC.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact. | PTC 13037 | 4911 | 221112 | 110058000000 | 02/19/2013 &nbsp;ACT | 05/14/2013 &nbsp;ACT | 2013-06-19 | 2016-11-03 | B |  | Three GE LM6000 PC SPRINT natural gas fired turbines used to generate electricity for peak periods. | The permit was for the addition of 2 turbines to the station. Since a synthetic minor limit was relaxed for the first unit, BACT was required for all three turbines. | Natural gas-fired turbines | 15.11 | Natural gas | 451 | MMBTU/H | Rating is for each turbine. | Nitrogen Oxides (NOx) | Other - CEM | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 5 | PPPMVD | 4 HR. ROLLING AVERAGE EXCEPT FOR STARTUP | BACT-PSD | NSPS | U | 80 | N | 19 | LB/H | DURING STARTUP | 0 |  |  | 0 | 0 | N |  | RBLC Staff: Original Emis Limit 2 Units were Numeric Limit - &lsquo;&lsquo;LB&lsquo;&lsquo; and Avg Time/Condition - &lsquo;&lsquo;PER HOUR DURING STARTUP&lsquo;&lsquo; The Emission Units are usually &lsquo;&lsquo;mass unit PER time unit&lsquo;&lsquo;. Separating them out makes understanding limit difficult for the users. The units were combined. The corrected entry is: Numeric Limit - &lsquo;&lsquo;LB/H&lsquo;&lsquo; Avg Time/Condition - &lsquo;&lsquo;During Startup&lsquo;&lsquo;
CA-1223 | PIO PICO ENERGY CENTER | PIO PICO ENERGY CENTER, LLC | OTAY MESA | CA | 92154 | USA | GARY CHANDLER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SD 11-01 | 4911 | 221112 | 110045000000 | 06/14/2012 &nbsp;ACT | 11/19/2012 &nbsp;ACT | 2013-03-05 | 2014-01-28 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | CONSTRUCTION OF THREE GENERAL ELECTRIC (GE) LMS100 NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 100 MW EACH. THE PROJECT WILL HAVE AN ELECTRICAL OUTPUT OF 300 MW. | NOTE: PERMIT ISSUED 11/19/2012. ENVIRONMENTAL APPEALS BOARD REMANDED THE PM BACT ANALYSIS TO REGION 9 ON 8/2/2013. FINAL PERMIT ISSUED ON 2/28/2014. ONE PETITION FILED IN 9TH CIRCUIT FEDERAL COURT CHALLENGING THE FINAL PERMIT DECISION. THIS LAWSUIT WAS DISMISSED ON 6/17/2014 IN RESPONSE TO PETITIONERSâ€™ MOTION FOR VOLUNTARY DISMISSAL. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.11 | NATURAL GAS | 300 | MW | Three simple cycle combustion turbine generators (CTG). Each CTG rated at 100 MW (nominal net). | Nitrogen Oxides (NOx) | Other - EPA mETHOD 7E, OR METHOD 7E & 19 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR | 2.5 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 8.18 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N
CA-1176 | ORANGE GROVE PROJECT |  | SAN DIEGO | CA | 92059 | USA |  |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Camqui Nguyen (858)586-2747 camqui.nguyen@sdcounty.ca.gov | 985708 | 491 | 221122 | UNKNOWN | 11/03/2007 &nbsp;ACT | 12/04/2008 &nbsp;ACT | 2010-09-21 | 2011-06-27 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 49.8 | MW | Combustion turbine for peaking power plant | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR water injection | 2.5 | PPM | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1175 | ESCONDIDO ENERGY CENTER LLC |  | SAN DIEGO | CA | 92029 | USA |  |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Arthur Carbonell (858)-586-2741 arthur.carbonell@sdcounty.ca.gov | 985693 | 491 | 221122 | UNKNOWN | &nbsp; | 07/02/2008 &nbsp;ACT | 2010-09-21 | 2011-06-27 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 46.5 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR water injection | 2.5 | PPMV@15% OXYGEN | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055000000 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Three simple cycle combustion turbines | 15.11 | natural gas | 799.7 | MMBTU/H | Three GE, LMS100PA, natural gas-fired, simple cycle CTG rated at 799.7 MMBtu per hour each,based on HHV. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction (SCR) | 5 | PPMVD AT 15% O2 | 1-HR AVE | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 0 | U | 15.5 | LB/H | 30-DAY ROLLING AVE | 0 |  |  | 0 | 0 | N |  | startup limit = 12.0 lb per event shutdown limit = 18.0 lb per event compliance with BACT limits monitored via continuous emissions monitors.
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057000000 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | GE LMS-100 combustion turbines, simple cycle with water injection | 15.11 | natural gas | 1690 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | selective catalytic reduction (SCR) with aqueous ammonia injection at all times except during startup and shutdown; Limit the time in startup or shutdown. | 2.5 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON NG | BACT-PSD |  | U | 0 | U | 3.8 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON ULSD | 0 |  |  | 0 | 0 | N
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110031000000 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Generation Turbines (2) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Nitrogen Oxides (NOx) | EPA/OAR Mthd 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | water injection | 25 | ppmv | at 15% 02 HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 25 | PPMV | AT 15% O2 | 0 | 0 | N
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110031000000 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Refrigeration Compressor Turbines (16) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Nitrogen Oxides (NOx) | EPA/OAR Mthd 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | water injection | 20 | ppmv | at 15% 02HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 20 | PPMV | AT 15% O2 | 0 | 0 | N
OK-0127 | WESTERN FARMERS ELECTRIC ANADARKO | WESTERN FARMERS ELECTRIC COOPERATIVE | CADDO | OK | 73005 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2005-037-C(M-2) PSD | 4911 | 221112 | 110002000000 | 02/01/2008 &nbsp;ACT | 06/13/2008 &nbsp;ACT | 2008-12-31 | 2009-04-20 | B |  | THE FACILITY GENERATES WHOLESALE ELECTRICITY WHICH IS TRANSMITTED OVER WFECÂ¿S ELECTRICAL DISTRIBUTION SYSTEM. THE ELECTRICITY IS SOLD IN RURAL AREAS OF APPROXIMATELY 3/4 OF THE STATE OF OKLAHOMA. THE CURRENT FACILITY CONSISTS OF TWO NATURAL GAS FIRED HIGH PRESSURE BOILERS, A GAS/OIL FIRED HIGH PRESSURE BOILER, THREE GAS/OIL FIRED COMBINED CYCLE GAS TURBINES, A FIRE PUMP DIESEL ENGINE FOR EMERGENCY BACKUP, AND OTHER SOURCES WHICH ARE CONSIDERED INSIGNIFICANT OR TRIVIAL. THE THREE BOILERS ARE BACKUP UNITS THAT ONLY OPERATE WHEN IT IS FEASIBLE, SUCH AS DURING PEAK DEMAND. TWO OF THE BOILERS HAVE BEEN IDLE SINCE 1984. ONE BOILER WAS REPLACED IN 1997, AND ANOTHER WAS REPLACED IN 1998. | WESTERN FARMERS ELEC COOP PROPOSES TO CONSTRUCT AND OPERATE THREE NATURAL GAS-FIRED PEAKING ELECTRIC GENERATING UNITS AT THE FACILITY TO MEET ANTICIPATED FUTURE ENERGY DEMAND. EACH UNIT CAPACITY OF +/- 50 MW. | COMBUSTION TURBINE PEAKING UNIT(S) | 15.11 | NATURAL GAS | 462.7 | MMBTU/H | THE INSTALLATION WILL CONSIST OF THREE GENERAL ELECTRIC LM6000 SPRINT SIMPLE CYCLE AERODERIVATIVE COMBUSTION TURBINE GENERATORS. EACH OF THE TURBINES WILL HAVE A MAXIMUM PEAK HEAT INPUT RATE OF 462.7 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTUH). THE NEW COMBUSTION TURBINES WILL FIRE ONLY PIPELINE-QUALITY NATURAL GAS AND WILL BE EQUIPPED WITH WATER INJECTION. THE PROPOSED NEW UNITS WILL EACH HAVE A NOMINAL ELECTRICAL GENERATING CAPACITY OF 50 MW. ACTUAL UNIT CAPACITY WILL BE DETERMINED DURING DETAILED DESIGN OF THE PLANT AND MAY BE 5 TO 10-MW HIGHER OR LOWER THAN THE NOMINAL VALUE OF 50 MW, DEPENDING ON AMBIENT CONDITION RATINGS AND FINAL DESIGN. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | WATER INJECTION | 25 | PPM | ADJUSTED 15% O2 | BACT-PSD | NSPS | U | 0 | U | 42 | LB/H | 2,500 HR/YEAR | 0 |  |  | 0 | 0 | N |  | WATER INJECTION THAT ACHIEVES 25 PPMVD OR LESS CORRECTED TO 15% O2 IS DETERMINED ACCEPTABLE AS BACT.
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE LM6000PC SPRINT Simple cycle combustion turbine | 15.11 | Pipeline quality natural gas | 405.3 | MMBTU/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | water injection | 25 | PPMDV | 24-HR ROLLING AVE; CORRECTED TO 15% O | BACT-PSD |  | U | 0 | U | 269.3 | TONS | 12 MO CALENDAR BASIS, FOR ALL 4 UNITS | 0 |  |  | 0 | 0 | N
IN-0264 | MONTPELIER GENERATING STATION | AES OHIO GENERATION, LLC | WELLS | IN | 46781 | USA | DREW PARKER | 9373314993 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: MADHURIMA MOULIK 317-233-6663 MMOULIK@IDEM.IN.GOV SECTION CHIEF: JASON KRAWCZYK 317-234-5174 | 179-37209-00026 | 4911 | 221112 | 110021000000 | 05/23/2016 &nbsp;ACT | 01/06/2017 &nbsp;ACT | 2017-07-07 | 2017-11-17 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/37209F.PDF | COMBUSTION TURBINES |  | PRATT &amp; TWIN-PAC SIMPLE CYCLE TURBINES | 15.11 | NATURAL GAS | 270.9 | MMBTU/H | NO. 2 DIESEL OIL BACKUP FUEL | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | WATER INJECTION | 25 | PPMV | AT 15% O2 FOR NATURAL GAS | BACT-PSD |  |  | 0 |  | 42 | PPMV | AT 15% O2 FOR FUEL OIL | 0 |  |  | 0 | 0 | N |  | 0.14 LB/MMBTU FOR NATURAL GAS AND 0.24 LB/MMBTU FOR FUEL OIL; EACH TURBINE LIMITED TO 4555 HOURS OF OPERATION PER 12 MONTH PERIOD
[40 empty] | Range Low | 2.5 | PPMV
[40 empty] | Range High | 25 | PPMV
[40 empty] | Mean | 10.7222 | PPMV
[40 empty] | Median | 9 | PPMV
[40 empty] | Mode | 9 | PPMV

## DLN
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
TX-0686 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JEFF PIPPIN | 806-418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, 512-239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358 | 4911 | 221112 | 110043000000 | 04/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-03-18 | 2016-05-09 | B |  | GSEC is proposing to build three additional new CTGs at the existing Antelope Elk Energy Center. The new facility will provide primarily peaking and intermediate power needs. The new units will be GE 7F5-Series gas turbines in simple cycle application, rated at 202 MW. Each turbine will operate a maximum of 4,572 hours per year. |  | Combustion Turbine-Generator(CTG) | 15.11 | Natural Gas | 202 | MW | Simple Cycle | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DLN | 9 | PPM | 15% O2, 3 HR. ROLLING AVG. | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0690 | CEDAR BAYOU ELECTRIC GERNERATION STATION | NRG TEXAS POWER | CHAMBERS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 105810, PSDTX1308 | 4911 | 221112 | 110016000000 | 08/29/2014 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power generation station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the simple cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The units will produce between 215-263 MW each. |  | Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 225 | MW | The gas turbines will be one of three options: (1) Two Siemens Model F5 (SF5) CTGs each rated at nominal capability of 225 megawatts (MW). (2) Two General Electric Model 7FA (GE7FA) CTGs each rated at nominal capability of 215 MW. (3) Two Mitsubishi Heavy Industry G Frame (MHI501G) CTGs each rated at a nominal electric output of 263 MW. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DLN | 9 | PPM | 3HR. ROLLING AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0688 | SR BERTRON ELECTRIC GENERATION STATION | NRG TEXAS POWER | HARRIS | TX |  | USA | CRAIG ECKBERT | 713-795-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez, 512-239-5220, Ruth.Alvirez@tceq.texas.gov | 102731, PSDTX1294 | 4911 | 221112 | 110035000000 | 05/10/2012 &nbsp;ACT | 12/19/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG is proposing to construct an additional electric power generation station at the existing site. The project will include two power blocks that can be operated in simple cycle or combined cycle modes. This entry is for the simple cycle operation. Each power block will contain a CTG with duct burners and HRSG. Three options were proposed: Siemens Model F5, GE7Fa, and Mitsubishi Heavy Industry G Frame. The new units will produce between 215-263 MW each. |  | Simple cycle natural gas turbines | 15.11 | Natural Gas | 225 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DLN | 9 | PPM | 3HR ROLLING AVG. | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0355 | FORT MYERS PLANT | FLORIDA POWER & LIGHT (FPL) | LEE | FL | 33905 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0710002-022-AC | 4911 | 221112 | 110000000000 | 05/12/2015 &nbsp;ACT | 09/10/2015 &nbsp;ACT | 2016-03-10 | 2016-07-06 | D | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.80831.1]&[profile=Permitting_Authorization] | Electric power plant, consists of a 6-on-2 combined-cycle unit (Units 2A through 2F) and two modern simple-cycle combustion turbines. Primary fuel is natural gas. Also includes 12 gas turbines (63 MW each) for peaking, introduced into service in 1974. This project entails decommissioning 10 of the 12 peaking turbines. They will be replaced with two new GE 7F.05 turbines, each with nominal capacity of 200 MW | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0710002.022.AC.D.ZIP | Combustion Turbines | 15.11 | Natural gas | 2262.4 | MMBtu/hr gas | Two GE 7F.05 turbines, approximately 200 MW each. Natural-gas is primary fuel. Permitted 3390 hr/yr of operation, of which no more than 500 hr may be on fuel oil. Dry Low-NOx, with wet injection for oil firing. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DLN | 9 | PPMVD@15% O2 | GAS FIRING, 24-HR BLOCK AVG | BACT-PSD | NSPS | U | 0 | U | 42 | PPMVD@15% O2 | ULSD FIRING, 4-HR ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Compliance by NOx CEMS. Also subject to low-load (<75%) Subpart KKKK NOx limit.
FL-0310 | SHADY HILLS GENERATING STATION | SHADY HILLS POWER COMPANY | PASCO | FL | 6927 | USA | ROY S. BELDEN | 2033576820 | ROY.BELDEN@GE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | SYED ARIF, PROJECT ENGINEER PHONE 850/ 921-9528 SYED.ARIF@DEP.STATE.FL.US TERESA HERON PHONE 850/921-9529 TERESA.HERON@DEP.STATE.FL.US | PSD-FL-402 | 4911 | 221122 | 1210100373 | 05/13/2008 &nbsp;ACT | 01/12/2009 &nbsp;ACT | 2009-07-29 | 2010-01-26 | B |  | THIS FACILITY CONSISTS OF THREE, DUAL-FUEL, NOMINAL 170 MW GENERAL ELECTRIC MODEL PG7241FA (GE 7FA) SIMPLE CYCLE COMBUSTION TURBINES-ELECTRICAL GENERATORS, THREE EXHAUST STACKS THAT ARE 18 FEET IN DIAMETER AND 75 FEET TALL, AND ONE 2.8-MILLION GALLON DISTILLATE FUEL OIL STORAGE TANK. THE COMBUSTION TURBINE UNITS CAN OPERATE IN SIMPLE-CYCLE MODE AND INTERMITTENT DUTY MODE. THE UNITS ARE EQUIPPED WITH DRY LOW-NITROGEN OXIDES (NOX) COMBUSTORS AND WATER INJECTION CAPABILITY. THE THREE COMBUSTION TURBINES ARE REGULATED UNDER PHASE II OF THE FEDERAL ACID RAIN PROGRAM. THIS FACILITY OPERATES DURING PEAK HOURS OF ELECTRICAL USE. |  | TWO SIMPLE CYCLE COMBUSTION TURBINE - MODEL 7FA | 15.11 | NATURAL GAS | 170 | MW | BACKUP FUEL: ULTRA LOW SULFUR DIESEL WITH A MAXIMUM SULFUR CONTENT OF 0.0015%, BY WEIGHT | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DLN 2.6 COMBUSTORS TO MINIMIZE NOX EMISSSIONS. | 9 | PPMVD @ 15% O2 | 24-HR BLOCK AVG BY CEMS | BACT-PSD |  | Y | 0 | U | 59 | LB/H | 3 ONE HOUR RUN BY 7E OR 20 | 9 | PPMVD @ 15% O2 | 24-HR BLOCK AVG BY CEMS | 0 | 0 | N
TX-0769 | VAN ALSTYNE ENERGY CENTER (VAEC) | NAVASOTA NORTH COUNTRY PEAKERS OPERATING COMPANY I | GRAYSON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 121051 AND PSDTX1418 | 4911 | 221112 | UNKNOWN | 12/22/2014 &nbsp;ACT | 10/27/2015 &nbsp;ACT | 2015-10-30 | 2016-07-06 | A |  | Navasota North Country Peakers Operating Company I LLC. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 MW each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN burners | 9 | PPMVD @ 15% O2 | 3-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK and IIII CTGs will operate at 2500 hours of operation per year at baseload.
TX-0695 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX |  | USA | JIM SHIELD | (312) 582-1440 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | 110423 PSDTX1366 | 4911 | 221112 | 110057000000 | 05/13/2013 &nbsp;ACT | 08/01/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | The proposed project is to construct and operate two natural gas-fired simple-cycle combustion turbine generators (CTGs) at the Ector County Energy Center (ECEC), located approximately 20 miles northwest of Odessa, Texas, in Ector County. |  | (2) combustion turbines | 15.11 | natural gas | 180 | MW | (2) GE 7FA.03, 2500 hours of operation per year each | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 9 | PPMVD | @15% O2, 3-HR ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 2500 hr/yr operation
TX-0696 | ROANâ€™S PRAIRIE GENERATING STATION | TENASKA ROANâ€™S PRAIRIE PARTNERS (TRPP), LLC | GRIMES | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 erik.hendrickson@tceq.texas.gov | 114698 PSDTX1378 | 4911 | 221112 | 110028000000 | 10/25/2013 &nbsp;ACT | 09/22/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | The proposed project is to construct and operate the RPGS comprised of three new simple cycle combustion turbine generators (CTG), fueled by pipeline quality natural gas. The new CTGs will be peaking units, designed to operate during periods of high electric demand. The three CTGs will produce between 507 and 694 MW of electricity combined, depending on ambient temperature and the model of combustion turbine (CT) selected. The applicant is considering three models of CTs; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. |  | (2) simple cycle turbines | 15.11 | natural gas | 600 | MW | The three possible CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. will operate 2,920 hours per year at full load for each CT | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 9 | PPMVD | @15% O2, 3-HR ROLLING AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | will operate 2,920 hours per year at full load for each CT
TX-0694 | INDECK WHARTON ENERGY CENTER | INDECK WHARTON, L.L.C. | WHARTON | TX |  | USA | JAMES SCHNEIDER | (847) 520-3212 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 111724 PSDTX1374 | 4911 | 221112 | unknown | 06/18/2013 &nbsp;ACT | 02/02/2015 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | Indeck Wharton, L.L.C. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will either be the General Electric 7FA (~214 MW each) or the Siemens SGT6-5000F (~227 MW each), operating as peaking units in simple cycle mode. |  | (3) combustion turbines | 15.11 | natural gas | 220 | MW | The CTGs will either be the General Electric 7FA (~214 MW each) or the Siemens SGT6-5000F (~227 MW each), operating as peaking units in simple cycle mode | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 9 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0693 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE INC | HALE | TX |  | USA | JEFF PIPPIN | (806) 418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson 512-239-2175 laura.gibson@tceq.texas.gov | 109148 PSDTX1358 | 4911 | 221112 | 110043000000 | 04/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-03-19 | 2016-07-29 | B |  | Golden Spread Electric Cooperative (GSEC) currently owns and operates Antelope Station (now renamed Antelope Elk Energy Center), a 168 MW generating facility made up of 18 quick start WÃ¤rtsilÃ¤ engines. GSEC is proposing to build a new combustion turbine-generator (CTG) facility at Antelope Station, while the 18 WÃ¤rtsilÃ¤ engines will remain and continue to be authorized by TCEQ Standard Permit. The new turbine-generator will provide primarily peaking and intermediate power needs in a highly cyclical operation. The CTG will produce approximately 100 - 200 MW of electricity, depending on loading and ambient temperature. |  | combustion turbine | 15.11 | natural gas | 202 | MW | new GE 7FA 5-Series gas turbine in a simple cycle application, with a maximum electric output of 202 megawatts (MW) and a maximum design capacity of 1,941 million British thermal units per hour (MMBtu/hr). The turbine will operate a maximum of 4,572 hours per year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 9 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*WV-0028 | WAVERLY POWER PLANT | PLEASANTS ENERGY LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 3046654201 | GERALD.GATTI@DYNEGY.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Steve Pursley, PE Engineer West Virginia Division of Air Quality 601-57th St., SE Charleston, WV 25304 Phone: (304) 926-0499 x1218 Fax: (304) 926-0478 steve.r.pursley@wv.gov | R14-0034A | 4911 | 221112 | 110063000000 | 11/30/2017 &nbsp;ACT | 03/13/2018 &nbsp;ACT | 2018-05-29 | 2018-05-29 | U | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/073-00022_PERM_R14-0034A.pdf | 300 MW Sinple-Cycle Peaking Plant | Modification to existing PSD Permit (R14-0034, RBLC Number WV-0027) to add &lsquo;&lsquo;advanced gas path&lsquo;&lsquo; technology to the turbines that was defined as a &lsquo;&lsquo;change in the method of operation&lsquo;&lsquo; that resulted a major modification to the turbines. | GE 7FA.004 Turbine | 15.11 | Natural Gas | 167.8 | MW | This one entry is for both turbines as they are the same. Each turbine, after this modification, is a nominal 167.8 MW GE Model 7FA.004. Has oil-fire backup. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry LNB | 9 | ppmv |  | BACT-PSD | NSPS | U | 0 | U | 232.3 | TONS/YEAR |  | 9 | PPM |  | 0 | 0 | N
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry low NOx burners | 9 | PPMVD |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0777 | UNION VALLEY ENERGY CENTER | NAVASOTA SOUTH PEAKERS OPERATING COMPANY I, LLC. | NIXON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 120973 AND PSDTX1420 | 4911 | 221112 | UNKNOWN | 02/06/2015 &nbsp;ACT | 12/09/2015 &nbsp;ACT | 2015-12-03 | 2016-07-06 | A |  | three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 megawatt (MW) each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low NOX burners | 9 | PPMVD @ 15% O2 | 3-HR ROLLING AVERAGE PEAK | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & IIII
TX-0768 | SHAWNEE ENERGY CENTER | SHAWNEE ENERGY CENTER, LLC | HILL | TX |  | USA | NEIL O'DONOVAN | 312-422-1608 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, P.E., 512-239-1353, joseph.janecka@tceq.texas.gov | PSDTX1442, 125963 | 4911 | 221112 | UNKNOWN | 07/31/2015 &nbsp;ACT | 10/09/2015 &nbsp;ACT | 2015-10-05 | 2016-07-06 | A |  | Electric Generating Utility: The project will consist of four gas fired combustion turbines (CTGs). The CTGs are fueled with pipeline quality natural gas and will operate in simple cycle mode. The gas turbines will be one of two options. |  | Simple cycle turbines greater than 25 megawatts (MW) | 15.11 | natural gas | 230 | MW | Siemens Model SGT6-5000 F5ee â€“ 230 MW or Second turbine option: General Electric Model 7FA.05TP â€“ 227 MW | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx burners | 9 | PPMVD @ 15% O2 |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,920 hours on a 12-month rolling average.
TX-0733 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JOLLY HAYDEN | 806-349-5250 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, (512)239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358M1 | 4911 | 221112 | 110043000000 | 03/20/2015 &nbsp;ACT | 05/12/2015 &nbsp;ACT | 2015-05-04 | 2016-06-08 | B |  | Golden Spread Electric Cooperative, Inc. (GSEC) is requesting authorization for three additional simple cycle electric generating plants at an existing site to meet increased energy demand in the area. The generating equipment consists of three new GE 7F5-Series natural gas-fired combustion turbine generators (CTGs). Each turbine has a maximum electric output of 202 MW. |  | Simple Cycle Turbine &amp; Generator | 15.11 | natural gas | 202 | MW | 3 additional GE 7F 5-Series Combustion Turbine Generators | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx burners | 9 | PPMVD AT 15% O2 |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | operation of each turbine is limited to 4,572 hours per year
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Simple Cycle Turbine | 15.11 | natural gas | 227.5 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx burners (control), natural gas, good combustion practices, limited operating hours (prevention) | 9 | PPMV | 15% O2 3-H AVG | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Economic reasonableness, operation of each turbine is limited to 2000 hours per year.
GA-0139 | DAHLBERG COMBUSDTION TURBINE ELECTRIC GENERATING FACILITY (P | SOUTHERN POWER COMPANY | JACKSON | GA | 30565 | USA | MR. E.S. (SCOTT) DIAL | 704 278-6601 | ESDIAL@SOUTHERNCO.COM | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-157-0034-V-04-1 | 4911 | 221112 | UNKNOWN | 07/10/2008 &nbsp;ACT | 05/14/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | C |  | PLANT DAHLBERG HAS PROPOSED TO CONSTRUCT AND OPERATE FOUR ADDITIONAL SIMPLE-CYCLE COMBUSTION TURBINES (SOURCE CODES: CT11-CT14) AND ONE FUEL OIL STORAGE TANK. THE PROPOSED PROJECT WILL HAVE A NOMINAL GENERATING CAPACITY OF 760 MW. THE FACILITY IS CURRENTLY PERMITTED TO OPERATE 10 DUAL-FUELED SIMPLE-CYCLE CTG's. AFTER THE EXPANSION, THE FACILITY WILL HAVE A TOTAL NOMINAL GENERATING CAPACITY OF 1530 MW. |  | SIMPLE CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.11 | NATURAL GASE | 1530 | MW | THE PROCESS USES FUEL OIL FOR BACKUP AT THE RATE OF 2129 MMBUT/H | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | DRY LOW NOX BURNERS (FIRING NATURAL GAS). WATER INJECTION (FIRING FUEL OIL). | 9 | PPM@15%02 | 3 HOUR AVERAGE/CONDITION 3.3.23 | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 42 | PPM@15%02 | 3 HOUR AVERAGE/CONTIION 3.3.27 | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE 7FA Simple Cycle Combustion Turbine | 15.11 | Pipeline quality natural gas | 1780 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low NOx burners and fire only pipeline natural gas | 9 | PPMDV | 24-HR ROLLING AVE, CORRECTED TO 15% O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0764 | NACOGDOCHES POWER ELECTRIC GENERATING PLANT | NACOGDOCHES POWER, LLC | NACOGDOCHES | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem 512-239-1310 Tzvi.shalem@tceq.texas.gov | 77679, PSDTX1061M1 & O-3455 | 4911 | 221112 | 110044000000 | 06/25/2015 &nbsp;ACT | 10/14/2015 &nbsp;ACT | 2015-09-16 | 2016-07-06 | B |  | Nacogdoches Power, LLC is requesting authorization for one natural gas fired, simple cycle combustion turbine generator (CTG). The CTG will be a Siemens F5 and have a nominal electric output of 232 megawatts (MW). |  | Natural Gas Simple Cycle Turbine (&gt;25 MW) | 15.11 | natural gas | 232 | MW | One Siemens F5 simple cycle combustion turbine generator | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry Low NOx burners, good combustion practices, limited operations | 9 | PPMVD @ 15% O2 |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,500 hours on a 12-month rolling average.
TX-0701 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX |  | USA | JIM SHIELD | 312-582-1440 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Marc Sturdivant, 512-239-1313, Marc.Sturdivant@tceq.texas.gov | 110423, PSDTX1366 | 4911 | 221112 | 110013000000 | 08/01/2014 &nbsp;ACT | 05/13/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is for two natural gas fired simple cycle CTGs. The proposed models include GE7Fa.03 and GE7Fa.05. They have an output of 165-193 MW. The new CTGs will operate as peaking units and will be limited to 2500 hours per year of operation each. |  | Simple Cycle Combustion Turbines | 15.11 | natural gas | 180 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Dry low NOx combustor | 9 | PPMVD | 15%O2, 3HR ROLLING BASIS | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0734 | CLEAR SPRINGS ENERGY CENTER (CSEC) | NAVASOTA SOUTH PEAKERS OPERATING COMPANY II, LLC. | GUADALUPE | TX | 78155 | USA | FRANK GIACALONE | (281) 252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jack Coleman, 512-239-1255, jack.coleman@tceq.texas.gov | 120849 AND PSDTX1414 | 4911 | 221112 | Not Found | 02/20/2015 &nbsp;ACT | 05/08/2015 &nbsp;ACT | 2015-05-08 | 2018-04-18 | A |  | Navasota South Peakers Operating Company II LLC. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 MW each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low-NOx (DLN) burners | 9 | PPMVD @ 15% O2 | 3-HR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK & IIII CTGs will operate at 2500 hours of operation per year at baseload.
TX-0540 | BOSQUE COUNTY POWER PLANT | BOSQUE POWER COMPANY LLC | BOSQUE | TX | 76644 | USA | MS KATHY FRENCH | 6365322200 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | MS. BRIDGET MALONE (512) 239-4286 | 40620 | 4911 | 221112 | 4803500002 | 10/26/2007 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | PSDTX931M1 | ELECTRICAL GENERATION | 15.11 | NATURAL GAS | 170 | MW | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DRY LOW-NOX (DLN) COMBUSTERS WHEN THE COMBUSTION TURBINE IS OPERATING IN THE SIMPLE CYCLE MODE. | 9 | PPMVD | 24-HOUR 15% O2 | BACT-PSD |  |  | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0826 | MUSTANG STATION | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | YOAKUM | TX |  | USA | JEFF PIPPIN | 806-418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | 72579, PSDTX1080M1, GHGPSDTX13 | 4911 | 221112 | 110042000000 | 06/12/2017 &nbsp;ACT | 08/16/2017 &nbsp;ACT | 2017-07-24 | 2018-04-18 | C |  | GE7FA combustion turbine (Unit 6) to increase the hours of operation to 3000 hours per year. The turbine construction was completed the first quarter of 2013 and initial firing began on April 1, 2013. |  | Simple Cycle Turbine | 15.11 | NATURAL GAS | 162.8 | MW | Unit 6 Turbine is limited to 3000 hours per year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low-NOx burners | 9 | PPMVD |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK MACT YYYY
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110065000000 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Large Combustion Turbines &gt; 25 MW | 15.11 | natural gas | 232 | MW | 4 Simple cycle CTGs, 2,500 hr/yr operational limitation. Facility will consist of either 232 MW (Siemens) or 220 MW (GE) | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low-NOx burners (DLN), good combustion practices | 9 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Subparts KKKK and TTTT
ND-0028 | R.M. HESKETT STATION | MONTANA-DAKOTA UTILITIES CO. | MORTON | ND | 58554 | USA | ABBIE KREBSBACH | (701) 222-7844 | ABBIE.KREBSBACH@MDU.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Primary contact is Tom Bachman at (701) 328-5188. | PTC13016 | 4911 | 221112 | 110022000000 | 11/07/2012 &nbsp;ACT | 02/22/2013 &nbsp;ACT | 2013-04-01 | 2017-04-28 | B |  | Addition of a natural gas-fired turbine (Unit 3) to an exisiting coal-fired power plant. The turbine will be used for supplying peak power and is rated at 986 MMBtu/hr and 88 MWe at average site conditions. |  | Combustion Turbine | 15.11 | Natural gas | 986 | MMBTU/H | Turbine is a GE Model PG 7121 (7EA) used as a peaking unit. | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low-NOx combustion (DLN) | 9 | PPMVD @15% OYYGEN | 4 H.R.A. WHEN > 50MWE AND > 0 DEGREES F | BACT-PSD | NSPS | Y | 0 | U | 96 | PPMVD @15% OXYGEN | 4 H.R.A. WHEN < 50 MWE OR < 0 DEGREES F | 399 | LB/H | 1 HOUR AVG./ANY TIME | 0 | 0 | N | 2012
WV-0026 | WAVERLY FACILITY | PLEASANTS ENERGY, LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 304-665-4201 | GERALD.GATTI@GDFSUEZNA.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0034 | 4911 | 221112 | 110010000000 | 04/18/2016 &nbsp;ACT | 01/23/2017 &nbsp;ACT | 2017-03-21 | 2018-05-01 | D | http://www.dep.wv.gov/daq/Documents/January 2017 Permits and Evals/073-00022_PERM_R14-0034.pdf | 300 MW, natural gas fired, simple cycle peaking power facility | In this permitting action PSD only applies to the modified combustion turbines based on the relaxation of an original synthetic minor permit issued in 1999. Project also involves previous installation of turbo-charging. All BACT emission limits are given without turbocharging and startup/shutdown emissions are not included. Please contact above engineer for more information. There are two identical turbines but only one is listed. | GE Model 7FA Turbine | 15.11 | Natural Gas | 1571 | mmbtu/hr | There are two identical units at the facility. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry Low-NOx Combustion System (DLNB), Water Injection | 9 | PPM | NATURAL GAS | BACT-PSD | NSPS | U | 0 | U | 49 | PPM | FUEL OIL | 9 | PPM | NATURAL GAS | 0 | 0 | N |  | Additional emission limits are in the permit for use of turbocharging and startup/shutdown emissions. Please contact if need additional information.
IL-0121 | INVENERGY NELSON EXPANSION LLC | INVENERGY | LEE | IL | 61058 | USA | GORDON GRAY | 312-582-1290 | GGRAY@INVENERGY.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Bob Smet; 217-785-9250; robert.smet@illinois.gov | 15060042 | 4911 | 221112 | Not Found | 07/28/2016 &nbsp;ACT | 09/27/2016 &nbsp;ACT | 2017-01-27 | 2017-04-28 | B | https://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/9dbc452815081576862580b2006897b4/$FILE/ATT4AK5N.pdf/15060042.pdf | Peaking facility at an existing major source. The expansion will consist of two simple cycle combustion turbines and a fuel heater. |  | Two Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 190 | MW | Two simple cycle combustion turbines used for peaking purposes and fired primarily on natural gas with ULSD as a secondary fuel. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry low-NOx combustion technology for natural gas and low-NOx combustion technology and water injection for ULSD. | 9 | ppmv |  | BACT-PSD | NSPS | N | 0 | U | 0.164 | LB/MMBTU |  | 0 |  |  | 0 | 0 | Y |  | Natural Gas: 9 ppmv at 15 percent O2 (equivalent to 0.033 lb/mmBtu, HHV). ULSD: 42 ppmv at 15 percent O2 (equivalent to 0.164 lb/mmBtu, HHV). During commissioning, NOx shall not exceed: Natural gas: 110 lb/hr, 110 lb/cycle ULSD: 349 lb/hr, 275 lb/cycle
MN-0075 | GREAT RIVER ENERGY - ELK RIVER STATION | GREAT RIVER ENERGY | SHERBURNE | MN | 55330 | USA | MARK STROHFUS | 7634455210 | MSTROHFU@GRENERGY.COM | 5 | MN001 | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | MR. RICHARD CORDES | (651)757-2291 | RICHARD.CORDES@STATE.MN.US | TONI VOLKMEIER, TONI.VOLKMEIER@PCA.STATE.MN.US | 14100003-004 | 4911 | 221119 | UNKNOWN | 03/31/2008 &nbsp;EST | 07/01/2008 &nbsp;ACT | 2008-12-01 | 2009-01-26 | B |  | THE FACILITY IS AN ELECTRIC POWER GENERATING STATION BURNING REFUSE DERIVED FUEL (RDF). THE RDF BURNED AT THIS FACILITY IS PROCESSED FROM MUNICIPAL SOLID WASTE. THE FACILITY PRODUCES APPROXIMATELY 40 MEGAWATTS OF ELECTRICITY. THERE IS ALSO A SINGLE CYCLE COMBUSTION TURBINE GENERATOR (CTG) |  | COMBUSTION TURBINE GENERATOR | 15.11 | NATURAL GAS | 2169 | MMBTU/H | GENERATOR IS A SIMPLE CYCLE COMBUSTION TURBINE, WHICH WILL BE OPERATED AS A PEAK-SHAVING UNIT. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DRY LOW-NOX COMBUSTION WHEN COMBUSTING NATURAL GAS | 9 | PPM | 4 HR ROLLING AVG, NG, >/= 60% LOAD | BACT-PSD | OTHER , NSPS | Y | 0 | U | 25 | PPM | 4 HR ROLLING AVG, NG, <60% LOAD | 96 | PPM | 4 HR ROLLING AVG, <75% LOAD | 0 | 0 | N |  | SEPARATE LIMIT DEVELOPED FOR NOX WHEN COMBUSTION NATURAL GAS OR FUEL OIL, AT DIFFERING LOADS
TX-0794 | HILL COUNTY GENERATING FACILITY | BRAZOS ELECTRIC COOPERATIVE | HILL | TX |  | USA | MIKE MEYERS | (254)750-6228 | MMEYERS@BRAZOSELECTRIC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512)239-1512, randy.hamilton@tceq.texas.gov | 130051,PSDTX1450, GHGPSDTX131 | 4911 | 221112 | UNKNOWN | 12/18/2015 &nbsp;ACT | 04/07/2016 &nbsp;ACT | 2016-04-05 | 2016-07-29 | A |  | Four simple cycle combustion turbine electric generators are proposed. Natural gas or ultra-low sulfur diesel fuel oil are the fuels. Turbine model options are: General Electric (GE) 7FA.03, GE 7FA.04, GE 7FA.05, and Siemes SGT6-5000(5)ee. Electric output is between 684 and 928 megawatts (MW). |  | Simple cycle turbine | 15.11 | natural gas | 171 | MW | Each combustion turbine is limited to 2,920 hours of annual operation, including startup and shutdown hours. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low-NOx combustors (DLN). DLN combustors use two stages of combustion, transitioning from initial startup with fuel and flame in the primary nozzles only, through a lean lean stage with fuel and flame in the primary and secondary nozzles, to fuel in the secondary stage only, extinguishing the primary flame, and in full operation, premix mode, with fuel to both nozzles, but flame only in the second stage. When natural gas and air are well-mixed before combustion, the flame temperature and resulting NOx emissions are greatly reduced compared to conventional diffusion flame combustion. | 9 | PPMVD @ 15% O2 | 3-HR ROLLING AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
FL-0346 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-011-AC | 4911 | 221112 | 110002000000 | 11/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-01-08 | 2016-05-05 | D | http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | In this project, 24 peaking turbines from the Lauderdale facility are being replaced with five 200 MW combustion turbines at Lauderdale. The turbines will fire primarily natural gas, but may also fire ULSD fuel oil. Triggers PSD for NOx, PM, CO, VOC, and GHG. GHG permit issued by US EPA Region 4. Technical evaluation available at http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2000 | MMBtu/hr (approx) | Throughput could vary slightly (+/- 120 MMBtu/hr) depending on final selection of turbine model and firing of natural gas or oil. Primary fuel is expected to be gas. Each turbine limited to 3300 hrs per rolling 12-month period. Of these 3300 hrs, no more than 500 may use ULSD fuel oil. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | dry low-NOx technology and wet injection. Water injection must be used when firing ULSD. | 9 | PPMVD @ 15% 02 | 24-HR BLOCK AVG, BY CEMS (NAT GAS) | BACT-PSD | NSPS | U | 0 | U | 77 | LB/H | 24-HR BLOCK, BY CEMS (NAT GAS) | 0 |  |  | 0 | 0 | N |  | NOx CEMS required -- employing EPA Method 7E. For natural gas, 9.0 ppmvd@15% O2 and 77 lb/hr. For oil, 42.0 ppmvd@15% O2 and 378.0 lb/hr.
FL-0354 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-013-AC | 4911 | 221112 | 110002000000 | 04/20/2015 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2016-02-17 | 2016-07-06 | D | https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | Re-affirmed BACT determinations in Permit No. 0110037-011-AC. Also, new GHG BACT determination. Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.D.ZIP | Five 200-MW combustion turbines | 15.11 | Natural gas | 2100 | MMBtu/hr (approx) | Five simple cycle GE 7F.05 turbines. Max of 3390 hours per year per turbine. Of the 3390 hours per year, up to 500 hour may be on ULSD fuel oil. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Dry-low-NOx combustion system. Wet injection when firing ULSD. | 9 | PPMVD@15%O2 | 24-HR BLOCK AVERAGE | BACT-PSD | NSPS | U | 0 | U | 42 | PPMVD@15%O2 | 4-HR ROLLING | 0 |  |  | 0 | 0 | N |  | Compliance by NOx CEMS. Also subject to NSPS Subpart KKKK.
TX-0691 | PH ROBINSON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | GALVESTON | TX |  | USA | CRAIG ECKBERG | (832) 357-5291 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 erik.hendrickson@tceq.texas.gov | 108182 PSDTX1346 | 4911 | 221112 | 110002000000 | 02/06/2013 &nbsp;ACT | 05/20/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG proposes to construct six natural gas-fired simple cycle combustion turbine generators (CTG) for peaking, designed to operate during periods of high electric demand. The six CTGs selected by NRG are General Electric Frame 7E turbines have an ISO rating of 65 MW and a nominal maximum generating capacity of 80 MW. Each of the turbines will not exceed 20 percent annual capacity (equivalent to 1,752 full load hours) in any single year or 10 percent annual capacity factor (equivalent to 876 full load hours) averaged over any three year period. |  | (6) simple cycle turbines | 15.11 | natural gas | 65 | MW | General Electric Frame 7E turbines have an ISO rating of 65 MW and a nominal maximum generating capacity of 80 MW. The turbines were originally constructed as Frame 7B units that were remanufactured in 1999 and upgraded to 7E machines Each of the turbines will not exceed 20 percent annual capacity (equivalent to 1,752 full load hours) in any single year or 10 percent annual capacity factor (equivalent to 876 full load hours) averaged over any three year period, which qualifies each of the CTGs as Acid Rain Peaking Units under 40 CFR 72.2 | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DLN combustors | 15 | PPMVD | @15% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | limited use
OH-0333 | DAYTON POWER & LIGHT ENERGY LLC | DAYTON POWER & LIGHT COMPANY | MONTGOMERY | OH | 45439 | USA | CARRIE BURKS | 937-331-3042 |  | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104867 | 4911 | 221112 | 110000000000 | 04/30/2009 &nbsp;ACT | 12/03/2009 &nbsp;ACT | 2010-05-13 | 2010-05-20 | C |  | Seven simple cycle stationary combustion turbines all with rating of 80 MW and nominal heat input of 1115.2 mmBtu/hr using natural gas or No. 2 fuel oil and all with water injection control and last 5 also with low NOx burners. | Simple cycle stationary combution turbines issed in 2 different permits. Four turbines in this permit with dry low NOx combustion and water injection controls. Administrative Modification to original PTI #08-04153 issued 8/7/01, to incorporate low mass emissions methodology as allowed per 40 CFR 75.19 in lieu of methods under Appendix D or E to Part 75, by meeting the requirements of having mass emissions of less than 25 T/YR SO2 and less than 100 T/YR NOx (per turbine) based on 3 years of operation. Modification also reduced permitted formaldehyde emissions by 8.7 tons, recalculated based on the restriction on hours of operation. | Turbines (4), simple cycle, natural gas | 15.11 | NATURAL GAS | 15020 | H/YR | Hours per year for all 4 turbines | Nitrogen Oxides (NOx) | Other - Method 7 or 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low NOx burners | 15 | ppmv | at 15% 02EACH TURBINE | BACT-PSD | SIP | U | 0 | Y | 1373.32 | T/YR | PER ROLLING 12-MO. FOR 4 UNITS &ALL FUEL | 15 | PPMV | AT 15% OXYGEN ON A DRY BASIS AS 1HR AVG. | 0 | 0 | N |  | T/YR limit is for both fuels and for the 4 turbines combined.
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110030000000 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | dry low nox burners | 15 | PPMVD | @15%O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0258 | CALCASIEU PLANT | ENTERGY GULF STATES LA LLC | CALCASIEU | LA | 70665 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: TEGAN TREADAWAY, (225) 219-3408 | PSD-LA-746 | 4911 | 221112 | 110007000000 | 11/10/2009 &nbsp;ACT | 12/21/2011 &nbsp;ACT | 2012-02-01 | 2012-04-03 | C |  | 320 MW POWER PLANT COMPRISED OF 2 NATURAL GAS-FIRED SIMPLE CYCLE COMBUSTION TURBINES. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS PSD TRIGGERED DUE TO RELAXATION OF A FEDERALLY-ENFORCEABLE CONDITION LIMITING POTENTIAL EMISSIONS BELOW MAJOR STATIONARY SOURCE THRESHOLDS. | TURBINE EXHAUST STACK NO. 1 &amp; NO. 2 | 15.11 | NATURAL GAS | 1900 | MM BTU/H EACH |  | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | DRY LOW NOX COMBUSTORS | 17.5 | ppmv | at 15% 02 HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 798 | LB/H | HOURLY MAXIMUM / STARTUP & SHUTDOWN ONLY | 17.5 | PPMVD @ 15% O2 |  | 0 | 0 | N |  | LIMITS ARE PER TURBINE EXHAUST STACK. AGGREGATE NOX EMISSIONS FROM BOTH TURBINE EXHAUST STACKS ARE LIMITED TO 391.30 TONS PER YEAR. STARTUP & SHUTDOWN OPERATIONS ARE LIMITED TO 520 HOURS PER YEAR.
TX-0816 | CORPUS CHRISTI LIQUEFACTION | CORPUS CHRISTI LIQUEFACTION STAGE III, LLC | SAN PATRICIO | TX |  | USA | KEITH LITTLE | (713) 375-5204 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 139479, PSDTX1496, GHGPSDTX157 | 4925 | 221210 | Not Found | 11/16/2016 &nbsp;ACT | 02/14/2017 &nbsp;ACT | 2017-02-07 | 2018-04-18 | B |  | Trains 4 and 5 will consist of 12 natural gas compressor turbines, 2 thermal oxidizers, 2 sets of flares each comprised of one wet gas flare and one dry gas flare, 2 amine surge tanks (maintenance, startup, and shutdown [MSS] only), 3 diesel generators, 3 fire-water pump diesel engines, 6 fixed roof diesel storage tanks, and piping components. |  | Refrigeration compressor turbines | 15.11 | NATURAL GAS | 40000 | HP | 2 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane, ethylene, and methane section compressors. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low emission burners | 25 | PPMDV | @ 15% O2 | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Subpart KKKK
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057000000 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.11 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane and methane section compressors. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry low emission combustors | 25 | PPMVD | @ 15% O2, 4 HOUR ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069000000 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Gas Turbines (8 units) | 15.11 | natural gas | 333 | mm btu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry Low NOX burners and good combustion practices | 25 | PPMVD | @15 %O2 | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
[40 empty] | Range Low | 9 | PPMV
[40 empty] | Range High | 25 | PPMV
[40 empty] | Mean | 10.9605 | PPMV
[40 empty] | Median | 9 | PPMV
[40 empty] | Mode | 9 | PPMV

## SCR
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Trubine (EP04) | 15.11 | Natural Gas | 40 | MW |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 5 | PPMV AT 15% O2 | 1-HOUR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 7.7 | LB/H | 30-DAY ROLLING AVERAGE | 36 | T/YR |  | 8308 | 8308 | N | 2011
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP03) | 15.11 | Natural Gas | 40 | MW |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 5 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD | NSPS | N | 0 | U | 7.7 | LB/H | 30-DAY ROLLING AVERAGE | 36 | T/YR |  | 8308 | 8308 | N | 2011
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP05) | 15.11 | Natural Gas | 40 | MW |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 5 | PPMV AT 15% O2 | 1-HOUR | BACT-PSD | NSPS | N | 0 | U | 7.7 | LB/H | 30-DAY ROLLING AVERAGE | 36 | T/YR |  | 8308 | 8308 | N | 2011
ND-0030 | LONESOME CREEK GENERATING STATION | BASIN ELECTRIC POWER COOP. | MCKENZIE | ND | 58831 | USA | JERRY MENGE | (701)223-0441 |  | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact at (701) 328-5188. | PTC 13049 | 4911 | 221112 | 110057000000 | 04/05/2013 &nbsp;EST | 09/16/2013 &nbsp;ACT | 2013-09-24 | 2017-06-28 | B |  | Three natural gas fired simple cycle turbines used to generate electricity for peak power demand. The turbines are GE LM6000 PF Sprint units with a nominal capacity of 45 MW each. |  | Natural Gas Fired Simple Cycle Turbines | 15.11 | Natural gas | 412 | MMBTU/H | The heat input is for a single unit. | Nitrogen Oxides (NOx) | Other - CEM | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 5 | PPMVD | 4 HOUR ROLLING AVERAGE EXCEPT STARTUP | BACT-PSD | NSPS | N | 90 | N | 18.5 | LB | TOTAL FOR 30 MINUTES DURING STARTUP | 0 |  |  | 0 | 0 | N |  | The startup limit is for each unit. The three units are limited to a total combined emission rate of 42.9 pounds per hour (1-hour average) at all times.
CA-1174 | EL CAJON ENERGY LLC | EL CAJON ENERGY LLC | SAN DIEGO | CA | 92020 | USA | GENEVIEVE HUFFMAN |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Evariste Haury (858)-586-2745 Evariste.Haury@sdcounty.ca.gov | 987824 | 519 | 311999 | 110043000000 | 11/01/2008 &nbsp;ACT | 12/11/2009 &nbsp;ACT | 2010-09-20 | 2011-04-11 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 49.95 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 2.5 | PPMV | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ND-0029 | PIONEER GENERATING STATION | BASIN ELECTRIC POWER COOPERATIVE | WILLIAMS | ND |  | USA | JERRY MENGE | 7012230441 | JMENGE@BEPC.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact. | PTC 13037 | 4911 | 221112 | 110058000000 | 02/19/2013 &nbsp;ACT | 05/14/2013 &nbsp;ACT | 2013-06-19 | 2016-11-03 | B |  | Three GE LM6000 PC SPRINT natural gas fired turbines used to generate electricity for peak periods. | The permit was for the addition of 2 turbines to the station. Since a synthetic minor limit was relaxed for the first unit, BACT was required for all three turbines. | Natural gas-fired turbines | 15.11 | Natural gas | 451 | MMBTU/H | Rating is for each turbine. | Nitrogen Oxides (NOx) | Other - CEM | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 5 | PPPMVD | 4 HR. ROLLING AVERAGE EXCEPT FOR STARTUP | BACT-PSD | NSPS | U | 80 | N | 19 | LB/H | DURING STARTUP | 0 |  |  | 0 | 0 | N |  | RBLC Staff: Original Emis Limit 2 Units were Numeric Limit - &lsquo;&lsquo;LB&lsquo;&lsquo; and Avg Time/Condition - &lsquo;&lsquo;PER HOUR DURING STARTUP&lsquo;&lsquo; The Emission Units are usually &lsquo;&lsquo;mass unit PER time unit&lsquo;&lsquo;. Separating them out makes understanding limit difficult for the users. The units were combined. The corrected entry is: Numeric Limit - &lsquo;&lsquo;LB/H&lsquo;&lsquo; Avg Time/Condition - &lsquo;&lsquo;During Startup&lsquo;&lsquo;
CA-1223 | PIO PICO ENERGY CENTER | PIO PICO ENERGY CENTER, LLC | OTAY MESA | CA | 92154 | USA | GARY CHANDLER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SD 11-01 | 4911 | 221112 | 110045000000 | 06/14/2012 &nbsp;ACT | 11/19/2012 &nbsp;ACT | 2013-03-05 | 2014-01-28 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | CONSTRUCTION OF THREE GENERAL ELECTRIC (GE) LMS100 NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 100 MW EACH. THE PROJECT WILL HAVE AN ELECTRICAL OUTPUT OF 300 MW. | NOTE: PERMIT ISSUED 11/19/2012. ENVIRONMENTAL APPEALS BOARD REMANDED THE PM BACT ANALYSIS TO REGION 9 ON 8/2/2013. FINAL PERMIT ISSUED ON 2/28/2014. ONE PETITION FILED IN 9TH CIRCUIT FEDERAL COURT CHALLENGING THE FINAL PERMIT DECISION. THIS LAWSUIT WAS DISMISSED ON 6/17/2014 IN RESPONSE TO PETITIONERSâ€™ MOTION FOR VOLUNTARY DISMISSAL. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.11 | NATURAL GAS | 300 | MW | Three simple cycle combustion turbine generators (CTG). Each CTG rated at 100 MW (nominal net). | Nitrogen Oxides (NOx) | Other - EPA mETHOD 7E, OR METHOD 7E & 19 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR | 2.5 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 8.18 | LB/H | 1-HR AVG | 0 |  |  | 0 | 0 | N
CA-1176 | ORANGE GROVE PROJECT |  | SAN DIEGO | CA | 92059 | USA |  |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Camqui Nguyen (858)586-2747 camqui.nguyen@sdcounty.ca.gov | 985708 | 491 | 221122 | UNKNOWN | 11/03/2007 &nbsp;ACT | 12/04/2008 &nbsp;ACT | 2010-09-21 | 2011-06-27 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 49.8 | MW | Combustion turbine for peaking power plant | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR water injection | 2.5 | PPM | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1175 | ESCONDIDO ENERGY CENTER LLC |  | SAN DIEGO | CA | 92029 | USA |  |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Arthur Carbonell (858)-586-2741 arthur.carbonell@sdcounty.ca.gov | 985693 | 491 | 221122 | UNKNOWN | &nbsp; | 07/02/2008 &nbsp;ACT | 2010-09-21 | 2011-06-27 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 46.5 | MW |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR water injection | 2.5 | PPMV@15% OXYGEN | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055000000 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Three simple cycle combustion turbines | 15.11 | natural gas | 799.7 | MMBTU/H | Three GE, LMS100PA, natural gas-fired, simple cycle CTG rated at 799.7 MMBtu per hour each,based on HHV. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction (SCR) | 5 | PPMVD AT 15% O2 | 1-HR AVE | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 0 | U | 15.5 | LB/H | 30-DAY ROLLING AVE | 0 |  |  | 0 | 0 | N |  | startup limit = 12.0 lb per event shutdown limit = 18.0 lb per event compliance with BACT limits monitored via continuous emissions monitors.
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057000000 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | GE LMS-100 combustion turbines, simple cycle with water injection | 15.11 | natural gas | 1690 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | selective catalytic reduction (SCR) with aqueous ammonia injection at all times except during startup and shutdown; Limit the time in startup or shutdown. | 2.5 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON NG | BACT-PSD |  | U | 0 | U | 3.8 | PPMDV AT 15% O2 | 3-HR ROLLING AVERAGE ON ULSD | 0 |  |  | 0 | 0 | N
[40 empty] | Range Low | 2.5 | PPMV
[40 empty] | Range High | 5 | PPMV
[40 empty] | Mean | 3.8636 | PPMV
[40 empty] | Median | 5 | PPMV
[40 empty] | Mode | 5 | PPMV

## Water Injection
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110031000000 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Generation Turbines (2) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Nitrogen Oxides (NOx) | EPA/OAR Mthd 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | water injection | 25 | ppmv | at 15% 02 HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 25 | PPMV | AT 15% O2 | 0 | 0 | N
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110031000000 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Refrigeration Compressor Turbines (16) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Nitrogen Oxides (NOx) | EPA/OAR Mthd 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | water injection | 20 | ppmv | at 15% 02HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 20 | PPMV | AT 15% O2 | 0 | 0 | N
OK-0127 | WESTERN FARMERS ELECTRIC ANADARKO | WESTERN FARMERS ELECTRIC COOPERATIVE | CADDO | OK | 73005 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2005-037-C(M-2) PSD | 4911 | 221112 | 110002000000 | 02/01/2008 &nbsp;ACT | 06/13/2008 &nbsp;ACT | 2008-12-31 | 2009-04-20 | B |  | THE FACILITY GENERATES WHOLESALE ELECTRICITY WHICH IS TRANSMITTED OVER WFECÂ¿S ELECTRICAL DISTRIBUTION SYSTEM. THE ELECTRICITY IS SOLD IN RURAL AREAS OF APPROXIMATELY 3/4 OF THE STATE OF OKLAHOMA. THE CURRENT FACILITY CONSISTS OF TWO NATURAL GAS FIRED HIGH PRESSURE BOILERS, A GAS/OIL FIRED HIGH PRESSURE BOILER, THREE GAS/OIL FIRED COMBINED CYCLE GAS TURBINES, A FIRE PUMP DIESEL ENGINE FOR EMERGENCY BACKUP, AND OTHER SOURCES WHICH ARE CONSIDERED INSIGNIFICANT OR TRIVIAL. THE THREE BOILERS ARE BACKUP UNITS THAT ONLY OPERATE WHEN IT IS FEASIBLE, SUCH AS DURING PEAK DEMAND. TWO OF THE BOILERS HAVE BEEN IDLE SINCE 1984. ONE BOILER WAS REPLACED IN 1997, AND ANOTHER WAS REPLACED IN 1998. | WESTERN FARMERS ELEC COOP PROPOSES TO CONSTRUCT AND OPERATE THREE NATURAL GAS-FIRED PEAKING ELECTRIC GENERATING UNITS AT THE FACILITY TO MEET ANTICIPATED FUTURE ENERGY DEMAND. EACH UNIT CAPACITY OF +/- 50 MW. | COMBUSTION TURBINE PEAKING UNIT(S) | 15.11 | NATURAL GAS | 462.7 | MMBTU/H | THE INSTALLATION WILL CONSIST OF THREE GENERAL ELECTRIC LM6000 SPRINT SIMPLE CYCLE AERODERIVATIVE COMBUSTION TURBINE GENERATORS. EACH OF THE TURBINES WILL HAVE A MAXIMUM PEAK HEAT INPUT RATE OF 462.7 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTUH). THE NEW COMBUSTION TURBINES WILL FIRE ONLY PIPELINE-QUALITY NATURAL GAS AND WILL BE EQUIPPED WITH WATER INJECTION. THE PROPOSED NEW UNITS WILL EACH HAVE A NOMINAL ELECTRICAL GENERATING CAPACITY OF 50 MW. ACTUAL UNIT CAPACITY WILL BE DETERMINED DURING DETAILED DESIGN OF THE PLANT AND MAY BE 5 TO 10-MW HIGHER OR LOWER THAN THE NOMINAL VALUE OF 50 MW, DEPENDING ON AMBIENT CONDITION RATINGS AND FINAL DESIGN. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | WATER INJECTION | 25 | PPM | ADJUSTED 15% O2 | BACT-PSD | NSPS | U | 0 | U | 42 | LB/H | 2,500 HR/YEAR | 0 |  |  | 0 | 0 | N |  | WATER INJECTION THAT ACHIEVES 25 PPMVD OR LESS CORRECTED TO 15% O2 IS DETERMINED ACCEPTABLE AS BACT.
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE LM6000PC SPRINT Simple cycle combustion turbine | 15.11 | Pipeline quality natural gas | 405.3 | MMBTU/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | water injection | 25 | PPMDV | 24-HR ROLLING AVE; CORRECTED TO 15% O | BACT-PSD |  | U | 0 | U | 269.3 | TONS | 12 MO CALENDAR BASIS, FOR ALL 4 UNITS | 0 |  |  | 0 | 0 | N
IN-0264 | MONTPELIER GENERATING STATION | AES OHIO GENERATION, LLC | WELLS | IN | 46781 | USA | DREW PARKER | 9373314993 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: MADHURIMA MOULIK 317-233-6663 MMOULIK@IDEM.IN.GOV SECTION CHIEF: JASON KRAWCZYK 317-234-5174 | 179-37209-00026 | 4911 | 221112 | 110021000000 | 05/23/2016 &nbsp;ACT | 01/06/2017 &nbsp;ACT | 2017-07-07 | 2017-11-17 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/37209F.PDF | COMBUSTION TURBINES |  | PRATT &amp; TWIN-PAC SIMPLE CYCLE TURBINES | 15.11 | NATURAL GAS | 270.9 | MMBTU/H | NO. 2 DIESEL OIL BACKUP FUEL | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | WATER INJECTION | 25 | PPMV | AT 15% O2 FOR NATURAL GAS | BACT-PSD |  |  | 0 |  | 42 | PPMV | AT 15% O2 FOR FUEL OIL | 0 |  |  | 0 | 0 | N |  | 0.14 LB/MMBTU FOR NATURAL GAS AND 0.24 LB/MMBTU FOR FUEL OIL; EACH TURBINE LIMITED TO 4555 HOURS OF OPERATION PER 12 MONTH PERIOD
[40 empty] | Range Low | 20 | PPMV
[40 empty] | Range High | 25 | PPMV
[40 empty] | Mean | 24 | PPMV
[40 empty] | Median | 25 | PPMV
[40 empty] | Mode | 25 | PPMV