## PermitSearchResults (47)
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 2 COMBUSTION TURBINES | 15.11 | NATURAL GAS | 130 | MW | TWO GENERAL ELECTRIC (GE) FRAME 7EA COMBUSTION TURBINES (CTS) WITH A NOMINAL NET 87.2 MEGAWATT (MW) RATED CAPACITY, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), EQUIPPED WITH DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION SYSTEM (SCR), AND OXIDATION CATALYST | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF FACILITY PROCESS FUEL GAS OR PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.0033 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0121 | INVENERGY NELSON EXPANSION LLC | INVENERGY | LEE | IL | 61058 | USA | GORDON GRAY | 312-582-1290 | GGRAY@INVENERGY.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Bob Smet; 217-785-9250; robert.smet@illinois.gov | 15060042 | 4911 | 221112 | Not Found | 07/28/2016 &nbsp;ACT | 09/27/2016 &nbsp;ACT | 2017-01-27 | 2017-04-28 | B | https://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/9dbc452815081576862580b2006897b4/$FILE/ATT4AK5N.pdf/15060042.pdf | Peaking facility at an existing major source. The expansion will consist of two simple cycle combustion turbines and a fuel heater. |  | Two Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 190 | MW | Two simple cycle combustion turbines used for peaking purposes and fired primarily on natural gas with ULSD as a secondary fuel. | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | turbine design and good combustion practices | 0.0038 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0.015 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission 1 (natural gas): 0.0038 lb/mmbtu* Emission 2 (ULSD): 0.0150 lb/mmbtu* *During an hour that includes a startup, the particulate emissions of the turbine shall not exceed 7.5 lb/hr (natural gas) and 32.2 lb/hr (ULSD).
IL-0121 | INVENERGY NELSON EXPANSION LLC | INVENERGY | LEE | IL | 61058 | USA | GORDON GRAY | 312-582-1290 | GGRAY@INVENERGY.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Bob Smet; 217-785-9250; robert.smet@illinois.gov | 15060042 | 4911 | 221112 | Not Found | 07/28/2016 &nbsp;ACT | 09/27/2016 &nbsp;ACT | 2017-01-27 | 2017-04-28 | B | https://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/9dbc452815081576862580b2006897b4/$FILE/ATT4AK5N.pdf/15060042.pdf | Peaking facility at an existing major source. The expansion will consist of two simple cycle combustion turbines and a fuel heater. |  | Two Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 190 | MW | Two simple cycle combustion turbines used for peaking purposes and fired primarily on natural gas with ULSD as a secondary fuel. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | turbine design and good combustion practices | 0.005 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0.02 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission 1 (natural gas): 0.0050 lb/mmbtu* Emission 2 (ULSD): 0.020 lb/mmbtu* *During an hour that includes a startup, the particulate emissions of the turbine shall not exceed 10.0 lb/hr (natural gas) and 42.7 lb/hr (ULSD).
IL-0121 | INVENERGY NELSON EXPANSION LLC | INVENERGY | LEE | IL | 61058 | USA | GORDON GRAY | 312-582-1290 | GGRAY@INVENERGY.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Bob Smet; 217-785-9250; robert.smet@illinois.gov | 15060042 | 4911 | 221112 | Not Found | 07/28/2016 &nbsp;ACT | 09/27/2016 &nbsp;ACT | 2017-01-27 | 2017-04-28 | B | https://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/9dbc452815081576862580b2006897b4/$FILE/ATT4AK5N.pdf/15060042.pdf | Peaking facility at an existing major source. The expansion will consist of two simple cycle combustion turbines and a fuel heater. |  | Two Simple Cycle Combustion Turbines | 15.11 | Natural Gas | 190 | MW | Two simple cycle combustion turbines used for peaking purposes and fired primarily on natural gas with ULSD as a secondary fuel. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - USEPA Method 201A & 202 | (Particulate Matter (PM)) | PM | P | turbine design and good combustion practices | 0.005 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0.02 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission 1 (natural gas): 0.0050 lb/mmbtu* Emission 2 (ULSD): 0.020 lb/mmbtu* *During an hour that includes a startup, the particulate emissions of the turbine shall not exceed 10.0 lb/hr (natural gas) and 42.7 lb/hr (ULSD).
NY-0103 | CRICKET VALLEY ENERGY CENTER | CRICKET VALLEY ENERGY CENTER LLC | USA | NY | 12522-0407 | USA |  | 845-877-0596 | INFO@CRICKETVALLEY.COM | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-1326-00275/00009 | 4911 | 221112 | 110043340364 | 02/03/2016 &nbsp;ACT | 02/03/2016 &nbsp;ACT | 2017-08-24 | 2017-09-28 | A | http://www.dec.ny.gov/chemical/32249.html | Cricket Valley Energy Center LLC (CVEC) constructed the Cricket Valley Energy Center (the Facility), a nominal net 1,000-megawatt (MW) combined-cycle gas turbine electric generating facility, on a site located in Dover, Dutchess County, New York. The Facility consists of three General Electric (GE) Model 7FA.05 combustion turbine generators (CTGs) operating in combined-cycle mode with supplemental firing of the heat recovery steam generators (HRSGs); natural gas will be the sole fuel fired in the CTGs and duct burners. The Facility will include a natural gas-fired auxiliary boiler, four ultra-low sulfur distillate (ULSD) fired black-start generator engines and a ULSD-fired emergency fire pump engine. In addition to the air emitting equipment, the Facility will include three steam turbine generators (STGs), an air cooled condenser (ACC) and associated auxiliary equipment and systems. Each combined cycle generating unit consisting of the CTG, HRSG and STG will be exhausted through its own stack. Air emissions from the proposed Facility primarily consist of products of combustion from the CTGs, HRSG duct burners, and ancillary combustion sources. Dutchess County is designated as in attainment with respect to the National Ambient Air Quality Standards (NAAQS) for all criteria pollutants with the exception of ozone. Based upon the potential to emit (PTE) estimates, the Facility is subject to Prevention of Significant Deterioration (PSD) requirements for emissions of carbon monoxide (CO); nitrogen oxides (NOx); particulate matter (PM) with a diameter equal to or less than 10 microns (PM10), PM with a diameter equal to or less than 2.5 microns (PM2.5); greenhouse gases (GHG); sulfuric acid mist (H2SO4); and volatile organic compounds (VOC). In accordance with the NYSDECâ€™s Nonattainment New Source Review (NNSR) permitting program, the Facility is also subject to NNSR for emissions of NOx and VOC. |  | Turbines and duct burners | 15.11 | natural gas | 228 | mw |  | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | good combustion practiced and pipeline quality natural gas | 0.005 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Also for PM-10 EPA Method 201/201A or 202 0.005 lb/mmBtu without duct firing 0.006 lb/mmBtu with duct firing Applies to all operating loads, except during startup and shutdown.
CA-1223 | PIO PICO ENERGY CENTER | PIO PICO ENERGY CENTER, LLC | OTAY MESA | CA | 92154 | USA | GARY CHANDLER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SD 11-01 | 4911 | 221112 | 110045006943 | 06/14/2012 &nbsp;ACT | 11/19/2012 &nbsp;ACT | 2013-03-05 | 2014-01-28 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | CONSTRUCTION OF THREE GENERAL ELECTRIC (GE) LMS100 NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 100 MW EACH. THE PROJECT WILL HAVE AN ELECTRICAL OUTPUT OF 300 MW. | NOTE: PERMIT ISSUED 11/19/2012. ENVIRONMENTAL APPEALS BOARD REMANDED THE PM BACT ANALYSIS TO REGION 9 ON 8/2/2013. FINAL PERMIT ISSUED ON 2/28/2014. ONE PETITION FILED IN 9TH CIRCUIT FEDERAL COURT CHALLENGING THE FINAL PERMIT DECISION. THIS LAWSUIT WAS DISMISSED ON 6/17/2014 IN RESPONSE TO PETITIONERSâ€™ MOTION FOR VOLUNTARY DISMISSAL. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.11 | NATURAL GAS | 300 | MW | Three simple cycle combustion turbine generators (CTG). Each CTG rated at 100 MW (nominal net). | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Other - EPA METHOD 5 & 202, OR CTM 039 | (Particulate Matter (PM)) | PM | P | PUC-QUALITY NATURAL GAS | 0.0065 | LB/MMBTU (HHV) | AT LOADS OF 80% OR HIGHER | BACT-PSD |  | U | 0 | U | 5.5 | LB/H |  | 0 |  |  | 0 | 0 | N
CA-1223 | PIO PICO ENERGY CENTER | PIO PICO ENERGY CENTER, LLC | OTAY MESA | CA | 92154 | USA | GARY CHANDLER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SD 11-01 | 4911 | 221112 | 110045006943 | 06/14/2012 &nbsp;ACT | 11/19/2012 &nbsp;ACT | 2013-03-05 | 2014-01-28 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | CONSTRUCTION OF THREE GENERAL ELECTRIC (GE) LMS100 NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 100 MW EACH. THE PROJECT WILL HAVE AN ELECTRICAL OUTPUT OF 300 MW. | NOTE: PERMIT ISSUED 11/19/2012. ENVIRONMENTAL APPEALS BOARD REMANDED THE PM BACT ANALYSIS TO REGION 9 ON 8/2/2013. FINAL PERMIT ISSUED ON 2/28/2014. ONE PETITION FILED IN 9TH CIRCUIT FEDERAL COURT CHALLENGING THE FINAL PERMIT DECISION. THIS LAWSUIT WAS DISMISSED ON 6/17/2014 IN RESPONSE TO PETITIONERSâ€™ MOTION FOR VOLUNTARY DISMISSAL. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.11 | NATURAL GAS | 300 | MW | Three simple cycle combustion turbine generators (CTG). Each CTG rated at 100 MW (nominal net). | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA METHOD 5 & 202, OR CTM 039 | (Particulate Matter (PM)) | PM | P | PUC-QUALITY NATURAL GAS | 0.0065 | LB/MMBTU (HHV) | AT LOADS OF 80% OR HIGHER | BACT-PSD |  | U | 0 | U | 5.5 | LB/H |  | 0 |  |  | 0 | 0 | N
CA-1223 | PIO PICO ENERGY CENTER | PIO PICO ENERGY CENTER, LLC | OTAY MESA | CA | 92154 | USA | GARY CHANDLER |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SD 11-01 | 4911 | 221112 | 110045006943 | 06/14/2012 &nbsp;ACT | 11/19/2012 &nbsp;ACT | 2013-03-05 | 2014-01-28 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | CONSTRUCTION OF THREE GENERAL ELECTRIC (GE) LMS100 NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 100 MW EACH. THE PROJECT WILL HAVE AN ELECTRICAL OUTPUT OF 300 MW. | NOTE: PERMIT ISSUED 11/19/2012. ENVIRONMENTAL APPEALS BOARD REMANDED THE PM BACT ANALYSIS TO REGION 9 ON 8/2/2013. FINAL PERMIT ISSUED ON 2/28/2014. ONE PETITION FILED IN 9TH CIRCUIT FEDERAL COURT CHALLENGING THE FINAL PERMIT DECISION. THIS LAWSUIT WAS DISMISSED ON 6/17/2014 IN RESPONSE TO PETITIONERSâ€™ MOTION FOR VOLUNTARY DISMISSAL. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.11 | NATURAL GAS | 300 | MW | Three simple cycle combustion turbine generators (CTG). Each CTG rated at 100 MW (nominal net). | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | PUC-QUALITY NATURAL GAS | 0.0065 | LB/MMBTU (HHV) | AT LOADS OF 80% OR HIGHER | BACT-PSD |  | U | 0 | U | 5.5 | LB/H |  | 0 |  |  | 0 | 0 | N
*PA-0305 | SHELL CHEM APPALACHIA/PETROCHEMICALS COMPLEX | SHELL CHEMICAL APPALACHIA | BEAVER | PA | 15061-2210 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 04-00740A | 2821 | 325110 | 110060029115 | 05/01/2014 &nbsp;ACT | 06/18/2015 &nbsp;ACT | 2017-06-05 | 2017-07-12 | A |  | The plan approval will allow the construction and temporary operation of seven (7) 620 MMBtu/hr ethane cracking furnaces fired primarily by tail gas and natural gas for the production of approximately 1.5 million metric tons/year of polyethylene. Byproducts from the ethylene production include coke residue/tar, light gasoline, pyrolysis fuel oil, and a C3+ mixture and will be remove from the site for disposal or use as appropriate. Additional facilities include an electric and steam cogeneration from three (3) combustion turbines with duct burners and heat recovery steam generators with a plant capacity of 250.4 MW, four (4) emergency generators, three (3) diesel-fired fire pump engines, cooling towers, flares, and storage tanks. | (7) 620.000 MMBtu/hr Ethane cracking furnaces, (3) 664.000 combustion turbines with duct burners. Shell intends to convert ethane in to ethylene for manufacturing of various grades of low density and high density polyethylene as a final product. | Combustion turbine wih duct burner and heat recovery steam generator | 15.11 | Natural Gas | 0 | Three 40.6 MW turbines | Three (3) General Electric Frame 6B NG fired turbine with duct burners and heat recovery steam generators. Total electric generating capacity will be 250.4 MW from cogeneration three turbines at 40.6 MW and two HRSG at 64.3 MW. Excess electricity generated will be sold to the grid in quantities sufficient to classify the facility as an electric utility. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0066 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0264 | MONTPELIER GENERATING STATION | AES OHIO GENERATION, LLC | WELLS | IN | 46781 | USA | DREW PARKER | 9373314993 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: MADHURIMA MOULIK 317-233-6663 MMOULIK@IDEM.IN.GOV SECTION CHIEF: JASON KRAWCZYK 317-234-5174 | 179-37209-00026 | 4911 | 221112 | 110021089061 | 05/23/2016 &nbsp;ACT | 01/06/2017 &nbsp;ACT | 2017-07-07 | 2017-11-17 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/37209F.PDF | COMBUSTION TURBINES |  | PRATT &amp; TWIN-PAC SIMPLE CYCLE TURBINES | 15.11 | NATURAL GAS | 270.9 | MMBTU/H | NO. 2 DIESEL OIL BACKUP FUEL | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS AS PRIMARY FUEL; GOOD COMBUSTION PRACTICES | 0.0066 | LB/MMBTU | 3-HR AVG FOR NATURAL GAS | BACT-PSD |  |  | 0 |  | 0.012 | LB/MMBTU | 3-HR AVG FOR FUEL OIL | 0 |  |  | 0 | 0 | N |  | EACH OF 8 TURBINES LIMITED TO 500 HOURS OF FUEL OIL COMBUSTION PER 12 MONTH PERIOD
IN-0264 | MONTPELIER GENERATING STATION | AES OHIO GENERATION, LLC | WELLS | IN | 46781 | USA | DREW PARKER | 9373314993 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: MADHURIMA MOULIK 317-233-6663 MMOULIK@IDEM.IN.GOV SECTION CHIEF: JASON KRAWCZYK 317-234-5174 | 179-37209-00026 | 4911 | 221112 | 110021089061 | 05/23/2016 &nbsp;ACT | 01/06/2017 &nbsp;ACT | 2017-07-07 | 2017-11-17 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/37209F.PDF | COMBUSTION TURBINES |  | PRATT &amp; TWIN-PAC SIMPLE CYCLE TURBINES | 15.11 | NATURAL GAS | 270.9 | MMBTU/H | NO. 2 DIESEL OIL BACKUP FUEL | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS PRIMARY FUEL; GOOD COMBUSTION PRACTICES | 0.0066 | LB/MMBTU | 3-HR AVG FOR NATURAL GAS | BACT-PSD |  |  | 0 |  | 0.012 | LB/MMBTU | 3-HR AVG FOR FUEL OIL | 0 |  |  | 0 | 0 | N |  | EACH OF 8 TURBINES LIMITED TO 500 HOURS FUEL OIL USAGE PER 12 MONTH PERIOD
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 2 COMBUSTION TURBINES | 15.11 | NATURAL GAS | 130 | MW | TWO GENERAL ELECTRIC (GE) FRAME 7EA COMBUSTION TURBINES (CTS) WITH A NOMINAL NET 87.2 MEGAWATT (MW) RATED CAPACITY, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), EQUIPPED WITH DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION SYSTEM (SCR), AND OXIDATION CATALYST | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF FACILITY PROCESS FUEL GAS OR PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.007 | LB/MMBTU | 3 STACK TEST RUN AVERAGE, EXCEPT SU/SD | BACT-PSD |  |  | 0 |  | 300.8 | LB/EVENT | FOR ALL STARTUPS | 0 |  |  | 0 | 0 | N |  | 5.6 LBS/SHUTDOWN EVENT. LIMITS ARE TOTAL FOR BOTH FRAME 7 CTS PER STARTUP OR SHUTDOWN EVENT.
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 2 COMBUSTION TURBINES | 15.11 | NATURAL GAS | 130 | MW | TWO GENERAL ELECTRIC (GE) FRAME 7EA COMBUSTION TURBINES (CTS) WITH A NOMINAL NET 87.2 MEGAWATT (MW) RATED CAPACITY, COUPLED WITH A HEAT RECOVERY STEAM GENERATOR (HRSG), EQUIPPED WITH DRY LOW-NOX COMBUSTORS, SELECTIVE CATALYTIC REDUCTION SYSTEM (SCR), AND OXIDATION CATALYST | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF FACILITY PROCESS FUEL GAS OR PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.007 | LB/MMBTU | 3 STACK TEST RUN AVERAGE, EXCEPT SU/SD | BACT-PSD |  |  | 0 |  | 300.8 | LB/EVENT | FOR ALL STARTUPS | 0 |  |  | 0 | 0 | N |  | 5.6 LBS/SHUTDOWN EVENT. LIMITS ARE TOTAL FOR BOTH FRAME 7 CTS PER STARTUP OR SHUTDOWN EVENT
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110029511883 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and fueled by natural gas | 0.0076 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110029511883 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and fueled by natural gas | 0.0076 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0043 | PERRYMAN GENERATING STATION | CONSTELLATION POWER SOURCE GENERATION, INC. | HARFORD | MD | 21130 | USA | BILL LEEDY | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9136 | 4911 | 221119 | 110000499559 | 07/01/2014 &nbsp;ACT | 07/01/2014 &nbsp;ACT | 2015-07-31 | 2016-07-25 | B |  | 120 MEGAWATT SIMPLE CYCLE NATURAL GAS FIRED POWER PLANTPERRYMAN 6 PROJECT-WIDE EMISSION LIMITS: PM10 = 43.0 TONS/YR PM2.5 = 43.0 TONS/YR NOX = 58.5 TONS/YR CO2E = 430,210 TONS/YR | PERRYMAN 6 PROJECT-WIDE EMISSION LIMITS: PM10 = 43.0 TONS/YR PM2.5 = 43.0 TONS/YR NOX = 58.5 TONS/YR CO2E = 430,210 TONS/YR | (2) 60-MW SIMPLE CYCLE COMBUSTION TURBINES, FIRING NATURAL GAS | 15.11 | NATURAL GAS | 120 | MW | (2) 60-MEGAWATT PRATT & WHITNEY GAS TURBINE GENERATOR PACKAGE | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND USE OF NATURAL GAS | 0.0079 | LB/MM BTU | 3 STACK TEST RUNS | BACT-PSD |  |  | 0 |  | 0.0079 | LB/MMBTU | HIGH HEAT VALUE (HHV) | 0 |  |  | 0 | 0 | N
KY-0104 | CASH CREEK GENERATING STATION | CASH CREEK GENERATION, L.L.C | HENDERSON | KY | 41047 | USA | MIKE MCINNUS | 502 357 9907 | MMCINNIS@ERORA.COM | 4 | KY001 | KENTUCKY DEP, DIV FOR AIR QUALITY | MR. RICK SHEWEKAH, MGR | (502)564-3999 | Sreenivas.Kesaraju@ky.gov |  | V-14-011 | 4911 | 221112 | 110042328479 | 06/18/2014 &nbsp;ACT | 06/10/2015 &nbsp;ACT | 2017-02-28 | 2017-04-28 | A |  | natural gas fired combined cycle power plant |  | Combined cycle combustion turnbine with HRSG and duct firing | 15.11 | Natural gas pipeline quality | 849 | MW | Two CT with HRSGs with duct burner Max fuel input for CTs and HRSGs 6,714 mmBtu/hr HHV Max Gross output 849 MW at 0F | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Combust only pipeline quality natural gas | 0.0088 | LB/MM BTU | THREE(3) HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KY-0104 | CASH CREEK GENERATING STATION | CASH CREEK GENERATION, L.L.C | HENDERSON | KY | 41047 | USA | MIKE MCINNUS | 502 357 9907 | MMCINNIS@ERORA.COM | 4 | KY001 | KENTUCKY DEP, DIV FOR AIR QUALITY | MR. RICK SHEWEKAH, MGR | (502)564-3999 | Sreenivas.Kesaraju@ky.gov |  | V-14-011 | 4911 | 221112 | 110042328479 | 06/18/2014 &nbsp;ACT | 06/10/2015 &nbsp;ACT | 2017-02-28 | 2017-04-28 | A |  | natural gas fired combined cycle power plant |  | Combined cycle combustion turnbine with HRSG and duct firing | 15.11 | Natural gas pipeline quality | 849 | MW | Two CT with HRSGs with duct burner Max fuel input for CTs and HRSGs 6,714 mmBtu/hr HHV Max Gross output 849 MW at 0F | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Combust only pipeline quality natural gas | 0.0088 | LB/MM BTU | THREE HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KY-0104 | CASH CREEK GENERATING STATION | CASH CREEK GENERATION, L.L.C | HENDERSON | KY | 41047 | USA | MIKE MCINNUS | 502 357 9907 | MMCINNIS@ERORA.COM | 4 | KY001 | KENTUCKY DEP, DIV FOR AIR QUALITY | MR. RICK SHEWEKAH, MGR | (502)564-3999 | Sreenivas.Kesaraju@ky.gov |  | V-14-011 | 4911 | 221112 | 110042328479 | 06/18/2014 &nbsp;ACT | 06/10/2015 &nbsp;ACT | 2017-02-28 | 2017-04-28 | A |  | natural gas fired combined cycle power plant |  | Combined cycle combustion turnbine with HRSG and duct firing | 15.11 | Natural gas pipeline quality | 849 | MW | Two CT with HRSGs with duct burner Max fuel input for CTs and HRSGs 6,714 mmBtu/hr HHV Max Gross output 849 MW at 0F | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Combust pipeline quality natural gas only | 0.0088 | LB/MMBTU | THREE HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0540 | BOSQUE COUNTY POWER PLANT | BOSQUE POWER COMPANY LLC | BOSQUE | TX | 76644 | USA | MS KATHY FRENCH | 6365322200 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | MS. BRIDGET MALONE (512) 239-4286 | 40620 | 4911 | 221112 | 4803500002 | 10/26/2007 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | PSDTX931M1 | ELECTRICAL GENERATION | 15.11 | NATURAL GAS | 170 | MW | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | P | BACT IS THE USE OF PIPELINE-QUALITY NATURAL GAS AND THE APPLICATION OF GOOD COMBUSTION CONTROLS. WITH THIS METHOD OF CONTROL, PM/PM10 EMISSIONS SHOULD NOT EXCEED 0.01 LB/MMBTU FOR A 3-HOUR ROLLING PERIOD. | 0.01 | LB/MMBTU | 3 HR ROLLING PERIOD | BACT-PSD |  |  | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0113 | EDGEWOOD ENERGY LLC | EDGEWOOD ENERGY LLC | SUFFOLK | NY | 11717 | USA |  | 631-643-1560 |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 1 631-444-0200 | 1-4728-03244/00005 | 4911 | 221112 | 110038105993 | 07/09/2013 &nbsp;ACT | 07/09/2013 &nbsp;ACT | 2017-09-14 | 2017-09-28 | C | http://www.dec.ny.gov/chemical/32249.html | Edgewood Energy LLC is a power is a simple cycle combustion turbine plant located in Edgewood, Suffolk County, New York that contains two GE LM6000 combustion turbines that fire only natural gas. The facility has an optimum electrical output of 95 megawatts (MW) firing only natural gas. This electrical output represents an increase from the 79.9 MW limit. This increase was allowed through a declaratory ruling that the Department of Public Service issued. The facility is subject to PSD for greenhouse gases (GHGs) and PM-10 emissions. The facility is not subject to non-attainment NSR for any non-attainment contaminant. |  | Turbines - NG | 15.11 | natural gas | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0112 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | COMBUSTION TURBINES (2) | 15.11 | NATURAL GAS |  |  | GENERAL ELECTRIC 207FA COMBUSTION TURBINE WITH HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT FIRING CAPABILIY (DUCT BURNER EQUIPPED WITH LNB). EACH CT IS CAPABLE OF GENERATING A NOMINAL 176 MW OF ELECTRICITY. THE STEAM TURBINE IS CAPABLE OF GENERATING 304 MW OF ELECTRICITY. OVERALL FACILITY NOMINAL GENERATION CAPACITY OF 640 MW | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.012 | LB/MMBTU @ 15% O2 | 3-HR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | APPLICABLE TO OPERATING WITH OR WITHOUT DUCT BURNING
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | COMBUSTION TURBINES (2) | 15.11 | NATURAL GAS |  |  | GENERAL ELECTRIC 207FA COMBUSTION TURBINE WITH HEAT RECOVERY STEAM GENERATOR (HRSG) EQUIPPED WITH DUCT FIRING CAPABILIY (DUCT BURNER EQUIPPED WITH LNB). EACH CT IS CAPABLE OF GENERATING A NOMINAL 176 MW OF ELECTRICITY. THE STEAM TURBINE IS CAPABLE OF GENERATING 304 MW OF ELECTRICITY. OVERALL FACILITY NOMINAL GENERATION CAPACITY OF 640 MW | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.012 | LB/MMBTU @ 15% O2 | 3-HR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | APPLICABLE TO OPERATING WITH OR WITHOUT DUCT BURNING
OH-0333 | DAYTON POWER & LIGHT ENERGY LLC | DAYTON POWER & LIGHT COMPANY | MONTGOMERY | OH | 45439 | USA | CARRIE BURKS | 937-331-3042 |  | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104867 | 4911 | 221112 | 110000394145 | 04/30/2009 &nbsp;ACT | 12/03/2009 &nbsp;ACT | 2010-05-13 | 2010-05-20 | C |  | Seven simple cycle stationary combustion turbines all with rating of 80 MW and nominal heat input of 1115.2 mmBtu/hr using natural gas or No. 2 fuel oil and all with water injection control and last 5 also with low NOx burners. | Simple cycle stationary combution turbines issed in 2 different permits. Four turbines in this permit with dry low NOx combustion and water injection controls. Administrative Modification to original PTI #08-04153 issued 8/7/01, to incorporate low mass emissions methodology as allowed per 40 CFR 75.19 in lieu of methods under Appendix D or E to Part 75, by meeting the requirements of having mass emissions of less than 25 T/YR SO2 and less than 100 T/YR NOx (per turbine) based on 3 years of operation. Modification also reduced permitted formaldehyde emissions by 8.7 tons, recalculated based on the restriction on hours of operation. | Turbines (4), simple cycle, natural gas | 15.11 | NATURAL GAS | 15020 | H/YR | Hours per year for all 4 turbines | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Other - Method 201 or 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 0.013 | LB/MMBTU | ACTUAL HEAT INPUT | BACT-PSD | SIP | U | 0 | Y | 46.12 | T/YR | PER ROLLING 12-MO. FOR 4 UNITS &ALL FUEL | 0.013 | LB/MMBTU | ACTUAL HEAT INPUT | 0 | 0 | N |  | The emission factor for PM was used as a surrogate for PM10 and PM2.5 where there were no other emission factors available. T/YR limit is for both fuels and for the 4 turbines combined. BACT: using only clean fuels, natural gas or #2 fuel oil.
OH-0333 | DAYTON POWER & LIGHT ENERGY LLC | DAYTON POWER & LIGHT COMPANY | MONTGOMERY | OH | 45439 | USA | CARRIE BURKS | 937-331-3042 |  | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104867 | 4911 | 221112 | 110000394145 | 04/30/2009 &nbsp;ACT | 12/03/2009 &nbsp;ACT | 2010-05-13 | 2010-05-20 | C |  | Seven simple cycle stationary combustion turbines all with rating of 80 MW and nominal heat input of 1115.2 mmBtu/hr using natural gas or No. 2 fuel oil and all with water injection control and last 5 also with low NOx burners. | Simple cycle stationary combution turbines issed in 2 different permits. Four turbines in this permit with dry low NOx combustion and water injection controls. Administrative Modification to original PTI #08-04153 issued 8/7/01, to incorporate low mass emissions methodology as allowed per 40 CFR 75.19 in lieu of methods under Appendix D or E to Part 75, by meeting the requirements of having mass emissions of less than 25 T/YR SO2 and less than 100 T/YR NOx (per turbine) based on 3 years of operation. Modification also reduced permitted formaldehyde emissions by 8.7 tons, recalculated based on the restriction on hours of operation. | Turbines (4), simple cycle, natural gas | 15.11 | NATURAL GAS | 15020 | H/YR | Hours per year for all 4 turbines | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | N |  | 0.013 | LB/MMBTU | ACTUAL HEAT INPUT | BACT-PSD | SIP | U | 0 | Y | 46.12 | T/YR | PER ROLLING 12-MO. FOR 4 UNITS &ALL FUEL | 0.013 | LB/MMBTU | ACTUAL HEAT INPUT | 0 | 0 | N |  | The emission factor for PM was used as a surrogate for PM10 and PM2.5 where there were no other emission factors available. T/YR limit is for both fuels and for the 4 turbines combined. BACT: using only clean fuels, natural gas or #2 fuel oil.
[40 empty] | Range Low | 0.0033
[40 empty] | Range High | 0.013
[40 empty] | Mean | 0.007844
[40 empty] | Median | 0.007
[40 empty] | Mode | 0.005