## PermitSearchResults (5)
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
TX-0672 | CORPUS CHRISTI LIQUEFACTION PLANT | CORPUS CHRISTI LIQUEFACTION LLC | GREGORY | TX |  | USA | ANDREW CHARTRAND | (713) 375-5429 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | PSDTX1306 105710 | 4925 | 221210 | 110057000000 | 09/04/2012 &nbsp;ACT | 09/12/2014 &nbsp;ACT | 2015-03-13 | 2016-05-05 | A |  | Corpus Christi Liquefaction, LLC (CCL) proposes to construct and operate natural gas liquefaction and export plant and import facilities with regasification capabilities. The liquefied natural gas (LNG) terminal will be capable of processing an annual average of approximately 2.1 billion standard cubic feet per day of pipeline-quality natural gas in the liquefaction mode and 400 million standard cubic feet per day in the vaporization mode. The project will involve liquefying natural gas into LNG to be stored in three 160,000 cubic meters storage tanks. There will be 3 identical trains. LNG will be imported or exported via LNG carriers that will arrive at the projectâ€™s marine terminal. The facility will have the capability to liquefy natural gas from the pipeline system for export as LNG or import LNG and regasify it to send it out into the pipeline system. |  | Refrigeration compressor turbines | 15.11 | natural gas | 40000 | hp | 3 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane and methane section compressors. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.72 | LB/H | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Natural gas is the fuel. PM and PM10 are equal to PM2.5.
TX-0816 | CORPUS CHRISTI LIQUEFACTION | CORPUS CHRISTI LIQUEFACTION STAGE III, LLC | SAN PATRICIO | TX |  | USA | KEITH LITTLE | (713) 375-5204 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 139479, PSDTX1496, GHGPSDTX157 | 4925 | 221210 | Not Found | 11/16/2016 &nbsp;ACT | 02/14/2017 &nbsp;ACT | 2017-02-07 | 2018-04-18 | B |  | Trains 4 and 5 will consist of 12 natural gas compressor turbines, 2 thermal oxidizers, 2 sets of flares each comprised of one wet gas flare and one dry gas flare, 2 amine surge tanks (maintenance, startup, and shutdown [MSS] only), 3 diesel generators, 3 fire-water pump diesel engines, 6 fixed roof diesel storage tanks, and piping components. |  | Refrigeration compressor turbines | 15.11 | NATURAL GAS | 40000 | HP | 2 liquefied natural gas trains consisting of a total of (12) GE LM2500+ DLE turbines drive the propane, ethylene, and methane section compressors. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.75 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0264 | MONTPELIER GENERATING STATION | AES OHIO GENERATION, LLC | WELLS | IN | 46781 | USA | DREW PARKER | 9373314993 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: MADHURIMA MOULIK 317-233-6663 MMOULIK@IDEM.IN.GOV SECTION CHIEF: JASON KRAWCZYK 317-234-5174 | 179-37209-00026 | 4911 | 221112 | 110021000000 | 05/23/2016 &nbsp;ACT | 01/06/2017 &nbsp;ACT | 2017-07-07 | 2017-11-17 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/37209F.PDF | COMBUSTION TURBINES |  | PRATT &amp; TWIN-PAC SIMPLE CYCLE TURBINES | 15.11 | NATURAL GAS | 270.9 | MMBTU/H | NO. 2 DIESEL OIL BACKUP FUEL | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE NATURAL GAS AS PRIMARY FUEL; GOOD COMBUSTION PRACTICES | 1.7879 | LB/HR | 3-HR AVG FOR NATURAL GAS | BACT-PSD |  |  | 0 |  | 0.012 | LB/MMBTU | 3-HR AVG FOR FUEL OIL | 0 |  |  | 0 | 0 | N |  | EACH OF 8 TURBINES LIMITED TO 500 HOURS OF FUEL OIL COMBUSTION PER 12 MONTH PERIOD
IN-0264 | MONTPELIER GENERATING STATION | AES OHIO GENERATION, LLC | WELLS | IN | 46781 | USA | DREW PARKER | 9373314993 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: MADHURIMA MOULIK 317-233-6663 MMOULIK@IDEM.IN.GOV SECTION CHIEF: JASON KRAWCZYK 317-234-5174 | 179-37209-00026 | 4911 | 221112 | 110021000000 | 05/23/2016 &nbsp;ACT | 01/06/2017 &nbsp;ACT | 2017-07-07 | 2017-11-17 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/37209F.PDF | COMBUSTION TURBINES |  | PRATT &amp; TWIN-PAC SIMPLE CYCLE TURBINES | 15.11 | NATURAL GAS | 270.9 | MMBTU/H | NO. 2 DIESEL OIL BACKUP FUEL | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS PRIMARY FUEL; GOOD COMBUSTION PRACTICES | 1.7879 | LB/HR | 3-HR AVG FOR NATURAL GAS | BACT-PSD |  |  | 0 |  | 0.012 | LB/MMBTU | 3-HR AVG FOR FUEL OIL | 0 |  |  | 0 | 0 | N |  | EACH OF 8 TURBINES LIMITED TO 500 HOURS FUEL OIL USAGE PER 12 MONTH PERIOD
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110031000000 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Refrigeration Compressor Turbines (16) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and fueled by natural gas | 2.08 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | also for PM10 and PM2.5
LA-0257 | SABINE PASS LNG TERMINAL | SABINE PASS LNG, LP & SABINE PASS LIQUEFACTION, LL | CAMERON | LA | 70631 | USA | PATRICIA OUTTRIM | 713-375-5212 | PAT.OUTTRIM@CHENIERE.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen | PSD-LA-703(M3) | 4925 | 221210 | 110031000000 | 12/22/2010 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2012-01-23 | 2012-05-11 | B |  | A liquefaction section of the terminal which will include 24 compressor turbines, two generator turbines, two generator engines, flares, acid gas vents, and fugitives |  | Simple Cycle Generation Turbines (2) | 15.11 | Natural Gas | 286 | MMBTU/H | GE LM2500+G4 | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices and fueled by natural gas | 2.08 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | also for PM10 and PM2.5
OK-0127 | WESTERN FARMERS ELECTRIC ANADARKO | WESTERN FARMERS ELECTRIC COOPERATIVE | CADDO | OK | 73005 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2005-037-C(M-2) PSD | 4911 | 221112 | 110002000000 | 02/01/2008 &nbsp;ACT | 06/13/2008 &nbsp;ACT | 2008-12-31 | 2009-04-20 | B |  | THE FACILITY GENERATES WHOLESALE ELECTRICITY WHICH IS TRANSMITTED OVER WFECÂ¿S ELECTRICAL DISTRIBUTION SYSTEM. THE ELECTRICITY IS SOLD IN RURAL AREAS OF APPROXIMATELY 3/4 OF THE STATE OF OKLAHOMA. THE CURRENT FACILITY CONSISTS OF TWO NATURAL GAS FIRED HIGH PRESSURE BOILERS, A GAS/OIL FIRED HIGH PRESSURE BOILER, THREE GAS/OIL FIRED COMBINED CYCLE GAS TURBINES, A FIRE PUMP DIESEL ENGINE FOR EMERGENCY BACKUP, AND OTHER SOURCES WHICH ARE CONSIDERED INSIGNIFICANT OR TRIVIAL. THE THREE BOILERS ARE BACKUP UNITS THAT ONLY OPERATE WHEN IT IS FEASIBLE, SUCH AS DURING PEAK DEMAND. TWO OF THE BOILERS HAVE BEEN IDLE SINCE 1984. ONE BOILER WAS REPLACED IN 1997, AND ANOTHER WAS REPLACED IN 1998. | WESTERN FARMERS ELEC COOP PROPOSES TO CONSTRUCT AND OPERATE THREE NATURAL GAS-FIRED PEAKING ELECTRIC GENERATING UNITS AT THE FACILITY TO MEET ANTICIPATED FUTURE ENERGY DEMAND. EACH UNIT CAPACITY OF +/- 50 MW. | COMBUSTION TURBINE PEAKING UNIT(S) | 15.11 | NATURAL GAS | 462.7 | MMBTU/H | THE INSTALLATION WILL CONSIST OF THREE GENERAL ELECTRIC LM6000 SPRINT SIMPLE CYCLE AERODERIVATIVE COMBUSTION TURBINE GENERATORS. EACH OF THE TURBINES WILL HAVE A MAXIMUM PEAK HEAT INPUT RATE OF 462.7 MILLION BRITISH THERMAL UNITS PER HOUR (MMBTUH). THE NEW COMBUSTION TURBINES WILL FIRE ONLY PIPELINE-QUALITY NATURAL GAS AND WILL BE EQUIPPED WITH WATER INJECTION. THE PROPOSED NEW UNITS WILL EACH HAVE A NOMINAL ELECTRICAL GENERATING CAPACITY OF 50 MW. ACTUAL UNIT CAPACITY WILL BE DETERMINED DURING DETAILED DESIGN OF THE PLANT AND MAY BE 5 TO 10-MW HIGHER OR LOWER THAN THE NOMINAL VALUE OF 50 MW, DEPENDING ON AMBIENT CONDITION RATINGS AND FINAL DESIGN. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | NO CONTROLS FEASIBLE. | 4 | LB/H | 2,500 HR/YEAR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | GOOD COMBUSTION PRACTICES IN COMBINATION WITH USE OF NATURAL GAS IS DETERMINED ACCEPTABLE AS BACT.
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP03) | 15.11 | Natural Gas | 40 | MW |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 4 | LB/H | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 17.5 | TONS | CALENDAR YEAR | 0 |  |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Trubine (EP04) | 15.11 | Natural Gas | 40 | MW |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 4 | LB/H | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 17.5 | TONS | CALENDAR YEAR | 0 |  |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP05) | 15.11 | Natural Gas | 40 | MW |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 4 | LB/H | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 17.5 | TONS | CALENDAR YEAR | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110001000000 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine without Duct Burner Firing Natural Gas | 15.11 | Natural Gas | 28169501 | MMBTU/YR | Natural Gas Usage: <=28,169,501 MMBtu/year which includes maximum ultra low sulfur distillate oil usage of =2,371,943 MMBTU/year | Particulate matter, filterable (FPM) | Other - NJ TEST METHOD | (Particulate Matter (PM)) | PM | P | USE OF NATURAL GAS A CLEAN BURNING FUEL | 4.7 | LB/H | AV OF THREE ONE H STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
CO-0075 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO |  | USA | MARK LUX | 303-568-3241 | MARK.LUX@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 13PB2245 | 4911 | 221112 | 110058000000 | 09/10/2013 &nbsp;ACT | 05/30/2014 &nbsp;ACT | 2014-10-24 | 2016-02-19 | B |  | Power generation facility |  | Turbine - simple cycle gas | 15.11 | natural gas | 375 | MMBTU/H | One (1) General Electric, simple cycle, gas turbine electric generator, Unit 6 (CT08), model: LM6000, SN: N/A, rated at 375 MMBtu per hour. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Firing of pipeline quality natural gas as defined in 40 CFR Part 72. Specifically, the owner or the operator shall demonstrate that the natural gas burned has total sulfur content less than 0.5 grains/100 SCF. | 4.8 | LB/H | 3-HR AVE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CO-0075 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO |  | USA | MARK LUX | 303-568-3241 | MARK.LUX@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 13PB2245 | 4911 | 221112 | 110058000000 | 09/10/2013 &nbsp;ACT | 05/30/2014 &nbsp;ACT | 2014-10-24 | 2016-02-19 | B |  | Power generation facility |  | Turbine - simple cycle gas | 15.11 | natural gas | 375 | MMBTU/H | One (1) General Electric, simple cycle, gas turbine electric generator, Unit 6 (CT08), model: LM6000, SN: N/A, rated at 375 MMBtu per hour. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Firing of pipeline quality natural gas as defined in 40 CFR Part 72. Specifically, the owner or the operator shall demonstrate that the natural gas burned has total sulfur content less than 0.5 grains/100 SCF. | 4.8 | LB/H | 3-HR AVE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0077 | HOWARD DOWN STATION | VINELAND MUNICIPAL ELECTRIC UTILITY (VMEU) | CUMBERLAND | NJ | 8360 | USA |  | SYSNULL |  | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | MICHAEL HOGAN, PERMIT EVALUATOR, MICHAEL.HOGAN@DEP.STATE.NJ.US YOGESH DOSHI, SUPERVISOR, YOGESH.DOSHI@DEP.STATE.NJ.US | 75507-BOP090003 | 4911 | 221112 | 110021000000 | 10/28/2009 &nbsp;ACT | 09/16/2010 &nbsp;ACT | 2011-08-23 | 2012-01-05 | A |  |  |  | SIMPLE CYCLE (NO WASTE HEAT RECOVERY)(&gt;25 MW) | 15.11 | NATURAL GAS | 5000 | MMFT3/YR | THE PROCESS CONSISTS OF ONE NEW TRENT 60 SIMPLE CYCLE COMBUSTION TURBINE. THE TURBINE WILL GENERATE 64 MW OF ELECTRICITY USING NATURAL GAS AS A PRIMARY FUEL (UP TO 8760 HOURS PER YEAR), WITH A BACKUP FUEL OF ULTRA LOW SULFUR DIESEL FUEL (ULSD) WHICH CAN ONLY BE COMBUSTED FOR A MAXIMUM OF 500 HOURS PER YEAR AND ONLY DURING NATURAL GAS CURTAILMENT. THE MAXIMUM HEAT INPUT RATE WHILE COMBUSTING NATURAL GAS IS 590 MMBTU/HR AND THE MAXIMUM HEAT INPUT RATE WHILE COMBUSTING ULSD IS 568 MMBTU/HR. THE TURBINE WILL UTILIZE WATER INJECTION AND SELECTIVE CATALYTIC REDUCTION TO CONTROL NOX EMISSION AND A CATALYTIC OXIDIZER TO CONTROL CO AND VOC EMISSION. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Other - TEST METHODS M201A AND M202 | (Particulate Matter (PM)) | PM | N | USE OF CLEAN BURNING FUELS; NATURAL GAS AS PRIMARY FUEL AND ULTRA LOW SULFUR DISTILLATE OIL WITH 15 PPMSULFUR BY WEIGHT AS BACKUP FUEL | 5 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0077 | HOWARD DOWN STATION | VINELAND MUNICIPAL ELECTRIC UTILITY (VMEU) | CUMBERLAND | NJ | 8360 | USA |  | SYSNULL |  | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | MICHAEL HOGAN, PERMIT EVALUATOR, MICHAEL.HOGAN@DEP.STATE.NJ.US YOGESH DOSHI, SUPERVISOR, YOGESH.DOSHI@DEP.STATE.NJ.US | 75507-BOP090003 | 4911 | 221112 | 110021000000 | 10/28/2009 &nbsp;ACT | 09/16/2010 &nbsp;ACT | 2011-08-23 | 2012-01-05 | A |  |  |  | SIMPLE CYCLE (NO WASTE HEAT RECOVERY)(&gt;25 MW) | 15.11 | NATURAL GAS | 5000 | MMFT3/YR | THE PROCESS CONSISTS OF ONE NEW TRENT 60 SIMPLE CYCLE COMBUSTION TURBINE. THE TURBINE WILL GENERATE 64 MW OF ELECTRICITY USING NATURAL GAS AS A PRIMARY FUEL (UP TO 8760 HOURS PER YEAR), WITH A BACKUP FUEL OF ULTRA LOW SULFUR DIESEL FUEL (ULSD) WHICH CAN ONLY BE COMBUSTED FOR A MAXIMUM OF 500 HOURS PER YEAR AND ONLY DURING NATURAL GAS CURTAILMENT. THE MAXIMUM HEAT INPUT RATE WHILE COMBUSTING NATURAL GAS IS 590 MMBTU/HR AND THE MAXIMUM HEAT INPUT RATE WHILE COMBUSTING ULSD IS 568 MMBTU/HR. THE TURBINE WILL UTILIZE WATER INJECTION AND SELECTIVE CATALYTIC REDUCTION TO CONTROL NOX EMISSION AND A CATALYTIC OXIDIZER TO CONTROL CO AND VOC EMISSION. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Other - TEST METHODS M201A AND M202 | (Particulate Matter (PM)) | PM | N | USE OF CLEAN BURNING FUELS; NATURAL GAS AS PRIMARY FUEL AND ULTRA LOW SULFUR DISTILLATE OIL WITH 15 PPMSULFUR BY WEIGHT AS BACKUP FUEL | 5 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ND-0030 | LONESOME CREEK GENERATING STATION | BASIN ELECTRIC POWER COOP. | MCKENZIE | ND | 58831 | USA | JERRY MENGE | (701)223-0441 |  | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact at (701) 328-5188. | PTC 13049 | 4911 | 221112 | 110057000000 | 04/05/2013 &nbsp;EST | 09/16/2013 &nbsp;ACT | 2013-09-24 | 2017-06-28 | B |  | Three natural gas fired simple cycle turbines used to generate electricity for peak power demand. The turbines are GE LM6000 PF Sprint units with a nominal capacity of 45 MW each. |  | Natural Gas Fired Simple Cycle Turbines | 15.11 | Natural gas | 412 | MMBTU/H | The heat input is for a single unit. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - 1-4, 201a, 202 | (Particulate Matter (PM)) | PM | N |  | 5 | LB/H | AVERAGE OF THREE TEST RUNS | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit is for each unit.
IN-0261 | VERMILLION GENERATING STATION | DUKE ENERGY INDIANA, LLC VERMILLION GENERATING STA | VERMILLION | IN | 47928 | USA | PATRICK COUGHLIN | 3178382108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIP SINHA PH.D. 317-234-4907 | 165-36956-00022 | 4911 | 221112 | 110006000000 | 03/16/2016 &nbsp;ACT | 02/28/2017 &nbsp;ACT | 2017-07-07 | 2017-08-09 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36956F.PDF | ELECTRIC UTILITY SERVICES |  | SIMPLE CYCLE, NATURAL GAS FIRED COMBUSTION TURBINES | 15.11 | NATURAL GAS | 80 | MW |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 5 | LB/H | EACH TURBINE | BACT-PSD |  | N | 0 |  | 0.5 | TON/12 CONSEC. MONTH | COMPLIANCE DETERMINED END OF EACH MONTH | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: ONLY TWO TURBINES WILL OPERATE DURING LOW LOAD OPERATION.
IN-0261 | VERMILLION GENERATING STATION | DUKE ENERGY INDIANA, LLC VERMILLION GENERATING STA | VERMILLION | IN | 47928 | USA | PATRICK COUGHLIN | 3178382108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIP SINHA PH.D. 317-234-4907 | 165-36956-00022 | 4911 | 221112 | 110006000000 | 03/16/2016 &nbsp;ACT | 02/28/2017 &nbsp;ACT | 2017-07-07 | 2017-08-09 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36956F.PDF | ELECTRIC UTILITY SERVICES |  | SIMPLE CYCLE, NATURAL GAS FIRED COMBUSTION TURBINES | 15.11 | NATURAL GAS | 80 | MW |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 5 | LB/H | EACH TURBINE | BACT-PSD |  | N | 0 |  | 0.5 | TON/12 CONSEC. MONTH | COMPLIANCE DETERMINED END OF EACH MONTH | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: ONLY TWO TURBINES WILL OPERATE DURING LOW LOAD OPERATION.
MD-0043 | PERRYMAN GENERATING STATION | CONSTELLATION POWER SOURCE GENERATION, INC. | HARFORD | MD | 21130 | USA | BILL LEEDY | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9136 | 4911 | 221119 | 110000000000 | 07/01/2014 &nbsp;ACT | 07/01/2014 &nbsp;ACT | 2015-07-31 | 2016-07-25 | B |  | 120 MEGAWATT SIMPLE CYCLE NATURAL GAS FIRED POWER PLANTPERRYMAN 6 PROJECT-WIDE EMISSION LIMITS: PM10 = 43.0 TONS/YR PM2.5 = 43.0 TONS/YR NOX = 58.5 TONS/YR CO2E = 430,210 TONS/YR | PERRYMAN 6 PROJECT-WIDE EMISSION LIMITS: PM10 = 43.0 TONS/YR PM2.5 = 43.0 TONS/YR NOX = 58.5 TONS/YR CO2E = 430,210 TONS/YR | (2) 60-MW SIMPLE CYCLE COMBUSTION TURBINES, FIRING NATURAL GAS | 15.11 | NATURAL GAS | 120 | MW | (2) 60-MEGAWATT PRATT & WHITNEY GAS TURBINE GENERATOR PACKAGE | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND USE OF NATURAL GAS | 5 | LB/H | 3 STACK TEST RUNS | BACT-PSD |  |  | 0 |  | 0.0079 | LB/MMBTU | HIGH HEAT VALUE (HHV) | 0 |  |  | 0 | 0 | N
IN-0261 | VERMILLION GENERATING STATION | DUKE ENERGY INDIANA, LLC VERMILLION GENERATING STA | VERMILLION | IN | 47928 | USA | PATRICK COUGHLIN | 3178382108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIP SINHA PH.D. 317-234-4907 | 165-36956-00022 | 4911 | 221112 | 110006000000 | 03/16/2016 &nbsp;ACT | 02/28/2017 &nbsp;ACT | 2017-07-07 | 2017-08-09 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36956F.PDF | ELECTRIC UTILITY SERVICES |  | SIMPLE CYCLE, NATURAL GAS FIRED COMBUSTION TURBINES | 15.11 | NATURAL GAS | 80 | MW |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 5 | LB/H | EACH TURBINE | BACT-PSD |  | N | 0 |  | 0.5 | TON/12 CONSEC. MONTH | COMPLIANCE DETERMINED END OF EACH MONTH | 0 |  |  | 0 | 0 | N |  | THIRD LIMIT: ONLY TWO TURBINES WILL OPERATE DURING LOW LOAD OPERATION
NM-0051 | CUNNINGHAM POWER PLANT | SOUTHWESTERN PUBLIC SERVICE CO. | LEA | NM | 88241-1650 | USA | KEVIN WORLEY | 806 378 2185 | KEVIN.WORLEY@XCELENERGY.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Cember Hardison is permit writer. 505 476 4346. cember.hardison@state.nm.us | PSD-NM-622-M3 | 4911 | 221122 | 110011000000 | 03/08/2011 &nbsp;ACT | 05/02/2011 &nbsp;ACT | 2011-08-02 | 2012-01-05 | C |  | Electric steam generating facility providing commercial electric power using natural gas fired boilers and turbines. | Simple Cycle Combustion Turbines. Permit revises the NOx BACT ppmvd limit for turbines established in permit PSD-NM-622-M2 issued 2-10-97 because turbines have not been able to meet NOx BACT limits. No modification or change to mass emissions. Former NOx BACT was at 15 ppmvd w/out power augmentation (normal mode) and 25 ppmvd w/ power augmentation (see RBLC ID NM-0028). Entry also clarifies the existing CO, SOx, and PM BACT. | Normal Mode (without Power Augmentation) | 15.11 | natural gas | 0 |  |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | Good Combustion Practices as described in the permit. | 5.4 | LB/H | HOURLY | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | PM10 BACT as established in PSD-NM-622-M3 issued 2-10-97.
NM-0051 | CUNNINGHAM POWER PLANT | SOUTHWESTERN PUBLIC SERVICE CO. | LEA | NM | 88241-1650 | USA | KEVIN WORLEY | 806 378 2185 | KEVIN.WORLEY@XCELENERGY.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Cember Hardison is permit writer. 505 476 4346. cember.hardison@state.nm.us | PSD-NM-622-M3 | 4911 | 221122 | 110011000000 | 03/08/2011 &nbsp;ACT | 05/02/2011 &nbsp;ACT | 2011-08-02 | 2012-01-05 | C |  | Electric steam generating facility providing commercial electric power using natural gas fired boilers and turbines. | Simple Cycle Combustion Turbines. Permit revises the NOx BACT ppmvd limit for turbines established in permit PSD-NM-622-M2 issued 2-10-97 because turbines have not been able to meet NOx BACT limits. No modification or change to mass emissions. Former NOx BACT was at 15 ppmvd w/out power augmentation (normal mode) and 25 ppmvd w/ power augmentation (see RBLC ID NM-0028). Entry also clarifies the existing CO, SOx, and PM BACT. | Power Augmentation | 15.11 | natural gas | 0 |  | Increase power output by lowering the outlet air temperatur through water inejctinos into the compressor. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | Good combustion practices as defined in the permit. | 5.4 | LB/H | HOURLY | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | PM10 BACT established in PSD-NM-622-M2 issued 2-10-97.
ND-0029 | PIONEER GENERATING STATION | BASIN ELECTRIC POWER COOPERATIVE | WILLIAMS | ND |  | USA | JERRY MENGE | 7012230441 | JMENGE@BEPC.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Tom Bachman is the primary contact. | PTC 13037 | 4911 | 221112 | 110058000000 | 02/19/2013 &nbsp;ACT | 05/14/2013 &nbsp;ACT | 2013-06-19 | 2016-11-03 | B |  | Three GE LM6000 PC SPRINT natural gas fired turbines used to generate electricity for peak periods. | The permit was for the addition of 2 turbines to the station. Since a synthetic minor limit was relaxed for the first unit, BACT was required for all three turbines. | Natural gas-fired turbines | 15.11 | Natural gas | 451 | MMBTU/H | Rating is for each turbine. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - 1-4, 201a and 202 | (Particulate Matter (PM)) | PM | N |  | 5.4 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | RBLC Staff: Original Emis Limit 1 Units were Numeric Limit - &lsquo;&lsquo;LB&lsquo;&lsquo; and Avg Time/Condition - &lsquo;&lsquo;1 HOUR&lsquo;&lsquo; The Emission Units are usually &lsquo;&lsquo;mass unit PER time unit&lsquo;&lsquo;. Separating them out makes understanding limit difficult for the users. The units were combined. The corrected entry is: Numeric Limit - &lsquo;&lsquo;LB/H&lsquo;&lsquo; Avg Time/Condition - blank
NJ-0076 | PSEG FOSSIL LLC KEARNY GENERATING STATION | PSEG FOSSIL LLC | HUDSON | NJ | 7032 | USA |  |  |  | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | a. Aliya Khan, Permit evaluator, Aliya.Khan@dep.state.nj.us b. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS - yogesh.doshi@dep.state.nj.us- Phone Number 609-633-7249 | 12200-BOP100002 | 4911 | 221112 | 110043000000 | 08/03/2010 &nbsp;ACT | 10/27/2010 &nbsp;ACT | 2011-08-08 | 2011-09-07 | B |  | PSEG FOSSIL LLC KEARNY GENERATING STATION IS AN EXISTING ELECTRICITY GENERATING STATION. | This project consists of six new identical General Electric LM6000 sprint simple cycle combustion turbines burning natural gas. Each turbine will have a heat input rate of 485 million British thermal units per hour (MMBtu/hr) based on the high heating value of fuel (HHV). The combined maximum electricity generated by the six turbines will be 294 MW based on 2,978 hours of operation per turbine per year. All six new turbines will have water injection along with Selective Catalytic Reduction (SCR) systems to reduce Nitrogen Oxide (NOx) emissions and an oxidation catalyst to reduce Carbon Monoxide (CO) emissions | SIMPLE CYCLE TURBINE | 15.11 | Natural Gas | 8940000 | MMBtu/year (HHV) | Throughput <= 8.94xE6 MMBtu/year (HHV) combined for all six gas turbines. The 6 turbines are identical LM6000 simple cycle combustion turbines. | Particulate matter, filterable (FPM) | Other - New Jersey Air test method 1 | (Particulate Matter (PM)) | PM | P | Good combustion practice, Use of Clean Burning Fuel: Natural gas | 6 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0076 | PSEG FOSSIL LLC KEARNY GENERATING STATION | PSEG FOSSIL LLC | HUDSON | NJ | 7032 | USA |  |  |  | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | a. Aliya Khan, Permit evaluator, Aliya.Khan@dep.state.nj.us b. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS - yogesh.doshi@dep.state.nj.us- Phone Number 609-633-7249 | 12200-BOP100002 | 4911 | 221112 | 110043000000 | 08/03/2010 &nbsp;ACT | 10/27/2010 &nbsp;ACT | 2011-08-08 | 2011-09-07 | B |  | PSEG FOSSIL LLC KEARNY GENERATING STATION IS AN EXISTING ELECTRICITY GENERATING STATION. | This project consists of six new identical General Electric LM6000 sprint simple cycle combustion turbines burning natural gas. Each turbine will have a heat input rate of 485 million British thermal units per hour (MMBtu/hr) based on the high heating value of fuel (HHV). The combined maximum electricity generated by the six turbines will be 294 MW based on 2,978 hours of operation per turbine per year. All six new turbines will have water injection along with Selective Catalytic Reduction (SCR) systems to reduce Nitrogen Oxide (NOx) emissions and an oxidation catalyst to reduce Carbon Monoxide (CO) emissions | SIMPLE CYCLE TURBINE | 15.11 | Natural Gas | 8940000 | MMBtu/year (HHV) | Throughput <= 8.94xE6 MMBtu/year (HHV) combined for all six gas turbines. The 6 turbines are identical LM6000 simple cycle combustion turbines. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Good combustion practice, Use of Clean Burning Fuel: Natural gas | 6 | LB/H | AVERAGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0076 | PSEG FOSSIL LLC KEARNY GENERATING STATION | PSEG FOSSIL LLC | HUDSON | NJ | 7032 | USA |  |  |  | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | a. Aliya Khan, Permit evaluator, Aliya.Khan@dep.state.nj.us b. YOGESH DOSHI, SUPERVISOR, BUREAU OF AIR PERMITS - yogesh.doshi@dep.state.nj.us- Phone Number 609-633-7249 | 12200-BOP100002 | 4911 | 221112 | 110043000000 | 08/03/2010 &nbsp;ACT | 10/27/2010 &nbsp;ACT | 2011-08-08 | 2011-09-07 | B |  | PSEG FOSSIL LLC KEARNY GENERATING STATION IS AN EXISTING ELECTRICITY GENERATING STATION. | This project consists of six new identical General Electric LM6000 sprint simple cycle combustion turbines burning natural gas. Each turbine will have a heat input rate of 485 million British thermal units per hour (MMBtu/hr) based on the high heating value of fuel (HHV). The combined maximum electricity generated by the six turbines will be 294 MW based on 2,978 hours of operation per turbine per year. All six new turbines will have water injection along with Selective Catalytic Reduction (SCR) systems to reduce Nitrogen Oxide (NOx) emissions and an oxidation catalyst to reduce Carbon Monoxide (CO) emissions | SIMPLE CYCLE TURBINE | 15.11 | Natural Gas | 8940000 | MMBtu/year (HHV) | Throughput <= 8.94xE6 MMBtu/year (HHV) combined for all six gas turbines. The 6 turbines are identical LM6000 simple cycle combustion turbines. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - M201A and M202 | (Particulate Matter (PM)) | PM | P | Good combustion practice, Use of Clean Burning Fuel: Natural gas | 6 | LB/H | AVERGE OF THREE TESTS | BACT-PSD | OPERATING PERMIT | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE LM6000PC SPRINT Simple cycle combustion turbine | 15.11 | Pipeline quality natural gas | 405.3 | MMBTU/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | fire only pipeline quality natural gas | 6 | LB/HR | AT FULL OAD | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE LM6000PC SPRINT Simple cycle combustion turbine | 15.11 | Pipeline quality natural gas | 405.3 | MMBTU/hr |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | fire only pipeline quality natural gas | 6 | LB/HR | AT FULL LOAD | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055000000 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Three simple cycle combustion turbines | 15.11 | natural gas | 799.7 | MMBTU/H | Three GE, LMS100PA, natural gas-fired, simple cycle CTG rated at 799.7 MMBtu per hour each,based on HHV. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustor design | 6.6 | LB/H | AVE OVER STACK TEST LENGTH | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055000000 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Three simple cycle combustion turbines | 15.11 | natural gas | 799.7 | MMBTU/H | Three GE, LMS100PA, natural gas-fired, simple cycle CTG rated at 799.7 MMBtu per hour each,based on HHV. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of pipeline quality natural gas and good combustor design | 6.6 | LB/H | AVE OVER STACK TEST LENGTH | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ND-0028 | R.M. HESKETT STATION | MONTANA-DAKOTA UTILITIES CO. | MORTON | ND | 58554 | USA | ABBIE KREBSBACH | (701) 222-7844 | ABBIE.KREBSBACH@MDU.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Primary contact is Tom Bachman at (701) 328-5188. | PTC13016 | 4911 | 221112 | 110022000000 | 11/07/2012 &nbsp;ACT | 02/22/2013 &nbsp;ACT | 2013-04-01 | 2017-04-28 | B |  | Addition of a natural gas-fired turbine (Unit 3) to an exisiting coal-fired power plant. The turbine will be used for supplying peak power and is rated at 986 MMBtu/hr and 88 MWe at average site conditions. |  | Combustion Turbine | 15.11 | Natural gas | 986 | MMBTU/H | Turbine is a GE Model PG 7121 (7EA) used as a peaking unit. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 7.3 | LB/H | AVERAGE OF 3 TEST RUNS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ND-0028 | R.M. HESKETT STATION | MONTANA-DAKOTA UTILITIES CO. | MORTON | ND | 58554 | USA | ABBIE KREBSBACH | (701) 222-7844 | ABBIE.KREBSBACH@MDU.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV | Primary contact is Tom Bachman at (701) 328-5188. | PTC13016 | 4911 | 221112 | 110022000000 | 11/07/2012 &nbsp;ACT | 02/22/2013 &nbsp;ACT | 2013-04-01 | 2017-04-28 | B |  | Addition of a natural gas-fired turbine (Unit 3) to an exisiting coal-fired power plant. The turbine will be used for supplying peak power and is rated at 986 MMBtu/hr and 88 MWe at average site conditions. |  | Combustion Turbine | 15.11 | Natural gas | 986 | MMBTU/H | Turbine is a GE Model PG 7121 (7EA) used as a peaking unit. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 7.3 | LB/H | AVERAGE OF THREE TEST RUNS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110030000000 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and fueled by natural gas | 8.1244 | LB/HR | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110030000000 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and fueled by natural gas | 8.1244 | LB/HR | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0769 | VAN ALSTYNE ENERGY CENTER (VAEC) | NAVASOTA NORTH COUNTRY PEAKERS OPERATING COMPANY I | GRAYSON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 121051 AND PSDTX1418 | 4911 | 221112 | UNKNOWN | 12/22/2014 &nbsp;ACT | 10/27/2015 &nbsp;ACT | 2015-10-30 | 2016-07-06 | A |  | Navasota North Country Peakers Operating Company I LLC. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 MW each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline Quality Natural Gas | 8.6 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0777 | UNION VALLEY ENERGY CENTER | NAVASOTA SOUTH PEAKERS OPERATING COMPANY I, LLC. | NIXON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 120973 AND PSDTX1420 | 4911 | 221112 | UNKNOWN | 02/06/2015 &nbsp;ACT | 12/09/2015 &nbsp;ACT | 2015-12-03 | 2016-07-06 | A |  | three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 megawatt (MW) each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | pipeline quality natural gas, good combustion practices | 8.6 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0769 | VAN ALSTYNE ENERGY CENTER (VAEC) | NAVASOTA NORTH COUNTRY PEAKERS OPERATING COMPANY I | GRAYSON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 121051 AND PSDTX1418 | 4911 | 221112 | UNKNOWN | 12/22/2014 &nbsp;ACT | 10/27/2015 &nbsp;ACT | 2015-10-30 | 2016-07-06 | A |  | Navasota North Country Peakers Operating Company I LLC. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 MW each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle. |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline Quality Natural Gas | 8.6 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0777 | UNION VALLEY ENERGY CENTER | NAVASOTA SOUTH PEAKERS OPERATING COMPANY I, LLC. | NIXON | TX |  | USA | BILL SKINNER | 281-252-5202 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean Oâ€™Brien, sean.obrien@tceq.texas.gov 512-239-1137 | 120973 AND PSDTX1420 | 4911 | 221112 | UNKNOWN | 02/06/2015 &nbsp;ACT | 12/09/2015 &nbsp;ACT | 2015-12-03 | 2016-07-06 | A |  | three new natural gas fired combustion turbine generators (CTGs). The CTGs will be the General Electric 7FA.04 (~214 megawatt (MW) each; manufacturerâ€™s output at baseload, ISO at 183 MW), operating as peaking units in simple cycle |  | Simple Cycle Turbine | 15.11 | natural gas | 183 | MW | The CTGs will be three General Electric 7FA.04 (~183 MW each for a total of 550 MW), operating as peaking units in simple cycle mode. Each turbine will be limited to 2,500 hours of operation per year. The new CTGs will use dry low-NOx (DLN) burners and may employ evaporative cooling for power enhancement. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | pipeline quality natural gas, good combustion practices | 8.6 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
GA-0139 | DAHLBERG COMBUSDTION TURBINE ELECTRIC GENERATING FACILITY (P | SOUTHERN POWER COMPANY | JACKSON | GA | 30565 | USA | MR. E.S. (SCOTT) DIAL | 704 278-6601 | ESDIAL@SOUTHERNCO.COM | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-157-0034-V-04-1 | 4911 | 221112 | UNKNOWN | 07/10/2008 &nbsp;ACT | 05/14/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | C |  | PLANT DAHLBERG HAS PROPOSED TO CONSTRUCT AND OPERATE FOUR ADDITIONAL SIMPLE-CYCLE COMBUSTION TURBINES (SOURCE CODES: CT11-CT14) AND ONE FUEL OIL STORAGE TANK. THE PROPOSED PROJECT WILL HAVE A NOMINAL GENERATING CAPACITY OF 760 MW. THE FACILITY IS CURRENTLY PERMITTED TO OPERATE 10 DUAL-FUELED SIMPLE-CYCLE CTG's. AFTER THE EXPANSION, THE FACILITY WILL HAVE A TOTAL NOMINAL GENERATING CAPACITY OF 1530 MW. |  | SIMPLE CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.11 | NATURAL GASE | 1530 | MW | THE PROCESS USES FUEL OIL FOR BACKUP AT THE RATE OF 2129 MMBUT/H | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | GOOD COMBUSTION PRACTICES PIPELINE QUALITY NATURAL GAS, ULTRA LOW SULFUR DISTILLATE FUEL | 9.1 | LB/H | 3 HOUR AVERAGE/CONDITION 3.3.23 | BACT-PSD | OPERATING PERMIT | U | 0 | N | 69 | LB/H | 3 HOUR AVERAGE/CONDITION 3.3.28 | 0 |  |  | 0 | 0 | N
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057000000 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | GE LMS-100 combustion turbines, simple cycle with water injection | 15.11 | natural gas | 1690 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Utilize only natural gas or ULSD fuel; Limit the time in startup or shutdown. | 9.1 | LB/H TOTAL PM | 6-HR AVERAGE ON NG | BACT-PSD |  | U | 0 | U | 22.7 | LB/H TOTAL PM | 6-HR AVERAGE ON ULSD | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110001000000 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine with Duct Burner firing natural gas | 15.11 | Natural Gas | 0 |  |  | Particulate matter, filterable (FPM) | Other - NJ Test Method | (Particulate Matter (PM)) | PM | P | Use of clean burning fuel like natural gas | 12 | LB/H | AV OF THREE ONE H STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0764 | NACOGDOCHES POWER ELECTRIC GENERATING PLANT | NACOGDOCHES POWER, LLC | NACOGDOCHES | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem 512-239-1310 Tzvi.shalem@tceq.texas.gov | 77679, PSDTX1061M1 & O-3455 | 4911 | 221112 | 110044000000 | 06/25/2015 &nbsp;ACT | 10/14/2015 &nbsp;ACT | 2015-09-16 | 2016-07-06 | B |  | Nacogdoches Power, LLC is requesting authorization for one natural gas fired, simple cycle combustion turbine generator (CTG). The CTG will be a Siemens F5 and have a nominal electric output of 232 megawatts (MW). |  | Natural Gas Simple Cycle Turbine (&gt;25 MW) | 15.11 | natural gas | 232 | MW | One Siemens F5 simple cycle combustion turbine generator | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices. | 12.09 | LB/HR |  | BACT-PSD |  | N | 0 | U | 12.94 | TPY |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,500 hours on a 12-month rolling average.
TX-0764 | NACOGDOCHES POWER ELECTRIC GENERATING PLANT | NACOGDOCHES POWER, LLC | NACOGDOCHES | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem 512-239-1310 Tzvi.shalem@tceq.texas.gov | 77679, PSDTX1061M1 & O-3455 | 4911 | 221112 | 110044000000 | 06/25/2015 &nbsp;ACT | 10/14/2015 &nbsp;ACT | 2015-09-16 | 2016-07-06 | B |  | Nacogdoches Power, LLC is requesting authorization for one natural gas fired, simple cycle combustion turbine generator (CTG). The CTG will be a Siemens F5 and have a nominal electric output of 232 megawatts (MW). |  | Natural Gas Simple Cycle Turbine (&gt;25 MW) | 15.11 | natural gas | 232 | MW | One Siemens F5 simple cycle combustion turbine generator | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices. | 12.09 | LB/HR |  | BACT-PSD |  | N | 0 | U | 12.94 | TPY |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,500 hours on a 12-month rolling average.
TX-0764 | NACOGDOCHES POWER ELECTRIC GENERATING PLANT | NACOGDOCHES POWER, LLC | NACOGDOCHES | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem 512-239-1310 Tzvi.shalem@tceq.texas.gov | 77679, PSDTX1061M1 & O-3455 | 4911 | 221112 | 110044000000 | 06/25/2015 &nbsp;ACT | 10/14/2015 &nbsp;ACT | 2015-09-16 | 2016-07-06 | B |  | Nacogdoches Power, LLC is requesting authorization for one natural gas fired, simple cycle combustion turbine generator (CTG). The CTG will be a Siemens F5 and have a nominal electric output of 232 megawatts (MW). |  | Natural Gas Simple Cycle Turbine (&gt;25 MW) | 15.11 | natural gas | 232 | MW | One Siemens F5 simple cycle combustion turbine generator | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices. | 12.09 | LB/HR |  | BACT-PSD |  | N | 0 | U | 12.94 | TPY |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,500 hours on a 12-month rolling average.
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110065000000 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Large Combustion Turbines &gt; 25 MW | 15.11 | natural gas | 232 | MW | 4 Simple cycle CTGs, 2,500 hr/yr operational limitation. Facility will consist of either 232 MW (Siemens) or 220 MW (GE) | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices, low sulfur fuel | 13.4 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK AND TTTT
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110065000000 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Large Combustion Turbines &gt; 25 MW | 15.11 | natural gas | 232 | MW | 4 Simple cycle CTGs, 2,500 hr/yr operational limitation. Facility will consist of either 232 MW (Siemens) or 220 MW (GE) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices, low sulfur fuel | 13.4 | LB/H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK AND TTTT
TX-0794 | HILL COUNTY GENERATING FACILITY | BRAZOS ELECTRIC COOPERATIVE | HILL | TX |  | USA | MIKE MEYERS | (254)750-6228 | MMEYERS@BRAZOSELECTRIC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512)239-1512, randy.hamilton@tceq.texas.gov | 130051,PSDTX1450, GHGPSDTX131 | 4911 | 221112 | UNKNOWN | 12/18/2015 &nbsp;ACT | 04/07/2016 &nbsp;ACT | 2016-04-05 | 2016-07-29 | A |  | Four simple cycle combustion turbine electric generators are proposed. Natural gas or ultra-low sulfur diesel fuel oil are the fuels. Turbine model options are: General Electric (GE) 7FA.03, GE 7FA.04, GE 7FA.05, and Siemes SGT6-5000(5)ee. Electric output is between 684 and 928 megawatts (MW). |  | Simple cycle turbine | 15.11 | natural gas | 171 | MW | Each combustion turbine is limited to 2,920 hours of annual operation, including startup and shutdown hours. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - TM5 MODIFIED IMPINGER CATCH | (Particulate Matter (PM)) | PM | P | Premixing of fuel and air enhances combustion efficiency and minimizes emissions. | 14 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0794 | HILL COUNTY GENERATING FACILITY | BRAZOS ELECTRIC COOPERATIVE | HILL | TX |  | USA | MIKE MEYERS | (254)750-6228 | MMEYERS@BRAZOSELECTRIC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Randy Hamilton, (512)239-1512, randy.hamilton@tceq.texas.gov | 130051,PSDTX1450, GHGPSDTX131 | 4911 | 221112 | UNKNOWN | 12/18/2015 &nbsp;ACT | 04/07/2016 &nbsp;ACT | 2016-04-05 | 2016-07-29 | A |  | Four simple cycle combustion turbine electric generators are proposed. Natural gas or ultra-low sulfur diesel fuel oil are the fuels. Turbine model options are: General Electric (GE) 7FA.03, GE 7FA.04, GE 7FA.05, and Siemes SGT6-5000(5)ee. Electric output is between 684 and 928 megawatts (MW). |  | Simple cycle turbine | 15.11 | natural gas | 171 | MW | Each combustion turbine is limited to 2,920 hours of annual operation, including startup and shutdown hours. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - TM5, MODIFY IMPINGER CATCH | (Particulate Matter (PM)) | PM | P | Premixing of fuel and air enhances combustion efficiency and minimizes emissions. | 14 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110001000000 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine without Duct Burner Firing Natural Gas | 15.11 | Natural Gas | 28169501 | MMBTU/YR | Natural Gas Usage: <=28,169,501 MMBtu/year which includes maximum ultra low sulfur distillate oil usage of =2,371,943 MMBTU/year | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 14.4 | LB/H | AV OF THREE ONE H STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110001000000 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine without Duct Burner Firing Natural Gas | 15.11 | Natural Gas | 28169501 | MMBTU/YR | Natural Gas Usage: <=28,169,501 MMBtu/year which includes maximum ultra low sulfur distillate oil usage of =2,371,943 MMBTU/year | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 14.4 | LB/H | AV OF THREE ONE H STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0026 | WAVERLY FACILITY | PLEASANTS ENERGY, LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 304-665-4201 | GERALD.GATTI@GDFSUEZNA.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0034 | 4911 | 221112 | 110010000000 | 04/18/2016 &nbsp;ACT | 01/23/2017 &nbsp;ACT | 2017-03-21 | 2018-05-01 | D | http://www.dep.wv.gov/daq/Documents/January 2017 Permits and Evals/073-00022_PERM_R14-0034.pdf | 300 MW, natural gas fired, simple cycle peaking power facility | In this permitting action PSD only applies to the modified combustion turbines based on the relaxation of an original synthetic minor permit issued in 1999. Project also involves previous installation of turbo-charging. All BACT emission limits are given without turbocharging and startup/shutdown emissions are not included. Please contact above engineer for more information. There are two identical turbines but only one is listed. | GE Model 7FA Turbine | 15.11 | Natural Gas | 1571 | mmbtu/hr | There are two identical units at the facility. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Inlet Air Filtration, Use of Natural Gas, Ultra-Low Sulfur Diesel | 15 | LB/HR | NATURAL GAS | BACT-PSD |  | U | 0 | U | 39 | LB/HR | FUEL OIL | 15 | LB/HR | NATURAL GAS | 0 | 0 | N |  | All PM emissions assumed to be PM2.5 or less. PM and PM10 emission limits are the same as above. Additional emission limits are in the permit for use of turbocharging and startup/shutdown emissions. Please contact if need additional information.
*WV-0028 | WAVERLY POWER PLANT | PLEASANTS ENERGY LLC | PLEASANTS | WV | 26170 | USA | GERALD GATTI | 3046654201 | GERALD.GATTI@DYNEGY.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Mr. Steve Pursley, PE Engineer West Virginia Division of Air Quality 601-57th St., SE Charleston, WV 25304 Phone: (304) 926-0499 x1218 Fax: (304) 926-0478 steve.r.pursley@wv.gov | R14-0034A | 4911 | 221112 | 110063000000 | 11/30/2017 &nbsp;ACT | 03/13/2018 &nbsp;ACT | 2018-05-29 | 2018-05-29 | U | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/073-00022_PERM_R14-0034A.pdf | 300 MW Sinple-Cycle Peaking Plant | Modification to existing PSD Permit (R14-0034, RBLC Number WV-0027) to add &lsquo;&lsquo;advanced gas path&lsquo;&lsquo; technology to the turbines that was defined as a &lsquo;&lsquo;change in the method of operation&lsquo;&lsquo; that resulted a major modification to the turbines. | GE 7FA.004 Turbine | 15.11 | Natural Gas | 167.8 | MW | This one entry is for both turbines as they are the same. Each turbine, after this modification, is a nominal 167.8 MW GE Model 7FA.004. Has oil-fire backup. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Inlet air filtration. | 15.09 | LB/HR |  | BACT-PSD |  | U | 0 | U | 41.65 | TONS/YEAR |  | 15.09 | LB/HR |  | 0 | 0 | N
LA-0258 | CALCASIEU PLANT | ENTERGY GULF STATES LA LLC | CALCASIEU | LA | 70665 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: TEGAN TREADAWAY, (225) 219-3408 | PSD-LA-746 | 4911 | 221112 | 110007000000 | 11/10/2009 &nbsp;ACT | 12/21/2011 &nbsp;ACT | 2012-02-01 | 2012-04-03 | C |  | 320 MW POWER PLANT COMPRISED OF 2 NATURAL GAS-FIRED SIMPLE CYCLE COMBUSTION TURBINES. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS PSD TRIGGERED DUE TO RELAXATION OF A FEDERALLY-ENFORCEABLE CONDITION LIMITING POTENTIAL EMISSIONS BELOW MAJOR STATIONARY SOURCE THRESHOLDS. | TURBINE EXHAUST STACK NO. 1 &amp; NO. 2 | 15.11 | NATURAL GAS | 1900 | MM BTU/H EACH |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE NATURAL GAS | 17 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 17 | LB/H | HOURLY MAXIMUM / STARTUP & SHUTDOWN ONLY | 0 |  |  | 0 | 0 | N |  | LIMITS ARE PER TURBINE EXHAUST STACK. AGGREGATE PM10 EMISSIONS FROM BOTH TURBINE EXHAUST STACKS ARE LIMITED TO 30.94 TONS PER YEAR. STARTUP & SHUTDOWN OPERATIONS ARE LIMITED TO 520 HOURS PER YEAR.
LA-0258 | CALCASIEU PLANT | ENTERGY GULF STATES LA LLC | CALCASIEU | LA | 70665 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: TEGAN TREADAWAY, (225) 219-3408 | PSD-LA-746 | 4911 | 221112 | 110007000000 | 11/10/2009 &nbsp;ACT | 12/21/2011 &nbsp;ACT | 2012-02-01 | 2012-04-03 | C |  | 320 MW POWER PLANT COMPRISED OF 2 NATURAL GAS-FIRED SIMPLE CYCLE COMBUSTION TURBINES. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS PSD TRIGGERED DUE TO RELAXATION OF A FEDERALLY-ENFORCEABLE CONDITION LIMITING POTENTIAL EMISSIONS BELOW MAJOR STATIONARY SOURCE THRESHOLDS. | TURBINE EXHAUST STACK NO. 1 &amp; NO. 2 | 15.11 | NATURAL GAS | 1900 | MM BTU/H EACH |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | USE OF PIPELINE NATURAL GAS | 17 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 17 | LB/H | HOURLY MAXIMUM / STARTUP & SHUTDOWN ONLY | 0 |  |  | 0 | 0 | N |  | LIMITS ARE PER TURBINE EXHAUST STACK. AGGREGATE PM2.5 EMISSIONS FROM BOTH TURBINE EXHAUST STACKS ARE LIMITED TO 30.94 TONS PER YEAR. STARTUP & SHUTDOWN OPERATIONS ARE LIMITED TO 520 HOURS PER YEAR.
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE 7FA Simple Cycle Combustion Turbine | 15.11 | Pipeline quality natural gas | 1780 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | will fire only pipeline quality natural gas | 18 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | GE 7FA Simple Cycle Combustion Turbine | 15.11 | Pipeline quality natural gas | 1780 | MMBTU/HR |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | will fire only pipeline quality natural gas | 18 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110001000000 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine with Duct Burner firing natural gas | 15.11 | Natural Gas | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 22.6 | LB/H | AV OF THREE ONE H STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110001000000 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Combined Cycle Combustion Turbine with Duct Burner firing natural gas | 15.11 | Natural Gas | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Use of natural gas a clean burning fuel | 22.6 | LB/H | AV OF THREE ONE H STACK TESTS | BACT-PSD | OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0768 | SHAWNEE ENERGY CENTER | SHAWNEE ENERGY CENTER, LLC | HILL | TX |  | USA | NEIL O'DONOVAN | 312-422-1608 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, P.E., 512-239-1353, joseph.janecka@tceq.texas.gov | PSDTX1442, 125963 | 4911 | 221112 | UNKNOWN | 07/31/2015 &nbsp;ACT | 10/09/2015 &nbsp;ACT | 2015-10-05 | 2016-07-06 | A |  | Electric Generating Utility: The project will consist of four gas fired combustion turbines (CTGs). The CTGs are fueled with pipeline quality natural gas and will operate in simple cycle mode. The gas turbines will be one of two options. |  | Simple cycle turbines greater than 25 megawatts (MW) | 15.11 | natural gas | 230 | MW | Siemens Model SGT6-5000 F5ee â€“ 230 MW or Second turbine option: General Electric Model 7FA.05TP â€“ 227 MW | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices. | 84.1 | LB/HR |  | BACT-PSD | NSPS | N | 0 | U | 152.96 | TPY |  | 0 |  |  | 0 | 0 | N
TX-0768 | SHAWNEE ENERGY CENTER | SHAWNEE ENERGY CENTER, LLC | HILL | TX |  | USA | NEIL O'DONOVAN | 312-422-1608 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, P.E., 512-239-1353, joseph.janecka@tceq.texas.gov | PSDTX1442, 125963 | 4911 | 221112 | UNKNOWN | 07/31/2015 &nbsp;ACT | 10/09/2015 &nbsp;ACT | 2015-10-05 | 2016-07-06 | A |  | Electric Generating Utility: The project will consist of four gas fired combustion turbines (CTGs). The CTGs are fueled with pipeline quality natural gas and will operate in simple cycle mode. The gas turbines will be one of two options. |  | Simple cycle turbines greater than 25 megawatts (MW) | 15.11 | natural gas | 230 | MW | Siemens Model SGT6-5000 F5ee â€“ 230 MW or Second turbine option: General Electric Model 7FA.05TP â€“ 227 MW | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Pipeline quality natural gas; limited hours; good combustion practices. | 84.1 | LB/HR |  | BACT-PSD | NSPS | N | 0 | U | 152.96 | TPY |  | 0 |  |  | 0 | 0 | N
[40 empty] | Range Low | 0.72 | LB/HR
[40 empty] | Range High | 84.1 | LB/HR
[40 empty] | Mean | 11.0452 | LB/HR
[40 empty] | Median | 6.95 | LB/HR
[40 empty] | Mode | 5 | LB/HR