## PermitSearchResults (22)
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
TX-0696 | ROANâ€™S PRAIRIE GENERATING STATION | TENASKA ROANâ€™S PRAIRIE PARTNERS (TRPP), LLC | GRIMES | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 erik.hendrickson@tceq.texas.gov | 114698 PSDTX1378 | 4911 | 221112 | 110028000000 | 10/25/2013 &nbsp;ACT | 09/22/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | The proposed project is to construct and operate the RPGS comprised of three new simple cycle combustion turbine generators (CTG), fueled by pipeline quality natural gas. The new CTGs will be peaking units, designed to operate during periods of high electric demand. The three CTGs will produce between 507 and 694 MW of electricity combined, depending on ambient temperature and the model of combustion turbine (CT) selected. The applicant is considering three models of CTs; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. |  | (2) simple cycle turbines | 15.11 | natural gas | 600 | MW | The three possible CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. will operate 2,920 hours per year at full load for each CT | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion | 1.4 | PPMVD | @15% O2 GE OPTION | BACT-PSD |  | N | 0 | U | 1 | PPMVD | @15% O2 SIEMENS OPTION | 0 |  |  | 0 | 0 | N
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110065000000 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Large Combustion Turbines &gt; 25 MW | 15.11 | natural gas | 232 | MW | 4 Simple cycle CTGs, 2,500 hr/yr operational limitation. Facility will consist of either 232 MW (Siemens) or 220 MW (GE) | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 2 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | SUBPARTS KKKK AND TTTT
GA-0139 | DAHLBERG COMBUSDTION TURBINE ELECTRIC GENERATING FACILITY (P | SOUTHERN POWER COMPANY | JACKSON | GA | 30565 | USA | MR. E.S. (SCOTT) DIAL | 704 278-6601 | ESDIAL@SOUTHERNCO.COM | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-157-0034-V-04-1 | 4911 | 221112 | UNKNOWN | 07/10/2008 &nbsp;ACT | 05/14/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | C |  | PLANT DAHLBERG HAS PROPOSED TO CONSTRUCT AND OPERATE FOUR ADDITIONAL SIMPLE-CYCLE COMBUSTION TURBINES (SOURCE CODES: CT11-CT14) AND ONE FUEL OIL STORAGE TANK. THE PROPOSED PROJECT WILL HAVE A NOMINAL GENERATING CAPACITY OF 760 MW. THE FACILITY IS CURRENTLY PERMITTED TO OPERATE 10 DUAL-FUELED SIMPLE-CYCLE CTG's. AFTER THE EXPANSION, THE FACILITY WILL HAVE A TOTAL NOMINAL GENERATING CAPACITY OF 1530 MW. |  | SIMPLE CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.11 | NATURAL GASE | 1530 | MW | THE PROCESS USES FUEL OIL FOR BACKUP AT THE RATE OF 2129 MMBUT/H | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 5 | PPM@15%02 | 3 HOUR AVERAGE/CONTITION 3.3.24 | BACT-PSD | OPERATING PERMIT | U | 0 | N | 5 | PPM@15%02 | 3 HOUR AVERAGE/CONDITION 3.3.28 | 0 |  |  | 0 | 0 | N
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 2 | PPMVD |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0733 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JOLLY HAYDEN | 806-349-5250 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, (512)239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358M1 | 4911 | 221112 | 110043000000 | 03/20/2015 &nbsp;ACT | 05/12/2015 &nbsp;ACT | 2015-05-04 | 2016-06-08 | B |  | Golden Spread Electric Cooperative, Inc. (GSEC) is requesting authorization for three additional simple cycle electric generating plants at an existing site to meet increased energy demand in the area. The generating equipment consists of three new GE 7F5-Series natural gas-fired combustion turbine generators (CTGs). Each turbine has a maximum electric output of 202 MW. |  | Simple Cycle Turbine &amp; Generator | 15.11 | natural gas | 202 | MW | 3 additional GE 7F 5-Series Combustion Turbine Generators | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 2 | PPMVD @ 15% O2 |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of each turbine is limited to 4,572 hours per year
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110030000000 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices and fueled by natural gas | 1.6 | PPMVD | @15%O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0540 | BOSQUE COUNTY POWER PLANT | BOSQUE POWER COMPANY LLC | BOSQUE | TX | 76644 | USA | MS KATHY FRENCH | 6365322200 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | MS. BRIDGET MALONE (512) 239-4286 | 40620 | 4911 | 221112 | 4803500002 | 10/26/2007 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | PSDTX931M1 | ELECTRICAL GENERATION | 15.11 | NATURAL GAS | 170 | MW | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES TO MINIMIZE THE PRODUCTS OF INCOMPLETE COMBUSTION OF THE NATURAL GAS TO ACHIEVE LESS THAN 4 PPMV OVER A ROLLING 3-HOUR PERIOD. | 4 | PPMVD | 3 HOUR | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0768 | SHAWNEE ENERGY CENTER | SHAWNEE ENERGY CENTER, LLC | HILL | TX |  | USA | NEIL O'DONOVAN | 312-422-1608 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, P.E., 512-239-1353, joseph.janecka@tceq.texas.gov | PSDTX1442, 125963 | 4911 | 221112 | UNKNOWN | 07/31/2015 &nbsp;ACT | 10/09/2015 &nbsp;ACT | 2015-10-05 | 2016-07-06 | A |  | Electric Generating Utility: The project will consist of four gas fired combustion turbines (CTGs). The CTGs are fueled with pipeline quality natural gas and will operate in simple cycle mode. The gas turbines will be one of two options. |  | Simple cycle turbines greater than 25 megawatts (MW) | 15.11 | natural gas | 230 | MW | Siemens Model SGT6-5000 F5ee â€“ 230 MW or Second turbine option: General Electric Model 7FA.05TP â€“ 227 MW | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices; pipeline quality natural gas; limited hours | 1.4 | PPMV |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,920 hours on a 12-month rolling average.
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Simple Cycle Turbine | 15.11 | natural gas | 227.5 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices; pipeline quality natural gas; limited hours; | 2 | PPMVD | 145% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0764 | NACOGDOCHES POWER ELECTRIC GENERATING PLANT | NACOGDOCHES POWER, LLC | NACOGDOCHES | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem 512-239-1310 Tzvi.shalem@tceq.texas.gov | 77679, PSDTX1061M1 & O-3455 | 4911 | 221112 | 110044000000 | 06/25/2015 &nbsp;ACT | 10/14/2015 &nbsp;ACT | 2015-09-16 | 2016-07-06 | B |  | Nacogdoches Power, LLC is requesting authorization for one natural gas fired, simple cycle combustion turbine generator (CTG). The CTG will be a Siemens F5 and have a nominal electric output of 232 megawatts (MW). |  | Natural Gas Simple Cycle Turbine (&gt;25 MW) | 15.11 | natural gas | 232 | MW | One Siemens F5 simple cycle combustion turbine generator | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices; pipeline quality natural gas; limited hours; | 2 | PPMVD @ 15% O2 |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,500 hours on a 12-month rolling average.
CA-1176 | ORANGE GROVE PROJECT |  | SAN DIEGO | CA | 92059 | USA |  |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Camqui Nguyen (858)586-2747 camqui.nguyen@sdcounty.ca.gov | 985708 | 491 | 221122 | UNKNOWN | 11/03/2007 &nbsp;ACT | 12/04/2008 &nbsp;ACT | 2010-09-21 | 2011-06-27 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 49.8 | MW | Combustion turbine for peaking power plant | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation catalyst | 2 | PPM | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP03) | 15.11 | Natural Gas | 40 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 3 | PPMV AT 15% O2 | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 3 | LB/H | 3-HOUR AVERAGE | 14 | T/YR |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Trubine (EP04) | 15.11 | Natural Gas | 40 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 3 | PPMV AT 15% O2 | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 3 | LB/H | 3-HOUR AVERAGE | 14 | T/YR |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP05) | 15.11 | Natural Gas | 40 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 3 | PPMV AT 15% O2 | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 3 | LB/H | 3-HOUR AVERAGE | 14 | T/YR |  | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055000000 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Three simple cycle combustion turbines | 15.11 | natural gas | 799.7 | MMBTU/H | Three GE, LMS100PA, natural gas-fired, simple cycle CTG rated at 799.7 MMBtu per hour each,based on HHV. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst (CatOx) | 2.5 | PPMVD AT 15% O2 | AVE OVER STACK TEST LENGTH | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1174 | EL CAJON ENERGY LLC | EL CAJON ENERGY LLC | SAN DIEGO | CA | 92020 | USA | GENEVIEVE HUFFMAN |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Evariste Haury (858)-586-2745 Evariste.Haury@sdcounty.ca.gov | 987824 | 519 | 311999 | 110043000000 | 11/01/2008 &nbsp;ACT | 12/11/2009 &nbsp;ACT | 2010-09-20 | 2011-04-11 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 49.95 | MW |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxydation catalyst | 2 | PPMV | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1175 | ESCONDIDO ENERGY CENTER LLC |  | SAN DIEGO | CA | 92029 | USA |  |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Arthur Carbonell (858)-586-2741 arthur.carbonell@sdcounty.ca.gov | 985693 | 491 | 221122 | UNKNOWN | &nbsp; | 07/02/2008 &nbsp;ACT | 2010-09-21 | 2011-06-27 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 46.5 | MW |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxydation catalyst | 2 | PPMV@15% OXYGEN | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
[40 empty] | Range Low | 1.4 | PPM
[40 empty] | Range High | 5 | PPM
[40 empty] | Mean | 2.4059 | PPM
[40 empty] | Median | 2 | PPM
[40 empty] | Mode | 2 | PPM

## Good Combustion
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
TX-0696 | ROANâ€™S PRAIRIE GENERATING STATION | TENASKA ROANâ€™S PRAIRIE PARTNERS (TRPP), LLC | GRIMES | TX |  | USA | LARRY CARLSON | (402) 938-1661 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 erik.hendrickson@tceq.texas.gov | 114698 PSDTX1378 | 4911 | 221112 | 110028000000 | 10/25/2013 &nbsp;ACT | 09/22/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | The proposed project is to construct and operate the RPGS comprised of three new simple cycle combustion turbine generators (CTG), fueled by pipeline quality natural gas. The new CTGs will be peaking units, designed to operate during periods of high electric demand. The three CTGs will produce between 507 and 694 MW of electricity combined, depending on ambient temperature and the model of combustion turbine (CT) selected. The applicant is considering three models of CTs; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. |  | (2) simple cycle turbines | 15.11 | natural gas | 600 | MW | The three possible CT models are: (1) General Electric 7FA.04; (2) General Electric 7FA.05; or (3) Siemens SGT6- 5000F. will operate 2,920 hours per year at full load for each CT | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion | 1.4 | PPMVD | @15% O2 GE OPTION | BACT-PSD |  | N | 0 | U | 1 | PPMVD | @15% O2 SIEMENS OPTION | 0 |  |  | 0 | 0 | N
TX-0788 | NECHES STATION | APEX TEXAS POWER LLC | CHEROKEE | TX |  | USA | DAVID JENKINS | 317-431-1004 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ruth Alvirez 512-239-5220 Ruth.alvirez@tceq.texas .gov | 122401, PSDTX1428, GHGPSDTX111 | 4911 | 221112 | 110065000000 | 11/06/2015 &nbsp;ACT | 03/24/2016 &nbsp;ACT | 2016-02-19 | 2016-07-29 | A |  | either 4 simple cycle combustion turbine generators (CTGs) or two CTGs operating in simple cycle or combined cycle modes. The CTGs will be one of two options: Siemens or General Electric. |  | Large Combustion Turbines &gt; 25 MW | 15.11 | natural gas | 232 | MW | 4 Simple cycle CTGs, 2,500 hr/yr operational limitation. Facility will consist of either 232 MW (Siemens) or 220 MW (GE) | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 2 | PPM |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | SUBPARTS KKKK AND TTTT
GA-0139 | DAHLBERG COMBUSDTION TURBINE ELECTRIC GENERATING FACILITY (P | SOUTHERN POWER COMPANY | JACKSON | GA | 30565 | USA | MR. E.S. (SCOTT) DIAL | 704 278-6601 | ESDIAL@SOUTHERNCO.COM | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us |  | 4911-157-0034-V-04-1 | 4911 | 221112 | UNKNOWN | 07/10/2008 &nbsp;ACT | 05/14/2010 &nbsp;ACT | 2010-09-09 | 2010-09-10 | C |  | PLANT DAHLBERG HAS PROPOSED TO CONSTRUCT AND OPERATE FOUR ADDITIONAL SIMPLE-CYCLE COMBUSTION TURBINES (SOURCE CODES: CT11-CT14) AND ONE FUEL OIL STORAGE TANK. THE PROPOSED PROJECT WILL HAVE A NOMINAL GENERATING CAPACITY OF 760 MW. THE FACILITY IS CURRENTLY PERMITTED TO OPERATE 10 DUAL-FUELED SIMPLE-CYCLE CTG's. AFTER THE EXPANSION, THE FACILITY WILL HAVE A TOTAL NOMINAL GENERATING CAPACITY OF 1530 MW. |  | SIMPLE CYCLE COMBUSTION TURBINE - ELECTRIC GENERATING PLANT | 15.11 | NATURAL GASE | 1530 | MW | THE PROCESS USES FUEL OIL FOR BACKUP AT THE RATE OF 2129 MMBUT/H | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 5 | PPM@15%02 | 3 HOUR AVERAGE/CONTITION 3.3.24 | BACT-PSD | OPERATING PERMIT | U | 0 | N | 5 | PPM@15%02 | 3 HOUR AVERAGE/CONDITION 3.3.28 | 0 |  |  | 0 | 0 | N
*TX-0833 | JACKSON COUNTY GENERATORS | SOUTHERN POWER | JACKSON | TX |  | USA | SUSAN COMENSKY | 205-257-2098 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant, (512) 239-1313, Marc.Sturdivant@tceq.texas.gov | PSDTX1422 | 4911 | 221112 | not found | 01/26/2016 &nbsp;ACT | 01/26/2018 &nbsp;ACT | 2018-04-26 | 2018-05-02 | A |  | four natural gas-fired simple-cycle combustion turbines, five fuel gas heaters, and a firewater pump engine |  | Combustion Turbines | 15.11 | natural gas | 920 | MW | 4 identical units, each limited to 2500 hours of operation per year | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 2 | PPMVD |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS KKKK
TX-0733 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE, INC. | HALE | TX |  | USA | JOLLY HAYDEN | 806-349-5250 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Laura Gibson, (512)239-2175, laura.gibson@tceq.texas.gov | 109148, PSDTX1358M1 | 4911 | 221112 | 110043000000 | 03/20/2015 &nbsp;ACT | 05/12/2015 &nbsp;ACT | 2015-05-04 | 2016-06-08 | B |  | Golden Spread Electric Cooperative, Inc. (GSEC) is requesting authorization for three additional simple cycle electric generating plants at an existing site to meet increased energy demand in the area. The generating equipment consists of three new GE 7F5-Series natural gas-fired combustion turbine generators (CTGs). Each turbine has a maximum electric output of 202 MW. |  | Simple Cycle Turbine &amp; Generator | 15.11 | natural gas | 202 | MW | 3 additional GE 7F 5-Series Combustion Turbine Generators | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 2 | PPMVD @ 15% O2 |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of each turbine is limited to 4,572 hours per year
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110030000000 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | Gas turbines (9 units) | 15.11 | natural gas | 1069 | mm btu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices and fueled by natural gas | 1.6 | PPMVD | @15%O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0540 | BOSQUE COUNTY POWER PLANT | BOSQUE POWER COMPANY LLC | BOSQUE | TX | 76644 | USA | MS KATHY FRENCH | 6365322200 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | MS. BRIDGET MALONE (512) 239-4286 | 40620 | 4911 | 221112 | 4803500002 | 10/26/2007 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2009-11-06 | 2009-11-06 | A |  | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | PSDTX931M1 | ELECTRICAL GENERATION | 15.11 | NATURAL GAS | 170 | MW | BOSQUE POWER COMPANY IS SEEKING TO AMEND THEIR EXISTING PERMIT TO CONSTRUCT DUCT FIRING CAPABILITY TO THE HEAT RECOVERY STEAM GENERATORS (HRSGS) AUTHORIZED FOR THE UNIT 1 AND UNIT 2 GAS TURBINES. EACH COMBUSTION TURBINE IS NOMINALLY RATED AT 170 MEGAWATTS (MW) WHEN OPERATED IN THE SIMPLE CYCLE MODE (UP TO 8,760 HOURS A YEAR). UNITS 1 AND 2 ARE ALSO PERMITTED TO OPERATE IN COMBINED CYCLE MODE. WITH THE AMENDED PERMIT, EACH OF THE HRSGS WILL BE EQUIPPED WITH A 212 MMBTU/HR NATURAL GAS-FIRED DUCT BURNER UNIT TO BE OPERATED AS POWER DEMAND REQUIRES. ADDITIONAL EQUIPMENT ALREADY AUTHORIZED UNDER THE CURRENT PERMIT INCLUDES: TWO MULTI-CELL MECHANICAL COOLING TOWERS, A SMALL 16.8 MMBTU/HR NATURAL GAS FIRED HEATER AND NATURAL GAS PIPING. BOSQUE IS ALSO SEEKING AUTHORIZATION FOR THE ADDITION OF AN AMMONIA STORAGE AND HANDLING SYSTEM WITH THIS PERMIT AMENDMENT/RENEWAL APPLICATION. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES TO MINIMIZE THE PRODUCTS OF INCOMPLETE COMBUSTION OF THE NATURAL GAS TO ACHIEVE LESS THAN 4 PPMV OVER A ROLLING 3-HOUR PERIOD. | 4 | PPMVD | 3 HOUR | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0768 | SHAWNEE ENERGY CENTER | SHAWNEE ENERGY CENTER, LLC | HILL | TX |  | USA | NEIL O'DONOVAN | 312-422-1608 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, P.E., 512-239-1353, joseph.janecka@tceq.texas.gov | PSDTX1442, 125963 | 4911 | 221112 | UNKNOWN | 07/31/2015 &nbsp;ACT | 10/09/2015 &nbsp;ACT | 2015-10-05 | 2016-07-06 | A |  | Electric Generating Utility: The project will consist of four gas fired combustion turbines (CTGs). The CTGs are fueled with pipeline quality natural gas and will operate in simple cycle mode. The gas turbines will be one of two options. |  | Simple cycle turbines greater than 25 megawatts (MW) | 15.11 | natural gas | 230 | MW | Siemens Model SGT6-5000 F5ee â€“ 230 MW or Second turbine option: General Electric Model 7FA.05TP â€“ 227 MW | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices; pipeline quality natural gas; limited hours | 1.4 | PPMV |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,920 hours on a 12-month rolling average.
TX-0819 | GAINES COUNTY POWER PLANT | SOUTHWESTERN PUBLIC SERVICE COMPANY |  | TX |  | USA | DAVID LOW | 806-378-2730 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson, P.E., (512) 239-2175, Laura.Gibson@tceq.texas.gov | 135322, PSDTX1470, AND GHGPSDT | 4911 | 221112 | NOT FOUND | 12/15/2016 &nbsp;ACT | 04/28/2017 &nbsp;ACT | 2017-06-05 | 2017-06-12 | A |  | constructed in phases, with natural gas-fired simple cycle combustion turbines (SCCTs) with dry low nitrogen oxide (NOx) burners (DLN) to be converted into 2-on-1 combined cycle combustion turbines (CCCTs) with selective catalytic reduction (SCRs), heat recovery steam generators (HRSGs, one per combustion turbine) and one steam turbine per two CCCTs. Federal control review only applies to the turbines and HRSGs. |  | Simple Cycle Turbine | 15.11 | natural gas | 227.5 | MW | Four Siemens SGT6-5000F5 natural gas fired combustion turbines | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices; pipeline quality natural gas; limited hours; | 2 | PPMVD | 145% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0764 | NACOGDOCHES POWER ELECTRIC GENERATING PLANT | NACOGDOCHES POWER, LLC | NACOGDOCHES | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Tzvi Shalem 512-239-1310 Tzvi.shalem@tceq.texas.gov | 77679, PSDTX1061M1 & O-3455 | 4911 | 221112 | 110044000000 | 06/25/2015 &nbsp;ACT | 10/14/2015 &nbsp;ACT | 2015-09-16 | 2016-07-06 | B |  | Nacogdoches Power, LLC is requesting authorization for one natural gas fired, simple cycle combustion turbine generator (CTG). The CTG will be a Siemens F5 and have a nominal electric output of 232 megawatts (MW). |  | Natural Gas Simple Cycle Turbine (&gt;25 MW) | 15.11 | natural gas | 232 | MW | One Siemens F5 simple cycle combustion turbine generator | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices; pipeline quality natural gas; limited hours; | 2 | PPMVD @ 15% O2 |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Operation of the turbine is limited to 2,500 hours on a 12-month rolling average.
[40 empty] | Range Low | 1.4 | PPM
[40 empty] | Range High | 5 | PPM
[40 empty] | Mean | 2.34 | PPM
[40 empty] | Median | 2 | PPM
[40 empty] | Mode | 2 | PPM

## Oxidation Catalyst
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
CA-1176 | ORANGE GROVE PROJECT |  | SAN DIEGO | CA | 92059 | USA |  |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Camqui Nguyen (858)586-2747 camqui.nguyen@sdcounty.ca.gov | 985708 | 491 | 221122 | UNKNOWN | 11/03/2007 &nbsp;ACT | 12/04/2008 &nbsp;ACT | 2010-09-21 | 2011-06-27 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 49.8 | MW | Combustion turbine for peaking power plant | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation catalyst | 2 | PPM | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP03) | 15.11 | Natural Gas | 40 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 3 | PPMV AT 15% O2 | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 3 | LB/H | 3-HOUR AVERAGE | 14 | T/YR |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Trubine (EP04) | 15.11 | Natural Gas | 40 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 3 | PPMV AT 15% O2 | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 3 | LB/H | 3-HOUR AVERAGE | 14 | T/YR |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Simple Cycle Turbine (EP05) | 15.11 | Natural Gas | 40 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst | 3 | PPMV AT 15% O2 | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 3 | LB/H | 3-HOUR AVERAGE | 14 | T/YR |  | 0 | 0 | N
CO-0073 | PUEBLO AIRPORT GENERATING STATION | BLACK HILLS ELECTRIC GENERATION, LLC | PUEBLO | CO | 81001 | USA | TIM MORDHORST | 605-721-2181 | TIM.MORDHORST@BLACKHILLSCORP.COM | 8 | CO001 | COLORADO DEPT OF HEALTH - AIR POLL CTRL | MR. ROLAND HEA | (303) 692-3252 | Roland.Hea@state.co.us |  | 09PB0591 | 4911 | 221112 | 110055000000 | 09/23/2009 &nbsp;ACT | 07/22/2010 &nbsp;ACT | 2014-10-03 | 2017-09-12 | A |  | Combustion turbine power plant | New power plant consisting of 7 combustion turbines | Three simple cycle combustion turbines | 15.11 | natural gas | 799.7 | MMBTU/H | Three GE, LMS100PA, natural gas-fired, simple cycle CTG rated at 799.7 MMBtu per hour each,based on HHV. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst (CatOx) | 2.5 | PPMVD AT 15% O2 | AVE OVER STACK TEST LENGTH | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1174 | EL CAJON ENERGY LLC | EL CAJON ENERGY LLC | SAN DIEGO | CA | 92020 | USA | GENEVIEVE HUFFMAN |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Evariste Haury (858)-586-2745 Evariste.Haury@sdcounty.ca.gov | 987824 | 519 | 311999 | 110043000000 | 11/01/2008 &nbsp;ACT | 12/11/2009 &nbsp;ACT | 2010-09-20 | 2011-04-11 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 49.95 | MW |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Oxydation catalyst | 2 | PPMV | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1175 | ESCONDIDO ENERGY CENTER LLC |  | SAN DIEGO | CA | 92029 | USA |  |  |  | 9 | CA030 | SAN DIEGO COUNTY APCD, CA | MR. GARY SMITH | (858)586-2722 | gary.smith@sdcounty.ca.gov | Arthur Carbonell (858)-586-2741 arthur.carbonell@sdcounty.ca.gov | 985693 | 491 | 221122 | UNKNOWN | &nbsp; | 07/02/2008 &nbsp;ACT | 2010-09-21 | 2011-06-27 | A |  |  |  | Gas turbine simple cycle | 15.11 | Natural gas | 46.5 | MW |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxydation catalyst | 2 | PPMV@15% OXYGEN | 1 HOUR | BACT-PSD | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
[40 empty] | Range Low | 2 | PPM
[40 empty] | Range High | 3 | PPM
[40 empty] | Mean | 2.5 | PPM
[40 empty] | Median | 2.5 | PPM
[40 empty] | Mode | 2 | PPM