## Boiler Catalyst for CO_VOC
Appendix B
KNO Restart
Oxidation Catalyst for CO&VOC Control
Package Boilers
VOC Control Efficiency (%) | 80
CO Control Efficiency (%) | 99
Facility Input Data
Item | Value
Total Hours per year | 8760
Economic Life, years | 10
Interest Rate (%) | 7
CFR | 0.14238
SFF
Source(s) Controlled | Package Boilers
Rated Heat Input (MMBtu/hr) | 243
Total Flowrate (acfm) | 161157
VOC Emission Rate (lb/hr) | 1.3
VOC Emissions (tpy) | 5.694
CO Emission Rate (lb/hr) | 8.99
CO Emissions (tpy) | 39.3762
Site Specific Electricity Cost ($/kWh) | 0.10091 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Site Specific Operating Labor Cost ($/hr) | 48.8295 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Site Specific Maint. Labor Cost ($/hr) | 48.8295 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Capital Costs
| Value | Basis
Direct Costs
1.) Purchased Equipment Cost
a.) Equipment cost + auxiliaries | 169171.7499 | WE ENERGIES reference | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
b.) Instrumentation | 16900 | 0.10 x A
c.) Sales taxes | 11800 | 0.07 x A
d.) Freight | 8500 | 0.05 x A
Total Purchased equipment cost, (PEC) | 206371.7499 | B = 1.22 x A
2.) Direct installation costs
a.) Foundations and supports | 16500 | 0.08 x B
b.) Handling and erection | 28900 | 0.14 x B
c.) Electrical | 8300 | 0.04 x B
d.) Piping | 4100 | 0.02 x B
e.) Insulation for ductwork | 2100 | 0.01 x B
f.) Painting | 2100 | 0.01 x B
Total direct installation cost | 62000 | 0.30 x B
3.) Site preparation | NA | As Required, SP
4.) Buildings | NA | As Required, Bldg.
Total Direct Cost, DC | 268400 | 1.30B + SP + Bldg.
Indirect Costs (installation)
5.) Engineering | 20600 | 0.10 x B
6.) Construction and field expenses | 10300 | 0.05 x B
7.) Contractor fees | 20600 | 0.10 x B
8.) Start-up | 4100 | 0.02 x B
9.) Performance test | 2100 | 0.01 x B
10.) Contingencies | 6200 | 0.03 x B
11.) Maintenance Cost
Total Indirect Cost, IC | 63900 | 0.31B + Other
Total Capital Investment (TCI) = DC + IC | 332300 | 1.61B + SP + Bldg. + Other
CO Control Efficiency (%) | 99
Annual Costs
Item | Value | Basis | Source
1) Electricity
Reagent Pump Requirement (kW) | 1000 |  | Estimate
Electric Power Cost ($/kWh) | 0.10091
Cost ($/yr) | 884009.268
2) Operating Costs
Operating Labor Requirement (hr/hours of operation) | 0.5 | Estimate - 1/2 hr/shift | N/A
Unit Cost ($/hr) | 48.8295 | Estimate | N/A
Labor Cost ($/yr) | 26730 | Calculation | N/A
Total Operating Costs | 910739.268 |  | Estimate
3) Supervisory Labor
Cost ($/yr) | 4010 | 15% Operating Labor | OAQPS
4) Maintenance
Maintenance Labor Req. (hr/year) | 300 |  | Estimate
Catalyst Replacement Labor Req. (hr/yr) | 560 |  | Estimate
Unit Cost ($/hr) | 48.8295 | Facility Data | Estimate
Labor Cost ($/yr) | 41990 | Calculation | N/A
Material Cost ($/yr) | 41990 | 100% of Maintenance Labor | OAQPS
Total Cost ($/yr) | 83980 | Calculation | N/A
5) Catalyst Replacement
Catalyst Cost ($) | 112781.1666 |  | WE ENERGIES | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Sales Tax ($) | 0 | 0% Sales Tax | Estimate
Catalyst Life (yrs) | 5 | n | Estimate
Interest Rate (%) | 7 | i | Estimate
Factor | 0.17389
Annual Cost ($/yr) | 19610 | (Volume)(Unit Cost)(CRF) | N/A
6) Indirect Annual Costs
Overhead | 68830 | 60% of O&M Costs | OAQPS
Administration | 6650 | 2% of Total Capital Investment | OAQPS
Property Tax | 3320 | 1% of Total Capital Investment | OAQPS
Insurance | 3320 | 1% of Total Capital Investment | OAQPS
Capital Recovery | 31250 | 20 yr life; 7% interest (-cat. cost) | OAQPS
Total Indirect ($/yr) | 113370
Total Annualized Cost ($/yr) | 1131700
Total VOC Controlled (tpy) | 4.5552
Total CO Controlled (tpy) | 38.9824
VOC Cost Effectiveness ($/ton) | 248400
CO Cost Effectiveness ($/ton) | 29000

## WH_ST Catalyst for CO_VOC
Appendix B
KNO Restart
Oxidation Catalyst for CO&VOC Control
Waste Heat Boiler/Solar Turbine
VOC Control Efficiency (%) | 80
CO Control Efficiency (%) | 99
Facility Input Data
Item | Value
Total Hours per year | 8760
Economic Life, years | 10
Interest Rate (%) | 7
CFR | 0.14238
SFF
Source(s) Controlled | Waste Heat Boilers/Solar Turbines
Rated Heat Input (MMBtu/hr) | 102.172
Total Flowrate (acfm) | 46750 | Original flowrate from 2013 cost estimate
VOC Emission Rate (lb/hr) | 0.37
VOC Emissions (tpy) | 1.61
CO Emission Rate (lb/hr) | 11.14
CO Emissions (tpy) | 48.78
Site Specific Electricity Cost ($/kWh) | 0.10091 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Site Specific Operating Labor Cost ($/hr) | 48.8295 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Site Specific Maint. Labor Cost ($/hr) | 48.8295 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Capital Costs
| Value | Basis
Direct Costs
1.) Purchased Equipment Cost
a.) Equipment cost + auxiliaries | 71130.1071 | WE ENERGIES reference | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
b.) Instrumentation | 7100 | 0.10 x A
c.) Sales taxes | 5000 | 0.07 x A
d.) Freight | 3600 | 0.05 x A
Total Purchased equipment cost, (PEC) | 86830.1071 | B = 1.22 x A
2.) Direct installation costs
a.) Foundations and supports | 6900 | 0.08 x B
b.) Handling and erection | 12200 | 0.14 x B
c.) Electrical | 3500 | 0.04 x B
d.) Piping | 1700 | 0.02 x B
e.) Insulation for ductwork | 900 | 0.01 x B
f.) Painting | 900 | 0.01 x B
Total direct installation cost | 26100 | 0.30 x B
3.) Site preparation | NA | As Required, SP
4.) Buildings | NA | As Required, Bldg.
Total Direct Cost, DC | 112900 | 1.30B + SP + Bldg.
Indirect Costs (installation)
5.) Engineering | 8700 | 0.10 x B
6.) Construction and field expenses | 4300 | 0.05 x B
7.) Contractor fees | 8700 | 0.10 x B
8.) Start-up | 1700 | 0.02 x B
9.) Performance test | 900 | 0.01 x B
10.) Contingencies | 2600 | 0.03 x B
11.) Maintenance Cost
Total Indirect Cost, IC | 26900 | 0.31B + Other
Total Capital Investment (TCI) = DC + IC | 139800 | 1.61B + SP + Bldg. + Other
Annual Costs
Item | Value | Basis | Source
1) Electricity
Reagent Pump Requirement (kW) | 1000 |  | Estimate
Electric Power Cost ($/kWh) | 0.10091
Cost ($/yr) | 884009.268
2) Operating Costs
Operating Labor Requirement (hr/hours of operation) | 0.5 | Estimate - 1/2 hr/shift | N/A
Unit Cost ($/hr) | 48.8295 | Estimate | N/A
Labor Cost ($/yr) | 26730 | Calculation | N/A
Total Operating Costs | 910739.268 |  | Estimate
3) Supervisory Labor
Cost ($/yr) | 4010 | 15% Operating Labor | OAQPS
4) Maintenance
Maintenance Labor Req. (hr/year) | 300 |  | Estimate
Catalyst Replacement Labor Req. (hr/yr) | 230 |  | Estimate
Unit Cost ($/hr) | 48.8295 | Facility Data | Estimate
Labor Cost ($/yr) | 25880 | Calculation | N/A
Material Cost ($/yr) | 25880 | 100% of Maintenance Labor | OAQPS
Total Cost ($/yr) | 51760 | Calculation | N/A
5) Catalyst Replacement
Catalyst Cost ($) | 47420.0714 |  | WE ENERGIES | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Sales Tax ($) | 0 | 0% Sales Tax | Estimate
Catalyst Life (yrs) | 5 | n | Estimate
Interest Rate (%) | 7 | i | Estimate
Factor | 0.17389
Annual Cost ($/yr) | 8250 | (Volume)(Unit Cost)(CRF) | N/A
6) Indirect Annual Costs
Overhead | 49500 | 60% of O&M Costs | OAQPS
Administration | 2800 | 2% of Total Capital Investment | OAQPS
Property Tax | 1400 | 1% of Total Capital Investment | OAQPS
Insurance | 1400 | 1% of Total Capital Investment | OAQPS
Capital Recovery | 13150 | 20 yr life; 7% interest (-cat. cost) | OAQPS
Total Indirect ($/yr) | 68250
Total Annualized Cost ($/yr) | 1043000
Total VOC Controlled (tpy) | 1.288
Total CO Controlled (tpy) | 48.2922
VOC Cost Effectiveness ($/ton) | 809800
CO Cost Effectiveness ($/ton) | 21600

## Waste Heat Boilers Low NOx Burn
Appendix B
KNO Restart
Low NOx Burners for Waste Heat Boilers
Source |  | Waste Heat Boiler
Rated Heat Input (MMBtu/hr) |  | 46.729
Baseline Emissions |  | 20.066
Control Efficiency |  | 7.2%
|  | COST COMPONENT: |  | COST (x $1000)
DIRECT COSTS
Purchased Equipment Costs (Included in TCI)
Initial Equipment Costs
Instrumentation
Freight
Taxes
|  | Subtotal - Purchased Equipment Costs |  | 912.5691 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Direct Installation Costs(Included in TCI)
Foundations & supports; handling & erection; electrical; piping; etc. (25% of PEC)
Site Preparation / Buildings (25% of PEC)
|  | Subtotal - Direct Installation Costs |  | 214.8498 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
TOTAL DIRECT COSTS (TDC)
INDIRECT INSTALLATION COSTS
Engineering Costs (10% of Purchased Equip Costs)
Construct. & Field Expenses (5% of Purchased Equip Costs)
Contractor Fees (10% Purchased Equip Costs)
Start-up and Performance Test (2% of Purchased Equip Costs)
Contingency (3% of Purchased Equip Costs)
TOTAL INDIRECT COSTS |  |  |  | 0
TOTAL CAPITAL INVESTMENT (TCI) |  |  |  | 1127.4189
|  | COST COMPONENT: |  | COST (x $1000)
ANNUAL DIRECT COSTS
Operation and Maintenance Labor
|  | Operating Labor |  | 0
|  | O&M Supervision |  | 0
Maintenance Labor and Material (2.75% of PEC)
| Subtotal - Operation and Maintenance Labor |  |  | 0
Utilities
| Subtotal - Utilities |  |  | 0
TOTAL ANNUAL DIRECT COSTS |  |  |  | 0
|  | COST COMPONENT: |  | COST (x $1000)
INDIRECT COSTS
|  | Overhead (not applicable) |  | 0
|  | Property Tax (not applicable) |  | 0
|  | Insurance (negligibIe) |  | 0
|  | Administration (not applicable) |  | 0
TOTAL INDIRECT COSTS |  |  |  | 0
TOTAL ANNUAL O&M COSTS |  |  |  | 0
CAPITAL RECOVERY FACTOR
|  | Equipment Life (years) = | 10
|  | Interest Rate (%) = | 7
|  | Capital Recovery Factor |  | 0.14238
CAPITAL RECOVERY COSTS
|  | TOTAL CAPITAL REQUIREMENT |  | 1127.4189
|  | TOTAL ANNUAL CAPITAL REQUIREMENT |  | 160.5191
TOTAL ANNUALIZED COST |  |  |  | 160.5191
(Total annual O&M cost and annualized capital cost)
TONS OF POLLUTANT REMOVED PER YEAR (baseline * control efficiency) |  |  |  | 1.4448
COST-EFFECTIVENESS
ENVIRONMENTAL BASIS
|  | ($ per ton pollutant removed) |  | 111105
Baseline Emissions =
Heat Input Capacity (46.729 MMBtu/hr) * AP-42 CO Ef. Sm. Boiler (100 lb/106 scf) * (1 MMBtu/ 1,020 scf) * (8760 hrs/1 yr) * (1 ton/2000 lbs)

## Solar Turbine Water Injection
Appendix B
KNO Restart
Water injection for NOx control on Solar Turbines
Source |  | Solar Turbine
Rated Heat Input (MMBtu/hr) |  | 55.443
Baseline Emissions |  | 9.9565
Control Efficiency |  | 76%
|  | COST COMPONENT: |  | COST (x $1000)
DIRECT COSTS
Purchased Equipment Costs (Included in TCI)
Initial Equipment Costs
Instrumentation
Freight
Taxes
|  | Subtotal - Purchased Equipment Costs |  | 490.4652 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Direct Installation Costs(Included in TCI)
Foundations & supports; handling & erection; electrical; piping; etc. (25% of PEC)
Site Preparation / Buildings (25% of PEC)
|  | Subtotal - Direct Installation Costs |  | 0
TOTAL DIRECT COSTS (TDC)
INDIRECT INSTALLATION COSTS
Engineering Costs (10% of Purchased Equip Costs)
Construct. & Field Expenses (5% of Purchased Equip Costs)
Contractor Fees (10% Purchased Equip Costs)
Start-up and Performance Test (2% of Purchased Equip Costs)
Contingency (3% of Purchased Equip Costs)
TOTAL INDIRECT COSTS |  |  |  | 0
TOTAL CAPITAL INVESTMENT (TCI) |  |  |  | 490.4652
|  | COST COMPONENT: |  | COST (x $1000)
ANNUAL DIRECT COSTS
Operation and Maintenance Labor
|  | Operating Labor |  | 0
|  | O&M Supervision |  | 0
|  | Maintenance Labor and Material |  | 18.2069 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
| Subtotal - Operation and Maintenance Labor |  |  | 18.2069
Utilities
|  | Power |  | 4.9632 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
| Subtotal - Utilities |  |  | 4.9632
TOTAL ANNUAL DIRECT COSTS |  |  |  | 23.1701
|  | COST COMPONENT: |  | COST (x $1000)
INDIRECT COSTS
|  | Overhead (not applicable) |  | 0
|  | Property Tax (not applicable) |  | 0
|  | Insurance (negligibIe) |  | 0
|  | Administration (not applicable) |  | 0
TOTAL INDIRECT COSTS |  |  |  | 0
TOTAL ANNUAL O&M COSTS |  |  |  | 23.1701
CAPITAL RECOVERY FACTOR
|  | Equipment Life (years) = | 10
|  | Interest Rate (%) = | 7
|  | Capital Recovery Factor |  | 0.14238
CAPITAL RECOVERY COSTS
|  | TOTAL CAPITAL REQUIREMENT |  | 490.4652
|  | TOTAL ANNUAL CAPITAL REQUIREMENT |  | 69.8312
TOTAL ANNUALIZED COST |  |  |  | 93.0014
(Total annual O&M cost and annualized capital cost)
TONS OF POLLUTANT REMOVED PER YEAR (baseline * control efficiency) |  |  |  | 7.5669
COST-EFFECTIVENESS
ENVIRONMENTAL BASIS
|  | ($ per ton pollutant removed) |  | 12291
Baseline Emissions =
Heat Input Capacity (55.443 MMBtu/hr) * SCR Controlled Emission Rate (0.041 lb/MMBtu) * (8760 hrs/1 yr) * (1 ton/2000 lbs)