## Boiler Cat Ox
Agrium KNO - BACT Analysis
Catalytic Oxidizer VOC and CO Control
Package Boiler
VOC Control Efficiency (%) | 80
CO Control Efficiency (%) | 99
Facility Input Data
Item | Value
Total Hours per year | 8760
Economic Life, years | 10
Interest Rate (%) | 7
Source(s) Controlled | Package Boiler
Total Flowrate (scfm) | 67592.2721
VOC Emission Rate (lb/hr) | 1.3
VOC Emissions (tpy) | 5.694
CO Emission Rate (lb/hr) | 8.99
CO Emissions (tpy) | 39.3762
Site Specific Electricity Cost ($/kWh) | 0.10091 | (Estimated in 2013 - Adjusted for 8.51% inflation)
Site Specific Operating Labor Cost ($/hr) | 48.8295 | (Estimated in 2013 - Adjusted for 8.51% inflation)
Site Specific Maint. Labor Cost ($/hr) | 48.8295 | (Estimated in 2013 - Adjusted for 8.51% inflation)
Capital Costs
| Value | Basis
Direct Costs
1.) Purchased Equipment Cost
a.) Equipment cost + auxiliaries | 1139339.6046 | A (OAQPS) | (Calculated in 2013 - Adjusted for 8.51% inflation)
b.) Instrumentation | 113900 | 0.10 x A
c.) Sales taxes | 79800 | 0.07 x A
d.) Freight | 57000 | 0.05 x A
Total Purchased equipment cost, (PEC) | 1390039.6046 | B = 1.22 x A
2.) Direct installation costs
a.) Foundations and supports | 111200 | 0.08 x B
b.) Handling and erection | 194600 | 0.14 x B
c.) Electrical | 55600 | 0.04 x B
d.) Piping | 67800 | 0.02 x B + 40,000
e.) Insulation for ductwork | 13900 | 0.01 x B
f.) Painting | 13900 | 0.01 x B
Total direct installation cost | 457000 | 0.30 x B
3.) Site preparation | NA | As Required, SP
4.) Buildings | NA | As Required, Bldg.
Total Direct Cost, DC | 1847000 | 1.30B + SP + Bldg.
Indirect Costs (installation)
5.) Engineering | 139000 | 0.10 x B
6.) Construction and field expenses | 69500 | 0.05 x B
7.) Contractor fees | 139000 | 0.10 x B
8.) Start-up | 27800 | 0.02 x B
9.) Performance test | 13900 | 0.01 x B
10.) Contingencies | 41700 | 0.03 x B
Total Indirect Cost, IC | 430900 | 0.31B + Other
Total Capital Investment (TCI) = DC + IC | 2277900 | 1.61B + SP + Bldg. + Other
Annual Costs
Item | Value | Basis | Source
1) Operating Costs
Operating Labor Requirement (hr/hours of operation) | 0.5 | Estimate - 1/2 hr/shift | N/A
Unit Cost ($/hr) | 48.8295 | Estimate | N/A
Labor Cost ($/yr) | 26730 | Calculation | N/A
2) Supervisory Labor
Cost ($/yr) | 4010 | 15% Operating Labor | OAQPS
3) Maintenance
Maintenance Labor Req. (hr/year) | 182.5 | Estimate - 1/2 hr/day | Estimate
Unit Cost ($/hr) | 48.8295 | Estimate | N/A
Labor Cost ($/yr) | 8910 | Calculation | N/A
Material Cost ($/yr) | 8910 | 100% of Maintenance Labor | OAQPS
Total Cost ($/yr) | 17820 | Calculation | N/A
4) Indirect Annual Costs
Overhead | 29140 | 60% of O&M Costs | OAQPS
Administration | 45560 | 2% of Total Capital Investment | OAQPS
Property Tax | 22780 | 1% of Total Capital Investment | OAQPS
Insurance | 22780 | 1% of Total Capital Investment | OAQPS
Capital Recovery | 324320 | 20 yr life; 7% interest | OAQPS
Total Indirect ($/yr) | 444580 | Calculation | N/A
5) Utilities
Natural Gas ($/scf) | 0.0078356 | 7.682 |  | (2019 Q3 Cook Inlet Prevailing Value)
Natural Gas Required (btu/hr) | 14599930.7747
Natural Gas (BTU/scf) | 1020
Natural Gas Required (scf/hr) | 14313.6576
Natural Gas ($/yr) | 982492.4135
Electricity ($/yr) | 267988.5945 |  | OAQPS
Total Utilities Cost ($/yr) | 1250480
6) Catalyst Replacement
Catalyst volume (cf) | 13.5185 |  | OAQPS
Catalyst Cost ($) | 9534.7687 | Catalyst @ $650/cf | Vendor | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Sales Tax ($) | 0 | 0% Sales Tax | Estimate
Catalyst Life (yrs) | 3 | n | Estimate
Interest Rate (%) | 7 | i | Estimate
CRF | 0.38105 | Ammortization of Catalyst | OAQPS
Annual Cost ($/yr) | 3630 | (Volume)(Unit Cost)(CRF) | N/A
Total Annualized Cost ($/yr) | 1747300
Total VOC Controlled (tpy) | 4.5552
Total CO Controlled (tpy) | 38.9824
VOC Cost Effectiveness ($/ton) | 383583.5968
CO Cost Effectiveness ($/ton) | 44800

## WHB Turbine Cat Ox
Agrium KNO - BACT Analysis
Catalytic Oxidizer VOC and CO Control
Waste Heat Boilers/Solar Turbines
VOC Control Efficiency (%) | 80
CO Control Efficiency (%) | 99
Facility Input Data
Item | Value
Total Hours per year | 8760
Economic Life, years | 10
Interest Rate (%) | 7
Source(s) Controlled | Waste Heat Boilers/Solar Turbines
Total Flowrate (scfm) | 49539.4145
VOC Emission Rate (lb/hr) | 0.37
VOC Emissions (tpy) | 1.61
CO Emission Rate (lb/hr) | 11.14
CO Emissions (tpy) | 48.78
Site Specific Electricity Cost ($/kWh) | 0.10091 | (Estimated in 2013 - Adjusted for 8.51% inflation)
Site Specific Operating Labor Cost ($/hr) | 48.8295 | (Estimated in 2013 - Adjusted for 8.51% inflation)
Site Specific Maint. Labor Cost ($/hr) | 48.8295 | (Estimated in 2013 - Adjusted for 8.51% inflation)
Capital Costs
| Value | Basis
Direct Costs
1.) Purchased Equipment Cost
a.) Equipment cost + auxiliaries | 959551.8399 | A (OAQPS) | (Calculated in 2013 - Adjusted for 8.51% inflation)
b.) Instrumentation | 96000 | 0.10 x A
c.) Sales taxes | 67200 | 0.07 x A
d.) Freight | 48000 | 0.05 x A
Total Purchased equipment cost, (PEC) | 1170751.8399 | B = 1.22 x A
2.) Direct installation costs
a.) Foundations and supports | 93700 | 0.08 x B
b.) Handling and erection | 163900 | 0.14 x B
c.) Electrical | 46800 | 0.04 x B
d.) Piping | 63400 | 0.02 x B + 40,000
e.) Insulation for ductwork | 11700 | 0.01 x B
f.) Painting | 11700 | 0.01 x B
Total direct installation cost | 391200 | 0.30 x B
3.) Site preparation | NA | As Required, SP
4.) Buildings | NA | As Required, Bldg.
Total Direct Cost, DC | 1562000 | 1.30B + SP + Bldg.
Indirect Costs (installation)
5.) Engineering | 117100 | 0.10 x B
6.) Construction and field expenses | 58500 | 0.05 x B
7.) Contractor fees | 117100 | 0.10 x B
8.) Start-up | 23400 | 0.02 x B
9.) Performance test | 11700 | 0.01 x B
10.) Contingencies | 35100 | 0.03 x B
Total Indirect Cost, IC | 362900 | 0.31B + Other
Total Capital Investment (TCI) = DC + IC | 1924900 | 1.61B + SP + Bldg. + Other
Annual Costs
Item | Value | Basis | Source
1) Operating Costs
Operating Labor Requirement (hr/hours of operation) | 0.5 | Estimate - 1/2 hr/shift | N/A
Unit Cost ($/hr) | 48.8295 | Estimate | N/A
Labor Cost ($/yr) | 26730 | Calculation | N/A
2) Supervisory Labor
Cost ($/yr) | 4010 | 15% Operating Labor | OAQPS
3) Maintenance
Maintenance Labor Req. (hr/year) | 182.5 | Estimate - 1/2 hr/day | Estimate
Unit Cost ($/hr) | 48.8295 | Estimate | N/A
Labor Cost ($/yr) | 8910 | Calculation | N/A
Material Cost ($/yr) | 8910 | 100% of Maintenance Labor | OAQPS
Total Cost ($/yr) | 17820 | Calculation | N/A
4) Indirect Annual Costs
Overhead | 29140 | 60% of O&M Costs | OAQPS
Administration | 38500 | 2% of Total Capital Investment | OAQPS
Property Tax | 19250 | 1% of Total Capital Investment | OAQPS
Insurance | 19250 | 1% of Total Capital Investment | OAQPS
Capital Recovery | 274060 | 20 yr life; 7% interest | OAQPS
Total Indirect ($/yr) | 380200 | Calculation | N/A
5) Utilities
Natural Gas ($/scf) | 0.0078356 | 7.682 |  | (2019 Q3 Cook Inlet Prevailing Value)
Natural Gas Required (btu/hr) | 11235539.2034
Natural Gas (BTU/scf) | 1020
Natural Gas Required (scf/hr) | 11015.2345
Natural Gas ($/yr) | 756087.9705
Electricity ($/yr) | 196412.9574 |  | OAQPS
Total Utilities Cost ($/yr) | 952500
6) Catalyst Replacement
Catalyst volume (cf) | 9.9079 |  | OAQPS
Catalyst Cost ($) | 6988.1784 | Catalyst @ $650/cf | Vendor | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Sales Tax ($) | 0 | 0% Sales Tax | Estimate
Catalyst Life (yrs) | 3 | n | Estimate
Interest Rate (%) | 7 | i | Estimate
CRF | 0.38105 | Ammortization of Catalyst | OAQPS
Annual Cost ($/yr) | 2660 | (Volume)(Unit Cost)(CRF) | N/A
Total Annualized Cost ($/yr) | 1383900
Total VOC Controlled (tpy) | 1.288
Total CO Controlled (tpy) | 48.2922
VOC Cost Effectiveness ($/ton) | 1074456.5217
CO Cost Effectiveness ($/ton) | 28700

## Reformer Cat Ox
Agrium KNO - BACT Analysis
Catalytic Oxidizer VOC and CO Control
Reformer
VOC Control Efficiency (%) | 80
CO Control Efficiency (%) | 99
Facility Input Data
Item | Value
Total Hours per year | 8760
Economic Life, years | 10
Interest Rate (%) | 7
Source(s) Controlled | Reformer
Total Flowrate (acfm) | 543120
VOC Emission Rate (lb/hr) | 7.279
VOC Emissions (tpy) | 31.882
CO Emission Rate (lb/hr) | 57.507
CO Emissions (tpy) | 251.8807
Site Specific Electricity Cost ($/kWh) | 0.10091 | (Estimated in 2013 - Adjusted for 8.51% inflation)
Site Specific Operating Labor Cost ($/hr) | 48.8295 | (Estimated in 2013 - Adjusted for 8.51% inflation)
Site Specific Maint. Labor Cost ($/hr) | 48.8295 | (Estimated in 2013 - Adjusted for 8.51% inflation)
Capital Costs
| Value | Basis
Direct Costs
1.) Purchased Equipment Cost
a.) Equipment cost + auxiliaries | 3604508.08 | A (OAQPS) | (Calculated in 2013 - Adjusted for 8.51% inflation)
b.) Instrumentation | 360500 | 0.10 x A
c.) Sales taxes | 252300 | 0.07 x A
d.) Freight | 180200 | 0.05 x A
Total Purchased equipment cost, (PEC) | 4397508.08 | B = 1.22 x A
2.) Direct installation costs
a.) Foundations and supports | 351800 | 0.08 x B
b.) Handling and erection | 615700 | 0.14 x B
c.) Electrical | 175900 | 0.04 x B
d.) Piping | 128000 | 0.02 x B + 40,000
e.) Insulation for ductwork | 44000 | 0.01 x B
f.) Painting | 44000 | 0.01 x B
Total direct installation cost | 1359400 | 0.30 x B
3.) Site preparation | NA | As Required, SP
4.) Buildings | NA | As Required, Bldg.
Total Direct Cost, DC | 5756900 | 1.30B + SP + Bldg.
Indirect Costs (installation)
5.) Engineering | 439800 | 0.10 x B
6.) Construction and field expenses | 219900 | 0.05 x B
7.) Contractor fees | 439800 | 0.10 x B
8.) Start-up | 88000 | 0.02 x B
9.) Performance test | 44000 | 0.01 x B
10.) Contingencies | 131900 | 0.03 x B
Total Indirect Cost, IC | 1363400 | 0.31B + Other
Total Capital Investment (TCI) = DC + IC | 7120300 | 1.61B + SP + Bldg. + Other
Annual Costs
Item | Value | Basis | Source
1) Operating Costs
Operating Labor Requirement (hr/hours of operation) | 0.5 | Estimate - 1/2 hr/shift | N/A
Unit Cost ($/hr) | 48.8295 | Estimate | N/A
Labor Cost ($/yr) | 26730 | Calculation | N/A
2) Supervisory Labor
Cost ($/yr) | 4010 | 15% Operating Labor | OAQPS
3) Maintenance
Maintenance Labor Req. (hr/year) | 182.5 | Estimate - 1/2 hr/day | Estimate
Unit Cost ($/hr) | 48.8295 | Estimate | N/A
Labor Cost ($/yr) | 8910 | Calculation | N/A
Material Cost ($/yr) | 8910 | 100% of Maintenance Labor | OAQPS
Total Cost ($/yr) | 17820 | Calculation | N/A
4) Indirect Annual Costs
Overhead | 29140 | 60% of O&M Costs | OAQPS
Administration | 142410 | 2% of Total Capital Investment | OAQPS
Property Tax | 71200 | 1% of Total Capital Investment | OAQPS
Insurance | 71200 | 1% of Total Capital Investment | OAQPS
Capital Recovery | 1013770 | 20 yr life; 7% interest | OAQPS
Total Indirect ($/yr) | 1327720 | Calculation | N/A
5) Utilities
Natural Gas ($/scf) | 0.0078356 | 7.682 |  | (2019 Q3 Cook Inlet Prevailing Value)
Natural Gas Required (btu/hr) | 7038835.2
Natural Gas (BTU/scf) | 1020
Natural Gas Required (scf/hr) | 6900.8188
Natural Gas ($/yr) | 473673.6284
Electricity ($/yr) | 2153352.1647 |  | OAQPS
Total Utilities Cost ($/yr) | 2627030
6) Catalyst Replacement
Catalyst volume (cf) | 108.624 |  | OAQPS
Catalyst Cost ($) | 76614.1366 | Catalyst @ $650/cf | Vendor | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Sales Tax ($) | 0 | 0% Sales Tax | Estimate
Catalyst Life (yrs) | 3 | n | Estimate
Interest Rate (%) | 7 | i | Estimate
CRF | 0.38105 | Ammortization of Catalyst | OAQPS
Annual Cost ($/yr) | 29190 | (Volume)(Unit Cost)(CRF) | N/A
Total Annualized Cost ($/yr) | 4032500
Total VOC Controlled (tpy) | 25.5056
Total CO Controlled (tpy) | 249.3619
VOC Cost Effectiveness ($/ton) | 158102.4352
CO Cost Effectiveness ($/ton) | 16200

## Fuel Usage
CatOx Fuel Usage Estimates (Btu/hr)
Boiler CatOx |  | WHB Turbine CatOx |  | Reformer CatOx
Volumtric flow rate (acfm) | 67592.2721 | Volumtric flow rate (acfm) | 49539.4145 | Volumtric flow rate (acfm) | 543120
density of Air (lb/ft3) | 0.075 | density of Air (lb/ft3) | 0.075 | density of Air (lb/ft3) | 0.075
Mass flow rate (lbs/hr) | 304165.2245 | Mass flow rate (lbs/hr) | 222927.3651 | Mass flow rate (lbs/hr) | 2444040
Tinitial (°F) | 300 | Tinitial (°F) | 290 | Tinitial (°F) | 488
Tfinal (°F) | 500 | Tfinal (°F) | 500 | Tfinal (°F) | 500
Cp(btu/(lb°F)) | 0.24 | Cp(btu/(lb°F)) | 0.24 | Cp(btu/(lb°F)) | 0.24
∆H (btu/hr) | 14599930.7747 | ∆H (btu/hr) | 11235539.2034 | ∆H (btu/hr) | 7038835.2
Notes:
Tinitial (°F) = Outlet gas temperature from controlled emission unit prior to catalytic oxidizer.
Tfinal (°F) = Conservatively assumed to be the lowest operating temperature for a catalytic oxidizer.
Cp(btu/(lb°F)) = Specific Heat of Air