## Aux Boiler SCR for NOX
Appendix C
KNO Restart
SCR NOx Control
Startup Heater
Control Efficiency (%) | 90
Facility Input Data
Item | Value
Total Hours per year (potential) | 8760
Economic Life, years | 25
Interest Rate (%) | 3.25
Source(s) Controlled | Startup Heater
Total Flowrate (acfm) | 62719
NOX Emission Rate (lb/hr) | 9.9
NOX Emissions (tpy) | 0.99
Site Specific Electricity Cost ($/kWh) | 0.093
Site Specific Operating Labor Cost ($/hr) | 45
Site Specific Maint. Labor Cost ($/hr) | 45
Capital Costs
| Value | Basis
Direct Costs
1.) Total Direct Cost, DC | 2338917.6455 | A (OAQPS)
Indirect Installation Cost
2.) General Facilities ($) | 116945.8823 | 0.05*C
3.) Engineering and Home Office Fees | 233891.7645 | 0.10*C
4.) Process Contingency ($) | 116945.8823 | 0.05*C
Total Indirect Cost, IC | 467783.5291 | B = A * (0.05+0.10+0.05)
5.) Project Contingency ($) | 421005.1762 | C = (A+B)*0.15
Total Plant Cost ($) | 3227706.3507 | D = A+B+C
6.) Allowance for Funds During Construction ($) | 0 | E = 0 (Assumed for SCR)
7.) Royalty Allowance ($) | 0 | F = 0 (Assumed for SCR)
8.) Preproduction Cost ($) | 64554.127 | G = 0.02*(F+G)
9.) Inventory Capital* ($) | 14300 | H = Volreagent (gal) * Costreagent ($/gal)
10.) Initial Catalyst and Chemicals ($) | 0 | I = 0 (assumed for SCR)
Total Capital Investment (TCI) = DC + IC | 3306600 | TCI = D+E+F+G+H+I
*Cost for ammonia stored at site, i.e., the first fill of the reagent tanks
Annual Costs
Item | Value | Basis | Source
1) Electricity
Reagent Pump Requirement (kW) | 1000 |  | Estimate
Electric Power Cost ($/kWh) | 0.093
Cost ($/yr) | 814680
2) Operating Costs
Operating Labor Requirement (hr/hours of operation) | 0.5 | Estimate - 1/2 hr/shift | N/A
Unit Cost ($/hr) | 45 | Estimate | N/A
Labor Cost ($/yr) | 24640 | Calculation | N/A
3) Ammonia Costs ($/ton) | 260 | 50% of US Geological Survey Price | USGS
Annual requirement (Lbs/year) | 5356000 | EPA Clean Air Technology Center
Total Ammonia Costs ($/year) | 696280
Total Operating Costs | 1535600 |  | Estimate
4) Supervisory Labor
Cost ($/yr) | 3700 | 15% Operating Labor | OAQPS
5) Maintenance
Maintenance Labor Req. (hr/year) | 182.5 | Estimate - 1/2 hr/day | Estimate
Catalyst Replacement Labor Req. (hr/yr) | 128 | Estimate - 8 men for 160 hours every 10 yrs | Estimate
Unit Cost ($/hr) | 45 | Facility Data | Estimate
Labor Cost ($/yr) | 13970 | Calculation | N/A
Material Cost ($/yr) | 13970 | 100% of Maintenance Labor | OAQPS
Total Cost ($/yr) | 27940 | Calculation | N/A
6) Catalyst Replacement
Catalyst Cost ($) | 170000 | EPA Clean Air Technology Center | Estimate
Sales Tax ($) | 0 | 0% Sales Tax | Estimate
Catalyst Life (yrs) | 5 | EPA Clean Air Technology Center | Estimate
Interest Rate (%) | 3.25 | i | Estimate
CRF | 0.21992 | Ammortization of Catalyst | OAQPS
Annual Cost ($/yr) | 37390 | (Volume)(Unit Cost)(CRF) | N/A
7) Indirect Annual Costs
Overhead | 33770 | 60% of O&M Costs | OAQPS
Administration | 66130 | 2% of Total Capital Investment | OAQPS
Property Tax | 33070 | 1% of Total Capital Investment | OAQPS
Insurance | 33070 | 1% of Total Capital Investment | OAQPS
Capital Recovery | 185180 | 20 yr life; 7% interest (-cat. cost) | OAQPS
Total Indirect ($/yr) | 351220
Total Annualized Cost ($/yr) | 1955900
Total Controlled (tpy) | 0.891
Cost Effectiveness ($/ton) | 2195200
Note on B37: Matt Mihalek: One weeks supply assumed
Note on B67: Sameer Sane: Based on cost from EPA CATC for a 350 mmBtu/hr NG boiler operating at 85% capacity

## Reformer - Low NOx Burners
Cost Effectiveness Calculation for Low NOx Burners for Reformer
Source |  | Unit 12 - Reformer
Rated Heat Input (MMBtu/hr)
Baseline Emissions |  | 118.26
Control Efficiency |  | 33% | (Maximum additional reduction achievable)
|  | COST COMPONENT: |  | COST (x $1000)
DIRECT COSTS
Purchased Equipment Costs (Included in TCI)
Initial Equipment Costs/Engineering
Instrumentation
Freight
Taxes
|  | Subtotal - Purchased Equipment Costs |  | 1627.65 | (vendor supplied value) | Adjusted for inflation at 8.51% from 2013
Direct Installation Costs(Included in TCI)
|  | Labor and Installation |  | 4184.1456 | (vendor supplied value) | Adjusted for inflation at 8.51% from 2013
|  | Subtotal - Direct Installation Costs |  | 4184.1456
TOTAL DIRECT COSTS (TDC)
INDIRECT INSTALLATION COSTS
Engineering Costs (10% of Purchased Equip Costs)
Construct. & Field Expenses (5% of Purchased Equip Costs)
Contractor Fees (10% Purchased Equip Costs)
Start-up and Performance Test (2% of Purchased Equip Costs)
Contingency (3% of Purchased Equip Costs)
TOTAL INDIRECT COSTS |  |  |  | 0
TOTAL CAPITAL INVESTMENT (TCI) |  |  |  | 5811.7956
|  | COST COMPONENT: |  | COST (x $1000)
ANNUAL DIRECT COSTS
Operation and Maintenance Labor
|  | Operating Labor |  | 0
|  | O&M Supervision |  | 0
|  | Maintenance Labor and Material (2.75% of PEC) |  | 159.8244
| Subtotal - Operation and Maintenance Labor |  |  | 159.8244
Utilities
| Subtotal - Utilities |  |  | 0
TOTAL ANNUAL DIRECT COSTS |  |  |  | 159.8244
|  | COST COMPONENT: |  | COST (x $1000)
INDIRECT COSTS
|  | Overhead (not applicable) |  | 0
|  | Property Tax (not applicable) |  | 0
|  | Insurance (negligibIe) |  | 0
|  | Administration (not applicable) |  | 0
TOTAL INDIRECT COSTS |  |  |  | 0
TOTAL ANNUAL O&M COSTS |  |  |  | 159.8244
CAPITAL RECOVERY FACTOR
|  | Equipment Life (years) = | 25
|  | Interest Rate (%) = | 3.25
|  | Capital Recovery Factor |  | 0.059039
CAPITAL RECOVERY COSTS
|  | TOTAL CAPITAL REQUIREMENT |  | 5811.7956
|  | TOTAL ANNUAL CAPITAL REQUIREMENT |  | 343.1245
TOTAL ANNUALIZED COST |  |  |  | 502.9489
(Total annual O&M cost and annualized capital cost)
TONS OF POLLUTANT REMOVED PER YEAR (baseline * control efficiency) |  |  |  | 39.0258
COST-EFFECTIVENESS
ENVIRONMENTAL BASIS
|  | ($ per ton pollutant removed) |  | 12888

## Waste Heat Boilers Low NOx Burn
Appendix B
KNO Restart
Low NOx Burners for Waste Heat Boilers
Source |  | Waste Heat Boiler
Rated Heat Input (MMBtu/hr) |  | 46.729
Baseline Emissions |  | 20.066
Control Efficiency |  | 7.2%
|  | COST COMPONENT: |  | COST (x $1000)
DIRECT COSTS
Purchased Equipment Costs (Included in TCI)
Initial Equipment Costs
Instrumentation
Freight
Taxes
|  | Subtotal - Purchased Equipment Costs |  | 912.5691 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Direct Installation Costs(Included in TCI)
Foundations & supports; handling & erection; electrical; piping; etc. (25% of PEC)
Site Preparation / Buildings (25% of PEC)
|  | Subtotal - Direct Installation Costs |  | 214.8498 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
TOTAL DIRECT COSTS (TDC)
INDIRECT INSTALLATION COSTS
Engineering Costs (10% of Purchased Equip Costs)
Construct. & Field Expenses (5% of Purchased Equip Costs)
Contractor Fees (10% Purchased Equip Costs)
Start-up and Performance Test (2% of Purchased Equip Costs)
Contingency (3% of Purchased Equip Costs)
TOTAL INDIRECT COSTS |  |  |  | 0
TOTAL CAPITAL INVESTMENT (TCI) |  |  |  | 1127.4189
|  | COST COMPONENT: |  | COST (x $1000)
ANNUAL DIRECT COSTS
Operation and Maintenance Labor
|  | Operating Labor |  | 0
|  | O&M Supervision |  | 0
Maintenance Labor and Material (2.75% of PEC)
| Subtotal - Operation and Maintenance Labor |  |  | 0
Utilities
| Subtotal - Utilities |  |  | 0
TOTAL ANNUAL DIRECT COSTS |  |  |  | 0
|  | COST COMPONENT: |  | COST (x $1000)
INDIRECT COSTS
|  | Overhead (not applicable) |  | 0
|  | Property Tax (not applicable) |  | 0
|  | Insurance (negligibIe) |  | 0
|  | Administration (not applicable) |  | 0
TOTAL INDIRECT COSTS |  |  |  | 0
TOTAL ANNUAL O&M COSTS |  |  |  | 0
CAPITAL RECOVERY FACTOR
|  | Equipment Life (years) = | 10
|  | Interest Rate (%) = | 3.25
|  | Capital Recovery Factor |  | 0.11873
CAPITAL RECOVERY COSTS
|  | TOTAL CAPITAL REQUIREMENT |  | 1127.4189
|  | TOTAL ANNUAL CAPITAL REQUIREMENT |  | 133.8597
TOTAL ANNUALIZED COST |  |  |  | 133.8597
(Total annual O&M cost and annualized capital cost)
TONS OF POLLUTANT REMOVED PER YEAR (baseline * control efficiency) |  |  |  | 1.4448
COST-EFFECTIVENESS
ENVIRONMENTAL BASIS
|  | ($ per ton pollutant removed) |  | 92652
Baseline Emissions =
Heat Input Capacity (46.729 MMBtu/hr) * AP-42 CO Ef. Sm. Boiler (100 lb/106 scf) * (1 MMBtu/ 1,020 scf) * (8760 hrs/1 yr) * (1 ton/2000 lbs)

## Solar Turbine Water Injection
Appendix B
KNO Restart
Water injection for NOx control on Solar Turbines
Source |  | Solar Turbine
Rated Heat Input (MMBtu/hr) |  | 55.443
Baseline Emissions |  | 10.21
Control Efficiency |  | 60%
|  | COST COMPONENT: |  | COST (x $1000)
DIRECT COSTS
Purchased Equipment Costs (Included in TCI)
Initial Equipment Costs
Instrumentation
Freight
Taxes
|  | Subtotal - Purchased Equipment Costs |  | 490.4652 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
Direct Installation Costs(Included in TCI)
|  | Foundations & supports; handling & erection; electrical; piping; etc. (25% of PEC) |  | 122.6163
|  | Site Preparation / Buildings (25% of PEC) |  | 122.6163
|  | Subtotal - Direct Installation Costs |  | 245.2326
TOTAL DIRECT COSTS (TDC)
INDIRECT INSTALLATION COSTS
|  | Engineering Costs (10% of Purchased Equip Costs) |  | 49.0465
|  | Construct. & Field Expenses (5% of Purchased Equip Costs) |  | 24.5233
|  | Contractor Fees (10% Purchased Equip Costs) |  | 49.0465
|  | Start-up and Performance Test (2% of Purchased Equip Costs) |  | 9.8093
|  | Contingency (3% of Purchased Equip Costs) |  | 14.714
TOTAL INDIRECT COSTS |  |  |  | 147.1396
TOTAL CAPITAL INVESTMENT (TCI) |  |  |  | 882.8374
|  | COST COMPONENT: |  | COST (x $1000)
ANNUAL DIRECT COSTS
Operation and Maintenance Labor
|  | Operating Labor |  | 0
|  | O&M Supervision |  | 0
|  | Maintenance Labor and Material |  | 18.2069 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
| Subtotal - Operation and Maintenance Labor |  |  | 18.2069
Utilities
|  | Power |  | 4.9632 | (Vendor provided in 2013 - Adjusted for 8.51% inflation)
| Subtotal - Utilities |  |  | 4.9632
TOTAL ANNUAL DIRECT COSTS |  |  |  | 23.1701
|  | COST COMPONENT: |  | COST (x $1000)
INDIRECT COSTS
|  | Overhead (not applicable) |  | 0
|  | Property Tax (not applicable) |  | 0
|  | Insurance (negligibIe) |  | 0
|  | Administration (not applicable) |  | 0
TOTAL INDIRECT COSTS |  |  |  | 0
TOTAL ANNUAL O&M COSTS |  |  |  | 23.1701
CAPITAL RECOVERY FACTOR
|  | Equipment Life (years) = | 25
|  | Interest Rate (%) = | 3.25
|  | Capital Recovery Factor |  | 0.059039
CAPITAL RECOVERY COSTS
|  | TOTAL CAPITAL REQUIREMENT |  | 882.8374
|  | TOTAL ANNUAL CAPITAL REQUIREMENT |  | 52.1221
TOTAL ANNUALIZED COST |  |  |  | 75.2923
(Total annual O&M cost and annualized capital cost)
TONS OF POLLUTANT REMOVED PER YEAR (baseline * control efficiency) |  |  |  | 6.126
COST-EFFECTIVENESS
ENVIRONMENTAL BASIS
|  | ($ per ton pollutant removed) |  | 12291
Baseline Emissions =
Heat Input Capacity (55.443 MMBtu/hr) * SCR Controlled Emission Rate (0.041 lb/MMBtu) * (8760 hrs/1 yr) * (1 ton/2000 lbs)

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only