## All Pollutants_Small RICE 17.21
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Airstrip Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 490 | hp | One 490 hp Airstrip Generator Engine | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 163 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Agitator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 98 | hp | ULSD-fired 98 hp Agitator Generator Engine | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 356 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Incinerator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 102 | hp | ULSD-fired 102 hp Incinerator Generator Engine | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 516 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Diesel Fired Well Pump | 17.21 | Diesel | 2.7 | MMBTU/H | 2.7 MMBtu/hr Diesel Fired Well Pump. Installed in 1966. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Limited Operation of 168 hr/yr. | 37.2 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*AK-0084 | DONLIN GOLD PROJECT | DONLIN GOLD LLC. | BETHEL CENSUS AREA | AK | 99575 | USA | STAN FOO | 907-273-0200 | SFOO@DONLINGOLD.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | AK DEC DIV. OF AIR QUALITY 410 WILLOUGHBY AVE. SUITE 303 JUNEAU, AK 99801 | AQ0934CPT01 | 1041 | 212221 | Not Entered | 10/15/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2018-06-21 | 2018-06-22 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16763360/d1h2U6BIY-j857LFU-WYmw2 | The Donlin Gold Project is a gold mine located 12 miles north of Crooked Creek, Alaska on the Kuskokwim River, about 280 miles northwest of Anchorage. The deposit has proven and probable reserves estimated at 33.9 million ounces of gold at 2.1 g/t and could produce up to 1.5 million ounces annually. SIC Code 1041; NAICS Code 212221. |  | Fire Pump Diesel Internal Combustion Engines | 17.21 | Diesel | 252 | hp | Three (3) 252 hp fire pump diesel internal combustion engines. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 216 | TPY (COMBINED) | YEARLY | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 216 tpy CO2e for EUs 35 - 37 combined. NSPS Subpart IIII engines
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Wireline Unit Engines - C.R. Luigs | 17.21 | diesel | 300 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 536.6 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Fast Rescue Craft Diesel Engine - Development Driller 1 | 17.21 | Diesel | 142 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, and turbocharger | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Life Boat Diesel Engines - Development Driller 1 | 17.21 | Diesel | 110 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines and use of low sulfur diesel fuel | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Port and Stb Fwd and Aft Crane Diesel Engines - C.R. Luigs | 17.21 | diesel | 305 | HP |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 3083 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Life Boat Diesel Engines - C.R. Luigs | 17.21 | diesel | 39 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - Development Driller 1 | 17.21 | Diesel | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger, and high pressure fuel injection with aftercooler | 715.5 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Wireline Unit Diesel Engines - Development Driller 1 | 17.21 | Diesel | 0 |  | Wireline units including primary, alternative #2, power plant, and hydraulic generator | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 536.6 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Black Start Air Compressor - C.R. Luigs | 17.21 | diesel | 6 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for the engine and the use of low sulfur diesel fuel | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - C.R. Luigs | 17.21 | diesel | 0 |  | Cementing Units: Caterpillar 3412 CDITA 860 hp 2001 Nitrogen Pump: Caterpillar 3406 CDITA 490 hp 2000 | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger, and high pressure fuel injection with aftercooler | 628.9 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Carbon Dioxide Equivalent (CO2e) | Other - recordkeeping | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 91 | TONS/YR | ROLLING 12 MONTH TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0021 | MAGNIDA | MAGNOLIA NITROGEN IDAHO LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 303-905-2675 | THORNYAK@MAGNIDA.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV | DAN PITMAN, P.E., PERMIT WRITER | P-2013.0030 | 2873 | 325311 | Not Found | 12/02/2013 &nbsp;ACT | 04/21/2014 &nbsp;ACT | 2017-05-19 | 2017-09-11 | A | NO LONGER AVAILABLE ON-LINE AS THE PERMIT IS EXPIRED | MAGNOLIA NITROGEN IDAHO LLC (MAGNIDA) IS PROPOSING TO CONSTRUCT A NEW COMPLEX FOR MANUFACTURING NITROGEN-BASED FERTILIZERS FROM NATURAL GAS. THE FACILITY WILL PRODUCE AMMONIA, GRANULATED UREA, UREA AMMONIUM NITRATE (UAN), AND DEISEL EXHAUST FLUID (DEF) FOR COMMERCIAL USE. | THIS PERMIT EXPIRED IN NOV. 2016; THE PROJECT WILL NOT BE PURSUED BY MAGNOLIA/MAGNIDA. There is one non-emissions BACT limit: Startup Heater Code 19.6 - has only a gas usage limit of 2.7 MMSCF per rolling 12-month period. | EMERGENCY GENERATOR ENGINE | 17.21 | #2 Distillate w/sulfur content <= 15ppmw | 2000 | kW | This emergency generator will operate infrequently, primarily for routine testing and as needed during emergencies. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 22.6 | LBS | PER GAL. FUEL BURNED, ON A CO2E BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0021 | MAGNIDA | MAGNOLIA NITROGEN IDAHO LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 303-905-2675 | THORNYAK@MAGNIDA.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV | DAN PITMAN, P.E., PERMIT WRITER | P-2013.0030 | 2873 | 325311 | Not Found | 12/02/2013 &nbsp;ACT | 04/21/2014 &nbsp;ACT | 2017-05-19 | 2017-09-11 | A | NO LONGER AVAILABLE ON-LINE AS THE PERMIT IS EXPIRED | MAGNOLIA NITROGEN IDAHO LLC (MAGNIDA) IS PROPOSING TO CONSTRUCT A NEW COMPLEX FOR MANUFACTURING NITROGEN-BASED FERTILIZERS FROM NATURAL GAS. THE FACILITY WILL PRODUCE AMMONIA, GRANULATED UREA, UREA AMMONIUM NITRATE (UAN), AND DEISEL EXHAUST FLUID (DEF) FOR COMMERCIAL USE. | THIS PERMIT EXPIRED IN NOV. 2016; THE PROJECT WILL NOT BE PURSUED BY MAGNOLIA/MAGNIDA. There is one non-emissions BACT limit: Startup Heater Code 19.6 - has only a gas usage limit of 2.7 MMSCF per rolling 12-month period. | FIRE WATER PUMP ENGINE | 17.21 | #2 Distillate w/sulfur content <= 15ppmw | 500 | brake horsepower | This engine will operate infrequently, primarily for routine testing and as needed during emergencies. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 22.6 | LBS. | PER GAL. OF FUEL BURNED, ON A CO2E BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 72 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) FIREWATER PUMP DIESEL ENGINES | 17.21 | DIESEL | 371 | BHP, EACH | THE TWO FIREWATER PUMP ENGINES, IDENTIFIED AS FP01 AND FP02, EXHAUSTING THROUGH TWO (2) VENTS. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD ENGINEERING DESIGN AND FUEL EFFICIENT DESIGN | 172 | TONS | 12 CONSECUTIVE MONTH PERIOD | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LIMIT ONE: COMBINED EMISSION LIMIT: COMPLAINCE DETERMINED AT THE END OF THE MONTH
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Emergency diesel engine | 17.21 | diesel | 750 | KW | One (1) 1102 HP (750 KW) emergency diesel engine | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 59.5 | TONS PER YEAR | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Compliance with the CO2e BACT limit shall be demonstrated with an oxygen (O2) concentration monitor in accordance with CO2 calculations provided in 40 CFR Part 75. Calculations shall consist of CO2 emissions only, which account for 99.9% of total CO2e emissions.
LA-0301 | LAKE CHARLES CHEMICAL COMPLEX ETHYLENE 2 UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | (281) 588-3761 | ERIC.RODRIGUEZ@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-779 | 2869 | 325110 | 110017418061 | 05/02/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2016-09-27 | 2017-04-28 | B |  |  | Complete application date = date of administrative completeness This RBLC entry addresses Ethylene Unit 2 of the Lake Charles Cracker Project. This unit will produce ethylene by thermally cracking ethane in cracking furnaces. | Firewater Pump Nos. 1-3 (EQTs 997, 998, &amp; 999) | 17.21 | Diesel | 500 | HP | Non-emergency use operating time is limited to 100 hr/yr (per engine). | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Compliance with 40 CFR 60 Subpart IIII and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage | 10 | TPY | ANNUAL MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT is determined to be compliance with the limitations imposed by 40 CFR 60 Subpart IIII and its associated monitoring, recordkeeping, and reporting requirements; and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage. The CO2e limits are based on a CH4 global warming potential (GWP) of 21 and a N2O GWP of 310. In the event any GWP is revised, the CO2e limits shall be revised accordingly without the need to modify the permit.
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Genenerator Engine DEG-16-1 (EQT035) | 17.21 | Diesel | 460 | horsepower | Limit operations to 100 hrs/yr | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Meet NSPS Subpart IIII Limitations and Good Combustion Practices | 26 | Y/YR | ANNUAL MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 73.96 kg/MM BTU of CO2, 0.003 kg/MM BTU of CH4, and 0.0006 kg/MM BTU of N2O
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Pump Engines DFP-16-1 (EQT036) | 17.21 | Diesel | 225 | horsepower | Limit operations to 100 hour/year | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 13 | T/YR | ANNUAL MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 73.96 kg/MM BTU of CO2, 0.003 kg/MM BTU of CH4, and 0.0006 kg/MM BTU of N2O
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Pump Engine DFP-16-2 (EQT037) | 17.21 | Diesel | 225 | horsepower | Limit operations to 100 hr/yr | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 13 | T/YR | ANNUAL MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 73.96 kg/MM BTU of CO2, 0.003 kg/MM BTU of CH4, and 0.0006 kg/MM BTU of N2O
LA-0309 | BENTELER STEEL TUBE FACILITY | BENTELER STEEL / TUBE MANUFACTURING CORPORATION | CADDO | LA | 71115 | USA | MYRNA PACHECO PONCE DE LEON | 318-216-4206 | MYRNA.PACHECO@BENTELER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen - 225-219-3395 | PSD-LA-774(M1) | 3312 | 331111 | 110055592318 | 02/09/2015 &nbsp;ACT | 06/04/2015 &nbsp;ACT | 2017-03-09 | 2017-04-28 | A |  | A facility to produce 600,000 metric tons per year of seamless steel pipe from purchased billets. A steel production facility (including an electric arc furnace (EAF)) was added. | Permit PSD-LA-774 was issued on May 17, 2013 for the construction of the hot rolling mill. An EAF was authorized this time. | Firewater Pump Engines | 17.21 | Diesel | 288 | hp (each) |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Emergency Diesel Firewater Pump 1 | 17.21 | Diesel | 282 | HP |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT Limit = 527.40G/BHP-HR
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel Firewater pump engines (6 units) | 17.21 | diesel | 425 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel emergency generator engine - EGEN | 17.21 | diesel | 350 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110029511883 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | firewater pump engines (8 units) | 17.21 | diesel | 460 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0323 | MONSANTO LULING PLANT | MONSANTO COMPANY | ST. CHARLES PARISH | LA | 70070 | USA | ENRIQUE WEHLEN | 9857858211 | ENRIGUE.WEHLEN@MONSANTO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-890 | 2879 | 325320 | 110067118274 | 09/21/2015 &nbsp;ACT | 01/09/2017 &nbsp;ACT | 2017-09-26 | 2018-05-11 | D | http://edms.deq.louisiana.gov/app/doc/view.aspx?doc=10460194&ob=yes | Chemical Manufacture | Dicamba Manufacturing Facility expansion project. | Standby Generator No. 9 Engine | 17.21 | Diesel Fuel | 400 | hp | Operating hours limited to 100 hours/yr for ready testing. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Proper operation and limits on hours of operation for emergency engines and compliance with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000310459 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Fire Pump Engine | 17.21 | ULSD | 2.7 | MMBTU/H | â‰¤ 300 hours of operation per 12-month rolling period S in ULSD: â‰¤0.0015% by weight | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 162.85 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | EU-FPENGINE: Diesel fuel fired emergency backup fire pump | 17.21 | diesel fuel | 315 | hp nameplate | This is a diesel fuel fired emergency backup fire mump. It has a capacity of 315 hp, nameplate, and uses diesel fuel ASTM D975 Grade 2-D S15. Ultra low sulfur diesel fuel (15ppmw); 100 hours per year operation for maintenance and readiness testing. NSPS IIII and NESHAP ZZZZ. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Proper combustion design and ultra low sulfur diesel fuel. | 15.6 | T/YR | 12-MO. ROLL TIME PERIOD | BACT-PSD | N/A | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Ultra low sulfur diesel fuel (15 ppmw); 100 hour per year operation for maintenance and readiness testing.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Emergency Engine --Diesel Fire Pump (EUFPENGINE) | 17.21 | Diesel | 165 | HP | A 165 hoursepower (hp) diesel-fueled emergency engine manufactured in 2013, iwth a heat input of 1.35 MMBTU/hr. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 0.29 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 13.58 | T/YR | 12 MO. ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | diesel | 500 | H/YR | A 165 horsepower (hp) diesel-fueled emergency engine manufactured in 2016 with a heat input of 1.35 MMBTU/H. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices. | 55.6 | T/YR | 12-MONTH ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (South Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices. | 85.6 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (North Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices. | 85.6 | T/YR | 12-MONTH ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUFPENGINE: Fire pump engine | 17.21 | Diesel | 399 | BHP | A 399 brake HP diesel-fueled emergency fire pump engine with a model year of 2011 or later, and a displacement of <10 liters/cylinder. The engine is an EPA Tier 3 certified engine subject to NSPS IIII. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficient design | 86 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0103 | CRICKET VALLEY ENERGY CENTER | CRICKET VALLEY ENERGY CENTER LLC | USA | NY | 12522-0407 | USA |  | 845-877-0596 | INFO@CRICKETVALLEY.COM | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-1326-00275/00009 | 4911 | 221112 | 110043340364 | 02/03/2016 &nbsp;ACT | 02/03/2016 &nbsp;ACT | 2017-08-24 | 2017-09-28 | A | http://www.dec.ny.gov/chemical/32249.html | Cricket Valley Energy Center LLC (CVEC) constructed the Cricket Valley Energy Center (the Facility), a nominal net 1,000-megawatt (MW) combined-cycle gas turbine electric generating facility, on a site located in Dover, Dutchess County, New York. The Facility consists of three General Electric (GE) Model 7FA.05 combustion turbine generators (CTGs) operating in combined-cycle mode with supplemental firing of the heat recovery steam generators (HRSGs); natural gas will be the sole fuel fired in the CTGs and duct burners. The Facility will include a natural gas-fired auxiliary boiler, four ultra-low sulfur distillate (ULSD) fired black-start generator engines and a ULSD-fired emergency fire pump engine. In addition to the air emitting equipment, the Facility will include three steam turbine generators (STGs), an air cooled condenser (ACC) and associated auxiliary equipment and systems. Each combined cycle generating unit consisting of the CTG, HRSG and STG will be exhausted through its own stack. Air emissions from the proposed Facility primarily consist of products of combustion from the CTGs, HRSG duct burners, and ancillary combustion sources. Dutchess County is designated as in attainment with respect to the National Ambient Air Quality Standards (NAAQS) for all criteria pollutants with the exception of ozone. Based upon the potential to emit (PTE) estimates, the Facility is subject to Prevention of Significant Deterioration (PSD) requirements for emissions of carbon monoxide (CO); nitrogen oxides (NOx); particulate matter (PM) with a diameter equal to or less than 10 microns (PM10), PM with a diameter equal to or less than 2.5 microns (PM2.5); greenhouse gases (GHG); sulfuric acid mist (H2SO4); and volatile organic compounds (VOC). In accordance with the NYSDECâ€™s Nonattainment New Source Review (NNSR) permitting program, the Facility is also subject to NNSR for emissions of NOx and VOC. |  | Emergency fire pump | 17.21 | ultra low sulfur diesel | 460 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practice and efficient engine design. | 115 | TPY | MO | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | Emergency fire pump engine | 17.21 | diesel | 300 | HP | 223.8 kW. Emergency fire pump engine restricted to 500 hours of operation per rolling 12 months. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 87 | T/YR | PER ROLLING 12-MONTHS | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0164 | MIDWEST CITY AIR DEPOT | TINKER AIR FORCE BASE LOGISTICS CENTER | OKLAHOMA | OK | 73145 | USA | COL. CHRISTOPHER AZZANO | 405-734-2102 | 72ABW.WORKFLOW@TINKER.AF.MIL | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2009-394-C(M-2)PSD | 9711 | 928110 | 109-00090 | 04/09/2014 &nbsp;ACT | 01/08/2015 &nbsp;ACT | 2015-08-07 | 2016-07-06 | B |  | In February 2011, the U.S. Air Force (USAF) selected the Boeing KC-767 to replace its aging KC-135 tankers and assigned the new aircraft the designation KC-46A. Tinker AFB was selected to perform the programmed depot-level maintenance of the KC-46A aircraft. | Applicant requests authorization to construct facilities to accommodate new workload associated with the KC-46 aircraft. | Diesel-Fueled Fire Pump Engines | 17.21 | Ultra-Low Sulfur Distillate Fuel | 300 | HP | Operate for 100 hours maximum annually | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | 1. Good Combustion Practices. 2. Efficient Design. | 44 | TONS PER YEAR | TOTAL FOR 3 ENGINES. | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Fire pump engine | 17.21 | Ultra-low sulfur diesel | 15 | gal/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 9 | TON | 12-MONTH ROLLING BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
PR-0009 | ENERGY ANSWERS ARECIBO PUERTO RICO RENEWABLE ENERGY PROJECT | ENERGY ANSWERS ARECIBO, LLC | ARECIBO | PR |  | USA | MARK GREEN | (347)-351-5248 |  | 2 | OT003 | EPA REGION II | MR. FRANK JON | (212)637-4085 | jon.frank@epa.gov | Ms. Viorica Petriman petriman.viorica@epa.gov | R2-PSD 1 | 4953 | 221119 | FRL-9911-10-Region 2 | 11/11/2012 &nbsp;ACT | 04/10/2014 &nbsp;ACT | 2014-10-14 | 2016-05-05 | A |  | Energy Answers Arecibo is a new resource recovery facility capable of producing up to 77 megawatts (MW) of electrical power while combusting municipal solid waste, as the primary fuel. | This is a PSD permit for a new/greenfield facility. | Emergency Diesel Fire Pump | 17.21 | ULSD Fuel Oil #2 | 0 |  | The Emergency Fire Pump is rated at 335 BHP and limited to 500 hr/yr (emergency operations and testing and maintenance, combined). | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 91.3 | T/YR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0612 | THOMAS C. FERGUSON POWER PLANT | LOWER COLORADO RIVER AUTHORITY | LLANO | TX | 78767-7041 | USA | KENNETH TAYLOR | 979-249-8377 | KEN.TAYLOR@LCRA.ORG | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | Melanie Magee, 6PD-R Air Permit Section EPA Region VI (214)665-7161 | PSD-TX-1244-GHG | 4911 | 221122 | 110000456620 | 04/14/2011 &nbsp;ACT | 11/10/2011 &nbsp;ACT | 2012-02-08 | 2013-09-25 | D |  | Install 2 new natural gas-fired combined-cycle combustion turbine units (U1-STKand U2-STK) with a generating capacity of approximately 590 MW. The steam produced from the two new combustion turbines will exhaust to two dedicated Heat Recovery Steam Generators (HRSG) to produce steam. The steam produced from the two HRSGs is routed to the new shared steam turbine unit to produce electricity for sale to the Electric Reliability Council of Texas (ERCOT) power grid. |  | FWP1-STK DIESEL FIRED FIRE WATER PUMP | 17.21 | DIESEL | 617 | HP | 617 HP diesel fired Fire Water Pump. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3a or 3b for CO2 | (Greenhouse Gasses (GHG)) | CO2e | P | Best Work practice | 7027.8 | LB/H | 30-DAY ROLLING AVERAGE | BACT-PSD | NSPS | U | 0 | U | 351.4 | T/YR | 30-DAY ROLLING AVERAGE | 0 |  |  | 0 | 0 | N |  | 617 -horsepower(HP) Diesel Fire Water Pump rated at 43.2 MMBtu/hr and limited to 100 hours of operation per year for non-emergency activities.
TX-0753 | GUADALUPE GENERATING STATION | GUADALUPE POWER PARTNERS, L.P. | GUADALUPE | TX | 78124 | USA | BILL SKINNER | 281-252-5221 | BSKINNER@NAVASOTAENERGY.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Melanie Magee, EPA Region 6, Air Permits Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | PSD-TX-1310-GHG | 4911 | 221112 | 110021360329 | 10/24/2014 &nbsp;ACT | 12/02/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | B | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | GPP proposes to add two (2) new gas-fired simple-cycle combustion turbines of 227 MW (nominal) electric generating capacity each to the 1,000 MW (nominal) existing major stationary source, Guadalupe Generating Station (GGS), located in Marion, Texas. The proposed project will provide peaking capacity at an existing natural gas fired combined cycle electric generating station. The two new natural gas-fired simple-cycle turbines are proposed to provide a fast ramp up for additional peaking capacity during peak electricity demand periods. In addition, the project also includes the installation of a firewater pump engine, circuit breakers and associated fugitive emissions. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. See CN600132120 and RN100225820 | Fire Water Pump Engine | 17.21 | ULSD | 1.92 | MMBtu/hr (HHV) | Shall not exceed 100 hours of non-emergency operation on a 12-month rolling basis and shall be operated and maintained in accordance with the manufacturer's recommendations. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 15.71 | TPY CO2E |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Not to exceed 100 hours of non-emergency operation on a 12-month rolling basis. Use of good combustion practices.
TX-0757 | INDECK WHARTON ENERGY CENTER | INDECK WHARTON, LLC | WHARTON | TX | 77432 | USA | JAMES SCHNEIDER | 847-520-3212 | JSCHNEIDER@INDECKENERGY.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Jennifer Huser, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | PSD-TX-1374-GHG | 4911 | 221112 | Not Assigned | 04/05/2014 &nbsp;ACT | 05/12/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | A | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | Indeck proposes to construct a peaking power plant, the Indeck Wharton Energy Center, generally located south of Danevang, Texas. To meet the anticipated demand for peak power, Indeck proposes to construct three identical natural gas-fired F-class simple cycle combustion turbines with associated support equipment. Indeck proposes that the three new combustion turbine generators (CTGs) will be either General Electric (GE) 7FA.05 or Siemens SGT6-5000F(5). The GE 7FA.05 has a base-load electric power output of approximately 213 megawatts (MW, net nominal), and the Siemens SGT6-5000F(5) has a base-load electric power output of approximately 225 MW (net nominal). This project also proposes to install one emergency diesel generator, one diesel fire water pump, one natural gas pipeline heater, and other auxiliary equipment. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. | Firewater Pump Engine | 17.21 | ULSD | 175 | hp | Indeck will be equipped with one nominally rated 175-hp diesel-fired pump engine to provide water in the event of a fire. The fire water pump will operate a maximum of 52 hours of non-emergency operation on a 12-month rolling basis for testing and maintenance. The fire water pump engine emissions represent 0.003% of the total facility-wide GHG emissions. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 5.34 | TPY CO2E | 12-MONTH ROLLING TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT for the fire water pump engine will be to limit operation to no more than 52 hours of non-emergency operation per year for the purpose of maintenance, testing, and inspection. Indeck will also monitor hours of operation for the purpose of maintenance, testing, and inspection for each engine on a monthly basis. Compliance will be based on runtime hour meter readings on a 12-month rolling basis.
TX-0758 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX | 79741 | USA | MATTHEW THORNTON | 312-582-1527 | MTHORNTON@INVENERGYLLC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | EPA Region 6 Permit Writer: Anna Milburn, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | GHGPSDTX1366 | 4911 | 221112 | Not Assigned | 04/18/2014 &nbsp;ACT | 08/01/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | A | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | Invenergy proposes to construct a 330 MW peak power plant (known as the Ector County Energy Center Plant (ECEC)), located in Goldsmith, Ector County, Texas. With this proposed project, Invenergy plans to construct two natural gas-fired simple-cycle turbines, General Electric (GE) Model 7FA.03, and associated equipment, a fire water pump engine, a natural gas-fired dew-point heater, and two circuit breakers. For the purposes of this proposed permitting action, GHG emissions are permitted for the two turbines, the fire water pump engine, the natural gas-fired dew-point heater, and the circuit breakers, as well as for fugitive emissions, and maintenance, startup and shutdown emissions. | Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. | Firewater Pump Engine | 17.21 | Diesel | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 5 | TPY CO2E | 12-MONTH ROLLING TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Not to exceed 100 hours of non-emergency operation on a 12-month rolling basis. Use of good combustion practices
TX-0799 | BEAUMONT TERMINAL | PHILLIPS 66 PIPELINE LLC | JEFFERSON | TX |  | USA | CHINTAN MEHTA | 832-765-1677 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Beth Akers, 512-239-4620 beth.akers@tceq.texas.gov | 18295, PSDTX1466, GHGPSDTX139 | 5171 | 424710 | 110033444850 | 04/19/2016 &nbsp;ACT | 06/08/2016 &nbsp;ACT | 2016-06-17 | 2016-07-07 | C |  | This marine terminal receives, stores, and distributes various volatile organic liquids (VOLs) and refined petroleum products. | (consolidate and/or void: 1973, 8113, 481, 2365, 56419, 6312, and 6559) | EMERGENCY ENGINES | 17.21 | diesel | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Equipment specifications and good combustion practices. Operation limited to 100 hours per year. | 6.79 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0824 | JACKSON COUNTY GENERATING FACILITY | SOUTHERN POWER | JACKSON | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Marc Sturdivant, (512)239-1313, marc.sturdivant@tceq.texas.gov | GHGPSDTX118 | 4911 | 221112 | Not Found | 08/15/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-07-20 | 2017-11-16 | A |  | simple cycle electric generation |  | Emergency Diesel-Fired Equipment | 17.21 | DIESEL | 160 | HP |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good operating and maintenance practices, efficient design, and low annual capacity | 13 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0319 | GATEWAY COGENERATION 1, LLC - SMART WATER PROJECT | GATEWAY GREEN ENERGY | PRINCE GEORGE | VA | 23875-3000 | USA | T. EDWARD MCDANIEL | 972-638-8798 | EMCDANIEL@GGEHLLC.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52375-002 | 4911 | 221112 | 110045446718 | 01/11/2012 &nbsp;ACT | 08/27/2012 &nbsp;ACT | 2013-01-16 | 2015-05-29 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Combined cycle electrical power generating facility (160 MW), consisting of two combusion turbines (Rolls Royce Trent 60 WLE) with associated HRSG and no duct burning. |  | FIRE WATER PUMP | 17.21 | diesel (ultra low sulfur) | 1.86 | MMBTU/H | 500 H/Yr operation | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Fuel-efficient design | 30.5 | T/YR | 12 MO ROLLING AVG | BACT-PSD | NSPS , MACT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Fire Pump Engine | 17.21 | Diesel | 251 | HP | Limited to 100 Hours/year. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 309 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WY-0076 | ROCK SPRINGS FERTILIZER COMPLEX | SIMPLOT PHOSPHATES, LLC | SWEETWATER | WY | 82901 | USA | DARIN HOWE | 3073821519 | DARIN.HOWE@SIMPLOT.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | MD-14824 | 2874 | 325312 | 110040924033 | 11/13/2013 &nbsp;ACT | 07/01/2014 &nbsp;ACT | 2014-07-01 | 2016-01-08 | B |  | Phosphate fertilizer Plant | Installation of an anhydrous ammonia plant with a nominal production capacity of 600 short tons per day (t/day) | Fire Water Pump Engine | 17.21 | Diesel | 200 | HP | limited to 500 hours of operation | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | limited to 500 hours of operation per year | 58 | T/YR | ANNUAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Airstrip Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 490 | hp | One 490 hp Airstrip Generator Engine | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 2.6 | GRAMS/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Agitator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 98 | hp | ULSD-fired 98 hp Agitator Generator Engine | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 3.7 | GRAMS/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Incinerator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 102 | hp | ULSD-fired 102 hp Incinerator Generator Engine | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 3.7 | GRAMS/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Diesel Fired Well Pump | 17.21 | Diesel | 2.7 | MMBTU/H | 2.7 MMBtu/hr Diesel Fired Well Pump. Installed in 1966. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Limited Operation of 168 hr/yr. | 0.95 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*AK-0084 | DONLIN GOLD PROJECT | DONLIN GOLD LLC. | BETHEL CENSUS AREA | AK | 99575 | USA | STAN FOO | 907-273-0200 | SFOO@DONLINGOLD.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | AK DEC DIV. OF AIR QUALITY 410 WILLOUGHBY AVE. SUITE 303 JUNEAU, AK 99801 | AQ0934CPT01 | 1041 | 212221 | Not Entered | 10/15/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2018-06-21 | 2018-06-22 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16763360/d1h2U6BIY-j857LFU-WYmw2 | The Donlin Gold Project is a gold mine located 12 miles north of Crooked Creek, Alaska on the Kuskokwim River, about 280 miles northwest of Anchorage. The deposit has proven and probable reserves estimated at 33.9 million ounces of gold at 2.1 g/t and could produce up to 1.5 million ounces annually. SIC Code 1041; NAICS Code 212221. |  | Fire Pump Diesel Internal Combustion Engines | 17.21 | Diesel | 252 | hp | Three (3) 252 hp fire pump diesel internal combustion engines. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good Combustion Practices | 3.3 | G/KW-HR | 3-HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Subpart IIII engines
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | EMERGENCY FIREWATER PUMP ENGINE | 17.21 | DIESEL | 135 | KW | 135 KW (182 hp) IC Diesel-fired Emergency Firewater Pump Engine | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | N | OPERATIONAL RESTRICTION OF 50 HR/YR, OPERATE AS REQUIRED FOR FIRE SAFETY TESTING | 3.5 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 2.6 | G/HP-H |  | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | EMERGENCY FIREWATER PUMP ENGINE | 17.21 | DIESEL | 288 | HP |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | EQUIPPED W/ A TURBOCHARGER AND AN INTERCOOLER/AFTERCOOLER | 0.447 | G/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.21 | DIESEL | 182 | HP | UNIT IS 135 KW. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | N |  | 3.5 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 2.6 | G/HP-H |  | 0 |  |  | 0 | 0 | N
FL-0322 | SWEET SORGHUM-TO-ETHANOL ADVANCED BIOREFINERY | SOUTHEAST RENEWABLE FUELS (SRF), LLC | HENDRY COUNTY | FL | 33440 | USA | DON MARKLEY | 954-492-1588 | DMARKLEY@SERENEWABLE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Alvaro Linero, P.E. Administrator alvaro.linero@dep.state.fl.us Phone: 850-717-9076 David Read, Engineer david.read@dep.state.fl.us Phone: 850-717-9075 Teresa Heron, Engineer teresa.heron@dep.state.fl.us phone: 850-717-9082 | PSD-FL-412 (0510032-001-AC) | 2869 | 325193 | Not Applicable | 03/19/2010 &nbsp;ACT | 12/23/2010 &nbsp;ACT | 2011-01-31 | 2011-07-06 | A | http://www.dep.state.fl.us/Air/emission/bioenergy/southern_renewables.htm | The SRF facility will be located just East of County Road (CR) 835 at the intersection with Hill Grade Road and approximately 13 miles south southwest of Clewiston/Lake Okeechobee in Hendry County. Hendry County is bounded by Lee County to the west, Glades County to the north, Collier County to the south, Palm Beach County to the east and Broward County to the southeast. Lake Okeechobee is located immediately northeast of Hendry County. The Big Cypress Seminole Indian Reservation is located approximately 18 miles south southeast of the site entrance. Most of Hendry County is agricultural. | The applicant proposes to construct a sweet sorghum-to-ethanol advanced biorefinery with a capacity of 22.11 million gallons per year (MGPY). The sweet sorghum will be grown on adjacent farmland. The sweet sorghum juice will be squeezed from the sorghum stalks, fermented, distilled and blended to make a range of ethanol/gasoline products. The leftover stalk fiber (bagasse) and other parts of the plant (harvest field residue) will be combusted in a cogeneration biomass boiler to make process steam and up to 30 megawatts (MW, gross) of electricity. The applicant also plans to use sweet sorghum molasses in the ethanol process when sweet sorghum is not available. Wood and yard waste will be used as a backup and supplemental fuel for the biomass boiler. | Emergency Diesel Fire Pump, One 600 HP | 17.21 | ULSD | 0 |  |  | Carbon Monoxide | Other - Manufacturer Certification | (InOrganic Compounds) | 630-08-0 | N |  | 2.6 | G/HP-H |  | BACT-PSD |  | U | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The fire pumps shall comply with the emission limit and demonstrate compliance in accordance with the procedures given in NSPS 40 CFR 60, Subpart IIII. Manufacturer certification may be provided to the Department in lieu of actual testing. The fire pumps are Stationary Compression Ignition Internal Combustion Engines (Stationary ICE) and shall comply with applicable provisions of 40 CFR 60, Subpart IIII, including emission testing or certification.
FL-0324 | PALM BEACH RENEWABLE ENERGY PARK | SOLID WASTE AUTHORITY OF PALM BEACH COUNTY | PALM BEACH | FL | 33412 | USA | MARK HAMMOND | 561-640-4000 | MHAMMOND@SWA.ORG | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Alvaro Linero, P.E. Administrator alvaro.linero@dep.state.fl.us Phone: 850-717-9076 Robert Bull, Engineer robert.bull@dep.state.fl.us Phone: 850-717-9111 Teresa Heron, Engineer teresa.heron@dep.state.fl.us phone: 850-717-9082 | PSD-FL-413 | 4953 | 221119 | 110043792358 | 11/12/2010 &nbsp;ACT | 12/23/2010 &nbsp;ACT | 2011-04-07 | 2011-12-08 | B |  | The existing Palm Beach Renewable Energy Facility (PBREP-1) consists of Class I and Class III landfills, a biosolids pelletizer facility, a compost facility and a waste-to-energy (WTE) plant known as the North County Resource Recovery Facility (NCRRF). The new facility, PBREP-2, will consist of: â€¢Three nominal 1,000 TPD mass burn MWC, each with an estimated maximum continuous rating (MCR) of 416.7 million Btu per hour heat input (mmBtu/hr) and a peak rating of 458.3 mmBtu/hr; â€¢A 100 megawatt (MW) STG with an air cooled condenser; â€¢One ash building and handling system; â€¢Three lime storage silos and one carbon storage silo; and â€¢Two 250 horsepower (hp) diesel fire pumps and one 250 kilowatt (kW) emergency generator. This facility, is located at 7501 North Jog Road (immediately west of the Turnpike) in West Palm Beach. | This project will consist of three 1,000 TPD mass-burn MWC units each with a maximum steam production rate of 320,100 pounds per hour (lb/hr) on a 4-hour average block basis. The project also includes a 90 to100 MW STG; three lime storage silos; one carbon storage silo; two diesel fire pump engines; one emergency generator; and one ash handling system and building. The proposed work will be conducted at the existing PBREP. The project will incorporate the following pollution control equipment and measures: â€¢For each MWC unit, good combustion practices (GCP), spray dryers (SD), fabric filter (FF) baghouses, activated carbon injection (CI), selective catalytic reduction (SCR), as an option selective non-catalytic reduction (SNCR) and use of inherently clean natural gas as a startup, shutdown and flame stabilization fuel. â€¢Use of inherently clean ultra low sulfur distillate (ULSD) fuel oil and GCP in the emergency generator and emergency fire pump engines; and â€¢Reasonable precautions and best management practices (BMP) to minimize fugitive particulate matter (PM)/(PM10)/(PM2.5) emissions from MSW handling and processing; ash (bottom and fly) handling, storage and shipment; lime handling, storage and processing; and activated carbon handling, storage and processing. The project will incorporate continuous emission monitoring systems (CEMS) for CO, SO2, NOX and Hg and continuous opacity monitoring systems (COMS) for visible emissions (VE). | 250 Kw Emergency Generator | 17.21 | ULSD | 0 |  |  | Carbon Monoxide | Other - Manufacturer Certification | (InOrganic Compounds) | 630-08-0 | P | Use of inherently clean ultra low sulfur distillate (ULSD) fuel oil and GCP | 3.5 | G/KW-H |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Wireline Unit Engines - C.R. Luigs | 17.21 | diesel | 300 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 2.9 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Fast Rescue Craft Diesel Engine - Development Driller 1 | 17.21 | Diesel | 142 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, and turbocharger | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Life Boat Diesel Engines - Development Driller 1 | 17.21 | Diesel | 110 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines and use of low sulfur diesel fuel | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Port and Stb Fwd and Aft Crane Diesel Engines - C.R. Luigs | 17.21 | diesel | 305 | HP |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 17.85 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Seismic Operations Diesel Engines - Development Driller 1 | 17.21 | Diesel | 415 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, and turbocharger | 1.94 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Life Boat Diesel Engines - C.R. Luigs | 17.21 | diesel | 39 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - Development Driller 1 | 17.21 | Diesel | 0 |  |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger, and high pressure fuel injection with aftercooler | 3.73 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Wireline Unit Diesel Engines - Development Driller 1 | 17.21 | Diesel | 0 |  | Wireline units including primary, alternative #2, power plant, and hydraulic generator | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 2.9 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Black Start Air Compressor - C.R. Luigs | 17.21 | diesel | 6 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for the engine and the use of low sulfur diesel fuel | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - C.R. Luigs | 17.21 | diesel | 0 |  | Cementing Units: Caterpillar 3412 CDITA 860 hp 2001 Nitrogen Pump: Caterpillar 3406 CDITA 490 hp 2000 | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger, and high pressure fuel injection with aftercooler | 3.3 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0346 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-011-AC | 4911 | 221112 | 110002044065 | 11/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-01-08 | 2016-05-05 | D | http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | In this project, 24 peaking turbines from the Lauderdale facility are being replaced with five 200 MW combustion turbines at Lauderdale. The turbines will fire primarily natural gas, but may also fire ULSD fuel oil. Triggers PSD for NOx, PM, CO, VOC, and GHG. GHG permit issued by US EPA Region 4. Technical evaluation available at http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.D.ZIP | Emergency fire pump engine (300 HP) | 17.21 | USLD | 29 | MMBTU/H | Emergency engine. BACT = NSPS IIII. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practice. | 3.5 | GRAM PER KW-HR |  | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT = NSPS IIII; Certified IIII engine meets BACT.
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Diesel Powered Forklift Engine | 17.21 | Diesel | 30 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Wireline Diesel Engines | 17.21 | Diesel | 0 |  | Wireline engines, electric line engines, casing unit engines, tubing running engine, fluid filtration pump engine, powerpack engine, slickline powerpack engine, and CT pump engine | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Water Blasting Diesel Engine | 17.21 | Diesel | 208 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Well Evaluation Diesel Engine | 17.21 | Diesel | 140 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Fast Rescue Craft Diesel Engine | 17.21 | Diesel | 230 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Escape Capsule Diesel Engine | 17.21 | Diesel | 39 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Remotely Operated Vehicle Emergency Generator | 17.21 | Diesel | 427 | hp | 2004 Cummins QSM11-G2NR3 | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Use of good combustion practices based on the most recent manufacturer's specifications issued for engines and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0354 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-013-AC | 4911 | 221112 | 110002044065 | 04/20/2015 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2016-02-17 | 2016-07-06 | D | https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | Re-affirmed BACT determinations in Permit No. 0110037-011-AC. Also, new GHG BACT determination. Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.D.ZIP | Emergency fire pump engine, 300 HP | 17.21 | Diesel | 29 | MMBTU/H | Emergency engine. ULSD only. BACT limits equal NSPS IIII limits. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Low-emitting fuel and certified engine | 3.5 | G / KWH |  | BACT-PSD | NSPS , SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Must use certified engine, or perform stack tests.
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | One 422-hp emergency fire pump engine | 17.21 | ULSD | 0 |  | BACT limits equal to NSPS Subpart IIII limits. Will use IIII certified engine. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Use of clean engine technology | 3.5 | G / KW-HR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*FL-0363 | DANIA BEACH ENERGY CENTER | FLORIDA POWER AND LIGHT COMPANY | BROWARD | FL | 33314 | USA | JOHN HAMPP | 561-691-2894 | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-017-AC | 4911 | 221112 | 110002044065 | 07/27/2017 &nbsp;ACT | 12/04/2017 &nbsp;ACT | 2018-04-03 | 2018-04-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.F.ZIP | 1200 megawatt 2-on-1 combined cycle facility, natural gas-fired, with limited ULSD use. GE 7HA turbines | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.D.ZIP | Emergency Fire Pump Engine (422 hp) | 17.21 | ULSD | 0 |  | Limits equal Subpart IIII limits | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Certified engine | 3.5 | G / KWH |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Certified engine, no testing required
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | good combustion practices | 3.5 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.45 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
ID-0018 | LANGLEY GULCH POWER PLANT | IDAHO POWER COMPANY | PAYETTE | ID |  | USA |  | 2083885820 | TMAHLUM@IDAHOPOWER.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2009.0092 | 4911 | 221112 | UNKNOWN | 06/07/2009 &nbsp;ACT | 06/25/2010 &nbsp;ACT | 2010-08-09 | 2010-10-05 | A |  | ONE-ON-ONE COMBINED CYCLE PLANT CONSISTING OF (1) NATURAL GAS-FIRED COMBUSTION TURBINE (CT) AND (1) STEAM TURBINE. THE CT IS EQUIPPED WITH (1) HEAT RECOVERY STEAM GENERATOR (HRSG) AND DUCT BURNER. ANCILLARY EQUIPMENT INCLUDES (1) DIESEL-FIRED EMERGENCY GENERATOR, (1) DIESEL-FIRED FIRE PUMP, (1) WET COOLING TOWER, AND (6) DRY CHEMICAL STORAGE SILOS. |  | FIRE PUMP ENGINE | 17.21 | DIESEL | 235 | KW | COMPRESSION IGNITION INTERNAL COMBUSTION (CI ICE) | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | TIER 3 ENGINE-BASED, GOOD COMBUSTION PRACTICES (GCP) | 0 |  | SEE NOTE | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS ARE AVAILABLE
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 3.5 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) FIREWATER PUMP DIESEL ENGINES | 17.21 | DIESEL | 371 | BHP, EACH | THE TWO FIREWATER PUMP ENGINES, IDENTIFIED AS FP01 AND FP02, EXHAUSTING THROUGH TWO (2) VENTS. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | COMBUSTION DESIGN CONTROLS AND USAGE LIMITS | 2.6 | G/HP-H |  | BACT-PSD |  |  | 0 |  | 500 | HOURS OF OPERATION | YEARLY | 0 |  |  | 0 | 0 | N |  | LIMIT TWO IS FOR EACH FIREWATER PUMP ENGINE
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 2.6 | G/BHP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 2.6 | G/BHP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 2.6 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 2.6 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 2.6 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | EMERGENCY FIRE PUMP ENGINE | 17.21 | DISTILLATE OIL | 0 |  | 425 HP | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 2.01 | G/HP-H |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | THE AMOUNT OF DIESEL BURNED SHALL NOT EXCEED 1,128 GALLONS PER 12 MONTH PERIOD.
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Deisel | 150 | hp | 2 units at 75 hp, 1 unit at 150 hp | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 3.08 | G/KW-HR |  | BACT-PSD | NESHAP | U | 0 | U | 0.0067 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | CO emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Diesel | 250 | hp | 2 units | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 3.08 | G/HP-HR |  | BACT-PSD | NESHAP | U | 0 | U | 0.0067 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | CO emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | Cummins 6BTA 5.9F-1 Diesel Engine Fire Pump | 17.21 | No. 2 Fuel Oil | 182 | BHP |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | utilize efficient combustion/design technology | 0.53 | LB/HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | IBERVILLE | LA |  | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: ANTHONY RANDALL, 225-219-3181 | PSD-LA-709(M-1) | 2821 | 325211 | 110020900104 | 03/03/2008 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2006-06-25 | 2009-08-06 | A |  | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | VINYL CHLORIDE - 28.82 TPY. VINYL CHLORIDE (VC) WAS REGULATED AS A PSD POLLUTANT (SIGNIFICANCE LEVEL OF 1 TPY) IN LOUISIANA WHEN THIS PERMIT WAS ISSUED. LOUISIANA'S NSR REFORM RULES, ADOPTED DECEMBER 20, 2005, DELISTED VC. HAPS FROM THE PVC UNIT WERE SUBJECTED TO A 112(J) MACT DETERMINATION AFTER VACATURE OF 40 CFR 63 SUBPART J ON APRIL 19, 2005. BACT FOR VC IS EQUIVALENT TO MACT FOR VC. NNSR: BECAUSE VOC AND NOX EMISSIONS ARE LESS THAN 100 TPY, LAER WAS NOT REQUIRED. OFFSETS WERE REQUIRED PURSUANT TO A STATE-ONLY PROVISION IN LAC 33:III.504. PSD-LA-709(M-1) IS FOR 1) REMOVING A COOLING TOWER (M-8), CORRECTING CAPACITY OF COOLING TOWER M-7, AND 3) INCLUDING 19 EMERGENCY ENGINES AND THREE LOADING HOPPERS. | SMALL EMERGENCY ENGINES | 17.21 | DIESEL |  |  | U-7A, U-7B, U-7C: 420 HP EACH U-8A, U-8B, U-8C: 442 HP EACH U-9: 450 HP; M-16B: 439 HP M-16C, M-16D, M-16E: 180 HP EACH P-28A: 540 HP; P-28B: 340 HP; P28C: 180 HP | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES AND GASEOUS FUEL BURNING | 0.95 | LB/MMBTU |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0224 | ARSENAL HILL POWER PLANT | SOUTHWEST ELECTRIC POWER COMPANY (SWEPCO) | CADDO | LA | 71101 | USA | KRIS GAUS | 2147771113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-726 | 4911 | 221112 | 110001270847 | 01/07/2008 &nbsp;ACT | 03/20/2008 &nbsp;ACT | 2008-04-18 | 2012-05-18 | B |  | NATURAL GAS FIRED ELECTRICAL GENERATION PLANT. |  | DFP DIESEL FIRE PUMP | 17.21 | DIESEL | 310 | HP | EQT-016 | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N | USE OF LOW-SULFUR FUELS, LIMITING OPERATING HOURS AND PROPER ENGINE MAINTENANCE | 2.07 | LB/H | MAX | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0251 | FLOPAM INC. FACILITY | FLOPAM INC. | IBERVILLE | LA | 70764 | USA | GARY RYALS | 912-884-3366 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: DAN NGUYEN (225)219-3181 | PSD-LA-747(M1) | 2869 | 325998 | 110041935779 | 11/18/2010 &nbsp;ACT | 04/26/2011 &nbsp;ACT | 2011-09-01 | 2011-12-12 | A |  | A CHEMICAL MANUFACTURING COMPLEX IS UNDER CONSTRUCTION (PSD-LA-747 - LA0240). EQUIPMENT IS ADDED OR REDESIGNED. (ENGINES, COOLING TOWERS, MATERIAL HANDLING). PERMIT PSD-LA-747(M2) WAS ISSUED JULY 5, 2012 FOR ADDITIONAL DUST FILTERS TO CONTROL PM/PM10 FROM THE PERMITTED POWDER PLANTS. SIMILAR DUST FILTERS WERE DETERMINED AS BACT FOR SAME POWDER PLANTS. NO ADDITIONAL BACT ANALYSIS IS REQUIRED. |  | Small Generator Engine | 17.21 | diesel | 193 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 0.16 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 0.01 | T/YR |  | 3.5 | G/KW-H |  | 0 | 0 | N
LA-0251 | FLOPAM INC. FACILITY | FLOPAM INC. | IBERVILLE | LA | 70764 | USA | GARY RYALS | 912-884-3366 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: DAN NGUYEN (225)219-3181 | PSD-LA-747(M1) | 2869 | 325998 | 110041935779 | 11/18/2010 &nbsp;ACT | 04/26/2011 &nbsp;ACT | 2011-09-01 | 2011-12-12 | A |  | A CHEMICAL MANUFACTURING COMPLEX IS UNDER CONSTRUCTION (PSD-LA-747 - LA0240). EQUIPMENT IS ADDED OR REDESIGNED. (ENGINES, COOLING TOWERS, MATERIAL HANDLING). PERMIT PSD-LA-747(M2) WAS ISSUED JULY 5, 2012 FOR ADDITIONAL DUST FILTERS TO CONTROL PM/PM10 FROM THE PERMITTED POWDER PLANTS. SIMILAR DUST FILTERS WERE DETERMINED AS BACT FOR SAME POWDER PLANTS. NO ADDITIONAL BACT ANALYSIS IS REQUIRED. |  | Fire Pump Engines - 2 units | 17.21 | diesel | 444 | hp | each | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N | good equipment design and proper combustion practices | 0.65 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 0.03 | T/YR |  | 0 |  |  | 0 | 0 | N
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002049328 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | EMERGENCY FIRE PUMP | 17.21 | DIESEL | 350 | HP |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | ULTRA LOW SULFUR DIESEL AND GOOD COMBUSTION PRACTICES | 2.6 | G/HP-H | LB/MM BTU | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 2.6 | G/HP-H | ANNUAL AVERAGE | 0 | 0 | N
LA-0301 | LAKE CHARLES CHEMICAL COMPLEX ETHYLENE 2 UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | (281) 588-3761 | ERIC.RODRIGUEZ@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-779 | 2869 | 325110 | 110017418061 | 05/02/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2016-09-27 | 2017-04-28 | B |  |  | Complete application date = date of administrative completeness This RBLC entry addresses Ethylene Unit 2 of the Lake Charles Cracker Project. This unit will produce ethylene by thermally cracking ethane in cracking furnaces. | Firewater Pump Nos. 1-3 (EQTs 997, 998, &amp; 999) | 17.21 | Diesel | 500 | HP | Non-emergency use operating time is limited to 100 hr/yr (per engine). | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Compliance with 40 CFR 60 Subpart IIII and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage | 2.87 | LB/HR | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.14 | TPY | ANNUAL MAXIMUM | 2.6 | G/BHP-HR |  | 0 | 0 | N |  | BACT is determined to be compliance with the limitations imposed by 40 CFR 60 Subpart IIII and its associated monitoring, recordkeeping, and reporting requirements; and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage.
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Genenerator Engine DEG-16-1 (EQT035) | 17.21 | Diesel | 460 | horsepower | Limit operations to 100 hrs/yr | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Meet NSPS Subpart IIII Limitations and Good Combustion Practices | 3.18 | LB/H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.13 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | 3.5 g/hp-hr
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Pump Engines DFP-16-1 (EQT036) | 17.21 | Diesel | 225 | horsepower | Limit operations to 100 hour/year | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Meet NSPS Subpart IIII Limitations and Good Combustion Practices | 1.55 | LB/H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | 2.6 g/hp-hr
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Pump Engine DFP-16-2 (EQT037) | 17.21 | Diesel | 225 | horsepower | Limit operations to 100 hr/yr | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Meet NSPS Subpart IIII Limitations and Good Combustion Practices | 1.55 | LB/H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | 2.6 g/hp-hr
LA-0309 | BENTELER STEEL TUBE FACILITY | BENTELER STEEL / TUBE MANUFACTURING CORPORATION | CADDO | LA | 71115 | USA | MYRNA PACHECO PONCE DE LEON | 318-216-4206 | MYRNA.PACHECO@BENTELER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen - 225-219-3395 | PSD-LA-774(M1) | 3312 | 331111 | 110055592318 | 02/09/2015 &nbsp;ACT | 06/04/2015 &nbsp;ACT | 2017-03-09 | 2017-04-28 | A |  | A facility to produce 600,000 metric tons per year of seamless steel pipe from purchased billets. A steel production facility (including an electric arc furnace (EAF)) was added. | Permit PSD-LA-774 was issued on May 17, 2013 for the construction of the hot rolling mill. An EAF was authorized this time. | Firewater Pump Engines | 17.21 | Diesel | 288 | hp (each) |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Complying with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Emergency Diesel Firewater Pump 1 | 17.21 | Diesel | 282 | HP |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | Compliance with NESHAP 40 CFR 63 Subpart ZZZZ and NSPS 40 CFR 60 Subpart IIII, and good combustion practices (use of ultra-low sulfur diesel fuel). | 1.62 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0.4 | T/YR | ANNUAL MAXIMUM | 2.6 | G/BHP-H |  | 0 | 0 | N |  | BACT Limit = 2.6 G/BHP-HR
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel Firewater pump engines (6 units) | 17.21 | diesel | 425 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel emergency generator engine - EGEN | 17.21 | diesel | 350 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110029511883 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | firewater pump engines (8 units) | 17.21 | diesel | 460 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Complying with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0323 | MONSANTO LULING PLANT | MONSANTO COMPANY | ST. CHARLES PARISH | LA | 70070 | USA | ENRIQUE WEHLEN | 9857858211 | ENRIGUE.WEHLEN@MONSANTO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-890 | 2879 | 325320 | 110067118274 | 09/21/2015 &nbsp;ACT | 01/09/2017 &nbsp;ACT | 2017-09-26 | 2018-05-11 | D | http://edms.deq.louisiana.gov/app/doc/view.aspx?doc=10460194&ob=yes | Chemical Manufacture | Dicamba Manufacturing Facility expansion project. | Standby Generator No. 9 Engine | 17.21 | Diesel Fuel | 400 | hp | Operating hours limited to 100 hours/yr for ready testing. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Proper operation and limits on hours of operation for emergency engines and compliance with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY FIRE WATER PUMP | 17.21 | DIESEL | 300 | HP |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 2.6 | G/HP-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY GENERATOR | 17.21 | DIESEL |  |  | 1500 KW UNIT | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 2.6 | G/HP-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | EMERGENCY GENERATOR | 17.21 | ULTRA-LOW SULFUR DIESEL | 1500 | KW | 40 CFR 60 SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | USE OF ULTRA LOW SULFUR DIESEL AND GOOD COMBUSTION PRACTICES | 2.6 | G/HP-H | N/A | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA-LOW SULFUR DIESEL | 300 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | USE OF ULTRA LOW SULFUR DIESEL AND GOOD COMBUSTION PRACTICES | 2.6 | G/HP-H | N/A | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA LOW SULFUR DIESEL | 477 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | USE OF ULSD FUEL, GOOD COMBUSTION PRACTICES AND HOURS OF OPERATION LIMITED TO 100 HOURS PER YEAR | 2.6 | G/HP-H |  | BACT-PSD | NSPS |  | 0 |  | 3.49 | G/KW-H |  | 0 |  |  | 0 | 0 | N |  | NSPS 40 CFR 60 SUBPART IIII
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 5 EMERGENCY FIRE WATER PUMP ENGINES | 17.21 | ULTRA LOW SULFUR DIESEL | 350 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES AND DESIGNED TO MEET EMISSION LIMIT | 3 | G/HP-H |  | BACT-PSD |  |  | 0 |  | 4 | G/KW-H |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY GENERATOR | 17.21 | ULTRA-LOW SULFUR DIESEL | 1490 | HP | 40 CFR 60 SUBPART IIII, 40 CFR 63 SUBPART ZZZZ ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | EXCLUSIVE USE OF ULTRA LOW SULFUR FUEL AND GOOD COMBUSTION PRACTICES | 3.5 | G/KW-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS SUBPART IIII.
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA-LOW SULFUR DIESEL | 305 | HP | 40 CFR 60, SUBPART IIII, 40 CFR 63 SUBPART ZZZZ, ULTRA LOW-SULFURDIESEL FUEL, GOOD COMBUSTION PRACTICES | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | USE OF ULTRA LOW SULFUR DIESEL AND GOOD COMBUSTION PRACTICES | 3.5 | G/KW-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS SUBPART IIII.
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | DIESEL-FIRED AUXILIARY (EMERGENCY) ENGINES (TWO) | 17.21 | ULTRA-LOW SULFUR DIESEL | 1500 | KW | TWO DIESEL-FIRED AUXILIARY GENERATORS (EMERGENCY GENERATORS), EACH RATED AT NOMINAL 1,500-KILOWATT (KW) SUBJECT TO 40 CFR 60 SUBPART IIII, 40 CFR 63 SUBPART ZZZZ ULTRA LOW-SULFUR DIESEL FUEL | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | EXCLUSIVE USE OF ULTRA LOW SULFUR FUEL AND GOOD COMBUSTION PRACTICES | 3.5 | G/KW-H |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS SUBPART IIII
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | DIESEL-FIRED FIRE PUMP ENGINE | 17.21 | ULTRA-LOW SULFUR DIESEL | 300 | HP | ONE DIESEL-FIRED FIRE PUMP ENGINE, RATED AT A NOMINAL 300-HORSEPOWER. SUBJECT TO 40 CFR 63 SUBPART ZZZZ. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | EXCLUSIVE USE OF ULTRA LOW SULFUR DIESEL FUEL AND GOOD COMBUSTION PRACTICES | 3.5 | G/KW-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS SUBPART IIII
MI-0389 | KARN WEADOCK GENERATING COMPLEX | CONSUMERS ENERGY | BAY | MI | 48732-9601 | USA | JAMES M. WALKER | 5177880428 | JMWALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | FOR TECHNICAL QUESTIONS ABOUT THIS PERMIT, PLEASE CONTACT THE PERMIT ENGINEER - DAVID K. RIDDLE RIDDLED@MICHIGAN.GOV (517-373-7081) | 341-07 | 4911 | 221112 | 26-01700033 | 10/15/2007 &nbsp;ACT | 12/29/2009 &nbsp;ACT | 2010-03-08 | 2010-12-16 | U |  | ELECTRICITY GENERATING FACILITY, EXISTING CAPACITY GREATER THAN 2,000 MW. | AFTER CONSTRUCTION CONSUMERS WILL RETIRE 5 TO 7 COAL-FIRED BOILERS (638 - 958 MW) STATEWIDE. FINAL CONDITIONS WILL BE AT WWW.DEQ.STATE.MI.US/APS/FINALCONDITIONS.SHTML. MATERIAL HANDLING - CONTACT PERMIT ENGINEER FOR TECHNICAL INFORMATION (DAVID RIDDLE, 517-373-7081). INCLUDES 9 EMISSION UNITS. COAL, LIMESTONE, SORBENT AND ASH HANDLING PROCESSES. VARIOUS BACT LIMITS FOR OPACITY, PM AND PM10. BACT FOR THE MATERIAL HANDLING EQUIPMENT CONSISTED OF A COMBINATION OF PASSIVE CONTROL EQUIPMENT SUCH AS WET/CHEMICAL SUPPRESSION SYSTEMS AND ENCLOSED CONVEYORS; AND ACTIVE CONTROL SUCH AS FABRIC FILTERS. ACTIVE CONTROL IS LIMITED TO 0.004 GR/DSCF. | FIRE BOOSTER PUMP | 17.21 | ULTRA LOW SULFUR DIESEL | 40 | KW | OPERATIONAL LIMITS 1 HR/DAY AND 500 HRS/YR FOR PM2.5 NAAQS. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | ENGINE DESIGN AND OPERATION. 15 PPM SULFUR FUEL. | 5 | G/KW-H | TEST METHOD | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0399 | DETROIT EDISON--MONROE | DETROIT EDISON | MONROE | MI | 48161-1970 | USA | LILLIAN WOOLLEY | 313-235-5611 | WOOLLEYL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Julie Brunner at 517-373-7088 with questions related to the permit. Thank you. | 93-09A | 4911 | 221112 | 26-11500020 | 09/29/2010 &nbsp;ACT | 12/21/2010 &nbsp;ACT | 2012-10-17 | 2016-04-14 | D |  | Utility--Coal fired power plant |  | 4 Diesel-fired quench pumps | 17.21 | Diesel fuel | 252 | HP | Each pump engine is 252 HP. They are limited to emergency use and subject to NSPS Subpart IIII. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices. | 2.6 | G/HP-H | EACH PUMP; TEST PROTOCOL | BACT-PSD | NSPS , OTHER | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | EU-FPENGINE: Diesel fuel fired emergency backup fire pump | 17.21 | diesel fuel | 315 | hp nameplate | This is a diesel fuel fired emergency backup fire mump. It has a capacity of 315 hp, nameplate, and uses diesel fuel ASTM D975 Grade 2-D S15. Ultra low sulfur diesel fuel (15ppmw); 100 hours per year operation for maintenance and readiness testing. NSPS IIII and NESHAP ZZZZ. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Proper combustion design and ultra low sulfur diesel fuel. | 2.6 | G/HP-H | TEST PROTOCOL WILL SPECIFY AVG. TIME. | BACT-PSD | NSPS , NESHAP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ultra low sulfur diesel fuel (15 pppmw); 100 hours per year operation for maintenance and readiness testing; NSPS IIII and NESHAP ZZZZ.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Emergency Engine --Diesel Fire Pump (EUFPENGINE) | 17.21 | Diesel | 165 | HP | A 165 hoursepower (hp) diesel-fueled emergency engine manufactured in 2013, iwth a heat input of 1.35 MMBTU/hr. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 3.7 | G/HP-H | TEST PROTOCOL | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An oxidation catalyst is greater than $619,000/ton for CO and VOC together.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 2.6 | G/BHP-H | TEST PROTOCOL WILL SPECIFY AVG. TIME | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | On average, an oxidation catalyst is greater than $308,000/ton for CO and VOC together.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | diesel | 500 | H/YR | A 165 horsepower (hp) diesel-fueled emergency engine manufactured in 2016 with a heat input of 1.35 MMBTU/H. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices. | 3.7 | G/HP-H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An oxidation catalyst is greater than $501,000/ton for CO and VOC together.
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (South Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 2.6 | G/BPH-H | HOURLY | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An oxidation catalyst is $39,500/ton for PM10, CO and VOC together.
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (North Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 2.6 | G/BHP-H | HOURLY | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An oxidation catalyst is $39,500/ton for PM10, CO and VOC together.
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUFPENGINE: Fire pump engine | 17.21 | Diesel | 399 | BHP | A 399 brake HP diesel-fueled emergency fire pump engine with a model year of 2011 or later, and a displacement of <10 liters/cylinder. The engine is an EPA Tier 3 certified engine subject to NSPS IIII. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | State of the art combustion design. | 3.5 | G/KW-H | HOURLY | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MN-0079 | MINNESOTA POWER, INC. - BOSWELL ENERGY CTR. | MINNESOTA POWER DIVISION OF ALLETE, INC. | ITASCA | MN | 55721 | USA | MELISSA WEGLARZ | 218-355-3321 | MWEGLARZ@ALLETE.COM | 5 | MN004 | MINNEAPOLIS POLLUTION CONTROL DIV, MN |  |  |  | BENJAMIN KLISMITH, BENJAMIN.KLISMITH@STATE.MN.US | 06100004-004 | 4911 | 221112 | 110000426281 | 03/10/2009 &nbsp;ACT | 08/13/2009 &nbsp;ACT | 2010-06-10 | 2010-08-05 | A |  | THE BOSWELL ENERGY CENTER (FACILITY) IS A COAL-FIRED ELECTRIC UTILITY STEAM GENERATING PLANT. EMISSION UNITS AT THE FACILITY INCLUDE FOUR POWER BOILERS, EMERGENCY ENGINE GENERATORS, AND FUEL, ADDITIVE AND ASH HANDLING EQUIPMENT. |  | EMERGENCY GEN. UNIT 3 - 300Kw - CU | 17.21 | FUEL OIL #2 (DIESEL) | 300 | KW |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 3 | G/KW-H |  | BACT-PSD | MACT , NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LIMIT ACHIEVED BY ENGINE DESIGN AND GOOD COMBUSTION PRACTICES. PERFORMANCE STACK TEST.
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | firewater pumps, diesel | 17.21 | diesel | 325 | HP, EACH | Eight 325 hp diesel firewater pumps | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | comply with NSPS IIII, 52 hr/yr non-emergency operation
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | Emergency diesel fire pump | 17.21 | Ultra Low Sulfur Distillate oil | 0 |  | The fire pump has a maximum heat input rate of 2.63 MMBtu/hr (approximately 250 HP) and is permitted for 100 hrs per year for testing and maintenance | Carbon Monoxide | Other - No testing | (InOrganic Compounds) | 630-08-0 | N |  | 0.079 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 2.6 | G/B-HP-H |  | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110000801614 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Emergency Diesel Fire Pump | 17.21 | ULSD | 100 | H/YR | Maximum heat Input Rate = 2.6 MMBtu/hr | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | use of ULSD a clean burning fuel, and limited hours of operation | 1.1 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | EMERGENCY GENERATOR DIESEL | 17.21 | DIESEL OIL | 0 | 100 H/YR |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Use of Ultra Low Sulfur Diesel (ULSD) Oil a clean burning fuel and limited hours of operation (<= 100 H/YR) | 11.6 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | EMERGENCY DIESEL FIRE PUMP | 17.21 | ULSD | 100 | H/YR | ULSD: Ultra low sulfur diesel | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Use of Ultra Low Sulfur Diesel (ULSD) Oil a clean burning fuel and limited hours of operation | 1.87 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0103 | CRICKET VALLEY ENERGY CENTER | CRICKET VALLEY ENERGY CENTER LLC | USA | NY | 12522-0407 | USA |  | 845-877-0596 | INFO@CRICKETVALLEY.COM | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-1326-00275/00009 | 4911 | 221112 | 110043340364 | 02/03/2016 &nbsp;ACT | 02/03/2016 &nbsp;ACT | 2017-08-24 | 2017-09-28 | A | http://www.dec.ny.gov/chemical/32249.html | Cricket Valley Energy Center LLC (CVEC) constructed the Cricket Valley Energy Center (the Facility), a nominal net 1,000-megawatt (MW) combined-cycle gas turbine electric generating facility, on a site located in Dover, Dutchess County, New York. The Facility consists of three General Electric (GE) Model 7FA.05 combustion turbine generators (CTGs) operating in combined-cycle mode with supplemental firing of the heat recovery steam generators (HRSGs); natural gas will be the sole fuel fired in the CTGs and duct burners. The Facility will include a natural gas-fired auxiliary boiler, four ultra-low sulfur distillate (ULSD) fired black-start generator engines and a ULSD-fired emergency fire pump engine. In addition to the air emitting equipment, the Facility will include three steam turbine generators (STGs), an air cooled condenser (ACC) and associated auxiliary equipment and systems. Each combined cycle generating unit consisting of the CTG, HRSG and STG will be exhausted through its own stack. Air emissions from the proposed Facility primarily consist of products of combustion from the CTGs, HRSG duct burners, and ancillary combustion sources. Dutchess County is designated as in attainment with respect to the National Ambient Air Quality Standards (NAAQS) for all criteria pollutants with the exception of ozone. Based upon the potential to emit (PTE) estimates, the Facility is subject to Prevention of Significant Deterioration (PSD) requirements for emissions of carbon monoxide (CO); nitrogen oxides (NOx); particulate matter (PM) with a diameter equal to or less than 10 microns (PM10), PM with a diameter equal to or less than 2.5 microns (PM2.5); greenhouse gases (GHG); sulfuric acid mist (H2SO4); and volatile organic compounds (VOC). In accordance with the NYSDECâ€™s Nonattainment New Source Review (NNSR) permitting program, the Facility is also subject to NNSR for emissions of NOx and VOC. |  | Emergency fire pump | 17.21 | ultra low sulfur diesel | 460 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Compliance demonstrated with vendor emission certification and adherence to vendor-specified maintenance recommendations. | 0.53 | G/BHP-H | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0104 | CPV VALLEY ENERGY CENTER | CPV VALLEY LLC | ORANGE | NY | 10940 | USA |  |  |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-335600136/00001 | 4911 | 221112 | 110043332471 | 08/01/2013 &nbsp;ACT | 08/01/2013 &nbsp;ACT | 2017-08-25 | 2017-09-28 | A |  | CPV Valley Energy Center is a 680 MW combined cycle electric generating facility located in Middletown, NY. The combustion turbines are rated at 2,234 MMBTU/H firing natural gas and 2,145 MMBTU/H firing diesel fuel. The duct burners are rated for 500 MMBTU/H firing natural gas. In addition to the turbines their emission limits for the auxiliary boiler (73.5 MMBTU/H), emergency generator, fire pump, and gas heater. | State Facility Permit | Fire pump | 17.21 | ultra low sulfur diesel | 0 |  |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Good combustion practice. | 0.75 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0317 | OHIO RIVER CLEAN FUELS, LLC | OHIO RIVER CLEAN FUELS, LLC | COLUMBIANA | OH |  | USA | STEPHAN M. DOPUCH | 4402570054 | SDOPUCH@BAARDENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | 02-22896 | 2869 | 325110 | UNKNOWN | 12/21/2007 &nbsp;ACT | 11/20/2008 &nbsp;ACT | 2008-11-28 | 2012-05-18 | A |  | COAL/BIOMASS-TO-LIQUIDS FACILITY. THE PRIMARY INDUSTRIAL PROCESSES: COAL/BIOMASS STORAGE AND HANDLING; COAL GASIFICATION; SYNGAS CLEANING (ACID GASS REMOVAL AND SULFUR RECOVERY PLANT); FISCHER-TROPSCH PROCESS (INDUSTRIAL ORGANIC CHEMICALS); PRODUCT UPGRADE PROCESS (SIMILAR TO PETROLEUM REFINING); LIQUID PRODUCT STORAGE &amp; LOADING; ELECTRIC POWER GENERATION (USE FOR ON SITE ONLY). BIOMASS IS RESTRICTED TO ONLY SAWDUST AND WOOD CHIPS. | NEW INDUSTRY, SIC AND NAICS CODE SELECTED BY FACILITY | FIRE PUMP ENGINES (2) | 17.21 | DIESEL FUEL OIL | 300 | HP | SUBJECT TO NSPS SUBPART IIII. WILL INSTALL NON-RESETTABLE HOUR METER PRIOR TO STARTUP PER 40 CFR 60.4209(A) DIESEL FUEL SHALL MEET THE REQUIREMENTS OF 40 CFR 80.510 AND 60.4207: SULFUR CONTENT OF 15 PPM MAXIMUM, CETANE INDEX OF 40 MINIMUM OR AROMATIC CONTENT OF 35 VOLUME % MAXIMUM | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES AND GOOD ENGINE DESIGN | 1.72 | LB/H | FOR EACH ENGINE | BACT-PSD | SIP , NSPS | U | 0 | N | 0.43 | T/YR | PER ROLLING 12-MONTH PERIOD | 2.6 | G/HP-H | FROM TABLE 4 OF SUBPART IIII | 0 | 0 | N |  | LIMITS FOR EACH ENGINE. SUBJECT TO NSPS SUBPART IIII
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | Emergency fire pump engine | 17.21 | diesel | 300 | HP | 223.8 kW. Emergency fire pump engine restricted to 500 hours of operation per rolling 12 months. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Purchased certified to the standards in NSPS Subpart IIII | 1.7 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.43 | T/YR | PER ROLLING 12-MONTHS | 0 |  | SEE NOTES | 0 | 0 | N |  | Additional limit: 3.5 g CO/kW-h, standard from Subpart IIII If required Method 10.
OK-0129 | CHOUTEAU POWER PLANT | ASSOCIATED ELECTRIC COOPERATIVE INC | MAYES | OK | 74362 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2007-115-C(M-1)PSD | 4911 | 221112 | 4009700017 | 06/19/2008 &nbsp;ACT | 01/23/2009 &nbsp;ACT | 2009-11-20 | 2010-02-18 | B |  |  |  | EMERGENCY FIRE PUMP (267-HP DIESEL) | 17.21 | LOW SULFUR DIESEL | 267 | HP |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 2.6 | G/HP-H | NSPS | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Fire pump engine | 17.21 | Ultra-low sulfur diesel | 15 | gal/hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 0.5 | GM/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.009 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Emergency Fire Pump Engine | 17.21 | ULSD | 0 |  | Sulfur content of diesel fuel shall not exceed 15 ppm, operation of engine shall not exceed 100 hr on a 12-month rolling basis. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 2.61 | G/BHP-HR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
PR-0009 | ENERGY ANSWERS ARECIBO PUERTO RICO RENEWABLE ENERGY PROJECT | ENERGY ANSWERS ARECIBO, LLC | ARECIBO | PR |  | USA | MARK GREEN | (347)-351-5248 |  | 2 | OT003 | EPA REGION II | MR. FRANK JON | (212)637-4085 | jon.frank@epa.gov | Ms. Viorica Petriman petriman.viorica@epa.gov | R2-PSD 1 | 4953 | 221119 | FRL-9911-10-Region 2 | 11/11/2012 &nbsp;ACT | 04/10/2014 &nbsp;ACT | 2014-10-14 | 2016-05-05 | A |  | Energy Answers Arecibo is a new resource recovery facility capable of producing up to 77 megawatts (MW) of electrical power while combusting municipal solid waste, as the primary fuel. | This is a PSD permit for a new/greenfield facility. | Emergency Diesel Fire Pump | 17.21 | ULSD Fuel Oil #2 | 0 |  | The Emergency Fire Pump is rated at 335 BHP and limited to 500 hr/yr (emergency operations and testing and maintenance, combined). | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 2.6 | G/B-HP-H |  | BACT-PSD |  | U | 0 | U | 1.93 | LB/H |  | 0 |  |  | 0 | 0 | N
SC-0113 | PYRAMAX CERAMICS, LLC | PYRAMAX CERAMICS, LLC | ALLENDALE | SC | 29810 | USA | RICHARD DERBAWKA | 7705690079 | R.DERBAWKA@PYRAMAXCERAMICS.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MS. ALYSON HAYES | (803)898-3836 | camitdr@dhec.sc.gov | GEORGE S. ROBINSON (803) 898-4123 | 0160-0023 | 3295 | 327992 | Not Available | 09/16/2011 &nbsp;ACT | 02/08/2012 &nbsp;ACT | 2012-05-09 | 2012-10-17 | A |  | PYRAMAX CERAMICS PLANS TO CONSTRUCT A MANUFACTURING FACILITY FOR THE PRODUCTION OF PROPPANT BEADS FOR USE IN THE OIL AND GAS INDUSTRY. THE MAJOR RAW MATERIAL IS CLAY. THE CLAY IS MIXED WITH CHEMICALS AND THEN FIRED IN A KILN TO PRODUCE CERAMIC BEADS. INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | EMERGENCY ENGINE 1 THRU 8 | 17.21 | DIESEL | 29 | HP | THE CONSTRUCTION PERMIT AUTHORIZES THE CONSTRUCTION OF EIGHT (8) IDENTICAL EMERGENCY ENGINES. THIS PROCESS AND POLLUTANT INFORMATION IS FOR ONE SINGLE ENGINE. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | PURCHASE OF CERTIFIED ENGINE. HOURS OF OPERATION LIMITED TO 100 HOURS FOR MAINTENANCE AND TESTING. | 5.5 | GR/KW-H |  | BACT-PSD | NSPS | Y | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | FACILITY WILL PURCHASE ENGINES CERTIFIED BY MANUFACTURER TO MEET REQUIREMENTS OF NSPS, SUBPART IIII
SC-0113 | PYRAMAX CERAMICS, LLC | PYRAMAX CERAMICS, LLC | ALLENDALE | SC | 29810 | USA | RICHARD DERBAWKA | 7705690079 | R.DERBAWKA@PYRAMAXCERAMICS.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MS. ALYSON HAYES | (803)898-3836 | camitdr@dhec.sc.gov | GEORGE S. ROBINSON (803) 898-4123 | 0160-0023 | 3295 | 327992 | Not Available | 09/16/2011 &nbsp;ACT | 02/08/2012 &nbsp;ACT | 2012-05-09 | 2012-10-17 | A |  | PYRAMAX CERAMICS PLANS TO CONSTRUCT A MANUFACTURING FACILITY FOR THE PRODUCTION OF PROPPANT BEADS FOR USE IN THE OIL AND GAS INDUSTRY. THE MAJOR RAW MATERIAL IS CLAY. THE CLAY IS MIXED WITH CHEMICALS AND THEN FIRED IN A KILN TO PRODUCE CERAMIC BEADS. INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | FIRE PUMP | 17.21 | DIESEL | 500 | HP | THE CONSTRUCTION PERMIT AUTHORIZES THE CONSTRUCTION OF ONE (1) FIRE PUMP. THIS PROCESS AND POLLUTANT INFORMATION IS FOR THIS ONE SINGLE FIRE PUMP. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | ENGINES CERTIFIED TO MEET NSPS, SUBPART IIII. HOURS OF OPERATION LIMITED TO 100 HOURS PER YEAR FOR MAINTENANCE AND TESTING. | 3.5 | GR/KW-H |  | BACT-PSD | NSPS | Y | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | FACILITY MUST PURCHASE ENGINES CERTIFIED BY THE MANUFACTURER TO MEET NSPS, SUBPART IIII. HOURS OF OPERATION LIMITED TO 100 HOURS PER YEAR FOR MAINTENANCE AND TESTING.
TX-0799 | BEAUMONT TERMINAL | PHILLIPS 66 PIPELINE LLC | JEFFERSON | TX |  | USA | CHINTAN MEHTA | 832-765-1677 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Beth Akers, 512-239-4620 beth.akers@tceq.texas.gov | 18295, PSDTX1466, GHGPSDTX139 | 5171 | 424710 | 110033444850 | 04/19/2016 &nbsp;ACT | 06/08/2016 &nbsp;ACT | 2016-06-17 | 2016-07-07 | C |  | This marine terminal receives, stores, and distributes various volatile organic liquids (VOLs) and refined petroleum products. | (consolidate and/or void: 1973, 8113, 481, 2365, 56419, 6312, and 6559) | EMERGENCY ENGINES | 17.21 | diesel | 0 |  |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Equipment specifications and good combustion practices. Operation limited to 100 hours per year. | 0.0068 | LB/HP-HR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0321 | BRUNSWICK COUNTY POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | BRUNSWICK | VA | 23856 | USA | JEFFREY ZEHNER | 804-273-3145 | JEFFREY.R.ZEHNER@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit writer, Alison Sinclar, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52404-001 | 4911 | 221112 | 110055066440 | 12/21/2012 &nbsp;ACT | 03/12/2013 &nbsp;ACT | 2013-04-03 | 2016-07-07 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx,http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | New, combined-cycle, natural gas-fired, electrical power generating facility. |  | Diesel Fire water pump 376 bhp | 17.21 | diesel | 500 | h/yr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion practices | 0.9 | G/KW-HR |  | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | emergency use only, operate according to mfr instructions and procedures, non-resettable hour meter
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Fire Pump Engine | 17.21 | Diesel | 251 | HP | Limited to 100 Hours/year. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 1.44 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Diesel Fire Pump Engine (EP16) | 17.21 | Ultra Low Sulfur Diesel | 327 | hp |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | EPA Tier 3 rated | 0 |  |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | limited to 250 hours of non-emergency operation per calendar year
WY-0071 | SINCLAIR REFINERY | SINCLAIR WYOMING REFINING COMPANY | CARBON | WY | 82334 | USA | SAM GREENE | (801) 524-2729 | SGREENE@SINCLAIROIL.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | MD-12620 | 2911 | 324110 | 110040906945 | 05/01/2012 &nbsp;ACT | 10/15/2012 &nbsp;ACT | 2012-10-05 | 2016-04-14 | D |  | Crude Oil Refinery | (1) Crude Optimization Project; (2) remove the firing rate limits for the #1 HDS heater, Naphtha Splitter Heater, and Hydrocraker H5 Heater; (3) installation of a new Naphtha Splitter and Benzene Saturation/Isomerization (BSI) Unit; (4) increasing the capacity of the existing sour water stripping system and installation of an additional sour water stripper; and (5) install a new 400 hp emergency air compressor | Emergency Air Compressor | 17.21 | Ultra Low Sulfur Diesel | 400 | hp |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | EPA Tier 3 Rated Diesel Engine | 0 |  |  | BACT-PSD | NSPS , NESHAP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limited to 500 hours of operation
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Airstrip Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 490 | hp | One 490 hp Airstrip Generator Engine | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 4.8 | GRAMS/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Agitator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 98 | hp | ULSD-fired 98 hp Agitator Generator Engine | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 5.6 | GRAMS/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Diesel Fired Well Pump | 17.21 | Diesel | 2.7 | MMBTU/H | 2.7 MMBtu/hr Diesel Fired Well Pump. Installed in 1966. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Limited Operation of 168 hr/yr. | 4.41 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*AK-0084 | DONLIN GOLD PROJECT | DONLIN GOLD LLC. | BETHEL CENSUS AREA | AK | 99575 | USA | STAN FOO | 907-273-0200 | SFOO@DONLINGOLD.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | AK DEC DIV. OF AIR QUALITY 410 WILLOUGHBY AVE. SUITE 303 JUNEAU, AK 99801 | AQ0934CPT01 | 1041 | 212221 | Not Entered | 10/15/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2018-06-21 | 2018-06-22 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16763360/d1h2U6BIY-j857LFU-WYmw2 | The Donlin Gold Project is a gold mine located 12 miles north of Crooked Creek, Alaska on the Kuskokwim River, about 280 miles northwest of Anchorage. The deposit has proven and probable reserves estimated at 33.9 million ounces of gold at 2.1 g/t and could produce up to 1.5 million ounces annually. SIC Code 1041; NAICS Code 212221. |  | Fire Pump Diesel Internal Combustion Engines | 17.21 | Diesel | 252 | hp | Three (3) 252 hp fire pump diesel internal combustion engines. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good Combustion Practices | 3.7 | G/KW-HR | 3-HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 83.70 g/kW-hr includes NOx and VOC emissions. NSPS Subpart IIII engines.
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | EMERGENCY FIREWATER PUMP ENGINE | 17.21 | DIESEL | 135 | KW | 135 KW (182 hp) IC Diesel-fired Emergency Firewater Pump Engine | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | OPERATIONAL RESTRICTION OF 50 HR/YR, OPERATE AS REQUIRED FOR FIRE SAFETY TESTING | 3.8 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 2.8 | G/HP-H |  | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | EMERGENCY FIREWATER PUMP ENGINE | 17.21 | DIESEL | 288 | HP |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | EQUIPPED W/ A TURBOCHARGER AND AN INTERCOOLER/AFTERCOOLER | 3.4 | G/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.21 | DIESEL | 182 | HP | UNIT IS 135 KW. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 4 | G/KW-H | 3-HR AVG | BACT-PSD |  | U | 0 | U | 3 | G/HP-H | 3-HR AVG | 0 |  |  | 0 | 0 | N
FL-0324 | PALM BEACH RENEWABLE ENERGY PARK | SOLID WASTE AUTHORITY OF PALM BEACH COUNTY | PALM BEACH | FL | 33412 | USA | MARK HAMMOND | 561-640-4000 | MHAMMOND@SWA.ORG | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Alvaro Linero, P.E. Administrator alvaro.linero@dep.state.fl.us Phone: 850-717-9076 Robert Bull, Engineer robert.bull@dep.state.fl.us Phone: 850-717-9111 Teresa Heron, Engineer teresa.heron@dep.state.fl.us phone: 850-717-9082 | PSD-FL-413 | 4953 | 221119 | 110043792358 | 11/12/2010 &nbsp;ACT | 12/23/2010 &nbsp;ACT | 2011-04-07 | 2011-12-08 | B |  | The existing Palm Beach Renewable Energy Facility (PBREP-1) consists of Class I and Class III landfills, a biosolids pelletizer facility, a compost facility and a waste-to-energy (WTE) plant known as the North County Resource Recovery Facility (NCRRF). The new facility, PBREP-2, will consist of: â€¢Three nominal 1,000 TPD mass burn MWC, each with an estimated maximum continuous rating (MCR) of 416.7 million Btu per hour heat input (mmBtu/hr) and a peak rating of 458.3 mmBtu/hr; â€¢A 100 megawatt (MW) STG with an air cooled condenser; â€¢One ash building and handling system; â€¢Three lime storage silos and one carbon storage silo; and â€¢Two 250 horsepower (hp) diesel fire pumps and one 250 kilowatt (kW) emergency generator. This facility, is located at 7501 North Jog Road (immediately west of the Turnpike) in West Palm Beach. | This project will consist of three 1,000 TPD mass-burn MWC units each with a maximum steam production rate of 320,100 pounds per hour (lb/hr) on a 4-hour average block basis. The project also includes a 90 to100 MW STG; three lime storage silos; one carbon storage silo; two diesel fire pump engines; one emergency generator; and one ash handling system and building. The proposed work will be conducted at the existing PBREP. The project will incorporate the following pollution control equipment and measures: â€¢For each MWC unit, good combustion practices (GCP), spray dryers (SD), fabric filter (FF) baghouses, activated carbon injection (CI), selective catalytic reduction (SCR), as an option selective non-catalytic reduction (SNCR) and use of inherently clean natural gas as a startup, shutdown and flame stabilization fuel. â€¢Use of inherently clean ultra low sulfur distillate (ULSD) fuel oil and GCP in the emergency generator and emergency fire pump engines; and â€¢Reasonable precautions and best management practices (BMP) to minimize fugitive particulate matter (PM)/(PM10)/(PM2.5) emissions from MSW handling and processing; ash (bottom and fly) handling, storage and shipment; lime handling, storage and processing; and activated carbon handling, storage and processing. The project will incorporate continuous emission monitoring systems (CEMS) for CO, SO2, NOX and Hg and continuous opacity monitoring systems (COMS) for visible emissions (VE). | 250 Kw Emergency Generator | 17.21 | ULSD | 0 |  |  | Nitrogen Oxides (NOx) | Other - Manufacturer Certification | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Use of inherently clean ultra low sulfur distillate (ULSD) fuel oil and GCP | 4 | G/KW-H |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Wireline Unit Engines - C.R. Luigs | 17.21 | diesel | 300 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 8.92 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Fast Rescue Craft Diesel Engine - Development Driller 1 | 17.21 | Diesel | 142 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, and turbocharger | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Port and Stb Fwd and Aft Crane Diesel Engines - C.R. Luigs | 17.21 | diesel | 305 | HP |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 82.83 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Seismic Operations Diesel Engines - Development Driller 1 | 17.21 | Diesel | 415 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, and turbocharger | 3.54 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Life Boat Diesel Engines - C.R. Luigs | 17.21 | diesel | 39 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - Development Driller 1 | 17.21 | Diesel | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger, and high pressure fuel injection with aftercooler | 9.5 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Wireline Unit Diesel Engines - Development Driller 1 | 17.21 | Diesel | 0 |  | Wireline units including primary, alternative #2, power plant, and hydraulic generator | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 8.92 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - C.R. Luigs | 17.21 | diesel | 0 |  | Cementing Units: Caterpillar 3412 CDITA 860 hp 2001 Nitrogen Pump: Caterpillar 3406 CDITA 490 hp 2000 | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger, and high pressure fuel injection with aftercooler | 8.69 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Diesel Powered Forklift Engine | 17.21 | Diesel | 30 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Wireline Diesel Engines | 17.21 | Diesel | 0 |  | Wireline engines, electric line engines, casing unit engines, tubing running engine, fluid filtration pump engine, powerpack engine, slickline powerpack engine, and CT pump engine | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Water Blasting Diesel Engine | 17.21 | Diesel | 208 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Well Evaluation Diesel Engine | 17.21 | Diesel | 140 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Fast Rescue Craft Diesel Engine | 17.21 | Diesel | 230 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Escape Capsule Diesel Engine | 17.21 | Diesel | 39 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Remotely Operated Vehicle Emergency Generator | 17.21 | Diesel | 427 | hp | 2004 Cummins QSM11-G2NR3 | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Use of good combustion practices based on the most recent manufacturer's specifications issued for engines and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0348 | MURPHY EXPLORATION & PRODUCTION CO. | MURPHY EXPLORATION & PRODUCTION CO. | NA | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4009 | 1381 | 213111 | NA | 04/22/2011 &nbsp;ACT | 05/15/2012 &nbsp;ACT | 2015-09-21 | 2016-07-07 | A | http://www2.epa.gov/caa-permitting/murphy-exploration-and-production-co-outer-continental-shelf-ocs-final-permit | The facility consists of the dynamically positioned Diamond Offshore deepwater drilling vessel Ocean Confidence and an associated support fleet to conduct exploratory drilling and well completion for up to 90 calendar days within a two year period at a single well location within its Lloyd Ridge lease block 317. The drill site is located on the OCS in the Gulf of Mexico, approximately 135 miles southeast of the mouth of the Mississippi River and 180 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21. This permit is based upon the permit application materials submitted to EPA by Murphy Exploration & Production Co. (Murphy) dated January 13, 2011, March 21, 2011, June 22, 2011, September 12, 2011 and supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Main Propulsion Generators | 17.21 | Diesel | 4425 | hp | Eight 1986 WÃ¤rtsilÃ¤ F316A Diesel Engines | Nitrogen Oxides (NOx) | Other - Parametric | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Use of engine with turbo charger with after cooler, an enhanced work practice power management, NOx emissions maintenance system, and good combustion and maintenance practices based on the current manufacturerâ€™s specifications for each engine | 26 | G/KW-H | ROLLING 24-HOUR AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0354 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-013-AC | 4911 | 221112 | 110002044065 | 04/20/2015 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2016-02-17 | 2016-07-06 | D | https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | Re-affirmed BACT determinations in Permit No. 0110037-011-AC. Also, new GHG BACT determination. Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.D.ZIP | Emergency fire pump engine, 300 HP | 17.21 | Diesel | 29 | MMBTU/H | Emergency engine. ULSD only. BACT limits equal NSPS IIII limits. | Nitrogen Oxides (NOx) | Other - Certified engine | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low-emitting fuel and certified engine | 4 | G / KWH | NMHC + NOX (SUBPART IIII) | BACT-PSD | NSPS , SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 4.0 grams per kilowatt-hour, pursuant to Subpart IIII. Must use certified engine, or perform stack tests.
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | good combustion practices | 3.75 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.49 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
ID-0018 | LANGLEY GULCH POWER PLANT | IDAHO POWER COMPANY | PAYETTE | ID |  | USA |  | 2083885820 | TMAHLUM@IDAHOPOWER.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2009.0092 | 4911 | 221112 | UNKNOWN | 06/07/2009 &nbsp;ACT | 06/25/2010 &nbsp;ACT | 2010-08-09 | 2010-10-05 | A |  | ONE-ON-ONE COMBINED CYCLE PLANT CONSISTING OF (1) NATURAL GAS-FIRED COMBUSTION TURBINE (CT) AND (1) STEAM TURBINE. THE CT IS EQUIPPED WITH (1) HEAT RECOVERY STEAM GENERATOR (HRSG) AND DUCT BURNER. ANCILLARY EQUIPMENT INCLUDES (1) DIESEL-FIRED EMERGENCY GENERATOR, (1) DIESEL-FIRED FIRE PUMP, (1) WET COOLING TOWER, AND (6) DRY CHEMICAL STORAGE SILOS. |  | FIRE PUMP ENGINE | 17.21 | DIESEL | 235 | KW | COMPRESSION IGNITION INTERNAL COMBUSTION (CI ICE) | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | TIER 3 ENGINE-BASED GOOD COMBUSTION PRACTICES (GCP) | 4 | G/KW-H | NOX+NMHC | BACT-PSD | NSPS | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LIMIT APPLIES TO NOX+NMHC COMBINED EMISSIONS.
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 3.5 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) FIREWATER PUMP DIESEL ENGINES | 17.21 | DIESEL | 371 | BHP, EACH | THE TWO FIREWATER PUMP ENGINES, IDENTIFIED AS FP01 AND FP02, EXHAUSTING THROUGH TWO (2) VENTS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | COMBUSTION DESIGN CONTROLS AND USAGE LIMITS | 3 | G/HP-H | 3 HOURS | BACT-PSD |  |  | 0 |  | 500 | HOURS OF OPERATION | YEARLY | 0 |  |  | 0 | 0 | N |  | LIMIT TWO IS FOR EACH FIREWATER PUMP ENGINE
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES | 2.83 | G/BHP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES | 2.83 | G/BHP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES | 2.86 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES | 2.83 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES | 2.83 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | EMERGENCY FIRE PUMP ENGINE | 17.21 | DISTILLATE OIL | 0 |  | 425 HP | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES | 9.5 | G/HP-H |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | THE AMOUNT OF DIESEL BURNED SHALL NOT EXCEED 1,128 GALLONS PER 12 MONTH PERIOD
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Deisel | 150 | hp | 2 units at 75 hp, 1 unit at 150 hp | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 14.06 | G/HP-HR |  | BACT-PSD | NESHAP | U | 0 | U | 0.031 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | NOx emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Diesel | 250 | hp | 2 units | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 9.2 | G/KW-HR |  | BACT-PSD | NESHAP | U | 0 | U | 6.86 | G/HP-HR |  | 0 |  |  | 0 | 0 | N |  | NOx emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
*KS-0030 | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | GRANT | KS | 67601 | USA | PAUL REYNOLDS | 620-277-4522 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Mindy Bowman, E-mail address: Mindy.Bowman@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-13309 | 4911 | 221112 | Not Found | 03/07/2017 &nbsp;ACT | 03/31/2016 &nbsp;ACT | 2017-04-06 | 2017-07-19 | C |  | Mid-Kansas Electric Company, LLC (Mid-Kansas Electric) (Source ID: 0670173) operates the Rubart Station located in Grant County, Kansas. The facility currently consist of twelve (12) new spark ignition four-stroke lean burn (4SLB) reciprocating internal combustion engines (RICE) used to generate electricity (the proposed project consist of 24 new 4SLB RICE). The generating capacity of each unit is 10 megawatts (approximately 13,410 BHP). Also located at the station is a diesel fire pump, natural gas emergency generator, heater, circuit breakers and switches. The insignificant activities include a diesel storage tank. | This PSD permit with tracking number C-13309 a modification of PSD permits C-12896 (PSD Administrative Amendment, issued on 5/7/2015), C-12721 (PSD Revisions, issued on 4/28/2015), and C-10021 (original PSD permit for the proposed project, issued on 1/28/2013). | Compression ignition RICE emergency fire pump | 17.21 | Ultra-lowsulfur diesel (ULSD) | 197 | HP | One (1) compression ignition emergency fire pump engine, rated at 197 HP, which shall burn only ultra-low sulfur diesel (ULSD, 15 ppm sulfur or less). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 3 | G/HP-HR | EXCLUDES STARTUP, SHUTDOWN & MALFUNCTION | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | Cummins 6BTA 5.9F-1 Diesel Engine Fire Pump | 17.21 | No. 2 Fuel Oil | 182 | BHP |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | utilize efficient combustion/design technology | 2 | LB/HR | AT FULL LOAD | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | IBERVILLE | LA |  | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: ANTHONY RANDALL, 225-219-3181 | PSD-LA-709(M-1) | 2821 | 325211 | 110020900104 | 03/03/2008 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2006-06-25 | 2009-08-06 | A |  | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | VINYL CHLORIDE - 28.82 TPY. VINYL CHLORIDE (VC) WAS REGULATED AS A PSD POLLUTANT (SIGNIFICANCE LEVEL OF 1 TPY) IN LOUISIANA WHEN THIS PERMIT WAS ISSUED. LOUISIANA'S NSR REFORM RULES, ADOPTED DECEMBER 20, 2005, DELISTED VC. HAPS FROM THE PVC UNIT WERE SUBJECTED TO A 112(J) MACT DETERMINATION AFTER VACATURE OF 40 CFR 63 SUBPART J ON APRIL 19, 2005. BACT FOR VC IS EQUIVALENT TO MACT FOR VC. NNSR: BECAUSE VOC AND NOX EMISSIONS ARE LESS THAN 100 TPY, LAER WAS NOT REQUIRED. OFFSETS WERE REQUIRED PURSUANT TO A STATE-ONLY PROVISION IN LAC 33:III.504. PSD-LA-709(M-1) IS FOR 1) REMOVING A COOLING TOWER (M-8), CORRECTING CAPACITY OF COOLING TOWER M-7, AND 3) INCLUDING 19 EMERGENCY ENGINES AND THREE LOADING HOPPERS. | SMALL EMERGENCY ENGINES | 17.21 | DIESEL |  |  | U-7A, U-7B, U-7C: 420 HP EACH U-8A, U-8B, U-8C: 442 HP EACH U-9: 450 HP; M-16B: 439 HP M-16C, M-16D, M-16E: 180 HP EACH P-28A: 540 HP; P-28B: 340 HP; P28C: 180 HP | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES AND GASEOUS FUEL BURNING | 4.41 | LB/MMBTU |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0224 | ARSENAL HILL POWER PLANT | SOUTHWEST ELECTRIC POWER COMPANY (SWEPCO) | CADDO | LA | 71101 | USA | KRIS GAUS | 2147771113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-726 | 4911 | 221112 | 110001270847 | 01/07/2008 &nbsp;ACT | 03/20/2008 &nbsp;ACT | 2008-04-18 | 2012-05-18 | B |  | NATURAL GAS FIRED ELECTRICAL GENERATION PLANT. |  | DFP DIESEL FIRE PUMP | 17.21 | DIESEL | 310 | HP | EQT-016 | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N | USE OF LOW-SULFUR FUELS, LIMITING OPERATING HOURS AND PROPER ENGINE MAINTENANCE | 9.61 | LB/H | MAX | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0251 | FLOPAM INC. FACILITY | FLOPAM INC. | IBERVILLE | LA | 70764 | USA | GARY RYALS | 912-884-3366 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: DAN NGUYEN (225)219-3181 | PSD-LA-747(M1) | 2869 | 325998 | 110041935779 | 11/18/2010 &nbsp;ACT | 04/26/2011 &nbsp;ACT | 2011-09-01 | 2011-12-12 | A |  | A CHEMICAL MANUFACTURING COMPLEX IS UNDER CONSTRUCTION (PSD-LA-747 - LA0240). EQUIPMENT IS ADDED OR REDESIGNED. (ENGINES, COOLING TOWERS, MATERIAL HANDLING). PERMIT PSD-LA-747(M2) WAS ISSUED JULY 5, 2012 FOR ADDITIONAL DUST FILTERS TO CONTROL PM/PM10 FROM THE PERMITTED POWDER PLANTS. SIMILAR DUST FILTERS WERE DETERMINED AS BACT FOR SAME POWDER PLANTS. NO ADDITIONAL BACT ANALYSIS IS REQUIRED. |  | Small Generator Engine | 17.21 | diesel | 193 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 1.28 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 0.06 | T/YR |  | 4 | G/KW-H | (NOX + NMHC) | 0 | 0 | N
LA-0251 | FLOPAM INC. FACILITY | FLOPAM INC. | IBERVILLE | LA | 70764 | USA | GARY RYALS | 912-884-3366 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: DAN NGUYEN (225)219-3181 | PSD-LA-747(M1) | 2869 | 325998 | 110041935779 | 11/18/2010 &nbsp;ACT | 04/26/2011 &nbsp;ACT | 2011-09-01 | 2011-12-12 | A |  | A CHEMICAL MANUFACTURING COMPLEX IS UNDER CONSTRUCTION (PSD-LA-747 - LA0240). EQUIPMENT IS ADDED OR REDESIGNED. (ENGINES, COOLING TOWERS, MATERIAL HANDLING). PERMIT PSD-LA-747(M2) WAS ISSUED JULY 5, 2012 FOR ADDITIONAL DUST FILTERS TO CONTROL PM/PM10 FROM THE PERMITTED POWDER PLANTS. SIMILAR DUST FILTERS WERE DETERMINED AS BACT FOR SAME POWDER PLANTS. NO ADDITIONAL BACT ANALYSIS IS REQUIRED. |  | Fire Pump Engines - 2 units | 17.21 | diesel | 444 | hp | each | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 5.82 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 0.29 | T/YR |  | 3 | G/HP-H | (NOX + NMHC) | 0 | 0 | N
LA-0301 | LAKE CHARLES CHEMICAL COMPLEX ETHYLENE 2 UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | (281) 588-3761 | ERIC.RODRIGUEZ@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-779 | 2869 | 325110 | 110017418061 | 05/02/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2016-09-27 | 2017-04-28 | B |  |  | Complete application date = date of administrative completeness This RBLC entry addresses Ethylene Unit 2 of the Lake Charles Cracker Project. This unit will produce ethylene by thermally cracking ethane in cracking furnaces. | Firewater Pump Nos. 1-3 (EQTs 997, 998, &amp; 999) | 17.21 | Diesel | 500 | HP | Non-emergency use operating time is limited to 100 hr/yr (per engine). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Compliance with 40 CFR 60 Subpart IIII and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage | 3.21 | LB/HR | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.16 | TPY | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | NOx + NMHC emissions are limited to 3.0 g/hp-hr. BACT is determined to be compliance with the limitations imposed by 40 CFR 60 Subpart IIII and its associated monitoring, recordkeeping, and reporting requirements; and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage.
LA-0308 | MORGAN CITY POWER PLANT | LOUISIANA ENERGY AND POWER AUTHORITY (LEPA) | ST. MARY | LA | 70380 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-767 | 4911 | 221112 | Not Found | 09/24/2012 &nbsp;ACT | 09/26/2013 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  |  |  | 380 HP Diesel Fired Pump Engine | 17.21 | Diesel | 2.3 | MMBTU/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion and maintenance practices, and compliance with NSPS 40 CFR 60 Subpart IIII | 2.92 | LB/H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.12 | T/YR | ANNUAL MAXIMUM | 2.2 | G/B-HP-H | 12 MONTH AVERAGE | 0 | 0 | N
LA-0309 | BENTELER STEEL TUBE FACILITY | BENTELER STEEL / TUBE MANUFACTURING CORPORATION | CADDO | LA | 71115 | USA | MYRNA PACHECO PONCE DE LEON | 318-216-4206 | MYRNA.PACHECO@BENTELER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen - 225-219-3395 | PSD-LA-774(M1) | 3312 | 331111 | 110055592318 | 02/09/2015 &nbsp;ACT | 06/04/2015 &nbsp;ACT | 2017-03-09 | 2017-04-28 | A |  | A facility to produce 600,000 metric tons per year of seamless steel pipe from purchased billets. A steel production facility (including an electric arc furnace (EAF)) was added. | Permit PSD-LA-774 was issued on May 17, 2013 for the construction of the hot rolling mill. An EAF was authorized this time. | Firewater Pump Engines | 17.21 | Diesel | 288 | hp (each) |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Complying with 40 CFR 60 Subpart IIII | 3 | G/BHP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Emergency Diesel Firewater Pump 1 | 17.21 | Diesel | 282 | HP |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Compliance with NESHAP 40 CFR 63 Subpart ZZZZ and NSPS 40 CFR 60 Subpart IIII, and good combustion practices (use of ultra-low sulfur diesel fuel). | 1.87 | LB/H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.47 | T/YR | ANNUAL MAXIMUM | 3 | G/BHP-H |  | 0 | 0 | N |  | BACT Limit = 3.0 G/BHP-HR (NMHC + NOx)
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel Firewater pump engines (6 units) | 17.21 | diesel | 425 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel emergency generator engine - EGEN | 17.21 | diesel | 350 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0323 | MONSANTO LULING PLANT | MONSANTO COMPANY | ST. CHARLES PARISH | LA | 70070 | USA | ENRIQUE WEHLEN | 9857858211 | ENRIGUE.WEHLEN@MONSANTO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-890 | 2879 | 325320 | 110067118274 | 09/21/2015 &nbsp;ACT | 01/09/2017 &nbsp;ACT | 2017-09-26 | 2018-05-11 | D | http://edms.deq.louisiana.gov/app/doc/view.aspx?doc=10460194&ob=yes | Chemical Manufacture | Dicamba Manufacturing Facility expansion project. | Standby Generator No. 9 Engine | 17.21 | Diesel Fuel | 400 | hp | Operating hours limited to 100 hours/yr for ready testing. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Proper operation and limits on hours of operation for emergency engines and compliance with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY FIRE WATER PUMP | 17.21 | DIESEL | 300 | HP |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 3 | G/HP-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMBINED NOX AND NON-METHANE HYDROCARBON LIMIT, LAER
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY GENERATOR | 17.21 | DIESEL |  |  | 1500 KW UNIT | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 4.8 | G/HP-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COMBINED LIMIT FOR NOX AND NON-METHANE HYDROCARBONS
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY GENERATOR | 17.21 | ULTRA-LOW SULFUR DIESEL | 1490 | HP | 40 CFR 60 SUBPART IIII, 40 CFR 63 SUBPART ZZZZ ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | EXCLUSIVE USE OF ULTRA LOW SULFUR FUEL AND GOOD COMBUSTION PRACTICES | 6.4 | G/KW-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | INCLUDES NITROGEN OXIDES (NOX) AND NON-METHANE HYDROCARBONS (NMHC). NSPS SUBPART IIII.
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | DIESEL-FIRED AUXILIARY (EMERGENCY) ENGINES (TWO) | 17.21 | ULTRA-LOW SULFUR DIESEL | 1500 | KW | TWO DIESEL-FIRED AUXILIARY GENERATORS (EMERGENCY GENERATORS), EACH RATED AT NOMINAL 1,500-KILOWATT (KW) SUBJECT TO 40 CFR 60 SUBPART IIII, 40 CFR 63 SUBPART ZZZZ ULTRA LOW-SULFUR DIESEL FUEL | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | EXCLUSIVE USE OF ULTRA LOW SULFUR FUEL AND GOOD COMBUSTION PRACTICES | 6.4 | G/KW-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | FOR COMBINED NON-METHANE HYDROCARBONS (NMHC) AND NITROGEN OXIDES (NOX). NSPS SUBPART IIII.
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | DIESEL-FIRED FIRE PUMP ENGINE | 17.21 | ULTRA-LOW SULFUR DIESEL | 300 | HP | ONE DIESEL-FIRED FIRE PUMP ENGINE, RATED AT A NOMINAL 300-HORSEPOWER. SUBJECT TO 40 CFR 63 SUBPART ZZZZ. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | EXCLUSIVE USE OF ULTRA LOW SULFUR DIESEL FUEL AND GOOD COMBUSTION PRACTICES | 4 | G/KW-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | FOR COMBINED NON-METHANE HYDROCARBONS (NMHC) AND NITROGEN OXIDES (NOX). NSPS SUBPART IIII.
MI-0399 | DETROIT EDISON--MONROE | DETROIT EDISON | MONROE | MI | 48161-1970 | USA | LILLIAN WOOLLEY | 313-235-5611 | WOOLLEYL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Julie Brunner at 517-373-7088 with questions related to the permit. Thank you. | 93-09A | 4911 | 221112 | 26-11500020 | 09/29/2010 &nbsp;ACT | 12/21/2010 &nbsp;ACT | 2012-10-17 | 2016-04-14 | D |  | Utility--Coal fired power plant |  | 4 Diesel-fired quench pumps | 17.21 | Diesel fuel | 252 | HP | Each pump engine is 252 HP. They are limited to emergency use and subject to NSPS Subpart IIII. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices. | 7.8 | G/HP-H | QP1&QP2 EACH; TEST PROTOCOL | BACT-PSD | NSPS | N | 0 | N | 3 | G/HP-H | QP3&QP4 EACH; TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Limits are as NMHC+NOx based upon NSPS Subpart IIII.
MI-0400 | WOLVERINE POWER | WOLVERINE POWER SUPPLY COOPERATIVE, INC. | PRESQUE ISLE | MI | 49779 | USA | BRIAN WARNER | 2317755700 X 3336 | BWARNER@WPSCI.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Melissa Byrnes at 517-373-7065 with questions regarding this permit. Thank you. | 317-07 | 4911 | 221112 | 26-14105823 | 09/26/2007 &nbsp;ACT | 06/29/2011 &nbsp;ACT | 2012-10-18 | 2016-04-14 | A |  | Coal-fired power plant. |  | Fire Pump | 17.21 | Diesel | 420 | HP | Maximum operation was based on 500 hours per year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 3 | G/HP-H | TEST PROTOCOL; BACT/SIP/NSPS | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NOTE: Emission limit is expresssed as NMHC+NOx = 3.0 G/HP-H.
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | EU-FPENGINE: Diesel fuel fired emergency backup fire pump | 17.21 | diesel fuel | 315 | hp nameplate | This is a diesel fuel fired emergency backup fire mump. It has a capacity of 315 hp, nameplate, and uses diesel fuel ASTM D975 Grade 2-D S15. Ultra low sulfur diesel fuel (15ppmw); 100 hours per year operation for maintenance and readiness testing. NSPS IIII and NESHAP ZZZZ. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Proper combustion design and ultra low sulfur diesel fuel. | 3 | G/HP-H | TEST PROTOCOL WILL SPECIFY AVG. TIME. | BACT-PSD | NSPS , NESHAP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is NMHC + NOx, but that pollutant is not an option in the 'Pollutant' field above. Ultra low sulfur diesel fuel (15 ppmw); 100 hours per year operation for maintenance and readiness testing; NSPS IIII and NESHAP ZZZZ.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Emergency Engine --Diesel Fire Pump (EUFPENGINE) | 17.21 | Diesel | 165 | HP | A 165 hoursepower (hp) diesel-fueled emergency engine manufactured in 2013, iwth a heat input of 1.35 MMBTU/hr. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices | 3 | G/HP-H | TEST PROTOCOL | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 3 | G/BHP-H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is actually in &lsquo;&lsquo;NMHC + NOx&lsquo;&lsquo; (nonmethane hydrocarbon plus NOx), which is what is required in the NSPS.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | diesel | 500 | H/YR | A 165 horsepower (hp) diesel-fueled emergency engine manufactured in 2016 with a heat input of 1.35 MMBTU/H. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices. | 3 | G/HP-H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (South Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 3 | G/BHP-H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is actually in &lsquo;&lsquo;NMHC + NOx&lsquo;&lsquo; (nonmethane hydrocarbon plus NOx) which is what is required in the NSPS.
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (North Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 3 | G/BHP-H | HOURLY | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is actually in &lsquo;&lsquo;NMHC+NOx&lsquo;&lsquo; (nonmethane hydrocarbon plus NOx), which is what is required in the NSPS.
*MI-0434 | FLAT ROCK ASSEMBLY PLANT | FORD MOTOR COMPANY | WAYNE | MI | 48134 | USA | JOSEPH VICARI | 313-999-0364 | JVICARI@FORD.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov for technical questions regarding this permit. Thank you. | 122-17 | 8741 | 561110 | Not Found | 09/11/2017 &nbsp;ACT | 03/22/2018 &nbsp;ACT | 2018-08-22 | 2018-08-22 | B |  | The existing Flat Rock Assembly Plant (FRAP) is an automotive manufacturing plant which consists of a stamping operation, a body shop, a paint shop, and a final assembly shop. The permit application is for the proposed installation of an electronic data center (EDC) with backup emergency generators at FRAP. |  | EUFIREPUMPENGS (2 emergency fire pump engines) | 17.21 | Diesel | 250 | BHP | EUFIREPUMPENGS - Two (2) diesel-fueled emergency fire pump engines rated at 250 brake horsepower (BHP). No add-on control. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices. | 3 | G/B-HP-H | HOURLY; EACH ENGINE (NMHC+NOX) | BACT-PSD | NSPS , SIP | U | 0 | N | 2.8 | LB/H | HOURLY; EACH ENGINE (NOX) | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above is actually in &lsquo;&lsquo;NMHC+NOx&lsquo;&lsquo; (nonmethane hydrocarbon plus NOx) and is 3.0 G/B-HP-H for each engine and is based upon NSPS IIII. Emission limit 2 is actually a NOx limit and is 2.8 LB/H for each engine.
*MI-0434 | FLAT ROCK ASSEMBLY PLANT | FORD MOTOR COMPANY | WAYNE | MI | 48134 | USA | JOSEPH VICARI | 313-999-0364 | JVICARI@FORD.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov for technical questions regarding this permit. Thank you. | 122-17 | 8741 | 561110 | Not Found | 09/11/2017 &nbsp;ACT | 03/22/2018 &nbsp;ACT | 2018-08-22 | 2018-08-22 | B |  | The existing Flat Rock Assembly Plant (FRAP) is an automotive manufacturing plant which consists of a stamping operation, a body shop, a paint shop, and a final assembly shop. The permit application is for the proposed installation of an electronic data center (EDC) with backup emergency generators at FRAP. |  | EULIFESAFETYENG - One diesel-fueled emergency engine/generator | 17.21 | Diesel | 500 | KW | EULIFESAFETYENG - One (1) diesel-fueled emergency engine/generator rated at 500 KW. No add-on control. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices. | 4 | G/KW-H | HOURLY; NMHC+NOX | BACT-PSD | NSPS , SIP | N | 0 | N | 8.47 | LB/H | HOURLY; NOX | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above is actually in &lsquo;&lsquo;NMHC+NOx&lsquo;&lsquo; (nonmethane hydrocarbon plus NOx) and is 4.0 G/KW-H based upon NSPS IIII. Emission limit 2 is actually NOx and is 8.47 LB/H.
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUFPENGINE: Fire pump engine | 17.21 | Diesel | 399 | BHP | A 399 brake HP diesel-fueled emergency fire pump engine with a model year of 2011 or later, and a displacement of <10 liters/cylinder. The engine is an EPA Tier 3 certified engine subject to NSPS IIII. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | State of the art combustion design. | 4 | G/KW-H | HOURLY | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is actually in &lsquo;&lsquo;NMHC+ NOx&lsquo;&lsquo; (nonmethane hydrocarbon plus NOx) which is what is required in the NSPS.
NV-0047 | NELLIS AIR FORCE BASE | 99 CIVIL ENGINEER SQUADRON OF USAF | CLARK | NV | 891555210 | USA | SHIMI MATHEW | 7026522548 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, TEL: 702-455-1673 | 114 | 9711 | 928110 | 110027848319 | 09/26/2007 &nbsp;ACT | 02/26/2008 &nbsp;ACT | 2008-10-21 | 2008-10-21 | A |  | THE FACILITY IS A MILITARY INSTALLATION WITH A LARGE NUMBER OF PROCESSES SUPPORTING THE AIR FORCE'S OPERATIONS. | THIS REPORT IS BASED ON THE PERMIT ISSUED TO THE NELLIS AIR FORCE BASE FOR MODIFICATION 37, REVISION 2. THE FACILITY IS A MAJOR STATIONARY SOURCE FOR NITROGEN OXIDES. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE, PM-10, AND CARBON MONOXIDE. A FEW MINOR PROCESSES, WHICH WERE NOT REVIEWED IN THIS PERMITTING ACTION, ARE NOT INCLUDED IN THIS REPORT. A PART 70 PERMIT FOR THIS NEW MAJOR SOURCE IS YET TO BE ISSUED. | SMALL INTERNAL COMBUSTION ENGINES (&lt;= 500 HP) | 17.21 | DIESEL OIL |  |  | THE PERMITTING ACTION APPROVED A TOTAL OF 42 NEW UNITS. THE FACILITY HAS A TOTAL OF 49 REGULATED UNITS AND 11 EXEMPT UNITS. ALL OF THEM ARE SUBJECT TO THE LIMIT OF OPERATING TIME FOR TESTING AND MAINTENANCE FOR 90 HOURS PER YEAR. UNIT G021 (ONAN GENERATOR, 317 HP) IS SELECTED TO SHOW THE BACT DETERMINATIONS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | TURBOCHARGER AND AFTERCOOLER | 3.88 | G/B-HP-H |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | N | 2.71 | LB/H |  | 3.88 | G/B-HP-H |  | 0 | 0 | N
OH-0317 | OHIO RIVER CLEAN FUELS, LLC | OHIO RIVER CLEAN FUELS, LLC | COLUMBIANA | OH |  | USA | STEPHAN M. DOPUCH | 4402570054 | SDOPUCH@BAARDENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | 02-22896 | 2869 | 325110 | UNKNOWN | 12/21/2007 &nbsp;ACT | 11/20/2008 &nbsp;ACT | 2008-11-28 | 2012-05-18 | A |  | COAL/BIOMASS-TO-LIQUIDS FACILITY. THE PRIMARY INDUSTRIAL PROCESSES: COAL/BIOMASS STORAGE AND HANDLING; COAL GASIFICATION; SYNGAS CLEANING (ACID GASS REMOVAL AND SULFUR RECOVERY PLANT); FISCHER-TROPSCH PROCESS (INDUSTRIAL ORGANIC CHEMICALS); PRODUCT UPGRADE PROCESS (SIMILAR TO PETROLEUM REFINING); LIQUID PRODUCT STORAGE &amp; LOADING; ELECTRIC POWER GENERATION (USE FOR ON SITE ONLY). BIOMASS IS RESTRICTED TO ONLY SAWDUST AND WOOD CHIPS. | NEW INDUSTRY, SIC AND NAICS CODE SELECTED BY FACILITY | FIRE PUMP ENGINES (2) | 17.21 | DIESEL FUEL OIL | 300 | HP | SUBJECT TO NSPS SUBPART IIII. WILL INSTALL NON-RESETTABLE HOUR METER PRIOR TO STARTUP PER 40 CFR 60.4209(A) DIESEL FUEL SHALL MEET THE REQUIREMENTS OF 40 CFR 80.510 AND 60.4207: SULFUR CONTENT OF 15 PPM MAXIMUM, CETANE INDEX OF 40 MINIMUM OR AROMATIC CONTENT OF 35 VOLUME % MAXIMUM | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES, GOOD ENGINE DESIGN, IGNITION TIMING RETARD, TURBOCHARGER, AND LOW-TEMPERATURE AFTERCOOLER | 4.89 | LB/H | FOR EACH ENGINE | BACT-PSD | NSPS , SIP | U | 0 | N | 1.23 | T/YR | PER ROLLING 12-MONTH PERIOD | 7.8 | G/HP-H | FOR NMHC AND NOX COMBINED 95% NOX | 0 | 0 | N |  | 7.8 G/HP-H FOR NON-METHANE HYDROCARBONS AND NOX COMBINED LIMIT FROM NSPS SUBPART IIII, TABLE 4; 95% CONSIDERED NOX IN HOURLY LIMIT CALCULATION. LIMITS FOR EACH ENGINE.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | Emergency fire pump engine | 17.21 | diesel | 300 | HP | 223.8 kW. Emergency fire pump engine restricted to 500 hours of operation per rolling 12 months. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Purchased certified to the standards in NSPS Subpart IIII | 1.7 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.43 | T/YR | PER ROLLING 12-MONTHS | 0 |  | SEE NOTES | 0 | 0 | N |  | Additional limits: 3.5 g NOx/kW-H; and 4.0 g NMHC + NOx/kW-hr, the standard from Subpart IIII. Method 7E if required.
OK-0129 | CHOUTEAU POWER PLANT | ASSOCIATED ELECTRIC COOPERATIVE INC | MAYES | OK | 74362 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2007-115-C(M-1)PSD | 4911 | 221112 | 4009700017 | 06/19/2008 &nbsp;ACT | 01/23/2009 &nbsp;ACT | 2009-11-20 | 2010-02-18 | B |  |  |  | EMERGENCY FIRE PUMP (267-HP DIESEL) | 17.21 | LOW SULFUR DIESEL | 267 | HP |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 4.59 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 7.8 | G/HP-H | NSPS | 0 |  |  | 0 | 0 | N
PR-0009 | ENERGY ANSWERS ARECIBO PUERTO RICO RENEWABLE ENERGY PROJECT | ENERGY ANSWERS ARECIBO, LLC | ARECIBO | PR |  | USA | MARK GREEN | (347)-351-5248 |  | 2 | OT003 | EPA REGION II | MR. FRANK JON | (212)637-4085 | jon.frank@epa.gov | Ms. Viorica Petriman petriman.viorica@epa.gov | R2-PSD 1 | 4953 | 221119 | FRL-9911-10-Region 2 | 11/11/2012 &nbsp;ACT | 04/10/2014 &nbsp;ACT | 2014-10-14 | 2016-05-05 | A |  | Energy Answers Arecibo is a new resource recovery facility capable of producing up to 77 megawatts (MW) of electrical power while combusting municipal solid waste, as the primary fuel. | This is a PSD permit for a new/greenfield facility. | Emergency Diesel Fire Pump | 17.21 | ULSD Fuel Oil #2 | 0 |  | The Emergency Fire Pump is rated at 335 BHP and limited to 500 hr/yr (emergency operations and testing and maintenance, combined). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 2.85 | G/B-HP-H |  | BACT-PSD |  | U | 0 | U | 2.1 | LB/H |  | 0 |  |  | 0 | 0 | N
SC-0113 | PYRAMAX CERAMICS, LLC | PYRAMAX CERAMICS, LLC | ALLENDALE | SC | 29810 | USA | RICHARD DERBAWKA | 7705690079 | R.DERBAWKA@PYRAMAXCERAMICS.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MS. ALYSON HAYES | (803)898-3836 | camitdr@dhec.sc.gov | GEORGE S. ROBINSON (803) 898-4123 | 0160-0023 | 3295 | 327992 | Not Available | 09/16/2011 &nbsp;ACT | 02/08/2012 &nbsp;ACT | 2012-05-09 | 2012-10-17 | A |  | PYRAMAX CERAMICS PLANS TO CONSTRUCT A MANUFACTURING FACILITY FOR THE PRODUCTION OF PROPPANT BEADS FOR USE IN THE OIL AND GAS INDUSTRY. THE MAJOR RAW MATERIAL IS CLAY. THE CLAY IS MIXED WITH CHEMICALS AND THEN FIRED IN A KILN TO PRODUCE CERAMIC BEADS. INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | EMERGENCY ENGINE 1 THRU 8 | 17.21 | DIESEL | 29 | HP | THE CONSTRUCTION PERMIT AUTHORIZES THE CONSTRUCTION OF EIGHT (8) IDENTICAL EMERGENCY ENGINES. THIS PROCESS AND POLLUTANT INFORMATION IS FOR ONE SINGLE ENGINE. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | PURCHASE OF CERTIFIED ENGINE. | 7.5 | GR/KW-H |  | BACT-PSD | NSPS | Y | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | FACILITY WILL PURCHASE ENGINES CERTIFIED TO MEET NSPS, SUBPART IIII.
SC-0113 | PYRAMAX CERAMICS, LLC | PYRAMAX CERAMICS, LLC | ALLENDALE | SC | 29810 | USA | RICHARD DERBAWKA | 7705690079 | R.DERBAWKA@PYRAMAXCERAMICS.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MS. ALYSON HAYES | (803)898-3836 | camitdr@dhec.sc.gov | GEORGE S. ROBINSON (803) 898-4123 | 0160-0023 | 3295 | 327992 | Not Available | 09/16/2011 &nbsp;ACT | 02/08/2012 &nbsp;ACT | 2012-05-09 | 2012-10-17 | A |  | PYRAMAX CERAMICS PLANS TO CONSTRUCT A MANUFACTURING FACILITY FOR THE PRODUCTION OF PROPPANT BEADS FOR USE IN THE OIL AND GAS INDUSTRY. THE MAJOR RAW MATERIAL IS CLAY. THE CLAY IS MIXED WITH CHEMICALS AND THEN FIRED IN A KILN TO PRODUCE CERAMIC BEADS. INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | FIRE PUMP | 17.21 | DIESEL | 500 | HP | THE CONSTRUCTION PERMIT AUTHORIZES THE CONSTRUCTION OF ONE (1) FIRE PUMP. THIS PROCESS AND POLLUTANT INFORMATION IS FOR THIS ONE SINGLE FIRE PUMP. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | PURCHASE OF CERTIFIED ENGINE BASED ON NSPS, SUBPART IIII. | 4 | GR/KW-H |  | BACT-PSD | NSPS | Y | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | FACILITY SHALL PURCHASE ENGINE CERTIFIED BY THE MANUFACTURER TO MEET NSPS, SUBPART IIII. FACILITY TO MAINTAIN RECORDS TO DEMONSTARTE COMPLIANCE WITH NSPS, SUBPART IIII.
TX-0706 | NATURAL GAS FRACTIONATION | OCCIDENTAL CHEMICAL CORPORATION | SAN PATRICIO | TX |  | USA | PAUL THOMAS | 361-776-6169 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ozden Tamer Phone 5122394577 ozden.tamer@tceq.texas.gov | 102482, PSDTX1292 | 1321 | 325199 | 110000599807 | 04/27/2012 &nbsp;ACT | 01/23/2014 &nbsp;ACT | 2015-03-20 | 2016-05-16 | B |  | Occidental will build a NGL Fractionation Plant that will receive natural gas liquids by pipeline and fractionate these liquids into commercial grade products, including ethane, propane, butanes, and natural gasoline | This permit authorized Occidental to construct and operate an 87,000 barrel/day capacity Natural Gas Liquids Fractionation Plant immediately adjacent to its Vinyl Chloride Monomer Plant in Gregory, San Patricio County, Texas | Emergency Engines | 17.21 | Ultra-low sulfur diesel | 0 |  | The process includes 1 emergency generator and 4 emergency firewater pump engines. The sulfur in the diesel fuel will meet the sulfur requirement of 15 ppm in 40 CFR 80.510(b). The emissions from each engine result from weekly testing which will occur 52 hours a year for each engine. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.33 | TPY |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Fire Pump Engine | 17.21 | Diesel | 251 | HP | Limited to 100 Hours/year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 3 | G/HP-HR | NMHC + NOX | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Diesel Fire Pump Engine (EP16) | 17.21 | Ultra Low Sulfur Diesel | 327 | hp |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | EPA Tier 3 rated | 0 |  |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | limited to 250 hours of non-emergency operation per calendar year
WY-0071 | SINCLAIR REFINERY | SINCLAIR WYOMING REFINING COMPANY | CARBON | WY | 82334 | USA | SAM GREENE | (801) 524-2729 | SGREENE@SINCLAIROIL.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | MD-12620 | 2911 | 324110 | 110040906945 | 05/01/2012 &nbsp;ACT | 10/15/2012 &nbsp;ACT | 2012-10-05 | 2016-04-14 | D |  | Crude Oil Refinery | (1) Crude Optimization Project; (2) remove the firing rate limits for the #1 HDS heater, Naphtha Splitter Heater, and Hydrocraker H5 Heater; (3) installation of a new Naphtha Splitter and Benzene Saturation/Isomerization (BSI) Unit; (4) increasing the capacity of the existing sour water stripping system and installation of an additional sour water stripper; and (5) install a new 400 hp emergency air compressor | Emergency Air Compressor | 17.21 | Ultra Low Sulfur Diesel | 400 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | EPA Tier 3 Rated Diesel Engine | 0 |  |  | BACT-PSD | NSPS , NESHAP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limited to 500 hours of operation
ID-0018 | LANGLEY GULCH POWER PLANT | IDAHO POWER COMPANY | PAYETTE | ID |  | USA |  | 2083885820 | TMAHLUM@IDAHOPOWER.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2009.0092 | 4911 | 221112 | UNKNOWN | 06/07/2009 &nbsp;ACT | 06/25/2010 &nbsp;ACT | 2010-08-09 | 2010-10-05 | A |  | ONE-ON-ONE COMBINED CYCLE PLANT CONSISTING OF (1) NATURAL GAS-FIRED COMBUSTION TURBINE (CT) AND (1) STEAM TURBINE. THE CT IS EQUIPPED WITH (1) HEAT RECOVERY STEAM GENERATOR (HRSG) AND DUCT BURNER. ANCILLARY EQUIPMENT INCLUDES (1) DIESEL-FIRED EMERGENCY GENERATOR, (1) DIESEL-FIRED FIRE PUMP, (1) WET COOLING TOWER, AND (6) DRY CHEMICAL STORAGE SILOS. |  | FIRE PUMP ENGINE | 17.21 | DIESEL | 235 | KW | COMPRESSION IGNITION INTERNAL COMBUSTION (CI ICE) | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | P | TIER 3 ENGINE-BASED, GOOD COMBUSTION PRACTICES (GCP) | 0.2 | G/KW-H |  | BACT-PSD | NSPS | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY FIRE WATER PUMP | 17.21 | DIESEL | 300 | HP |  | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY GENERATOR | 17.21 | DIESEL |  |  | 1500 KW UNIT | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Airstrip Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 490 | hp | One 490 hp Airstrip Generator Engine | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | GRAMS/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Agitator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 98 | hp | ULSD-fired 98 hp Agitator Generator Engine | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.3 | GRAMS/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Incinerator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 102 | hp | ULSD-fired 102 hp Incinerator Generator Engine | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.22 | GRAMS/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) FIREWATER PUMP DIESEL ENGINES | 17.21 | DIESEL | 371 | BHP, EACH | THE TWO FIREWATER PUMP ENGINES, IDENTIFIED AS FP01 AND FP02, EXHAUSTING THROUGH TWO (2) VENTS. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION DESIGN CONTROLS AND USAGE LIMITS | 0.15 | G/HP-H |  | BACT-PSD |  |  | 0 |  | 500 | HOURS OF OPERATION | YEARLY | 0 |  |  | 0 | 0 | N |  | LIMIT TWO IS FOR EACH FIREWATER PUMP ENGINES
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Deisel | 150 | hp | 2 units at 75 hp, 1 unit at 150 hp | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 1.34 | G/KW-HR |  | BACT-PSD | NESHAP | N | 0 | U | 0.0022 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | PM10 emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Diesel | 250 | hp | 2 units | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 1.34 | G/KW-HR |  | BACT-PSD | NESHAP | U | 0 | U | 0.0022 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | PM10 emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
LA-0224 | ARSENAL HILL POWER PLANT | SOUTHWEST ELECTRIC POWER COMPANY (SWEPCO) | CADDO | LA | 71101 | USA | KRIS GAUS | 2147771113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-726 | 4911 | 221112 | 110001270847 | 01/07/2008 &nbsp;ACT | 03/20/2008 &nbsp;ACT | 2008-04-18 | 2012-05-18 | B |  | NATURAL GAS FIRED ELECTRICAL GENERATION PLANT. |  | DFP DIESEL FIRE PUMP | 17.21 | DIESEL | 310 | HP | EQT-016 | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | USE OF LOW-SULFUR FUELS, LIMITING OPERATING HOURS AND PROPER ENGINE MAINTENANCE | 0.68 | LB/H | MAX | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0251 | FLOPAM INC. FACILITY | FLOPAM INC. | IBERVILLE | LA | 70764 | USA | GARY RYALS | 912-884-3366 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: DAN NGUYEN (225)219-3181 | PSD-LA-747(M1) | 2869 | 325998 | 110041935779 | 11/18/2010 &nbsp;ACT | 04/26/2011 &nbsp;ACT | 2011-09-01 | 2011-12-12 | A |  | A CHEMICAL MANUFACTURING COMPLEX IS UNDER CONSTRUCTION (PSD-LA-747 - LA0240). EQUIPMENT IS ADDED OR REDESIGNED. (ENGINES, COOLING TOWERS, MATERIAL HANDLING). PERMIT PSD-LA-747(M2) WAS ISSUED JULY 5, 2012 FOR ADDITIONAL DUST FILTERS TO CONTROL PM/PM10 FROM THE PERMITTED POWDER PLANTS. SIMILAR DUST FILTERS WERE DETERMINED AS BACT FOR SAME POWDER PLANTS. NO ADDITIONAL BACT ANALYSIS IS REQUIRED. |  | Small Generator Engine | 17.21 | diesel | 193 | hp |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.01 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 0.01 | T/YR |  | 0.2 | G/KW-H |  | 0 | 0 | N
LA-0251 | FLOPAM INC. FACILITY | FLOPAM INC. | IBERVILLE | LA | 70764 | USA | GARY RYALS | 912-884-3366 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: DAN NGUYEN (225)219-3181 | PSD-LA-747(M1) | 2869 | 325998 | 110041935779 | 11/18/2010 &nbsp;ACT | 04/26/2011 &nbsp;ACT | 2011-09-01 | 2011-12-12 | A |  | A CHEMICAL MANUFACTURING COMPLEX IS UNDER CONSTRUCTION (PSD-LA-747 - LA0240). EQUIPMENT IS ADDED OR REDESIGNED. (ENGINES, COOLING TOWERS, MATERIAL HANDLING). PERMIT PSD-LA-747(M2) WAS ISSUED JULY 5, 2012 FOR ADDITIONAL DUST FILTERS TO CONTROL PM/PM10 FROM THE PERMITTED POWDER PLANTS. SIMILAR DUST FILTERS WERE DETERMINED AS BACT FOR SAME POWDER PLANTS. NO ADDITIONAL BACT ANALYSIS IS REQUIRED. |  | Fire Pump Engines - 2 units | 17.21 | diesel | 444 | hp | each | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.01 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 0.01 | T/YR |  | 0.15 | G/HP-H |  | 0 | 0 | N
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Emergency Diesel Firewater Pump 1 | 17.21 | Diesel | 282 | HP |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | Compliance with NESHAP 40 CFR 63 Subpart ZZZZ and NSPS 40 CFR 60 Subpart IIII, and good combustion practices (use of ultra-low sulfur diesel fuel). | 0.09 | LB/H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.02 | T/YR | ANNUAL MAXIMUM | 0.15 | G/BHP-H |  | 0 | 0 | N |  | BACT Limit = 0.15 G/BHP-HR
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY FIRE WATER PUMP | 17.21 | DIESEL | 300 | HP |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | GR-HP-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY GENERATOR | 17.21 | DIESEL |  |  | 1500 KW UNIT | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0317 | OHIO RIVER CLEAN FUELS, LLC | OHIO RIVER CLEAN FUELS, LLC | COLUMBIANA | OH |  | USA | STEPHAN M. DOPUCH | 4402570054 | SDOPUCH@BAARDENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | 02-22896 | 2869 | 325110 | UNKNOWN | 12/21/2007 &nbsp;ACT | 11/20/2008 &nbsp;ACT | 2008-11-28 | 2012-05-18 | A |  | COAL/BIOMASS-TO-LIQUIDS FACILITY. THE PRIMARY INDUSTRIAL PROCESSES: COAL/BIOMASS STORAGE AND HANDLING; COAL GASIFICATION; SYNGAS CLEANING (ACID GASS REMOVAL AND SULFUR RECOVERY PLANT); FISCHER-TROPSCH PROCESS (INDUSTRIAL ORGANIC CHEMICALS); PRODUCT UPGRADE PROCESS (SIMILAR TO PETROLEUM REFINING); LIQUID PRODUCT STORAGE &amp; LOADING; ELECTRIC POWER GENERATION (USE FOR ON SITE ONLY). BIOMASS IS RESTRICTED TO ONLY SAWDUST AND WOOD CHIPS. | NEW INDUSTRY, SIC AND NAICS CODE SELECTED BY FACILITY | FIRE PUMP ENGINES (2) | 17.21 | DIESEL FUEL OIL | 300 | HP | SUBJECT TO NSPS SUBPART IIII. WILL INSTALL NON-RESETTABLE HOUR METER PRIOR TO STARTUP PER 40 CFR 60.4209(A) DIESEL FUEL SHALL MEET THE REQUIREMENTS OF 40 CFR 80.510 AND 60.4207: SULFUR CONTENT OF 15 PPM MAXIMUM, CETANE INDEX OF 40 MINIMUM OR AROMATIC CONTENT OF 35 VOLUME % MAXIMUM | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND GOOD ENGINE DESIGN | 0.27 | LB/H | FOR EACH ENGINE | BACT-PSD | NSPS , SIP | U | 0 | N | 0.07 | T/YR | PER ROLLING 12-MONTH PERIOD | 0.4 | G/HP-H | FROM TABLE 4 OF SUBPART IIII | 0 | 0 | N |  | LIMITS FOR EACH ENGINE. SUBJECT TO NSPS SUBPART IIII.
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Airstrip Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 490 | hp | One 490 hp Airstrip Generator Engine | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | GRAMS/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Agitator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 98 | hp | ULSD-fired 98 hp Agitator Generator Engine | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.3 | GRAMS/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Incinerator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 102 | hp | ULSD-fired 102 hp Incinerator Generator Engine | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.22 | GRAMS/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) FIREWATER PUMP DIESEL ENGINES | 17.21 | DIESEL | 371 | BHP, EACH | THE TWO FIREWATER PUMP ENGINES, IDENTIFIED AS FP01 AND FP02, EXHAUSTING THROUGH TWO (2) VENTS. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION DESIGN CONTROLS AND USAGE LIMITS | 0.15 | G/HP-H | 3 HOURS | BACT-PSD |  |  | 0 |  | 500 | HOURS OF OPERATION | YEARLY | 0 |  |  | 0 | 0 | N |  | LIMIT TWO IS FOR EACH FIREWATER PUMP ENGINE
LA-0308 | MORGAN CITY POWER PLANT | LOUISIANA ENERGY AND POWER AUTHORITY (LEPA) | ST. MARY | LA | 70380 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-767 | 4911 | 221112 | Not Found | 09/24/2012 &nbsp;ACT | 09/26/2013 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  |  |  | 380 HP Diesel Fired Pump Engine | 17.21 | Diesel | 2.3 | MMBTU/hr |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion and maintenance practices, and compliance with NSPS 40 CFR 60 Subpart IIII | 0.15 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0.01 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.441 lb/MWh (12 month average)
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Emergency Diesel Firewater Pump 1 | 17.21 | Diesel | 282 | HP |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | B | Compliance with NESHAP 40 CFR 63 Subpart ZZZZ and NSPS 40 CFR 60 Subpart IIII, and good combustion practices (use of ultra-low sulfur diesel fuel). | 0.09 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0.02 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.05 G/BHP-HR
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Fire Pump Engine | 17.21 | Diesel | 251 | HP | Limited to 100 Hours/year. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0.15 | G/HP-HR |  | 0 | 0 | N
*FL-0363 | DANIA BEACH ENERGY CENTER | FLORIDA POWER AND LIGHT COMPANY | BROWARD | FL | 33314 | USA | JOHN HAMPP | 561-691-2894 | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-017-AC | 4911 | 221112 | 110002044065 | 07/27/2017 &nbsp;ACT | 12/04/2017 &nbsp;ACT | 2018-04-03 | 2018-04-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.F.ZIP | 1200 megawatt 2-on-1 combined cycle facility, natural gas-fired, with limited ULSD use. GE 7HA turbines | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.D.ZIP | Emergency Fire Pump Engine (422 hp) | 17.21 | ULSD | 0 |  | Limits equal Subpart IIII limits | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Certified engine | 0.2 | G / KWH |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Certified engine, no testing required
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 0.1 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) FIREWATER PUMP DIESEL ENGINES | 17.21 | DIESEL | 371 | BHP, EACH | THE TWO FIREWATER PUMP ENGINES, IDENTIFIED AS FP01 AND FP02, EXHAUSTING THROUGH TWO (2) VENTS. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION DESIGN CONTROLS AND USAGE LIMITS | 0.15 | G/HP-H |  | BACT-PSD |  |  | 0 |  | 500 | HOURS OF OPERATION | YEARLY | 0 |  |  | 0 | 0 | N |  | LIMIT TWO IS FOR EACH FIREWATER PUMP ENGINE
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/BHP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/BHP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | EMERGENCY FIRE PUMP ENGINE | 17.21 | DISTILLATE OIL | 0 |  | 425 HP | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.16 | G/HP-H |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | AMOUNT OF DIESEL FUEL BURNED SHALL NOT EXCEED 1,128 GALLONS PER 12 CONSECUTIVE MONTH PERIOD
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Deisel | 150 | hp | 2 units at 75 hp, 1 unit at 150 hp | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 1.34 | G/KW-HR |  | BACT-PSD | NESHAP | N | 0 | U | 0.0022 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | PM emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Diesel | 250 | hp | 2 units | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.54 | G/KW-HR |  | BACT-PSD | NESHAP | U | 0 | U | 0.0009 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | PM emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | EMERGENCY GENERATOR | 17.21 | ULTRA-LOW SULFUR DIESEL | 1500 | KW | 40 CFR 60 SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULTRA LOW SULFUR FUEL AND GOOD COMBUSTION PRACTICES | 0.15 | G/HP-H | N/A | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA-LOW SULFUR DIESEL | 300 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULTRA LOW SULFUR FUEL AND GOOD COMBUSTION PRACTICES | 0.15 | G/HP-H | N/A | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA LOW SULFUR DIESEL | 477 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULSD FUEL, GOOD COMBUSTION PRACTICES, LIMITED HOURS OF OPERATION, AND DESIGNED TO ACHIEVE EMISSION LIMITS | 0.15 | G/HP-H |  | BACT-PSD | NSPS |  | 0 |  | 0.2 | G/KW-H |  | 0 |  |  | 0 | 0 | N |  | NSPS 40 CFR 60 SUBPART IIII
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 5 EMERGENCY FIRE WATER PUMP ENGINES | 17.21 | ULTRA LOW SULFUR DIESEL | 350 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULSD FUEL, GOOD COMBUSTION PRACTICES AND DESIGNED TO ACHIEVE EMISSION LIMITS | 0.15 | G/BHP-H |  | BACT-PSD |  |  | 0 |  | 0.2 | G/KW-H |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY GENERATOR | 17.21 | ULTRA-LOW SULFUR DIESEL | 1490 | HP | 40 CFR 60 SUBPART IIII, 40 CFR 63 SUBPART ZZZZ ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULTRA LOW SULFUR FUEL AND GOOD COMBUSTION PRACTICES | 0.2 | G/KW-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS SUBPART IIII
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA-LOW SULFUR DIESEL | 305 | HP | 40 CFR 60, SUBPART IIII, 40 CFR 63 SUBPART ZZZZ, ULTRA LOW-SULFURDIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULTRA LOW SULFUR FUEL AND GOOD COMBUSTION PRACTICES | 0.2 | G/KW-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS SUBPART IIII
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | DIESEL-FIRED AUXILIARY (EMERGENCY) ENGINES (TWO) | 17.21 | ULTRA-LOW SULFUR DIESEL | 1500 | KW | TWO DIESEL-FIRED AUXILIARY GENERATORS (EMERGENCY GENERATORS), EACH RATED AT NOMINAL 1,500-KILOWATT (KW) SUBJECT TO 40 CFR 60 SUBPART IIII, 40 CFR 63 SUBPART ZZZZ ULTRA LOW-SULFUR DIESEL FUEL | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | USE OF ULTRA LOW SULFUR DIESEL AND GOOD COMBUSTION PRACTICES | 0.2 | G/KW-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS SUBPART IIII.
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | DIESEL-FIRED FIRE PUMP ENGINE | 17.21 | ULTRA-LOW SULFUR DIESEL | 300 | HP | ONE DIESEL-FIRED FIRE PUMP ENGINE, RATED AT A NOMINAL 300-HORSEPOWER. SUBJECT TO 40 CFR 63 SUBPART ZZZZ. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULTRA LOW SULFUR DIESEL FUEL AND GOOD COMBUSTION PRACTICES | 0.2 | G/KW-H |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS IIII
MI-0399 | DETROIT EDISON--MONROE | DETROIT EDISON | MONROE | MI | 48161-1970 | USA | LILLIAN WOOLLEY | 313-235-5611 | WOOLLEYL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Julie Brunner at 517-373-7088 with questions related to the permit. Thank you. | 93-09A | 4911 | 221112 | 26-11500020 | 09/29/2010 &nbsp;ACT | 12/21/2010 &nbsp;ACT | 2012-10-17 | 2016-04-14 | D |  | Utility--Coal fired power plant |  | 4 Diesel-fired quench pumps | 17.21 | Diesel fuel | 252 | HP | Each pump engine is 252 HP. They are limited to emergency use and subject to NSPS Subpart IIII. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.4 | G/HP-H | QP1&QP2 EACH, TEST PROTOCOL | BACT-PSD | NSPS | N | 0 | N | 0.15 | G/HP-H | QP3&QP4 EACH, TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Top ranking option. Note: QP1 = Quench pump#1; QP2= Quench pump#2; QP3=Quench pump#3; QP4 = Quench pump#4.
MI-0400 | WOLVERINE POWER | WOLVERINE POWER SUPPLY COOPERATIVE, INC. | PRESQUE ISLE | MI | 49779 | USA | BRIAN WARNER | 2317755700 X 3336 | BWARNER@WPSCI.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Melissa Byrnes at 517-373-7065 with questions regarding this permit. Thank you. | 317-07 | 4911 | 221112 | 26-14105823 | 09/26/2007 &nbsp;ACT | 06/29/2011 &nbsp;ACT | 2012-10-18 | 2016-04-14 | A |  | Coal-fired power plant. |  | Fire Pump | 17.21 | Diesel | 420 | HP | Maximum operation was based on 500 hours per year. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-H | TEST PROTOCOL; BACT/SIP/NSPS | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | EU-FPENGINE: Diesel fuel fired emergency backup fire pump | 17.21 | diesel fuel | 315 | hp nameplate | This is a diesel fuel fired emergency backup fire mump. It has a capacity of 315 hp, nameplate, and uses diesel fuel ASTM D975 Grade 2-D S15. Ultra low sulfur diesel fuel (15ppmw); 100 hours per year operation for maintenance and readiness testing. NSPS IIII and NESHAP ZZZZ. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Proper combustion design and ultra low sulfur diesel fuel. | 0.15 | G/HP-H | TEST PROTOCOL WILL SPECIFY AVG. TIME | BACT-PSD | NSPS , NESHAP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ultra low sulfur diesel fuel (15 pppmw); 100 hours per year operation for maintenance and readiness testing; NSPS IIII and NESHAP ZZZZ
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Emergency Engine --Diesel Fire Pump (EUFPENGINE) | 17.21 | Diesel | 165 | HP | A 165 hoursepower (hp) diesel-fueled emergency engine manufactured in 2013, iwth a heat input of 1.35 MMBTU/hr. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.22 | G/HP-H | TEST PROTOCOL | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 0.15 | G/BHP-H | TEST PROTOCOL WILL SPECIFY AVG TIME. | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | diesel | 500 | H/YR | A 165 horsepower (hp) diesel-fueled emergency engine manufactured in 2016 with a heat input of 1.35 MMBTU/H. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.22 | G/HP-H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (South Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | B | Diesel particulate filter, good combustion practices and meeting NSPS Subpart IIII requirements. | 0.15 | G/BHP-H | HOURLY | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (North Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | B | Diesel particulate filter, good combustion practices and meeting NSPS Subpart IIII requirements. | 0.15 | G/BHP-H | HOURLY | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUFPENGINE: Fire pump engine | 17.21 | Diesel | 399 | BHP | A 399 brake HP diesel-fueled emergency fire pump engine with a model year of 2011 or later, and a displacement of <10 liters/cylinder. The engine is an EPA Tier 3 certified engine subject to NSPS IIII. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | State of the art combustion design | 0.2 | G/KW-H | HOURLY | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MO-0089 | OWENS CORNING INSULATION SYSTEMS, LLC | OWENS CORNING | JASPER | MO | 64804 | USA |  |  |  | 7 | MO001 | MISSOURI DNR, AIR POLL CONTROL PROGRAM | MS. SUSAM HECKENKAMP | (573) 526-3835 | susan.heckenkamp@dnr.mo.gov |  | 052016-003 | 3296 | 327993 | 110069326688 | 11/06/2015 &nbsp;ACT | 05/12/2016 &nbsp;ACT | 2017-11-27 | 2018-05-11 | A | http://dnr.mo.gov/env/apcp/air_permits.htm |  | PM facility wide emissions (FWE) of 265.19 tpy is for PM10, not just PM filterable which is 93.46 tpy. | emergency engines | 17.21 | ULSD | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | good operating practices | 0 | G/KW |  | BACT-PSD | NSPS | N | 0 | U | 0 | LB/H |  | 0 |  |  | 0 | 0 | N |  | PM filterable, CO, NOx BACT limits equal to NSPS IIII standards. PM10 total, PM2.5 total, SO2, VOC, and CO2e BACT limits assigned based upon good operating practices, ULSD, and installation of Tier 3 (40 CFR 89) or Tier 4 (40 CFR 1039) engines.
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | Emergency diesel fire pump | 17.21 | Ultra Low Sulfur Distillate oil | 0 |  | The fire pump has a maximum heat input rate of 2.63 MMBtu/hr (approximately 250 HP) and is permitted for 100 hrs per year for testing and maintenance | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of Ultra low sulfur distillate oil | 0.15 | G/B-HP-H |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.099 | LB/H |  | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110000801614 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Emergency Diesel Fire Pump | 17.21 | ULSD | 100 | H/YR | Maximum heat Input Rate = 2.6 MMBtu/hr | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | use of ULSD a clean burning fuel, and limited hours of operation | 0.1 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | EMERGENCY GENERATOR DIESEL | 17.21 | DIESEL OIL | 0 | 100 H/YR |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of Ultra Low Sulfur Diesel (ULSD) Oil a clean burning fuel and limited hours of operation | 0.661 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | EMERGENCY DIESEL FIRE PUMP | 17.21 | ULSD | 100 | H/YR | ULSD: Ultra low sulfur diesel | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of Ultra Low Sulfur Diesel (ULSD) Oil a clean burning fuel and limited hours of operation | 0.108 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0103 | CRICKET VALLEY ENERGY CENTER | CRICKET VALLEY ENERGY CENTER LLC | USA | NY | 12522-0407 | USA |  | 845-877-0596 | INFO@CRICKETVALLEY.COM | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-1326-00275/00009 | 4911 | 221112 | 110043340364 | 02/03/2016 &nbsp;ACT | 02/03/2016 &nbsp;ACT | 2017-08-24 | 2017-09-28 | A | http://www.dec.ny.gov/chemical/32249.html | Cricket Valley Energy Center LLC (CVEC) constructed the Cricket Valley Energy Center (the Facility), a nominal net 1,000-megawatt (MW) combined-cycle gas turbine electric generating facility, on a site located in Dover, Dutchess County, New York. The Facility consists of three General Electric (GE) Model 7FA.05 combustion turbine generators (CTGs) operating in combined-cycle mode with supplemental firing of the heat recovery steam generators (HRSGs); natural gas will be the sole fuel fired in the CTGs and duct burners. The Facility will include a natural gas-fired auxiliary boiler, four ultra-low sulfur distillate (ULSD) fired black-start generator engines and a ULSD-fired emergency fire pump engine. In addition to the air emitting equipment, the Facility will include three steam turbine generators (STGs), an air cooled condenser (ACC) and associated auxiliary equipment and systems. Each combined cycle generating unit consisting of the CTG, HRSG and STG will be exhausted through its own stack. Air emissions from the proposed Facility primarily consist of products of combustion from the CTGs, HRSG duct burners, and ancillary combustion sources. Dutchess County is designated as in attainment with respect to the National Ambient Air Quality Standards (NAAQS) for all criteria pollutants with the exception of ozone. Based upon the potential to emit (PTE) estimates, the Facility is subject to Prevention of Significant Deterioration (PSD) requirements for emissions of carbon monoxide (CO); nitrogen oxides (NOx); particulate matter (PM) with a diameter equal to or less than 10 microns (PM10), PM with a diameter equal to or less than 2.5 microns (PM2.5); greenhouse gases (GHG); sulfuric acid mist (H2SO4); and volatile organic compounds (VOC). In accordance with the NYSDECâ€™s Nonattainment New Source Review (NNSR) permitting program, the Facility is also subject to NNSR for emissions of NOx and VOC. |  | Emergency fire pump | 17.21 | ultra low sulfur diesel | 460 | hp |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Compliance demonstrated with vendor emission certification and adherence to vendor-specified maintenance recommendations. | 0.087 | G/BHP-H | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0104 | CPV VALLEY ENERGY CENTER | CPV VALLEY LLC | ORANGE | NY | 10940 | USA |  |  |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-335600136/00001 | 4911 | 221112 | 110043332471 | 08/01/2013 &nbsp;ACT | 08/01/2013 &nbsp;ACT | 2017-08-25 | 2017-09-28 | A |  | CPV Valley Energy Center is a 680 MW combined cycle electric generating facility located in Middletown, NY. The combustion turbines are rated at 2,234 MMBTU/H firing natural gas and 2,145 MMBTU/H firing diesel fuel. The duct burners are rated for 500 MMBTU/H firing natural gas. In addition to the turbines their emission limits for the auxiliary boiler (73.5 MMBTU/H), emergency generator, fire pump, and gas heater. | State Facility Permit | Fire pump | 17.21 | ultra low sulfur diesel | 0 |  |  | Particulate matter, filterable (FPM) | Other - Methods 201/201A and 202 | (Particulate Matter (PM)) | PM | P | Ultra low sulfur diesel with maximum sulfur content 0.0015 percent. | 0.043 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Also PM-10.
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Fire pump engine | 17.21 | Ultra-low sulfur diesel | 15 | gal/hr |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.11 | GM/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.002 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
PR-0009 | ENERGY ANSWERS ARECIBO PUERTO RICO RENEWABLE ENERGY PROJECT | ENERGY ANSWERS ARECIBO, LLC | ARECIBO | PR |  | USA | MARK GREEN | (347)-351-5248 |  | 2 | OT003 | EPA REGION II | MR. FRANK JON | (212)637-4085 | jon.frank@epa.gov | Ms. Viorica Petriman petriman.viorica@epa.gov | R2-PSD 1 | 4953 | 221119 | FRL-9911-10-Region 2 | 11/11/2012 &nbsp;ACT | 04/10/2014 &nbsp;ACT | 2014-10-14 | 2016-05-05 | A |  | Energy Answers Arecibo is a new resource recovery facility capable of producing up to 77 megawatts (MW) of electrical power while combusting municipal solid waste, as the primary fuel. | This is a PSD permit for a new/greenfield facility. | Emergency Diesel Fire Pump | 17.21 | ULSD Fuel Oil #2 | 0 |  | The Emergency Fire Pump is rated at 335 BHP and limited to 500 hr/yr (emergency operations and testing and maintenance, combined). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/B-HP-H |  | BACT-PSD |  | U | 0 | U | 0.11 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Opacity of emissions from the emergency diesel fire pump's stack shall not exceed 20% except for one period of no more than six (6) minutes in any sixty (60) minute interval when opacity shall not exceed 27%. The opacity shall be measured annually by using EPA Method 9.
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Life Boat Diesel Engines - C.R. Luigs | 17.21 | diesel | 39 | hp |  | Particulate matter, fugitive | Unspecified |  | PM | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Diesel Fired Well Pump | 17.21 | Diesel | 2.7 | MMBTU/H | 2.7 MMBtu/hr Diesel Fired Well Pump. Installed in 1966. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Limited Operation of 168 hr/yr. | 0.31 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*AK-0084 | DONLIN GOLD PROJECT | DONLIN GOLD LLC. | BETHEL CENSUS AREA | AK | 99575 | USA | STAN FOO | 907-273-0200 | SFOO@DONLINGOLD.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | AK DEC DIV. OF AIR QUALITY 410 WILLOUGHBY AVE. SUITE 303 JUNEAU, AK 99801 | AQ0934CPT01 | 1041 | 212221 | Not Entered | 10/15/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2018-06-21 | 2018-06-22 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16763360/d1h2U6BIY-j857LFU-WYmw2 | The Donlin Gold Project is a gold mine located 12 miles north of Crooked Creek, Alaska on the Kuskokwim River, about 280 miles northwest of Anchorage. The deposit has proven and probable reserves estimated at 33.9 million ounces of gold at 2.1 g/t and could produce up to 1.5 million ounces annually. SIC Code 1041; NAICS Code 212221. |  | Fire Pump Diesel Internal Combustion Engines | 17.21 | Diesel | 252 | hp | Three (3) 252 hp fire pump diesel internal combustion engines. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean Fuel and Good Combustion Practices | 0.19 | G/KW-HR | 3-HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Subpart IIII engines
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | EMERGENCY FIREWATER PUMP ENGINE | 17.21 | DIESEL | 288 | HP |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE ULTRA LOW SULFUR FUEL NOT TO EXCEED 15 PPMVD FUEL SULFUR, OPERATIONAL LIMIT OF 50 HRS/YR | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.21 | DIESEL | 182 | HP | UNIT IS 135 KW. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | USE ULTRA LOW SULFUR FUEL | 0.2 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Port and Stb Fwd and Aft Crane Diesel Engines - C.R. Luigs | 17.21 | diesel | 305 | HP |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 5.88 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - Development Driller 1 | 17.21 | Diesel | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger, and high pressure fuel injection with aftercooler | 0.25 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - C.R. Luigs | 17.21 | diesel | 0 |  | Cementing Units: Caterpillar 3412 CDITA 860 hp 2001 Nitrogen Pump: Caterpillar 3406 CDITA 490 hp 2000 | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger, and high pressure fuel injection with aftercooler | 0.23 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.2 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.03 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 0.1 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/BHP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/BHP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | EMERGENCY FIRE PUMP ENGINE | 17.21 | DISTILLATE OIL | 0 |  | 425 HP | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.16 | G/HP-H |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | DIESEL BURNED SHALL NOT EXCEED 1,128 GALLONS PER 12 CONSECUTIVE MONTH PERIOD
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Emergency diesel engine | 17.21 | diesel | 750 | KW | One (1) 1102 HP (750 KW) emergency diesel engine | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur fuel oil (<15 ppm sulfur) | 0.15 | G PER BHP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0030 | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | GRANT | KS | 67601 | USA | PAUL REYNOLDS | 620-277-4522 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Mindy Bowman, E-mail address: Mindy.Bowman@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-13309 | 4911 | 221112 | Not Found | 03/07/2017 &nbsp;ACT | 03/31/2016 &nbsp;ACT | 2017-04-06 | 2017-07-19 | C |  | Mid-Kansas Electric Company, LLC (Mid-Kansas Electric) (Source ID: 0670173) operates the Rubart Station located in Grant County, Kansas. The facility currently consist of twelve (12) new spark ignition four-stroke lean burn (4SLB) reciprocating internal combustion engines (RICE) used to generate electricity (the proposed project consist of 24 new 4SLB RICE). The generating capacity of each unit is 10 megawatts (approximately 13,410 BHP). Also located at the station is a diesel fire pump, natural gas emergency generator, heater, circuit breakers and switches. The insignificant activities include a diesel storage tank. | This PSD permit with tracking number C-13309 a modification of PSD permits C-12896 (PSD Administrative Amendment, issued on 5/7/2015), C-12721 (PSD Revisions, issued on 4/28/2015), and C-10021 (original PSD permit for the proposed project, issued on 1/28/2013). | Compression ignition RICE emergency fire pump | 17.21 | Ultra-lowsulfur diesel (ULSD) | 197 | HP | One (1) compression ignition emergency fire pump engine, rated at 197 HP, which shall burn only ultra-low sulfur diesel (ULSD, 15 ppm sulfur or less). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR | EXCLUDES STARTUP, SHUTDOWN & MALFUNCTION | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | Cummins 6BTA 5.9F-1 Diesel Engine Fire Pump | 17.21 | No. 2 Fuel Oil | 182 | BHP |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | utilize efficient combustion/design technology | 0.25 | G/BHP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | IBERVILLE | LA |  | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: ANTHONY RANDALL, 225-219-3181 | PSD-LA-709(M-1) | 2821 | 325211 | 110020900104 | 03/03/2008 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2006-06-25 | 2009-08-06 | A |  | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | VINYL CHLORIDE - 28.82 TPY. VINYL CHLORIDE (VC) WAS REGULATED AS A PSD POLLUTANT (SIGNIFICANCE LEVEL OF 1 TPY) IN LOUISIANA WHEN THIS PERMIT WAS ISSUED. LOUISIANA'S NSR REFORM RULES, ADOPTED DECEMBER 20, 2005, DELISTED VC. HAPS FROM THE PVC UNIT WERE SUBJECTED TO A 112(J) MACT DETERMINATION AFTER VACATURE OF 40 CFR 63 SUBPART J ON APRIL 19, 2005. BACT FOR VC IS EQUIVALENT TO MACT FOR VC. NNSR: BECAUSE VOC AND NOX EMISSIONS ARE LESS THAN 100 TPY, LAER WAS NOT REQUIRED. OFFSETS WERE REQUIRED PURSUANT TO A STATE-ONLY PROVISION IN LAC 33:III.504. PSD-LA-709(M-1) IS FOR 1) REMOVING A COOLING TOWER (M-8), CORRECTING CAPACITY OF COOLING TOWER M-7, AND 3) INCLUDING 19 EMERGENCY ENGINES AND THREE LOADING HOPPERS. | SMALL EMERGENCY ENGINES | 17.21 | DIESEL |  |  | U-7A, U-7B, U-7C: 420 HP EACH U-8A, U-8B, U-8C: 442 HP EACH U-9: 450 HP; M-16B: 439 HP M-16C, M-16D, M-16E: 180 HP EACH P-28A: 540 HP; P-28B: 340 HP; P28C: 180 HP | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND GASEOUS FUEL BURNING | 0.31 | LB/MMBTU |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002049328 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | EMERGENCY FIRE PUMP | 17.21 | DIESEL | 350 | HP |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | ULTRA LOW SULFUR DIESEL AND GOOD COMBUSTION PRACTICES | 0.15 | G/HP-H | ANNUAL AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0.15 | G/HP-H | ANNUAL AVERAGE | 0 | 0 | N
LA-0301 | LAKE CHARLES CHEMICAL COMPLEX ETHYLENE 2 UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | (281) 588-3761 | ERIC.RODRIGUEZ@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-779 | 2869 | 325110 | 110017418061 | 05/02/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2016-09-27 | 2017-04-28 | B |  |  | Complete application date = date of administrative completeness This RBLC entry addresses Ethylene Unit 2 of the Lake Charles Cracker Project. This unit will produce ethylene by thermally cracking ethane in cracking furnaces. | Firewater Pump Nos. 1-3 (EQTs 997, 998, &amp; 999) | 17.21 | Diesel | 500 | HP | Non-emergency use operating time is limited to 100 hr/yr (per engine). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Compliance with 40 CFR 60 Subpart IIII and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage | 0.17 | LB/HR | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.01 | TPY | ANNUAL MAXIMUM | 0.15 | G/BHP-HR |  | 0 | 0 | N |  | BACT is determined to be compliance with the limitations imposed by 40 CFR 60 Subpart IIII and its associated monitoring, recordkeeping, and reporting requirements; and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage.
LA-0308 | MORGAN CITY POWER PLANT | LOUISIANA ENERGY AND POWER AUTHORITY (LEPA) | ST. MARY | LA | 70380 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-767 | 4911 | 221112 | Not Found | 09/24/2012 &nbsp;ACT | 09/26/2013 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  |  |  | 380 HP Diesel Fired Pump Engine | 17.21 | Diesel | 2.3 | MMBTU/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion and maintenance practices, and compliance with NSPS 40 CFR 60 Subpart IIII | 0.15 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0.01 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.441 lb/MWh (12 month average)
LA-0309 | BENTELER STEEL TUBE FACILITY | BENTELER STEEL / TUBE MANUFACTURING CORPORATION | CADDO | LA | 71115 | USA | MYRNA PACHECO PONCE DE LEON | 318-216-4206 | MYRNA.PACHECO@BENTELER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen - 225-219-3395 | PSD-LA-774(M1) | 3312 | 331111 | 110055592318 | 02/09/2015 &nbsp;ACT | 06/04/2015 &nbsp;ACT | 2017-03-09 | 2017-04-28 | A |  | A facility to produce 600,000 metric tons per year of seamless steel pipe from purchased billets. A steel production facility (including an electric arc furnace (EAF)) was added. | Permit PSD-LA-774 was issued on May 17, 2013 for the construction of the hot rolling mill. An EAF was authorized this time. | Firewater Pump Engines | 17.21 | Diesel | 288 | hp (each) |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Complying with 40 CFR 60 Subpart IIII | 0.15 | G/BHP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel Firewater pump engines (6 units) | 17.21 | diesel | 425 | hp |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel emergency generator engine - EGEN | 17.21 | diesel | 350 | hp |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110029511883 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | firewater pump engines (8 units) | 17.21 | diesel | 460 | hp |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Complying with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0323 | MONSANTO LULING PLANT | MONSANTO COMPANY | ST. CHARLES PARISH | LA | 70070 | USA | ENRIQUE WEHLEN | 9857858211 | ENRIGUE.WEHLEN@MONSANTO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-890 | 2879 | 325320 | 110067118274 | 09/21/2015 &nbsp;ACT | 01/09/2017 &nbsp;ACT | 2017-09-26 | 2018-05-11 | D | http://edms.deq.louisiana.gov/app/doc/view.aspx?doc=10460194&ob=yes | Chemical Manufacture | Dicamba Manufacturing Facility expansion project. | Standby Generator No. 9 Engine | 17.21 | Diesel Fuel | 400 | hp | Operating hours limited to 100 hours/yr for ready testing. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Proper operation and limits on hours of operation for emergency engines and compliance with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000310459 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Fire Pump Engine | 17.21 | ULSD | 2.7 | MMBTU/H | â‰¤ 300 hours of operation per 12-month rolling period S in ULSD: â‰¤0.0015% by weight | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | GM/BHP-H | 1 HR BLOCK AVERAGE | BACT-PSD | NSPS , NESHAP , SIP , OPERATING PERMIT | U | 0 | U | 0.12 | LB/H | 1 HR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | EMERGENCY GENERATOR | 17.21 | ULTRA-LOW SULFUR DIESEL | 1500 | KW | 40 CFR 60 SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULTRA LOW SULFUR FUEL AND GOOD COMBUSTION PRACTICES | 0.15 | G/HP-H | N/A | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA-LOW SULFUR DIESEL | 300 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULTRA LOW SULFUR FUEL AND GOOD COMBUSTION PRACTICES | 0.15 | G/HP-H | N/A | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA LOW SULFUR DIESEL | 477 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULSD FUEL, GOOD COMBUSTION PRACTICES, LIMITED HOURS OF OPERATION, AND DESIGNED TO ACHIEVE EMISSION LIMITS | 0.15 | G/HP-H |  | BACT-PSD | NSPS |  | 0 |  | 0.23 | G/KW-H |  | 0 |  |  | 0 | 0 | N |  | NSPS 40 CFR 60 SUBPART IIII
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 5 EMERGENCY FIRE WATER PUMP ENGINES | 17.21 | ULTRA LOW SULFUR DIESEL | 350 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULSD FUEL, GOOD COMBUSTION PRACTICES AND DESIGNED TO ACHIEVE EMISSION LIMITS | 0.17 | G/BHP-H |  | BACT-PSD |  |  | 0 |  | 0.23 | G/KW-H |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY GENERATOR | 17.21 | ULTRA-LOW SULFUR DIESEL | 1490 | HP | 40 CFR 60 SUBPART IIII, 40 CFR 63 SUBPART ZZZZ ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULTRA LOW SULFUR FUEL AND GOOD COMBUSTION PRACTICES. | 0.18 | G/HP-H |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA-LOW SULFUR DIESEL | 305 | HP | 40 CFR 60, SUBPART IIII, 40 CFR 63 SUBPART ZZZZ, ULTRA LOW-SULFURDIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULTRA LOW SULFUR FUEL AND GOOD COMBUSTION PRACTICES. | 0.18 | G/HP-H |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | DIESEL-FIRED AUXILIARY (EMERGENCY) ENGINES (TWO) | 17.21 | ULTRA-LOW SULFUR DIESEL | 1500 | KW | TWO DIESEL-FIRED AUXILIARY GENERATORS (EMERGENCY GENERATORS), EACH RATED AT NOMINAL 1,500-KILOWATT (KW) SUBJECT TO 40 CFR 60 SUBPART IIII, 40 CFR 63 SUBPART ZZZZ ULTRA LOW-SULFUR DIESEL FUEL | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | USE OF ULTRA LOW SULFUR DIESEL AND GOOD COMBUSTION PRACTICES. | 0.18 | G/HP-H |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | DIESEL-FIRED FIRE PUMP ENGINE | 17.21 | ULTRA-LOW SULFUR DIESEL | 300 | HP | ONE DIESEL-FIRED FIRE PUMP ENGINE, RATED AT A NOMINAL 300-HORSEPOWER. SUBJECT TO 40 CFR 63 SUBPART ZZZZ. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULTRA LOW SULFUR DIESEL FUEL AND GOOD COMBUSTION PRACTICES | 0.18 | G/HP-H |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0389 | KARN WEADOCK GENERATING COMPLEX | CONSUMERS ENERGY | BAY | MI | 48732-9601 | USA | JAMES M. WALKER | 5177880428 | JMWALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | FOR TECHNICAL QUESTIONS ABOUT THIS PERMIT, PLEASE CONTACT THE PERMIT ENGINEER - DAVID K. RIDDLE RIDDLED@MICHIGAN.GOV (517-373-7081) | 341-07 | 4911 | 221112 | 26-01700033 | 10/15/2007 &nbsp;ACT | 12/29/2009 &nbsp;ACT | 2010-03-08 | 2010-12-16 | U |  | ELECTRICITY GENERATING FACILITY, EXISTING CAPACITY GREATER THAN 2,000 MW. | AFTER CONSTRUCTION CONSUMERS WILL RETIRE 5 TO 7 COAL-FIRED BOILERS (638 - 958 MW) STATEWIDE. FINAL CONDITIONS WILL BE AT WWW.DEQ.STATE.MI.US/APS/FINALCONDITIONS.SHTML. MATERIAL HANDLING - CONTACT PERMIT ENGINEER FOR TECHNICAL INFORMATION (DAVID RIDDLE, 517-373-7081). INCLUDES 9 EMISSION UNITS. COAL, LIMESTONE, SORBENT AND ASH HANDLING PROCESSES. VARIOUS BACT LIMITS FOR OPACITY, PM AND PM10. BACT FOR THE MATERIAL HANDLING EQUIPMENT CONSISTED OF A COMBINATION OF PASSIVE CONTROL EQUIPMENT SUCH AS WET/CHEMICAL SUPPRESSION SYSTEMS AND ENCLOSED CONVEYORS; AND ACTIVE CONTROL SUCH AS FABRIC FILTERS. ACTIVE CONTROL IS LIMITED TO 0.004 GR/DSCF. | FIRE BOOSTER PUMP | 17.21 | ULTRA LOW SULFUR DIESEL | 40 | KW | OPERATIONAL LIMITS 1 HR/DAY AND 500 HRS/YR FOR PM2.5 NAAQS. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | ENGINE DESIGN AND OPERATION. 15 PPM SULFUR FUEL. | 0.31 | LB/MMBTU | TEST METHOD | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0399 | DETROIT EDISON--MONROE | DETROIT EDISON | MONROE | MI | 48161-1970 | USA | LILLIAN WOOLLEY | 313-235-5611 | WOOLLEYL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Julie Brunner at 517-373-7088 with questions related to the permit. Thank you. | 93-09A | 4911 | 221112 | 26-11500020 | 09/29/2010 &nbsp;ACT | 12/21/2010 &nbsp;ACT | 2012-10-17 | 2016-04-14 | D |  | Utility--Coal fired power plant |  | 4 Diesel-fired quench pumps | 17.21 | Diesel fuel | 252 | HP | Each pump engine is 252 HP. They are limited to emergency use and subject to NSPS Subpart IIII. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.4 | G/HP-H | QP1&QP2, EACH; TEST PROTOCOL | BACT-PSD | NSPS , OTHER | N | 0 | N | 0.15 | G/HP-H | QP3&QP4, EACH; TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Top ranking option Note: QP1=Quench pump #1; QP2=Quench pump#2; QP3=Quench pump#3; QP4=Quench pump#4.
MI-0400 | WOLVERINE POWER | WOLVERINE POWER SUPPLY COOPERATIVE, INC. | PRESQUE ISLE | MI | 49779 | USA | BRIAN WARNER | 2317755700 X 3336 | BWARNER@WPSCI.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Melissa Byrnes at 517-373-7065 with questions regarding this permit. Thank you. | 317-07 | 4911 | 221112 | 26-14105823 | 09/26/2007 &nbsp;ACT | 06/29/2011 &nbsp;ACT | 2012-10-18 | 2016-04-14 | A |  | Coal-fired power plant. |  | Fire Pump | 17.21 | Diesel | 420 | HP | Maximum operation was based on 500 hours per year. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.14 | LB/H | TEST PROTOCOL; BACT | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | EU-FPENGINE: Diesel fuel fired emergency backup fire pump | 17.21 | diesel fuel | 315 | hp nameplate | This is a diesel fuel fired emergency backup fire mump. It has a capacity of 315 hp, nameplate, and uses diesel fuel ASTM D975 Grade 2-D S15. Ultra low sulfur diesel fuel (15ppmw); 100 hours per year operation for maintenance and readiness testing. NSPS IIII and NESHAP ZZZZ. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Proper combustion design and ultra low sulfur diesel fuel | 0.6 | LB/H | TEST PROTOCOL WILL SPECIFY AVG. TIME | BACT-PSD | NSPS , NESHAP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ultra low sulfur diesel fuel (15 pppmw); 100 hours per year operation for maintenance and readiness testing; NSPS IIII and NESHAP ZZZZ.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Emergency Engine --Diesel Fire Pump (EUFPENGINE) | 17.21 | Diesel | 165 | HP | A 165 hoursepower (hp) diesel-fueled emergency engine manufactured in 2013, iwth a heat input of 1.35 MMBTU/hr. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.09 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.57 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | diesel | 500 | H/YR | A 165 horsepower (hp) diesel-fueled emergency engine manufactured in 2016 with a heat input of 1.35 MMBTU/H. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.09 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (South Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | Diesel particulate filter, good combustion practices and meeting NSPS Subpart IIII requirements. | 0.66 | LB/H | HOURLY | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An oxidation catalyst is $39,500/ton for PM10, CO and VOC together.
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (North Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | Diesel particulate filter, good combustion practices and meeting NSPS Subpart IIII requirements. | 0.66 | LB/H | HOURLY | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An oxidation catalyst is $39,500/ton for PM10, CO and VOC together.
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUFPENGINE: Fire pump engine | 17.21 | Diesel | 399 | BHP | A 399 brake HP diesel-fueled emergency fire pump engine with a model year of 2011 or later, and a displacement of <10 liters/cylinder. The engine is an EPA Tier 3 certified engine subject to NSPS IIII. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | State of the art combustion design. | 0.13 | LB/H | HOURLY | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | firewater pumps, diesel | 17.21 | diesel | 325 | HP, EACH | Eight 325 hp diesel firewater pumps | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | comply with NSPS IIII, 52 hr/yr non-emergency operation
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | Emergency diesel fire pump | 17.21 | Ultra Low Sulfur Distillate oil | 0 |  | The fire pump has a maximum heat input rate of 2.63 MMBtu/hr (approximately 250 HP) and is permitted for 100 hrs per year for testing and maintenance | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of ultra low sulfur distillate oil | 0.15 | G/B-HP-H |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.099 | LB/H |  | 0 |  |  | 0 | 0 | N
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110000801614 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Emergency Diesel Fire Pump | 17.21 | ULSD | 100 | H/YR | Maximum heat Input Rate = 2.6 MMBtu/hr | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | use of ULSD a clean burning fuel, and limited hours of operation | 0.1 | LB/H |  | BACT-PSD | OPERATING PERMIT , NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | EMERGENCY GENERATOR DIESEL | 17.21 | DIESEL OIL | 0 | 100 H/YR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of Ultra Low Sulfur Diesel (ULSD) Oil a clean burning fuel and limited hours of operation | 0.661 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | EMERGENCY DIESEL FIRE PUMP | 17.21 | ULSD | 100 | H/YR | ULSD: Ultra low sulfur diesel | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of Ultra Low Sulfur Diesel (ULSD) Oil a clean burning fuel and limited hours of operation | 0.108 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | Emergency fire pump engine | 17.21 | diesel | 300 | HP | 223.8 kW. Emergency fire pump engine restricted to 500 hours of operation per rolling 12 months. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Purchased certified to the standards in NSPS Subpart IIII | 0.1 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.025 | T/YR | PER ROLLING 12-MONTHS | 0 |  | SEE NOTES | 0 | 0 | N |  | Additional limit: 0.20 g PM10/kW-H NSPS standard If required Methods 201 or 201A and 202
OK-0129 | CHOUTEAU POWER PLANT | ASSOCIATED ELECTRIC COOPERATIVE INC | MAYES | OK | 74362 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2007-115-C(M-1)PSD | 4911 | 221112 | 4009700017 | 06/19/2008 &nbsp;ACT | 01/23/2009 &nbsp;ACT | 2009-11-20 | 2010-02-18 | B |  |  |  | EMERGENCY FIRE PUMP (267-HP DIESEL) | 17.21 | LOW SULFUR DIESEL | 267 | HP |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.24 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 0.4 | G/HP-H | NSPS | 0 |  |  | 0 | 0 | N
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Fire pump engine | 17.21 | Ultra-low sulfur diesel | 15 | gal/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.11 | GM/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.002 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
PR-0009 | ENERGY ANSWERS ARECIBO PUERTO RICO RENEWABLE ENERGY PROJECT | ENERGY ANSWERS ARECIBO, LLC | ARECIBO | PR |  | USA | MARK GREEN | (347)-351-5248 |  | 2 | OT003 | EPA REGION II | MR. FRANK JON | (212)637-4085 | jon.frank@epa.gov | Ms. Viorica Petriman petriman.viorica@epa.gov | R2-PSD 1 | 4953 | 221119 | FRL-9911-10-Region 2 | 11/11/2012 &nbsp;ACT | 04/10/2014 &nbsp;ACT | 2014-10-14 | 2016-05-05 | A |  | Energy Answers Arecibo is a new resource recovery facility capable of producing up to 77 megawatts (MW) of electrical power while combusting municipal solid waste, as the primary fuel. | This is a PSD permit for a new/greenfield facility. | Emergency Diesel Fire Pump | 17.21 | ULSD Fuel Oil #2 | 0 |  | The Emergency Fire Pump is rated at 335 BHP and limited to 500 hr/yr (emergency operations and testing and maintenance, combined). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/B-HP-H |  | BACT-PSD |  | U | 0 | U | 0.11 | LB/H |  | 0 |  |  | 0 | 0 | N
VA-0319 | GATEWAY COGENERATION 1, LLC - SMART WATER PROJECT | GATEWAY GREEN ENERGY | PRINCE GEORGE | VA | 23875-3000 | USA | T. EDWARD MCDANIEL | 972-638-8798 | EMCDANIEL@GGEHLLC.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52375-002 | 4911 | 221112 | 110045446718 | 01/11/2012 &nbsp;ACT | 08/27/2012 &nbsp;ACT | 2013-01-16 | 2015-05-29 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Combined cycle electrical power generating facility (160 MW), consisting of two combusion turbines (Rolls Royce Trent 60 WLE) with associated HRSG and no duct burning. |  | FIRE WATER PUMP | 17.21 | diesel (ultra low sulfur) | 1.86 | MMBTU/H | 500 H/Yr operation | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean burning ULSD fuel and good combusion practices | 0.15 | G/HP-H |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Diesel Fired Well Pump | 17.21 | Diesel | 2.7 | MMBTU/H | 2.7 MMBtu/hr Diesel Fired Well Pump. Installed in 1966. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Limited Operation of 168 hr/yr. | 0.31 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*AK-0084 | DONLIN GOLD PROJECT | DONLIN GOLD LLC. | BETHEL CENSUS AREA | AK | 99575 | USA | STAN FOO | 907-273-0200 | SFOO@DONLINGOLD.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | AK DEC DIV. OF AIR QUALITY 410 WILLOUGHBY AVE. SUITE 303 JUNEAU, AK 99801 | AQ0934CPT01 | 1041 | 212221 | Not Entered | 10/15/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2018-06-21 | 2018-06-22 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16763360/d1h2U6BIY-j857LFU-WYmw2 | The Donlin Gold Project is a gold mine located 12 miles north of Crooked Creek, Alaska on the Kuskokwim River, about 280 miles northwest of Anchorage. The deposit has proven and probable reserves estimated at 33.9 million ounces of gold at 2.1 g/t and could produce up to 1.5 million ounces annually. SIC Code 1041; NAICS Code 212221. |  | Fire Pump Diesel Internal Combustion Engines | 17.21 | Diesel | 252 | hp | Three (3) 252 hp fire pump diesel internal combustion engines. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean Fuel and Good Combustion Practices | 0.19 | G/KW-HR | 3-HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Subpart IIII engines
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | EMERGENCY FIREWATER PUMP ENGINE | 17.21 | DIESEL | 135 | KW | 135 KW (182 hp) IC Diesel-fired Emergency Firewater Pump Engine | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA Method 5 and 202, or CTM 039 or CTM 040 | (Particulate Matter (PM)) | PM | P | OPERATIONAL RESTRICTION OF 50 HR/YR, OPERATE AS REQUIRED FOR FIRE SAFETY TESTING | 0.2 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.21 | DIESEL | 182 | HP | UNIT IS 135 KW. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | USE ULTRA LOW SULFUR FUEL | 0.2 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Port and Stb Fwd and Aft Crane Diesel Engines - C.R. Luigs | 17.21 | diesel | 305 | HP |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 5.88 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - Development Driller 1 | 17.21 | Diesel | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger, and high pressure fuel injection with aftercooler | 0.25 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - C.R. Luigs | 17.21 | diesel | 0 |  | Cementing Units: Caterpillar 3412 CDITA 860 hp 2001 Nitrogen Pump: Caterpillar 3406 CDITA 490 hp 2000 | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger, and high pressure fuel injection with aftercooler | 0.22 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and 28 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.2 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.03 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 0.1 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/BHP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/BHP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Emergency diesel engine | 17.21 | diesel | 750 | KW | One (1) 1102 HP (750 KW) emergency diesel engine | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur fuel oil (<15 ppm sulfur) | 0.15 | G PER BHP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0030 | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | GRANT | KS | 67601 | USA | PAUL REYNOLDS | 620-277-4522 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Mindy Bowman, E-mail address: Mindy.Bowman@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-13309 | 4911 | 221112 | Not Found | 03/07/2017 &nbsp;ACT | 03/31/2016 &nbsp;ACT | 2017-04-06 | 2017-07-19 | C |  | Mid-Kansas Electric Company, LLC (Mid-Kansas Electric) (Source ID: 0670173) operates the Rubart Station located in Grant County, Kansas. The facility currently consist of twelve (12) new spark ignition four-stroke lean burn (4SLB) reciprocating internal combustion engines (RICE) used to generate electricity (the proposed project consist of 24 new 4SLB RICE). The generating capacity of each unit is 10 megawatts (approximately 13,410 BHP). Also located at the station is a diesel fire pump, natural gas emergency generator, heater, circuit breakers and switches. The insignificant activities include a diesel storage tank. | This PSD permit with tracking number C-13309 a modification of PSD permits C-12896 (PSD Administrative Amendment, issued on 5/7/2015), C-12721 (PSD Revisions, issued on 4/28/2015), and C-10021 (original PSD permit for the proposed project, issued on 1/28/2013). | Compression ignition RICE emergency fire pump | 17.21 | Ultra-lowsulfur diesel (ULSD) | 197 | HP | One (1) compression ignition emergency fire pump engine, rated at 197 HP, which shall burn only ultra-low sulfur diesel (ULSD, 15 ppm sulfur or less). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR | EXCLUDES STARTUP, SHUTDOWN & MALFUNCTION | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002049328 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | EMERGENCY FIRE PUMP | 17.21 | DIESEL | 350 | HP |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | ULTRA LOW SULFUR DIESEL AND GOOD COMBUSTION PRACTICES | 0.15 | G/HP-H | ANNUAL AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0.15 | G/HP-H | ANNUAL AVERAGE | 0 | 0 | N
LA-0301 | LAKE CHARLES CHEMICAL COMPLEX ETHYLENE 2 UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | (281) 588-3761 | ERIC.RODRIGUEZ@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-779 | 2869 | 325110 | 110017418061 | 05/02/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2016-09-27 | 2017-04-28 | B |  |  | Complete application date = date of administrative completeness This RBLC entry addresses Ethylene Unit 2 of the Lake Charles Cracker Project. This unit will produce ethylene by thermally cracking ethane in cracking furnaces. | Firewater Pump Nos. 1-3 (EQTs 997, 998, &amp; 999) | 17.21 | Diesel | 500 | HP | Non-emergency use operating time is limited to 100 hr/yr (per engine). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Compliance with 40 CFR 60 Subpart IIII and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage | 0.17 | LB/HR | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.01 | TPY | ANNUAL MAXIMUM | 0.15 | G/BHP-HR |  | 0 | 0 | N |  | BACT is determined to be compliance with the limitations imposed by 40 CFR 60 Subpart IIII and its associated monitoring, recordkeeping, and reporting requirements; and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage.
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Genenerator Engine DEG-16-1 (EQT035) | 17.21 | Diesel | 460 | horsepower | Limit operations to 100 hrs/yr | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Meet NSPS Subpart IIII Limitations and Good Combustion Practices | 0.18 | LB/H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.01 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | 0.2 g/hp-hr
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Pump Engines DFP-16-1 (EQT036) | 17.21 | Diesel | 225 | horsepower | Limit operations to 100 hour/year | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Meet NSPS Subpart IIII Limitations and Good Combustion Practices | 0.09 | LB/H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.01 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | 0.15 g/hp-hr
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Pump Engine DFP-16-2 (EQT037) | 17.21 | Diesel | 225 | horsepower | Limit operations to 100 hr/yr | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Meet NSPS Subpart IIII Limitations and Good Combustion Practices | 0.09 | LB/H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.01 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | 0.15 g/hp-hr
LA-0309 | BENTELER STEEL TUBE FACILITY | BENTELER STEEL / TUBE MANUFACTURING CORPORATION | CADDO | LA | 71115 | USA | MYRNA PACHECO PONCE DE LEON | 318-216-4206 | MYRNA.PACHECO@BENTELER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen - 225-219-3395 | PSD-LA-774(M1) | 3312 | 331111 | 110055592318 | 02/09/2015 &nbsp;ACT | 06/04/2015 &nbsp;ACT | 2017-03-09 | 2017-04-28 | A |  | A facility to produce 600,000 metric tons per year of seamless steel pipe from purchased billets. A steel production facility (including an electric arc furnace (EAF)) was added. | Permit PSD-LA-774 was issued on May 17, 2013 for the construction of the hot rolling mill. An EAF was authorized this time. | Firewater Pump Engines | 17.21 | Diesel | 288 | hp (each) |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Complying with 40 CFR 60 Subpart IIII | 0.15 | G/BHP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel Firewater pump engines (6 units) | 17.21 | diesel | 425 | hp |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel emergency generator engine - EGEN | 17.21 | diesel | 350 | hp |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110029511883 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | firewater pump engines (8 units) | 17.21 | diesel | 460 | hp |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Complying with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0323 | MONSANTO LULING PLANT | MONSANTO COMPANY | ST. CHARLES PARISH | LA | 70070 | USA | ENRIQUE WEHLEN | 9857858211 | ENRIGUE.WEHLEN@MONSANTO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-890 | 2879 | 325320 | 110067118274 | 09/21/2015 &nbsp;ACT | 01/09/2017 &nbsp;ACT | 2017-09-26 | 2018-05-11 | D | http://edms.deq.louisiana.gov/app/doc/view.aspx?doc=10460194&ob=yes | Chemical Manufacture | Dicamba Manufacturing Facility expansion project. | Standby Generator No. 9 Engine | 17.21 | Diesel Fuel | 400 | hp | Operating hours limited to 100 hours/yr for ready testing. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Proper operation and limits on hours of operation for emergency engines and compliance with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000310459 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Fire Pump Engine | 17.21 | ULSD | 2.7 | MMBTU/H | â‰¤ 300 hours of operation per 12-month rolling period S in ULSD: â‰¤0.0015% by weight | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | GM/BHP-H | 1 HR BLOCK AVERAGE | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 0.12 | LB/H | 1 HR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA LOW SULFUR DIESEL | 477 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULSD FUEL, GOOD COMBUSTION PRACTICES, LIMITED HOURS OF OPERATION, AND DESIGNED TO ACHIEVE EMISSION LIMITS | 0.15 | G/HP-H |  | BACT-PSD | NSPS |  | 0 |  | 0.23 | G/KW-H |  | 0 |  |  | 0 | 0 | N |  | NSPS 40 CFR 60 SUBPART IIII
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 5 EMERGENCY FIRE WATER PUMP ENGINES | 17.21 | ULTRA LOW SULFUR DIESEL | 350 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULSD FUEL, GOOD COMBUSTION PRACTICES AND DESIGNED TO ACHIEVE EMISSION LIMITS | 0.17 | G/BHP-H |  | BACT-PSD |  |  | 0 |  | 0.23 | G/KW-H |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY GENERATOR | 17.21 | ULTRA-LOW SULFUR DIESEL | 1490 | HP | 40 CFR 60 SUBPART IIII, 40 CFR 63 SUBPART ZZZZ ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULTRA LOW SULFUR FUEL AN DGOOD COMBUSTION PRACTICES | 0.18 | G/HP-H |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA-LOW SULFUR DIESEL | 305 | HP | 40 CFR 60, SUBPART IIII, 40 CFR 63 SUBPART ZZZZ, ULTRA LOW-SULFURDIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | EXCLUSIVE USE OF ULTRA LOW SULFUR FUEL AND GOOD COMBUSTION PRACTICES | 0.18 | G/HP-H |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0400 | WOLVERINE POWER | WOLVERINE POWER SUPPLY COOPERATIVE, INC. | PRESQUE ISLE | MI | 49779 | USA | BRIAN WARNER | 2317755700 X 3336 | BWARNER@WPSCI.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Melissa Byrnes at 517-373-7065 with questions regarding this permit. Thank you. | 317-07 | 4911 | 221112 | 26-14105823 | 09/26/2007 &nbsp;ACT | 06/29/2011 &nbsp;ACT | 2012-10-18 | 2016-04-14 | A |  | Coal-fired power plant. |  | Fire Pump | 17.21 | Diesel | 420 | HP | Maximum operation was based on 500 hours per year. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.14 | LB/H | TEST PROTOCOL; BACT | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | EU-FPENGINE: Diesel fuel fired emergency backup fire pump | 17.21 | diesel fuel | 315 | hp nameplate | This is a diesel fuel fired emergency backup fire mump. It has a capacity of 315 hp, nameplate, and uses diesel fuel ASTM D975 Grade 2-D S15. Ultra low sulfur diesel fuel (15ppmw); 100 hours per year operation for maintenance and readiness testing. NSPS IIII and NESHAP ZZZZ. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Proper combustion design and ultra low sulfur diesel fuel. | 0.6 | LB/H | TEST PROTOCOL WILL SPECIFY AVG. TIME | BACT-PSD | NSPS , NESHAP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ultra low sulfur diesel fuel (15 pppmw); 100 hours per year operation for maintenance and readiness testing; NSPS IIII and NESHAP ZZZZ.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Emergency Engine --Diesel Fire Pump (EUFPENGINE) | 17.21 | Diesel | 165 | HP | A 165 hoursepower (hp) diesel-fueled emergency engine manufactured in 2013, iwth a heat input of 1.35 MMBTU/hr. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.09 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.57 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | diesel | 500 | H/YR | A 165 horsepower (hp) diesel-fueled emergency engine manufactured in 2016 with a heat input of 1.35 MMBTU/H. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.09 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (South Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | B | Diesel particulate filter, good combustion practices and meeting NSPS Subpart IIII requirements. | 0.66 | LB/H | HOURLY | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (North Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | B | Diesel particulate filter, good combustion practices and meeting NSPS Subpart IIII requirements. | 0.66 | LB/H | HOURLY | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUFPENGINE: Fire pump engine | 17.21 | Diesel | 399 | BHP | A 399 brake HP diesel-fueled emergency fire pump engine with a model year of 2011 or later, and a displacement of <10 liters/cylinder. The engine is an EPA Tier 3 certified engine subject to NSPS IIII. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | State of the art combustion design. | 0.13 | LB/H | HOURLY | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | firewater pumps, diesel | 17.21 | diesel | 325 | HP, EACH | Eight 325 hp diesel firewater pumps | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | comply with NSPS IIII, 52 hr/yr non-emergency operation
NJ-0084 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX | NJ | 07095-1439 | USA | DOUGLAS GORDON | (973)430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen: Phone number: 609-633-1129 E-mail: david.owen@dep.nj.gov | 18068/BOP150001 | 4911 | 221112 | 110000801614 | 02/01/2016 &nbsp;ACT | 03/10/2016 &nbsp;ACT | 2016-05-13 | 2018-04-17 | B | http://www.state.nj.us/dep/aqpp/ | PSEG Fossil LLC Sewaren Generating Station (Sewaren or Facility) is located at 751 Cliff Road, Sewaren, New Jersey 07077-1439, Middlesex County, New Jersey. This â€œProjectâ€ to be built at Sewaren would be a 1-on-1 (1 combustion turbine and a single steam turbine) combined-cycle electric generating unit including its ancillary equipment. The electric output of the combined-cycle combustion turbine (CCCT) at ISO conditions will be approximately 345 MW and the approximate output of the steam turbine at these conditions and with 100% supplemental heat input will be 240 MW. | A. The Facility Wide emission Increase given below is from this project. B. The Project will consist of the following equipment: [1] One (1) General Electric (GE) 7HA.02 CCCT nominally rated at 345 MW at ISO conditions without duct firing with a maximum heat input rate of: 3,311 MMBtu/hr(HHV) at (94) degrees F, 47% RH firing natural gas 3,452 MMBtu/hr(HHV) at (0) degrees F, and 50% RH when firing ULSD [2.] One (1) 730 MMBtu/hr (HHV) natural gas-fired duct burner [3] One (1) 80 MMBtu/hr (HHV) natural gas fired auxiliary boiler [4] One (1) 2.60 MMBtu/hr (HHV), 360 brake horsepower, emergency diesel fire pump, [5] One (1) 19.1 MMBtu/hr (HHV), approximately 2,000 kW emergency diesel generator, and, [6] A 3-cell, 13,000 gallon per minute (â€œgpmâ€) auxiliary wet mechanical draft cooling tower. | Emergency Diesel Fire Pump | 17.21 | ULSD | 100 | H/YR | Maximum heat Input Rate = 2.6 MMBtu/hr | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | use of ULSD a clean burning fuel, and limited hours of operation | 0.1 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | EMERGENCY GENERATOR DIESEL | 17.21 | DIESEL OIL | 0 | 100 H/YR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of Ultra Low Sulfur Diesel (ULSD) Oil a clean burning fuel and limited hours of operation | 0.661 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0085 | MIDDLESEX ENERGY CENTER, LLC | STONEGATE POWER, LLC | MIDDLESEX | NJ | 8872 | USA | DAVID HIMELMAN | (908) 705-4970 | DHIMELMAN@STONEGATEPOWERGENERATION.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | PERMIT WRITER: MICHAEL HOGAN: MICHAEL.HOGAN@DEP.NJ.GOV SUPERVISOR: ALIYA KHAN (606) 292-2169; ALIYA.KHAN@DEP.NJ.GOV | 19149/PCP150001 | 4911 | 221112 | Not Entered | 08/10/2015 &nbsp;ACT | 07/19/2016 &nbsp;ACT | 2016-07-27 | 2016-11-03 | A | http://www.state.nj.us/dep/aqpp/ | NEW 633 MEGAWATT (MW) GROSS FACILITY CONSISTING OF 1. ONE GENERAL ELECTRIC (GE) 7HA.02 CCCT NOMINALLY RATED AT 380 MW AT ISO CONDITIONS WITHOUT DUCT FIRING WITH A MAXIMUM HEAT INPUT RATE OF: O 3,462 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING NATURAL GAS O 3,613 MMBTU/HR(HHV) AT (0) DEGREES F, 100% LOAD COMBUSTING ULSD WHICH WILL BE THE BACKUP FUEL OTHER EQUIPMENT INCLUDES: 2. ONE NATURAL GAS-FIRED DUCT BURNER (MAXIMUM HEAT INPUT OF 599 MMBTU/HR(HHV)) FOR SUPPLEMENTAL FIRING. 3. ONE 97.5 MMBTU/HR(HHV) NATURAL GAS FIRED AUXILIARY BOILER, EQUIPPED WITH LOW NOX BURNERS AND FLUE GAS RECIRCULATION FOR CONTROL OF NOX EMISSIONS; 4. ONE 2.25 MMBTU/HR(HHV), 327 BRAKE HORSEPOWER, ULSD FIRED EMERGENCY FIRE PUMP; 5. ONE 14.4 MMBTU/HR(HHV), APPROXIMATELY 1,500 KW ULSD FIRED EMERGENCY GENERATOR; AND 6. ONE 8-CELL, 124,800 GALLON PER MINUTE (GPM) MECHANICAL INDUCED DRAFT COOLING TOWER. |  | EMERGENCY DIESEL FIRE PUMP | 17.21 | ULSD | 100 | H/YR | ULSD: Ultra low sulfur diesel | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of ULSD a clean burning fuel and limited hours of operation | 0.108 | LB/H |  | BACT-PSD | OPERATING PERMIT , NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Fire pump engine | 17.21 | Ultra-low sulfur diesel | 15 | gal/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.11 | GM/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.002 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
PR-0009 | ENERGY ANSWERS ARECIBO PUERTO RICO RENEWABLE ENERGY PROJECT | ENERGY ANSWERS ARECIBO, LLC | ARECIBO | PR |  | USA | MARK GREEN | (347)-351-5248 |  | 2 | OT003 | EPA REGION II | MR. FRANK JON | (212)637-4085 | jon.frank@epa.gov | Ms. Viorica Petriman petriman.viorica@epa.gov | R2-PSD 1 | 4953 | 221119 | FRL-9911-10-Region 2 | 11/11/2012 &nbsp;ACT | 04/10/2014 &nbsp;ACT | 2014-10-14 | 2016-05-05 | A |  | Energy Answers Arecibo is a new resource recovery facility capable of producing up to 77 megawatts (MW) of electrical power while combusting municipal solid waste, as the primary fuel. | This is a PSD permit for a new/greenfield facility. | Emergency Diesel Fire Pump | 17.21 | ULSD Fuel Oil #2 | 0 |  | The Emergency Fire Pump is rated at 335 BHP and limited to 500 hr/yr (emergency operations and testing and maintenance, combined). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/B-HP-H |  | BACT-PSD |  | U | 0 | U | 0.11 | LB/H |  | 0 |  |  | 0 | 0 | N
VA-0319 | GATEWAY COGENERATION 1, LLC - SMART WATER PROJECT | GATEWAY GREEN ENERGY | PRINCE GEORGE | VA | 23875-3000 | USA | T. EDWARD MCDANIEL | 972-638-8798 | EMCDANIEL@GGEHLLC.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52375-002 | 4911 | 221112 | 110045446718 | 01/11/2012 &nbsp;ACT | 08/27/2012 &nbsp;ACT | 2013-01-16 | 2015-05-29 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Combined cycle electrical power generating facility (160 MW), consisting of two combusion turbines (Rolls Royce Trent 60 WLE) with associated HRSG and no duct burning. |  | FIRE WATER PUMP | 17.21 | diesel (ultra low sulfur) | 1.86 | MMBTU/H | 500 H/Yr operation | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean burning ULSD fuel and good combustion practices. | 0.15 | G/HP-H |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Diesel Fired Well Pump | 17.21 | Diesel | 2.7 | MMBTU/H | 2.7 MMBtu/hr Diesel Fired Well Pump. Installed in 1966. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Limited Operation of 168 hr/yr. | 0.31 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*AK-0084 | DONLIN GOLD PROJECT | DONLIN GOLD LLC. | BETHEL CENSUS AREA | AK | 99575 | USA | STAN FOO | 907-273-0200 | SFOO@DONLINGOLD.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | AK DEC DIV. OF AIR QUALITY 410 WILLOUGHBY AVE. SUITE 303 JUNEAU, AK 99801 | AQ0934CPT01 | 1041 | 212221 | Not Entered | 10/15/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2018-06-21 | 2018-06-22 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16763360/d1h2U6BIY-j857LFU-WYmw2 | The Donlin Gold Project is a gold mine located 12 miles north of Crooked Creek, Alaska on the Kuskokwim River, about 280 miles northwest of Anchorage. The deposit has proven and probable reserves estimated at 33.9 million ounces of gold at 2.1 g/t and could produce up to 1.5 million ounces annually. SIC Code 1041; NAICS Code 212221. |  | Fire Pump Diesel Internal Combustion Engines | 17.21 | Diesel | 252 | hp | Three (3) 252 hp fire pump diesel internal combustion engines. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Clean Fuel and Good Combustion Practices | 0.19 | G/KW-HR | 3-HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Subpart IIII engines
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | EMERGENCY FIREWATER PUMP ENGINE | 17.21 | DIESEL | 135 | KW | 135 KW (182 hp) IC Diesel-fired Emergency Firewater Pump Engine | Particulate matter, total (TPM) | Other - EPA Method 5 and 202, or CTM 039 or CTM 040 | (Particulate Matter (PM)) | PM | P | OPERATIONAL RESTRICTION OF 50 HR/YR, OPERATE AS REQUIRED FOR FIRE SAFETY TESTING | 0.2 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
CA-1192 | AVENAL ENERGY PROJECT | AVENAL POWER CENTER LLC | KINGS | CA | 93239 | USA | JIM REXROAD |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 08-01 | 4911 | 221112 | 110043970334 | 03/19/2008 &nbsp;ACT | 06/21/2011 &nbsp;ACT | 2012-11-08 | 2014-01-10 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 600 MW (NET) COMBINED CYCLE NATURAL GAS-FIRED POWER PLANT | PSD permit issued on May 27, 2011, and administratively amended on June 21, 2011. (Note: PSD permit appealed to the EAB. EAB denied petitions for review on 8/18/2011. Enviros sued EPA in the Ninth Circuit Court of Appeals for the issuance of the permit. This lawsuit is still in litigation. Facility has not yet been constructed. PSD permit expired on 2/18/2013. The applicant requested an extension of the PSD permit on 2/5/2013. EPA Region 9 is processing the permit extension request.) | EMERGENCY FIREWATER PUMP ENGINE | 17.21 | DIESEL | 288 | HP |  | Particulate matter, total (TPM) | Other - SEE POLLUTANT INFO | (Particulate Matter (PM)) | PM | P | USE ULTRA LOW SULFUR FUELNOT TO EXCEED 15 PPMVD FUEL SULFUR, OPERATIONAL LIMIT OF 50 HRS/YR | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | TEST METHODS: USE EPA METHOD 5 & 202, OR METHOD 201A & 202, OR USE CTM 039 IN LIEU OF METHOD 202
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.21 | DIESEL | 182 | HP | UNIT IS 135 KW. | Particulate matter, total (TPM) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | USE ULTRA LOW SULFUR FUEL | 0.2 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
FL-0322 | SWEET SORGHUM-TO-ETHANOL ADVANCED BIOREFINERY | SOUTHEAST RENEWABLE FUELS (SRF), LLC | HENDRY COUNTY | FL | 33440 | USA | DON MARKLEY | 954-492-1588 | DMARKLEY@SERENEWABLE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Alvaro Linero, P.E. Administrator alvaro.linero@dep.state.fl.us Phone: 850-717-9076 David Read, Engineer david.read@dep.state.fl.us Phone: 850-717-9075 Teresa Heron, Engineer teresa.heron@dep.state.fl.us phone: 850-717-9082 | PSD-FL-412 (0510032-001-AC) | 2869 | 325193 | Not Applicable | 03/19/2010 &nbsp;ACT | 12/23/2010 &nbsp;ACT | 2011-01-31 | 2011-07-06 | A | http://www.dep.state.fl.us/Air/emission/bioenergy/southern_renewables.htm | The SRF facility will be located just East of County Road (CR) 835 at the intersection with Hill Grade Road and approximately 13 miles south southwest of Clewiston/Lake Okeechobee in Hendry County. Hendry County is bounded by Lee County to the west, Glades County to the north, Collier County to the south, Palm Beach County to the east and Broward County to the southeast. Lake Okeechobee is located immediately northeast of Hendry County. The Big Cypress Seminole Indian Reservation is located approximately 18 miles south southeast of the site entrance. Most of Hendry County is agricultural. | The applicant proposes to construct a sweet sorghum-to-ethanol advanced biorefinery with a capacity of 22.11 million gallons per year (MGPY). The sweet sorghum will be grown on adjacent farmland. The sweet sorghum juice will be squeezed from the sorghum stalks, fermented, distilled and blended to make a range of ethanol/gasoline products. The leftover stalk fiber (bagasse) and other parts of the plant (harvest field residue) will be combusted in a cogeneration biomass boiler to make process steam and up to 30 megawatts (MW, gross) of electricity. The applicant also plans to use sweet sorghum molasses in the ethanol process when sweet sorghum is not available. Wood and yard waste will be used as a backup and supplemental fuel for the biomass boiler. | Emergency Diesel Fire Pump, One 600 HP | 17.21 | ULSD | 0 |  |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-H |  | BACT-PSD |  | U | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The fire pumps shall comply with the emission limit and demonstrate compliance in accordance with the procedures given in NSPS 40 CFR 60, Subpart IIII. Manufacturer certification may be provided to the Department in lieu of actual testing. The fire pumps are Stationary Compression Ignition Internal Combustion Engines (Stationary ICE) and shall comply with applicable provisions of 40 CFR 60, Subpart IIII, including emission testing or certification.
FL-0324 | PALM BEACH RENEWABLE ENERGY PARK | SOLID WASTE AUTHORITY OF PALM BEACH COUNTY | PALM BEACH | FL | 33412 | USA | MARK HAMMOND | 561-640-4000 | MHAMMOND@SWA.ORG | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Alvaro Linero, P.E. Administrator alvaro.linero@dep.state.fl.us Phone: 850-717-9076 Robert Bull, Engineer robert.bull@dep.state.fl.us Phone: 850-717-9111 Teresa Heron, Engineer teresa.heron@dep.state.fl.us phone: 850-717-9082 | PSD-FL-413 | 4953 | 221119 | 110043792358 | 11/12/2010 &nbsp;ACT | 12/23/2010 &nbsp;ACT | 2011-04-07 | 2011-12-08 | B |  | The existing Palm Beach Renewable Energy Facility (PBREP-1) consists of Class I and Class III landfills, a biosolids pelletizer facility, a compost facility and a waste-to-energy (WTE) plant known as the North County Resource Recovery Facility (NCRRF). The new facility, PBREP-2, will consist of: â€¢Three nominal 1,000 TPD mass burn MWC, each with an estimated maximum continuous rating (MCR) of 416.7 million Btu per hour heat input (mmBtu/hr) and a peak rating of 458.3 mmBtu/hr; â€¢A 100 megawatt (MW) STG with an air cooled condenser; â€¢One ash building and handling system; â€¢Three lime storage silos and one carbon storage silo; and â€¢Two 250 horsepower (hp) diesel fire pumps and one 250 kilowatt (kW) emergency generator. This facility, is located at 7501 North Jog Road (immediately west of the Turnpike) in West Palm Beach. | This project will consist of three 1,000 TPD mass-burn MWC units each with a maximum steam production rate of 320,100 pounds per hour (lb/hr) on a 4-hour average block basis. The project also includes a 90 to100 MW STG; three lime storage silos; one carbon storage silo; two diesel fire pump engines; one emergency generator; and one ash handling system and building. The proposed work will be conducted at the existing PBREP. The project will incorporate the following pollution control equipment and measures: â€¢For each MWC unit, good combustion practices (GCP), spray dryers (SD), fabric filter (FF) baghouses, activated carbon injection (CI), selective catalytic reduction (SCR), as an option selective non-catalytic reduction (SNCR) and use of inherently clean natural gas as a startup, shutdown and flame stabilization fuel. â€¢Use of inherently clean ultra low sulfur distillate (ULSD) fuel oil and GCP in the emergency generator and emergency fire pump engines; and â€¢Reasonable precautions and best management practices (BMP) to minimize fugitive particulate matter (PM)/(PM10)/(PM2.5) emissions from MSW handling and processing; ash (bottom and fly) handling, storage and shipment; lime handling, storage and processing; and activated carbon handling, storage and processing. The project will incorporate continuous emission monitoring systems (CEMS) for CO, SO2, NOX and Hg and continuous opacity monitoring systems (COMS) for visible emissions (VE). | 250 Kw Emergency Generator | 17.21 | ULSD | 0 |  |  | Particulate matter, total (TPM) | Other - Manufacturer Certification | (Particulate Matter (PM)) | PM | P | Use of inherently clean ultra low sulfur distillate (ULSD) fuel oil and GCP & demonstrate compliance in accordance with the procedures given in 40 CFR 60, Subpart IIII | 0.2 | G/KW-H |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emergency generator shall comply with the following emission limits and demonstrate compliance in accordance with the procedures given in 40 CFR 60, Subpart IIII. Manufacturer certification can be provided to the Department in lieu of actual stack testing.
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Wireline Unit Engines - C.R. Luigs | 17.21 | diesel | 300 | hp |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 0.6 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Fast Rescue Craft Diesel Engine - Development Driller 1 | 17.21 | Diesel | 142 | hp |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, and turbocharger | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Life Boat Diesel Engines - Development Driller 1 | 17.21 | Diesel | 110 | hp |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines and use of low sulfur diesel fuel | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Port and Stb Fwd and Aft Crane Diesel Engines - C.R. Luigs | 17.21 | diesel | 305 | HP |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 5.88 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Seismic Operations Diesel Engines - Development Driller 1 | 17.21 | Diesel | 415 | hp |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, and turbocharger | 0.11 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - Development Driller 1 | 17.21 | Diesel | 0 |  |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger, and high pressure fuel injection with aftercooler | 0.41 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Wireline Unit Diesel Engines - Development Driller 1 | 17.21 | Diesel | 0 |  | Wireline units including primary, alternative #2, power plant, and hydraulic generator | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 0.6 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Black Start Air Compressor - C.R. Luigs | 17.21 | diesel | 6 | hp |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for the engine and the use of low sulfur diesel fuel | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - C.R. Luigs | 17.21 | diesel | 0 |  | Cementing Units: Caterpillar 3412 CDITA 860 hp 2001 Nitrogen Pump: Caterpillar 3406 CDITA 490 hp 2000 | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger, and high pressure fuel injection with aftercooler | 0.38 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0346 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-011-AC | 4911 | 221112 | 110002044065 | 11/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-01-08 | 2016-05-05 | D | http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | In this project, 24 peaking turbines from the Lauderdale facility are being replaced with five 200 MW combustion turbines at Lauderdale. The turbines will fire primarily natural gas, but may also fire ULSD fuel oil. Triggers PSD for NOx, PM, CO, VOC, and GHG. GHG permit issued by US EPA Region 4. Technical evaluation available at http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.D.ZIP | Emergency fire pump engine (300 HP) | 17.21 | USLD | 29 | MMBTU/H | Emergency engine. BACT = NSPS IIII. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practice | 0.2 | GRAM PER HP-HR |  | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT = NSPS IIII; Certified IIII engine meets BACT.
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Diesel Powered Forklift Engine | 17.21 | Diesel | 30 | hp |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Wireline Diesel Engines | 17.21 | Diesel | 0 |  | Wireline engines, electric line engines, casing unit engines, tubing running engine, fluid filtration pump engine, powerpack engine, slickline powerpack engine, and CT pump engine | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Water Blasting Diesel Engine | 17.21 | Diesel | 208 | hp |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Well Evaluation Diesel Engine | 17.21 | Diesel | 140 | hp |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Fast Rescue Craft Diesel Engine | 17.21 | Diesel | 230 | hp |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Escape Capsule Diesel Engine | 17.21 | Diesel | 39 | hp |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Remotely Operated Vehicle Emergency Generator | 17.21 | Diesel | 427 | hp | 2004 Cummins QSM11-G2NR3 | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of good combustion practices based on the most recent manufacturer's specifications issued for engines and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0354 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-013-AC | 4911 | 221112 | 110002044065 | 04/20/2015 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2016-02-17 | 2016-07-06 | D | https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | Re-affirmed BACT determinations in Permit No. 0110037-011-AC. Also, new GHG BACT determination. Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.D.ZIP | Emergency fire pump engine, 300 HP | 17.21 | Diesel | 29 | MMBTU/H | Emergency engine. ULSD only. BACT limits equal NSPS IIII limits. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Low-emitting fuel and certified engine | 0.2 | G / KWH |  | BACT-PSD | NSPS , SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Must use certified engine, or perform stack tests.
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | One 422-hp emergency fire pump engine | 17.21 | ULSD | 0 |  | BACT limits equal to NSPS Subpart IIII limits. Will use IIII certified engine. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of clean fuel | 0.2 | G / KW-HR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.2 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.03 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Emergency diesel engine | 17.21 | diesel | 750 | KW | One (1) 1102 HP (750 KW) emergency diesel engine | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur fuel oil (<15 ppm sulfur) | 0.15 | G PER BHP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0030 | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | GRANT | KS | 67601 | USA | PAUL REYNOLDS | 620-277-4522 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Mindy Bowman, E-mail address: Mindy.Bowman@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-13309 | 4911 | 221112 | Not Found | 03/07/2017 &nbsp;ACT | 03/31/2016 &nbsp;ACT | 2017-04-06 | 2017-07-19 | C |  | Mid-Kansas Electric Company, LLC (Mid-Kansas Electric) (Source ID: 0670173) operates the Rubart Station located in Grant County, Kansas. The facility currently consist of twelve (12) new spark ignition four-stroke lean burn (4SLB) reciprocating internal combustion engines (RICE) used to generate electricity (the proposed project consist of 24 new 4SLB RICE). The generating capacity of each unit is 10 megawatts (approximately 13,410 BHP). Also located at the station is a diesel fire pump, natural gas emergency generator, heater, circuit breakers and switches. The insignificant activities include a diesel storage tank. | This PSD permit with tracking number C-13309 a modification of PSD permits C-12896 (PSD Administrative Amendment, issued on 5/7/2015), C-12721 (PSD Revisions, issued on 4/28/2015), and C-10021 (original PSD permit for the proposed project, issued on 1/28/2013). | Compression ignition RICE emergency fire pump | 17.21 | Ultra-lowsulfur diesel (ULSD) | 197 | HP | One (1) compression ignition emergency fire pump engine, rated at 197 HP, which shall burn only ultra-low sulfur diesel (ULSD, 15 ppm sulfur or less). | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR | EXCLUDES STARTUP, SHUTDOWN & MALFUNCTION | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | Cummins 6BTA 5.9F-1 Diesel Engine Fire Pump | 17.21 | No. 2 Fuel Oil | 182 | BHP |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | utilize efficient combustion/design technology | 0.25 | G/BHP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0389 | KARN WEADOCK GENERATING COMPLEX | CONSUMERS ENERGY | BAY | MI | 48732-9601 | USA | JAMES M. WALKER | 5177880428 | JMWALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | FOR TECHNICAL QUESTIONS ABOUT THIS PERMIT, PLEASE CONTACT THE PERMIT ENGINEER - DAVID K. RIDDLE RIDDLED@MICHIGAN.GOV (517-373-7081) | 341-07 | 4911 | 221112 | 26-01700033 | 10/15/2007 &nbsp;ACT | 12/29/2009 &nbsp;ACT | 2010-03-08 | 2010-12-16 | U |  | ELECTRICITY GENERATING FACILITY, EXISTING CAPACITY GREATER THAN 2,000 MW. | AFTER CONSTRUCTION CONSUMERS WILL RETIRE 5 TO 7 COAL-FIRED BOILERS (638 - 958 MW) STATEWIDE. FINAL CONDITIONS WILL BE AT WWW.DEQ.STATE.MI.US/APS/FINALCONDITIONS.SHTML. MATERIAL HANDLING - CONTACT PERMIT ENGINEER FOR TECHNICAL INFORMATION (DAVID RIDDLE, 517-373-7081). INCLUDES 9 EMISSION UNITS. COAL, LIMESTONE, SORBENT AND ASH HANDLING PROCESSES. VARIOUS BACT LIMITS FOR OPACITY, PM AND PM10. BACT FOR THE MATERIAL HANDLING EQUIPMENT CONSISTED OF A COMBINATION OF PASSIVE CONTROL EQUIPMENT SUCH AS WET/CHEMICAL SUPPRESSION SYSTEMS AND ENCLOSED CONVEYORS; AND ACTIVE CONTROL SUCH AS FABRIC FILTERS. ACTIVE CONTROL IS LIMITED TO 0.004 GR/DSCF. | FIRE BOOSTER PUMP | 17.21 | ULTRA LOW SULFUR DIESEL | 40 | KW | OPERATIONAL LIMITS 1 HR/DAY AND 500 HRS/YR FOR PM2.5 NAAQS. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | ENGINE DESIGN AND OPERATION. 15 PPM SULFUR FUEL. | 0.4 | G/KW-H | TEST METHOD | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | firewater pumps, diesel | 17.21 | diesel | 325 | HP, EACH | Eight 325 hp diesel firewater pumps | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | comply with NSPS IIII, 52 hr/yr non-emergency operation
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Emergency Fire Pump Engine | 17.21 | ULSD | 0 |  | Sulfur content of diesel fuel shall not exceed 15 ppm, operation of engine shall not exceed 100 hr on a 12-month rolling basis. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/BHP-HR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0324 | PALM BEACH RENEWABLE ENERGY PARK | SOLID WASTE AUTHORITY OF PALM BEACH COUNTY | PALM BEACH | FL | 33412 | USA | MARK HAMMOND | 561-640-4000 | MHAMMOND@SWA.ORG | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Alvaro Linero, P.E. Administrator alvaro.linero@dep.state.fl.us Phone: 850-717-9076 Robert Bull, Engineer robert.bull@dep.state.fl.us Phone: 850-717-9111 Teresa Heron, Engineer teresa.heron@dep.state.fl.us phone: 850-717-9082 | PSD-FL-413 | 4953 | 221119 | 110043792358 | 11/12/2010 &nbsp;ACT | 12/23/2010 &nbsp;ACT | 2011-04-07 | 2011-12-08 | B |  | The existing Palm Beach Renewable Energy Facility (PBREP-1) consists of Class I and Class III landfills, a biosolids pelletizer facility, a compost facility and a waste-to-energy (WTE) plant known as the North County Resource Recovery Facility (NCRRF). The new facility, PBREP-2, will consist of: â€¢Three nominal 1,000 TPD mass burn MWC, each with an estimated maximum continuous rating (MCR) of 416.7 million Btu per hour heat input (mmBtu/hr) and a peak rating of 458.3 mmBtu/hr; â€¢A 100 megawatt (MW) STG with an air cooled condenser; â€¢One ash building and handling system; â€¢Three lime storage silos and one carbon storage silo; and â€¢Two 250 horsepower (hp) diesel fire pumps and one 250 kilowatt (kW) emergency generator. This facility, is located at 7501 North Jog Road (immediately west of the Turnpike) in West Palm Beach. | This project will consist of three 1,000 TPD mass-burn MWC units each with a maximum steam production rate of 320,100 pounds per hour (lb/hr) on a 4-hour average block basis. The project also includes a 90 to100 MW STG; three lime storage silos; one carbon storage silo; two diesel fire pump engines; one emergency generator; and one ash handling system and building. The proposed work will be conducted at the existing PBREP. The project will incorporate the following pollution control equipment and measures: â€¢For each MWC unit, good combustion practices (GCP), spray dryers (SD), fabric filter (FF) baghouses, activated carbon injection (CI), selective catalytic reduction (SCR), as an option selective non-catalytic reduction (SNCR) and use of inherently clean natural gas as a startup, shutdown and flame stabilization fuel. â€¢Use of inherently clean ultra low sulfur distillate (ULSD) fuel oil and GCP in the emergency generator and emergency fire pump engines; and â€¢Reasonable precautions and best management practices (BMP) to minimize fugitive particulate matter (PM)/(PM10)/(PM2.5) emissions from MSW handling and processing; ash (bottom and fly) handling, storage and shipment; lime handling, storage and processing; and activated carbon handling, storage and processing. The project will incorporate continuous emission monitoring systems (CEMS) for CO, SO2, NOX and Hg and continuous opacity monitoring systems (COMS) for visible emissions (VE). | 250 Kw Emergency Generator | 17.21 | ULSD | 0 |  |  | Sulfur Dioxide (SO2) | Other - Fuel Analysis | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.0015 | % SULFUR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emergency generator shall comply with the following emission limits and demonstrate compliance in accordance with the procedures given in 40 CFR 60, Subpart IIII. Manufacturer certification can be provided to the Department in lieu of actual stack testing.
FL-0346 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-011-AC | 4911 | 221112 | 110002044065 | 11/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-01-08 | 2016-05-05 | D | http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | In this project, 24 peaking turbines from the Lauderdale facility are being replaced with five 200 MW combustion turbines at Lauderdale. The turbines will fire primarily natural gas, but may also fire ULSD fuel oil. Triggers PSD for NOx, PM, CO, VOC, and GHG. GHG permit issued by US EPA Region 4. Technical evaluation available at http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.D.ZIP | Emergency fire pump engine (300 HP) | 17.21 | USLD | 29 | MMBTU/H | Emergency engine. BACT = NSPS IIII. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practice and ULSD | 15 | PPM SULFUR IN FUEL |  | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT = NSPS IIII; Certified IIII engine meets BACT. ULSD specified in NSPS.
FL-0354 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-013-AC | 4911 | 221112 | 110002044065 | 04/20/2015 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2016-02-17 | 2016-07-06 | D | https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | Re-affirmed BACT determinations in Permit No. 0110037-011-AC. Also, new GHG BACT determination. Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.D.ZIP | Emergency fire pump engine, 300 HP | 17.21 | Diesel | 29 | MMBTU/H | Emergency engine. ULSD only. BACT limits equal NSPS IIII limits. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Limit in S in fuel | 0.0015 | % S IN ULSD | FUEL RECORD KEEPING | BACT-PSD | NSPS , SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Use of ULSD to control S emissions.
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | One 422-hp emergency fire pump engine | 17.21 | ULSD | 0 |  | BACT limits equal to NSPS Subpart IIII limits. Will use IIII certified engine. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Use of ULSD | 0.0015 | % S IN ULSD |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*FL-0363 | DANIA BEACH ENERGY CENTER | FLORIDA POWER AND LIGHT COMPANY | BROWARD | FL | 33314 | USA | JOHN HAMPP | 561-691-2894 | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-017-AC | 4911 | 221112 | 110002044065 | 07/27/2017 &nbsp;ACT | 12/04/2017 &nbsp;ACT | 2018-04-03 | 2018-04-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.F.ZIP | 1200 megawatt 2-on-1 combined cycle facility, natural gas-fired, with limited ULSD use. GE 7HA turbines | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.D.ZIP | Emergency Fire Pump Engine (422 hp) | 17.21 | ULSD | 0 |  | Limits equal Subpart IIII limits | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Clean fuel | 15 | PPM S IN FUEL |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ULSD fuel
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) FIREWATER PUMP DIESEL ENGINES | 17.21 | DIESEL | 371 | BHP, EACH | THE TWO FIREWATER PUMP ENGINES, IDENTIFIED AS FP01 AND FP02, EXHAUSTING THROUGH TWO (2) VENTS. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | ULTRA LOW SULFUR DISTILLATE AND USAGE LIMITS | 0.0015 | % SUFLUR DIESEL FUEL |  | BACT-PSD |  |  | 0 |  | 0.043 | LB/H |  | 0 |  |  | 0 | 0 | N |  | LIMIT ONE AND TWO ARE FOR EACH FIREWATER PUMP ENGINE. LIMIT THREE: EACH FIRE PUMP SHALL NOT EXCEED 500 HOURS OF OPERATION PER YEAR.
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | EMERGENCY FIRE PUMP ENGINE | 17.21 | DISTILLATE OIL | 0 |  | 425 HP | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | AMOUNT OF DIESEL BURNED SHALL NOT EXCEED 1,128 GALLONS PER 12 MONTH PERIOD | 0.0015 | % | SULFUR CONTENT | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | AMOUNT OF DIESEL BURNED SHALL NOT EXCEED 1,128 GALLONS PER 12 MONTH PERIOD
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Deisel | 150 | hp | 2 units at 75 hp, 1 unit at 150 hp | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.0015 | % | FUEL SULFUR CONTENT | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Diesel | 250 | hp | 2 units | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.0015 | % | FUEL SULFUR CONTENT | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | Cummins 6BTA 5.9F-1 Diesel Engine Fire Pump | 17.21 | No. 2 Fuel Oil | 182 | BHP |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | use low sulfur fuel oil | 0.05 | %S |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0224 | ARSENAL HILL POWER PLANT | SOUTHWEST ELECTRIC POWER COMPANY (SWEPCO) | CADDO | LA | 71101 | USA | KRIS GAUS | 2147771113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-726 | 4911 | 221112 | 110001270847 | 01/07/2008 &nbsp;ACT | 03/20/2008 &nbsp;ACT | 2008-04-18 | 2012-05-18 | B |  | NATURAL GAS FIRED ELECTRICAL GENERATION PLANT. |  | DFP DIESEL FIRE PUMP | 17.21 | DIESEL | 310 | HP | EQT-016 | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N | USE OF LOW-SULFUR FUELS, LIMITING OPERATING HOURS AND PROPER ENGINE MAINTENANCE | 0.64 | LB/H | MAX | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0301 | LAKE CHARLES CHEMICAL COMPLEX ETHYLENE 2 UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | (281) 588-3761 | ERIC.RODRIGUEZ@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-779 | 2869 | 325110 | 110017418061 | 05/02/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2016-09-27 | 2017-04-28 | B |  |  | Complete application date = date of administrative completeness This RBLC entry addresses Ethylene Unit 2 of the Lake Charles Cracker Project. This unit will produce ethylene by thermally cracking ethane in cracking furnaces. | Firewater Pump Nos. 1-3 (EQTs 997, 998, &amp; 999) | 17.21 | Diesel | 500 | HP | Non-emergency use operating time is limited to 100 hr/yr (per engine). | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Compliance with 40 CFR 60 Subpart IIII and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage | 0.005 | LB/HR | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.001 | TPY | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | Sulfur content of fuel is limited to 15 ppm. Annual SO2 limit is represented as &lsquo;&lsquo;<0.001 TPY&lsquo;&lsquo; in the permit. BACT is determined to be compliance with the limitations imposed by 40 CFR 60 Subpart IIII and its associated monitoring, recordkeeping, and reporting requirements; and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage.
LA-0309 | BENTELER STEEL TUBE FACILITY | BENTELER STEEL / TUBE MANUFACTURING CORPORATION | CADDO | LA | 71115 | USA | MYRNA PACHECO PONCE DE LEON | 318-216-4206 | MYRNA.PACHECO@BENTELER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen - 225-219-3395 | PSD-LA-774(M1) | 3312 | 331111 | 110055592318 | 02/09/2015 &nbsp;ACT | 06/04/2015 &nbsp;ACT | 2017-03-09 | 2017-04-28 | A |  | A facility to produce 600,000 metric tons per year of seamless steel pipe from purchased billets. A steel production facility (including an electric arc furnace (EAF)) was added. | Permit PSD-LA-774 was issued on May 17, 2013 for the construction of the hot rolling mill. An EAF was authorized this time. | Firewater Pump Engines | 17.21 | Diesel | 288 | hp (each) |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY FIRE WATER PUMP | 17.21 | DIESEL | 300 | HP |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P |  | 0 |  | SEE NOTE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | EXCLUSIVE USE OF ULTRA LOW SULFUR DIESEL FUEL WITH A SULFUR CONTENT NOT TO EXCEED 15 PARTS PER MILLION BY WEIGHT
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA LOW SULFUR DIESEL | 477 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | USE OF ULTRA-LOW DIESEL SULFUR FUEL, LIMITED HOURS OF OPERATION AND DESIGNED TO MEET SUBPART IIII LIMITS | 0.0049 | G/B-HP-H | 3-HOUR BLOCK AVERAGE | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 15 | PPM | FUEL SUP. CERT. RECORDS OR SAMPLE TEST | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The Avg. Time/Conditions for the emission limit above is fuel supplier certification records or fuel sample test data, for each delivery of diesel fuel oil. The diesel material limit is 15 ppm of sulfur (0.0015 percent) by weight.
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (South Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 15 | PPM | FUEL SUPPLIER RECORDS OR FUEL SAMPL DATA | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The diesel material limit is 15 ppm of sulfur (0.0015 percent) by weight based on fuel supplier certification records or fuel sample test data, for each delivery of diesel fuel oil.
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (North Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 15 | PPM | FUEL SUPPLIER RECORDS | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The diesel material limit is 15 ppm of sulfur (0.0015 percent) by weight.
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | Emergency diesel fire pump | 17.21 | Ultra Low Sulfur Distillate oil | 0 |  | The fire pump has a maximum heat input rate of 2.63 MMBtu/hr (approximately 250 HP) and is permitted for 100 hrs per year for testing and maintenance | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Use of Ultra low sulfur fuel oil | 0.002 | LB/MMBTU |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This project not subject to BACT or LAER for SO2.
NV-0047 | NELLIS AIR FORCE BASE | 99 CIVIL ENGINEER SQUADRON OF USAF | CLARK | NV | 891555210 | USA | SHIMI MATHEW | 7026522548 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, TEL: 702-455-1673 | 114 | 9711 | 928110 | 110027848319 | 09/26/2007 &nbsp;ACT | 02/26/2008 &nbsp;ACT | 2008-10-21 | 2008-10-21 | A |  | THE FACILITY IS A MILITARY INSTALLATION WITH A LARGE NUMBER OF PROCESSES SUPPORTING THE AIR FORCE'S OPERATIONS. | THIS REPORT IS BASED ON THE PERMIT ISSUED TO THE NELLIS AIR FORCE BASE FOR MODIFICATION 37, REVISION 2. THE FACILITY IS A MAJOR STATIONARY SOURCE FOR NITROGEN OXIDES. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE, PM-10, AND CARBON MONOXIDE. A FEW MINOR PROCESSES, WHICH WERE NOT REVIEWED IN THIS PERMITTING ACTION, ARE NOT INCLUDED IN THIS REPORT. A PART 70 PERMIT FOR THIS NEW MAJOR SOURCE IS YET TO BE ISSUED. | SMALL INTERNAL COMBUSTION ENGINES (&lt;= 500 HP) | 17.21 | DIESEL OIL |  |  | THE PERMITTING ACTION APPROVED A TOTAL OF 42 NEW UNITS. THE FACILITY HAS A TOTAL OF 49 REGULATED UNITS AND 11 EXEMPT UNITS. ALL OF THEM ARE SUBJECT TO THE LIMIT OF OPERATING TIME FOR TESTING AND MAINTENANCE FOR 90 HOURS PER YEAR. UNIT G021 (ONAN GENERATOR, 317 HP) IS SELECTED TO SHOW THE BACT DETERMINATIONS. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | LIMITING SULFUR CONTENT IN THE DIESEL OIL TO 0.05% | 0.99 | G/B-HP-H |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 0.69 | LB/H |  | 0.99 | G/B-HP-H |  | 0 | 0 | N
NY-0104 | CPV VALLEY ENERGY CENTER | CPV VALLEY LLC | ORANGE | NY | 10940 | USA |  |  |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-335600136/00001 | 4911 | 221112 | 110043332471 | 08/01/2013 &nbsp;ACT | 08/01/2013 &nbsp;ACT | 2017-08-25 | 2017-09-28 | A |  | CPV Valley Energy Center is a 680 MW combined cycle electric generating facility located in Middletown, NY. The combustion turbines are rated at 2,234 MMBTU/H firing natural gas and 2,145 MMBTU/H firing diesel fuel. The duct burners are rated for 500 MMBTU/H firing natural gas. In addition to the turbines their emission limits for the auxiliary boiler (73.5 MMBTU/H), emergency generator, fire pump, and gas heater. | State Facility Permit | Fire pump | 17.21 | ultra low sulfur diesel | 0 |  |  | Sulfur Dioxide (SO2) | Other - EPA approved method | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Ultra low sulfur diesel with maximum sulfur content 0.0015 percent. | 0.0014 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0129 | CHOUTEAU POWER PLANT | ASSOCIATED ELECTRIC COOPERATIVE INC | MAYES | OK | 74362 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2007-115-C(M-1)PSD | 4911 | 221112 | 4009700017 | 06/19/2008 &nbsp;ACT | 01/23/2009 &nbsp;ACT | 2009-11-20 | 2010-02-18 | B |  |  |  | EMERGENCY FIRE PUMP (267-HP DIESEL) | 17.21 | LOW SULFUR DIESEL | 267 | HP |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N | LOW SULFUR DIESEL | 0.11 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
PR-0009 | ENERGY ANSWERS ARECIBO PUERTO RICO RENEWABLE ENERGY PROJECT | ENERGY ANSWERS ARECIBO, LLC | ARECIBO | PR |  | USA | MARK GREEN | (347)-351-5248 |  | 2 | OT003 | EPA REGION II | MR. FRANK JON | (212)637-4085 | jon.frank@epa.gov | Ms. Viorica Petriman petriman.viorica@epa.gov | R2-PSD 1 | 4953 | 221119 | FRL-9911-10-Region 2 | 11/11/2012 &nbsp;ACT | 04/10/2014 &nbsp;ACT | 2014-10-14 | 2016-05-05 | A |  | Energy Answers Arecibo is a new resource recovery facility capable of producing up to 77 megawatts (MW) of electrical power while combusting municipal solid waste, as the primary fuel. | This is a PSD permit for a new/greenfield facility. | Emergency Diesel Fire Pump | 17.21 | ULSD Fuel Oil #2 | 0 |  | The Emergency Fire Pump is rated at 335 BHP and limited to 500 hr/yr (emergency operations and testing and maintenance, combined). | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.003 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
SC-0113 | PYRAMAX CERAMICS, LLC | PYRAMAX CERAMICS, LLC | ALLENDALE | SC | 29810 | USA | RICHARD DERBAWKA | 7705690079 | R.DERBAWKA@PYRAMAXCERAMICS.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MS. ALYSON HAYES | (803)898-3836 | camitdr@dhec.sc.gov | GEORGE S. ROBINSON (803) 898-4123 | 0160-0023 | 3295 | 327992 | Not Available | 09/16/2011 &nbsp;ACT | 02/08/2012 &nbsp;ACT | 2012-05-09 | 2012-10-17 | A |  | PYRAMAX CERAMICS PLANS TO CONSTRUCT A MANUFACTURING FACILITY FOR THE PRODUCTION OF PROPPANT BEADS FOR USE IN THE OIL AND GAS INDUSTRY. THE MAJOR RAW MATERIAL IS CLAY. THE CLAY IS MIXED WITH CHEMICALS AND THEN FIRED IN A KILN TO PRODUCE CERAMIC BEADS. INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | EMERGENCY ENGINE 1 THRU 8 | 17.21 | DIESEL | 29 | HP | THE CONSTRUCTION PERMIT AUTHORIZES THE CONSTRUCTION OF EIGHT (8) IDENTICAL EMERGENCY ENGINES. THIS PROCESS AND POLLUTANT INFORMATION IS FOR ONE SINGLE ENGINE. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | LOW SULFUR DIESEL. MAXIMUM OF 100 HOURS PER YEAR RUNNING TIME FOR MAINTENANCE AND TESTING. | 0 |  |  | BACT-PSD |  | Y | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | DIESEL FUEL SULFUR CONTENT SHALL BE < 0.0015 PERCENT. REPORTS OF FUEL SULFUR CONTENT SHALL BE MAINTAINED.
SC-0113 | PYRAMAX CERAMICS, LLC | PYRAMAX CERAMICS, LLC | ALLENDALE | SC | 29810 | USA | RICHARD DERBAWKA | 7705690079 | R.DERBAWKA@PYRAMAXCERAMICS.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MS. ALYSON HAYES | (803)898-3836 | camitdr@dhec.sc.gov | GEORGE S. ROBINSON (803) 898-4123 | 0160-0023 | 3295 | 327992 | Not Available | 09/16/2011 &nbsp;ACT | 02/08/2012 &nbsp;ACT | 2012-05-09 | 2012-10-17 | A |  | PYRAMAX CERAMICS PLANS TO CONSTRUCT A MANUFACTURING FACILITY FOR THE PRODUCTION OF PROPPANT BEADS FOR USE IN THE OIL AND GAS INDUSTRY. THE MAJOR RAW MATERIAL IS CLAY. THE CLAY IS MIXED WITH CHEMICALS AND THEN FIRED IN A KILN TO PRODUCE CERAMIC BEADS. INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | FIRE PUMP | 17.21 | DIESEL | 500 | HP | THE CONSTRUCTION PERMIT AUTHORIZES THE CONSTRUCTION OF ONE (1) FIRE PUMP. THIS PROCESS AND POLLUTANT INFORMATION IS FOR THIS ONE SINGLE FIRE PUMP. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | USE OF LOW SULFUR FUEL DIESEL, SULFUR CONTENT LESS THAN 0.0015 PERCENT. OPERATING HOURS LESS THAN 100 HOURS PER YEAR FOR MAINTENACE AND TESTING. | 0 |  |  | BACT-PSD |  | Y | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | SULFUR CONTENT OF DIESEL FUEL TO BE LESS THAT 0.0015 PERCENT. SUPPLIER CERTIFICATION OF FUEL SULFUR CONTENT SHALL BE MAINTAINED.
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Diesel Fire Pump Engine (EP16) | 17.21 | Ultra Low Sulfur Diesel | 327 | hp |  | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Ultra Low Sulfur Diesel | 0 |  |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | limited to 250 hours of non-emergency operation per calendar year
WY-0071 | SINCLAIR REFINERY | SINCLAIR WYOMING REFINING COMPANY | CARBON | WY | 82334 | USA | SAM GREENE | (801) 524-2729 | SGREENE@SINCLAIROIL.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | MD-12620 | 2911 | 324110 | 110040906945 | 05/01/2012 &nbsp;ACT | 10/15/2012 &nbsp;ACT | 2012-10-05 | 2016-04-14 | D |  | Crude Oil Refinery | (1) Crude Optimization Project; (2) remove the firing rate limits for the #1 HDS heater, Naphtha Splitter Heater, and Hydrocraker H5 Heater; (3) installation of a new Naphtha Splitter and Benzene Saturation/Isomerization (BSI) Unit; (4) increasing the capacity of the existing sour water stripping system and installation of an additional sour water stripper; and (5) install a new 400 hp emergency air compressor | Emergency Air Compressor | 17.21 | Ultra Low Sulfur Diesel | 400 | hp |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Ultra Low Sulfur Diesel | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Airstrip Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 490 | hp | One 490 hp Airstrip Generator Engine | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.0025 | LB/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Agitator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 98 | hp | ULSD-fired 98 hp Agitator Generator Engine | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.0025 | LB/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Incinerator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 102 | hp | ULSD-fired 102 hp Incinerator Generator Engine | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.0025 | LB/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Diesel Fired Well Pump | 17.21 | Diesel | 2.7 | MMBTU/H | 2.7 MMBtu/hr Diesel Fired Well Pump. Installed in 1966. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Limited Operation of 168 hr/yr. | 0.36 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Wireline Unit Engines - C.R. Luigs | 17.21 | diesel | 300 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 1.17 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Fast Rescue Craft Diesel Engine - Development Driller 1 | 17.21 | Diesel | 142 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, and turbocharger | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Life Boat Diesel Engines - Development Driller 1 | 17.21 | Diesel | 110 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines and use of low sulfur diesel fuel | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Port and Stb Fwd and Aft Crane Diesel Engines - C.R. Luigs | 17.21 | diesel | 305 | HP |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 6.72 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Seismic Operations Diesel Engines - Development Driller 1 | 17.21 | Diesel | 415 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, and turbocharger | 6.67 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Life Boat Diesel Engines - C.R. Luigs | 17.21 | diesel | 39 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - Development Driller 1 | 17.21 | Diesel | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger, and high pressure fuel injection with aftercooler | 0.57 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Wireline Unit Diesel Engines - Development Driller 1 | 17.21 | Diesel | 0 |  | Wireline units including primary, alternative #2, power plant, and hydraulic generator | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, turbocharger with aftercooler, high pressure fuel injection with aftercooler | 1.17 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Black Start Air Compressor - C.R. Luigs | 17.21 | diesel | 6 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Use of good combustion practices based on the current manufacturerâ€™s specifications for the engine and the use of low sulfur diesel fuel | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - C.R. Luigs | 17.21 | diesel | 0 |  | Cementing Units: Caterpillar 3412 CDITA 860 hp 2001 Nitrogen Pump: Caterpillar 3406 CDITA 490 hp 2000 | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Use of good combustion practices based on the current manufacturerâ€™s specifications for these engines, use of low sulfur diesel fuel, positive crankcase ventilation, turbocharger, and high pressure fuel injection with aftercooler | 0.38 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Diesel Powered Forklift Engine | 17.21 | Diesel | 30 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Wireline Diesel Engines | 17.21 | Diesel | 0 |  | Wireline engines, electric line engines, casing unit engines, tubing running engine, fluid filtration pump engine, powerpack engine, slickline powerpack engine, and CT pump engine | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Water Blasting Diesel Engine | 17.21 | Diesel | 208 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Well Evaluation Diesel Engine | 17.21 | Diesel | 140 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Fast Rescue Craft Diesel Engine | 17.21 | Diesel | 230 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Escape Capsule Diesel Engine | 17.21 | Diesel | 39 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Use of good combustion practices based on the most recent manufacturer's specifications issued for engine | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0347 | ANADARKO PETROLEUM CORPORATION - EGOM | ANADARKO PETROLEUM CORPORATION |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4015 | 1381 | 211111 | NA | 08/12/2013 &nbsp;ACT | 09/16/2014 &nbsp;ACT | 2015-09-21 | 2016-07-06 | A | http://www.regulations.gov/contentStreamer?documentId=EPA-R04-OAR-2014-0487-0069&disposition=attachment&contentType=pdf | The facility consists of a mobile offshore drilling unit using the Transocean Discoverer Spirit and associated support vessels. The drilling sites are located east of longitude 87.5, west of the Military Mission Line (86Â°41' west longitude), at least 100 miles from the Louisiana shoreline, and at least 125 miles from the Florida shoreline. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program regulations at 40 CFR part 71. This permit is based upon application materials submitted to EPA by Anadarko Petroleum Corporation (Anadarko) dated December 26, 2012, March 27,2013, April 26,2013, May 3, 2013, and July 2, 2013; supplemental submittals and information in the administrative record for this permit action; and upon the technical analysis performed by EPA. | Remotely Operated Vehicle Emergency Generator | 17.21 | Diesel | 427 | hp | 2004 Cummins QSM11-G2NR3 | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Use of good combustion practices based on the most recent manufacturer's specifications issued for engines and with turbocharger, aftercooler, and high injection pressure | 0 |  |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0.25 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.03 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
ID-0018 | LANGLEY GULCH POWER PLANT | IDAHO POWER COMPANY | PAYETTE | ID |  | USA |  | 2083885820 | TMAHLUM@IDAHOPOWER.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2009.0092 | 4911 | 221112 | UNKNOWN | 06/07/2009 &nbsp;ACT | 06/25/2010 &nbsp;ACT | 2010-08-09 | 2010-10-05 | A |  | ONE-ON-ONE COMBINED CYCLE PLANT CONSISTING OF (1) NATURAL GAS-FIRED COMBUSTION TURBINE (CT) AND (1) STEAM TURBINE. THE CT IS EQUIPPED WITH (1) HEAT RECOVERY STEAM GENERATOR (HRSG) AND DUCT BURNER. ANCILLARY EQUIPMENT INCLUDES (1) DIESEL-FIRED EMERGENCY GENERATOR, (1) DIESEL-FIRED FIRE PUMP, (1) WET COOLING TOWER, AND (6) DRY CHEMICAL STORAGE SILOS. |  | FIRE PUMP ENGINE | 17.21 | DIESEL | 235 | KW | COMPRESSION IGNITION INTERNAL COMBUSTION (CI ICE) | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | TIER 3 ENGINE-BASED, GOOD COMBUSTION PRACTICES (GCP) | 4 | G/KW-H | NOX+NMHC | BACT-PSD | NSPS | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LIMIT APPLIES TO NOX+NMHC COMBINED EMISSIONS.
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 0.4 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) FIREWATER PUMP DIESEL ENGINES | 17.21 | DIESEL | 371 | BHP, EACH | THE TWO FIREWATER PUMP ENGINES, IDENTIFIED AS FP01 AND FP02, EXHAUSTING THROUGH TWO (2) VENTS. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | COMBUSTION DESIGN CONTROLS AND USAGE LIMITS | 0.16 | LB/H |  | BACT-PSD |  |  | 0 |  | 500 | HOURS OF OPERATION | YEARLY | 0 |  |  | 0 | 0 | N |  | LIMIT ONE AND TWO ARE FOR EACH FIREWATER PUMP ENGINE
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.141 | G/BHP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.141 | G/BHP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.141 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.141 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.141 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | EMERGENCY FIRE PUMP ENGINE | 17.21 | DISTILLATE OIL | 0 |  | 425 HP | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.05 | G/HP-H |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | AMOUNT OF DIESEL BURNED SHALL NOT EXCEED 1,128 GALLONS PER 12 MONTH PERIOD
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Deisel | 150 | hp | 2 units at 75 hp, 1 unit at 150 hp | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 1.134 | G/HP-HR |  | BACT-PSD | NESHAP | U | 0 | U | 0.0025 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | VOC emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Diesel | 250 | hp | 2 units | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 1.134 | G/HP-HR |  | BACT-PSD | NESHAP | U | 0 | U | 0.0025 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | VOC emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
*KS-0030 | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | GRANT | KS | 67601 | USA | PAUL REYNOLDS | 620-277-4522 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Mindy Bowman, E-mail address: Mindy.Bowman@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-13309 | 4911 | 221112 | Not Found | 03/07/2017 &nbsp;ACT | 03/31/2016 &nbsp;ACT | 2017-04-06 | 2017-07-19 | C |  | Mid-Kansas Electric Company, LLC (Mid-Kansas Electric) (Source ID: 0670173) operates the Rubart Station located in Grant County, Kansas. The facility currently consist of twelve (12) new spark ignition four-stroke lean burn (4SLB) reciprocating internal combustion engines (RICE) used to generate electricity (the proposed project consist of 24 new 4SLB RICE). The generating capacity of each unit is 10 megawatts (approximately 13,410 BHP). Also located at the station is a diesel fire pump, natural gas emergency generator, heater, circuit breakers and switches. The insignificant activities include a diesel storage tank. | This PSD permit with tracking number C-13309 a modification of PSD permits C-12896 (PSD Administrative Amendment, issued on 5/7/2015), C-12721 (PSD Revisions, issued on 4/28/2015), and C-10021 (original PSD permit for the proposed project, issued on 1/28/2013). | Compression ignition RICE emergency fire pump | 17.21 | Ultra-lowsulfur diesel (ULSD) | 197 | HP | One (1) compression ignition emergency fire pump engine, rated at 197 HP, which shall burn only ultra-low sulfur diesel (ULSD, 15 ppm sulfur or less). | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 1.14 | G/HP-HR | EXCLUDES STARTUP, SHUTDOWN & MALFUNCTION | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | Cummins 6BTA 5.9F-1 Diesel Engine Fire Pump | 17.21 | No. 2 Fuel Oil | 182 | BHP |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | utilize efficient combustion/design technology | 0.77 | G/BHP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0224 | ARSENAL HILL POWER PLANT | SOUTHWEST ELECTRIC POWER COMPANY (SWEPCO) | CADDO | LA | 71101 | USA | KRIS GAUS | 2147771113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-726 | 4911 | 221112 | 110001270847 | 01/07/2008 &nbsp;ACT | 03/20/2008 &nbsp;ACT | 2008-04-18 | 2012-05-18 | B |  | NATURAL GAS FIRED ELECTRICAL GENERATION PLANT. |  | DFP DIESEL FIRE PUMP | 17.21 | DIESEL | 310 | HP | EQT-016 | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N | USE OF LOW-SULFUR FUELS, LIMITING OPERATING HOURS AND PROPER ENGINE MAINTENANCE | 0.77 | LB/H | MAX | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002049328 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | EMERGENCY FIRE PUMP | 17.21 | DIESEL | 350 | HP |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | ULTRA LOW SULFUR DIESEL AND GOOD COMBUSTION PRACTICES | 1 | G/HP-H | ANNUAL AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 1 | G/HP-H | ANNUAL AVERAGE | 0 | 0 | N
LA-0301 | LAKE CHARLES CHEMICAL COMPLEX ETHYLENE 2 UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | (281) 588-3761 | ERIC.RODRIGUEZ@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-779 | 2869 | 325110 | 110017418061 | 05/02/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2016-09-27 | 2017-04-28 | B |  |  | Complete application date = date of administrative completeness This RBLC entry addresses Ethylene Unit 2 of the Lake Charles Cracker Project. This unit will produce ethylene by thermally cracking ethane in cracking furnaces. | Firewater Pump Nos. 1-3 (EQTs 997, 998, &amp; 999) | 17.21 | Diesel | 500 | HP | Non-emergency use operating time is limited to 100 hr/yr (per engine). | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Compliance with 40 CFR 60 Subpart IIII and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage | 0.1 | LB/HR | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.005 | TPY | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | NOx + NMHC emissions are limited to 3.0 g/hp-hr. BACT is determined to be compliance with the limitations imposed by 40 CFR 60 Subpart IIII and its associated monitoring, recordkeeping, and reporting requirements; and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage.
LA-0309 | BENTELER STEEL TUBE FACILITY | BENTELER STEEL / TUBE MANUFACTURING CORPORATION | CADDO | LA | 71115 | USA | MYRNA PACHECO PONCE DE LEON | 318-216-4206 | MYRNA.PACHECO@BENTELER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen - 225-219-3395 | PSD-LA-774(M1) | 3312 | 331111 | 110055592318 | 02/09/2015 &nbsp;ACT | 06/04/2015 &nbsp;ACT | 2017-03-09 | 2017-04-28 | A |  | A facility to produce 600,000 metric tons per year of seamless steel pipe from purchased billets. A steel production facility (including an electric arc furnace (EAF)) was added. | Permit PSD-LA-774 was issued on May 17, 2013 for the construction of the hot rolling mill. An EAF was authorized this time. | Firewater Pump Engines | 17.21 | Diesel | 288 | hp (each) |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Complying with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Emergency Diesel Firewater Pump 1 | 17.21 | Diesel | 282 | HP |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 1.87 | LB/H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.47 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 3.0 G/BHP-HR (NMHC + NOx)
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel Firewater pump engines (6 units) | 17.21 | diesel | 425 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel emergency generator engine - EGEN | 17.21 | diesel | 350 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0316 | CAMERON LNG FACILITY | CAMERON LNG LLC | CAMERON | LA | 70645 | USA | CLAYTON MILLER | 337-680-4531 | CMILLER@CAMERONLNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-766(M3) | 4922 | 221210 | 110029511883 | 12/12/2016 &nbsp;ACT | 02/17/2017 &nbsp;ACT | 2017-03-14 | 2017-04-28 | B |  | a facility to liquefy natural gas for export (5 trains) | Permit PSD-LA-766, dated 10/1/13 for liquefaction trains 1,2, and 3 Permit PSD-LA-766(M1), dated 6/26/14, for minor changes; Permit PSD-LA-766(M2), dated 3/3/16, for train 4 and 5 | firewater pump engines (8 units) | 17.21 | diesel | 460 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Complying with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY GENERATOR | 17.21 | DIESEL |  |  | 1500 KW UNIT | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 4.8 | G/HP-H |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | WAS LISTED AS &lsquo;&lsquo;NONMETHANE HYDROCARBONS&lsquo;&lsquo;. CHANGED TO &lsquo;&lsquo;VOC&lsquo;&lsquo; BY RBLC STAFF ON 2/20/09. COMBINED LIMIT FOR NOX AND NON-METHANE HYDROCARBONS
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | EU-FPENGINE: Diesel fuel fired emergency backup fire pump | 17.21 | diesel fuel | 315 | hp nameplate | This is a diesel fuel fired emergency backup fire mump. It has a capacity of 315 hp, nameplate, and uses diesel fuel ASTM D975 Grade 2-D S15. Ultra low sulfur diesel fuel (15ppmw); 100 hours per year operation for maintenance and readiness testing. NSPS IIII and NESHAP ZZZZ. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Proper combustion design and ultra low sulfur diesel fuel. | 0 |  |  | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Ultra low sulfur diesel fuel (15 pppmw); 100 hours per year operation for maintenance and readiness testing. Both CO and VOC are products of incomplete combustion and are controlled using efficient combustion methods. The limitation on CO is an appropriate surrogate for VOC emissions. VOC also included in NMHC which is limited in combination with NOx.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Emergency Engine --Diesel Fire Pump (EUFPENGINE) | 17.21 | Diesel | 165 | HP | A 165 hoursepower (hp) diesel-fueled emergency engine manufactured in 2013, iwth a heat input of 1.35 MMBTU/hr. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 0.001 | LB/H | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An oxidation catalyst is greater than $619,000 for CO and VOC together.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 0.64 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | On average, an oxidation catalyst is greater than $308,000/ton for CO and VOC together.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | diesel | 500 | H/YR | A 165 horsepower (hp) diesel-fueled emergency engine manufactured in 2016 with a heat input of 1.35 MMBTU/H. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 0.47 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An oxidation catalyst is greater than $501,000/ton for CO and VOC together.
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (South Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices. | 0.75 | LB/H | HOURLY | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An oxidation catalyst is $39,500/ton for PM10, CO and VOC together.
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (North Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 0.75 | LB/H | HOURLY | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An oxidation catalyst is $39,500/ton for PM10, CO and VOC together.
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUFPENGINE: Fire pump engine | 17.21 | Diesel | 399 | BHP | A 399 brake HP diesel-fueled emergency fire pump engine with a model year of 2011 or later, and a displacement of <10 liters/cylinder. The engine is an EPA Tier 3 certified engine subject to NSPS IIII. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | State of the art combustion design. | 0.13 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | firewater pumps, diesel | 17.21 | diesel | 325 | HP, EACH | Eight 325 hp diesel firewater pumps | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | comply with NSPS IIII, 52 hr/yr non-emergency operation
OH-0317 | OHIO RIVER CLEAN FUELS, LLC | OHIO RIVER CLEAN FUELS, LLC | COLUMBIANA | OH |  | USA | STEPHAN M. DOPUCH | 4402570054 | SDOPUCH@BAARDENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | 02-22896 | 2869 | 325110 | UNKNOWN | 12/21/2007 &nbsp;ACT | 11/20/2008 &nbsp;ACT | 2008-11-28 | 2012-05-18 | A |  | COAL/BIOMASS-TO-LIQUIDS FACILITY. THE PRIMARY INDUSTRIAL PROCESSES: COAL/BIOMASS STORAGE AND HANDLING; COAL GASIFICATION; SYNGAS CLEANING (ACID GASS REMOVAL AND SULFUR RECOVERY PLANT); FISCHER-TROPSCH PROCESS (INDUSTRIAL ORGANIC CHEMICALS); PRODUCT UPGRADE PROCESS (SIMILAR TO PETROLEUM REFINING); LIQUID PRODUCT STORAGE &amp; LOADING; ELECTRIC POWER GENERATION (USE FOR ON SITE ONLY). BIOMASS IS RESTRICTED TO ONLY SAWDUST AND WOOD CHIPS. | NEW INDUSTRY, SIC AND NAICS CODE SELECTED BY FACILITY | FIRE PUMP ENGINES (2) | 17.21 | DIESEL FUEL OIL | 300 | HP | SUBJECT TO NSPS SUBPART IIII. WILL INSTALL NON-RESETTABLE HOUR METER PRIOR TO STARTUP PER 40 CFR 60.4209(A) DIESEL FUEL SHALL MEET THE REQUIREMENTS OF 40 CFR 80.510 AND 60.4207: SULFUR CONTENT OF 15 PPM MAXIMUM, CETANE INDEX OF 40 MINIMUM OR AROMATIC CONTENT OF 35 VOLUME % MAXIMUM | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES AND GOOD ENGINE DESIGN | 0.26 | LB/H | FOR EACH ENGINE | BACT-PSD | SIP , NSPS | U | 0 | N | 0.07 | T/YR | PER ROLLING 12-MONTH PERIOD | 7.8 | G/HP-H | FOR NMHC AND NOX COMBINED, 5% NMHC | 0 | 0 | N |  | POLLUTANT IS NON METHANE HYDROCARBONS. 7.8 G/HP-H FOR NON-METHANE HYDROCARBONS AND NOX COMBINED LIMIT FROM NSPS SUBPART IIII TABLE 4; 5% CONSIDERED NMHC IN HOURLY LIMIT CALCULATION LIMITS FOR EACH ENGINE.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | Emergency fire pump engine | 17.21 | diesel | 300 | HP | 223.8 kW. Emergency fire pump engine restricted to 500 hours of operation per rolling 12 months. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 24A | (Volatile Organic Compounds (VOC)) | VOC | P | Purchased certified to the standards in NSPS Subpart IIII | 0.25 | LB/H |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.06 | T/YR | PER ROLLING 12-MONTHS | 0 |  | SEE NOTES | 0 | 0 | N |  | Additional limit: 0.50 g VOC/kW-h; and 4.0 g NMHC + NOx/kW-h Subpart IIII standard. Method 25A if required
OK-0129 | CHOUTEAU POWER PLANT | ASSOCIATED ELECTRIC COOPERATIVE INC | MAYES | OK | 74362 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2007-115-C(M-1)PSD | 4911 | 221112 | 4009700017 | 06/19/2008 &nbsp;ACT | 01/23/2009 &nbsp;ACT | 2009-11-20 | 2010-02-18 | B |  |  |  | EMERGENCY FIRE PUMP (267-HP DIESEL) | 17.21 | LOW SULFUR DIESEL | 267 | HP |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N | GOOD COMBUSTION | 0.66 | LB/H |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0164 | MIDWEST CITY AIR DEPOT | TINKER AIR FORCE BASE LOGISTICS CENTER | OKLAHOMA | OK | 73145 | USA | COL. CHRISTOPHER AZZANO | 405-734-2102 | 72ABW.WORKFLOW@TINKER.AF.MIL | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2009-394-C(M-2)PSD | 9711 | 928110 | 109-00090 | 04/09/2014 &nbsp;ACT | 01/08/2015 &nbsp;ACT | 2015-08-07 | 2016-07-06 | B |  | In February 2011, the U.S. Air Force (USAF) selected the Boeing KC-767 to replace its aging KC-135 tankers and assigned the new aircraft the designation KC-46A. Tinker AFB was selected to perform the programmed depot-level maintenance of the KC-46A aircraft. | Applicant requests authorization to construct facilities to accommodate new workload associated with the KC-46 aircraft. | Diesel-Fueled Fire Pump Engines | 17.21 | Ultra-Low Sulfur Distillate Fuel | 300 | HP | Operate for 100 hours maximum annually | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | 1. Good Combustion Practices. | 0.15 | GRAMS PER HP-HR | TOTAL FOR 3 ENGINES. | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0175 | WILDHORSE TERMINAL | WILDHORSE TERMINAL LLC | LINCOLN | OK | 74023 | USA | GREG WARNOCK | 403-860-8760 | GREG_WARNOCK@KEYERA.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2016-1066-C PSD | 4612 | 486110 | Not Found | 09/30/2016 &nbsp;ACT | 06/29/2017 &nbsp;ACT | 2017-07-14 | 2018-05-11 | A |  | The new facility will be designed to receive crude oil via pipeline and tank trucks and store crude in tanks for later transportation via pipeline. No outbound loading stations for tank trucks will be located at the terminal. | FRS Entered as &lsquo;&lsquo;081-00099&lsquo;&lsquo;. Too short for a FRS. Wildhorse Terminal, LLC (WTL or the applicant) has submitted an application to construct a new bulk terminal located in Cushing, Oklahoma. The new facility is classified under NAICS Code 486110 â€“ Pipeline Transportation of Crude Oil. The proposed tanks will be subject to New Source Performance Standards 40 CFR Part 60 (NSPS), Subpart Kb. The facility is a listed Prevention of Significant Deterioration (PSD) major source, a crude oil storage facility exceeding 300,000-barrel (bbl) storage capacity with proposed permitted emissions in excess of 100 TPY. Potential VOC emissions have been estimated at 184.37 TPY. Therefore, the application required a full PSD review. | Emergency Use Engine less than or equal to 500 HP | 17.21 | Diesel | 0 |  | One (1) 275-hp emergency generator, two (2) 176-hp firewater pump engines, and one (1) 156-hp portable stripping engine. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices, certified to meet EPA Tier 3 engine standards. Gen-1, FP-1, and FP-2 shall be limited to operate no more than 500 hr/yr. | 3 | GM/HP-HR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 40 CFR Part 60, Subpart IIII.
OK-0176 | BPV GATHERING AND MARKETING CUSHING STATION | BPV GATHERING AND MARKETING LLC | LINCOLN | OK | 74023 | USA | TYLER FLEMING | 405-341-0789 | TFLEMING@BARCASLLC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2016-1247-C PSD | 4612 | 486110 | Not Found | 11/22/2016 &nbsp;ACT | 07/19/2017 &nbsp;ACT | 2017-07-25 | 2018-05-11 | A |  | The facility will consist of twenty-four (24) 250,000-bbl external floating roof (EFR) crude oil storage tanks. The proposed tanks will be subject to New Source Performance Standards 40 CFR Part 60 (NSPS), Subpart Kb. The new facility will be designed to receive crude oil via pipeline and store crude oil in tanks for later transportation via pipeline. There are no truck unloading facilities at this site. | FRS Entered as &lsquo;&lsquo;081-00101&lsquo;&lsquo;. Too short for a FRS. The project is subject to PSD review because it is a listed PSD-major source, a crude oil storage facility exceeding 300,000-barrel (bbl) storage capacity with current permitted emissions in excess of 100 TPY of VOC. | Emergency Generator | 17.21 | Diesel | 400 | HP | One (1) 400-hp emergency generator. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Equipped with non-resettable hour meter. Fired with ultra-low sulfur diesel fuel (0.015 % or less by wt. sulfur. | 217.24 | TONS/YEAR/FACILITY | 12-MONTH | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 40 CFR Part 60 Subpart IIII. 40 CFR Part 63 Subpart ZZZZ.
PR-0009 | ENERGY ANSWERS ARECIBO PUERTO RICO RENEWABLE ENERGY PROJECT | ENERGY ANSWERS ARECIBO, LLC | ARECIBO | PR |  | USA | MARK GREEN | (347)-351-5248 |  | 2 | OT003 | EPA REGION II | MR. FRANK JON | (212)637-4085 | jon.frank@epa.gov | Ms. Viorica Petriman petriman.viorica@epa.gov | R2-PSD 1 | 4953 | 221119 | FRL-9911-10-Region 2 | 11/11/2012 &nbsp;ACT | 04/10/2014 &nbsp;ACT | 2014-10-14 | 2016-05-05 | A |  | Energy Answers Arecibo is a new resource recovery facility capable of producing up to 77 megawatts (MW) of electrical power while combusting municipal solid waste, as the primary fuel. | This is a PSD permit for a new/greenfield facility. | Emergency Diesel Fire Pump | 17.21 | ULSD Fuel Oil #2 | 0 |  | The Emergency Fire Pump is rated at 335 BHP and limited to 500 hr/yr (emergency operations and testing and maintenance, combined). | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.15 | G/B-HP-H |  | BACT-PSD |  | U | 0 | U | 0.11 | LB/H |  | 0 |  |  | 0 | 0 | N
SC-0113 | PYRAMAX CERAMICS, LLC | PYRAMAX CERAMICS, LLC | ALLENDALE | SC | 29810 | USA | RICHARD DERBAWKA | 7705690079 | R.DERBAWKA@PYRAMAXCERAMICS.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MS. ALYSON HAYES | (803)898-3836 | camitdr@dhec.sc.gov | GEORGE S. ROBINSON (803) 898-4123 | 0160-0023 | 3295 | 327992 | Not Available | 09/16/2011 &nbsp;ACT | 02/08/2012 &nbsp;ACT | 2012-05-09 | 2012-10-17 | A |  | PYRAMAX CERAMICS PLANS TO CONSTRUCT A MANUFACTURING FACILITY FOR THE PRODUCTION OF PROPPANT BEADS FOR USE IN THE OIL AND GAS INDUSTRY. THE MAJOR RAW MATERIAL IS CLAY. THE CLAY IS MIXED WITH CHEMICALS AND THEN FIRED IN A KILN TO PRODUCE CERAMIC BEADS. INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | EMERGENCY ENGINE 1 THRU 8 | 17.21 | DIESEL | 29 | HP | THE CONSTRUCTION PERMIT AUTHORIZES THE CONSTRUCTION OF EIGHT (8) IDENTICAL EMERGENCY ENGINES. THIS PROCESS AND POLLUTANT INFORMATION IS FOR ONE SINGLE ENGINE. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | PURCHASE OF CERTIFIED ENGINES. HOURS OF OPERATION LIMITED TO 100 HOURS FOR MAINTENANCE AND TESTING. | 7.5 | GR/KW-H |  | BACT-PSD | NSPS | Y | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | FACILITY MUST PURCHASE ENGINES CERTIFIED BY THE MANUFACTURER TO MEET NSPS, SUBPART IIII. FACILITY WILL MAINTAIN RECORDS TO SHOW COMPLIANCE WITH NSPS, SUBPART IIII.
SC-0113 | PYRAMAX CERAMICS, LLC | PYRAMAX CERAMICS, LLC | ALLENDALE | SC | 29810 | USA | RICHARD DERBAWKA | 7705690079 | R.DERBAWKA@PYRAMAXCERAMICS.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MS. ALYSON HAYES | (803)898-3836 | camitdr@dhec.sc.gov | GEORGE S. ROBINSON (803) 898-4123 | 0160-0023 | 3295 | 327992 | Not Available | 09/16/2011 &nbsp;ACT | 02/08/2012 &nbsp;ACT | 2012-05-09 | 2012-10-17 | A |  | PYRAMAX CERAMICS PLANS TO CONSTRUCT A MANUFACTURING FACILITY FOR THE PRODUCTION OF PROPPANT BEADS FOR USE IN THE OIL AND GAS INDUSTRY. THE MAJOR RAW MATERIAL IS CLAY. THE CLAY IS MIXED WITH CHEMICALS AND THEN FIRED IN A KILN TO PRODUCE CERAMIC BEADS. INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | FIRE PUMP | 17.21 | DIESEL | 500 | HP | THE CONSTRUCTION PERMIT AUTHORIZES THE CONSTRUCTION OF ONE (1) FIRE PUMP. THIS PROCESS AND POLLUTANT INFORMATION IS FOR THIS ONE SINGLE FIRE PUMP. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | CERTIFIED ENGINES THAT COMPLY WITH NSPS, SUBPART IIII. HOURS OF OPERATION LIMITED TO 100 HOURS PER YEAR FOR MAINTENANCE AND TESTING. | 4 | GR/KW-H |  | BACT-PSD | NSPS | Y | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | FACILITY MUST PURCHASE ENGINES CERTIFIED BY THE MANUFACTURER TO MEET NSPS, SUBPART IIII. FACILITY TO MAINTAIN RECORDS TO SHOW COMPLIANCE WITH NSPS, SUBPART IIII.
SC-0159 | US10 FACILITY | MICHELIN NORTH AMERICA, INC. | ANDERSON | SC | 29684 | USA | MIKE ARNTZ | 8648717633 | MIKE.ARNTZ@US.MICHELIN.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MS. ALYSON HAYES | (803)898-3836 | camitdr@dhec.sc.gov |  | 0200-0225-CA | 3011 | 326211 | 1100555885500 | 02/07/2012 &nbsp;ACT | 07/09/2012 &nbsp;ACT | 2013-11-06 | 2014-08-27 | A |  | THE FACILITY PRODUCES COMPONENTS FOR EARTHMOVER TIRES AND THEN IN TURN ASSEMBLES TIRES FROM THESE COMPONENTS. |  | FIRE PUMPS, FIRE1, FIRE2, FIRE3 | 17.21 | DIESEL | 211 | KW | THREE (3) 211 KW/282 BHP (EACH) EMERGENCY DIESEL FIRE PUMPS THAT ARE EXPECTED TO BE OPERATED UP TO 100 HOURS PER YEAR OR LESS FOR TESTING AND MAINTENANCE. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 24A | (Volatile Organic Compounds (VOC)) | VOC | P | BACT HAS BEEN DETERMINED TO BE COMPLIANCE WITH NSPS, SUBPART IIII, 40 CFR60.4202 AND 40 CFR60.4205. | 4 | GKW-H |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | THIS LIMIT IS PER FIRE PUMP, NOT A TOTAL FOR ALL FIRE PUMPS.
TX-0706 | NATURAL GAS FRACTIONATION | OCCIDENTAL CHEMICAL CORPORATION | SAN PATRICIO | TX |  | USA | PAUL THOMAS | 361-776-6169 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ozden Tamer Phone 5122394577 ozden.tamer@tceq.texas.gov | 102482, PSDTX1292 | 1321 | 325199 | 110000599807 | 04/27/2012 &nbsp;ACT | 01/23/2014 &nbsp;ACT | 2015-03-20 | 2016-05-16 | B |  | Occidental will build a NGL Fractionation Plant that will receive natural gas liquids by pipeline and fractionate these liquids into commercial grade products, including ethane, propane, butanes, and natural gasoline | This permit authorized Occidental to construct and operate an 87,000 barrel/day capacity Natural Gas Liquids Fractionation Plant immediately adjacent to its Vinyl Chloride Monomer Plant in Gregory, San Patricio County, Texas | Emergency Engines | 17.21 | Ultra-low sulfur diesel | 0 |  | The process includes 1 emergency generator and 4 emergency firewater pump engines. The sulfur in the diesel fuel will meet the sulfur requirement of 15 ppm in 40 CFR 80.510(b). The emissions from each engine result from weekly testing which will occur 52 hours a year for each engine. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.03 | TPY |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0799 | BEAUMONT TERMINAL | PHILLIPS 66 PIPELINE LLC | JEFFERSON | TX |  | USA | CHINTAN MEHTA | 832-765-1677 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Beth Akers, 512-239-4620 beth.akers@tceq.texas.gov | 18295, PSDTX1466, GHGPSDTX139 | 5171 | 424710 | 110033444850 | 04/19/2016 &nbsp;ACT | 06/08/2016 &nbsp;ACT | 2016-06-17 | 2016-07-07 | C |  | This marine terminal receives, stores, and distributes various volatile organic liquids (VOLs) and refined petroleum products. | (consolidate and/or void: 1973, 8113, 481, 2365, 56419, 6312, and 6559) | EMERGENCY ENGINES | 17.21 | diesel | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Equipment specifications and good combustion practices. Operation limited to 100 hours per year. | 0.0025 | LB/HP-HR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*WI-0261 | ENBRIDGE ENERGY - SUPERIOR TERMINAL | ENBRIDGE ENERGY LIMITED PARTNERSHIP | DOUGLAS | WI | 54880-5247 | USA | RHONDA O'LEARY | 218-464-5626 | RHONDA.OLEARY@ENBRIDGE.COM | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov | Kristin.Hart@wisconsin.gov; Ronald.Binzley@wisconsin.gov Megan.Corrado@wisconsin.gov | 13-DCF-129 | 4612 | 486110 | 110000878097 | 04/11/2014 &nbsp;ACT | 06/12/2014 &nbsp;ACT | 2017-06-29 | 2017-07-07 | D | http://dnr.wi.gov/topic/AirPermits/Search.html | Petroleum (Crude Oil) storage facility and pipeline terminal FRS 110000878097 | Wisc. FID 816010580. Also see permit 12-DCF-205. FRS 110000878097 Crude oil (petroleum) pipeline terminal | EG7 - Diesel Emergency Electric Generator w/ tank | 17.21 | Diesel fuel oil | 197 | BHP | 197 BHP / 147 KW; 1.38 MMBTU/hr (est. 125 KWe). Limited to 200 hours / year. Distillate fuel oil storage tank | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | NSPS engine [Tier 3 emergency engine]. EG7 Storage tank, conventional fuel oil storage tank, good operating practices; limiting leakage, spills. (FT01). Engine limited to 200 hours / year (total) and NSPS requirements. | 3.75 | GRAM / HP-HR | NOX + NMHC HOURLY AVG., FOR EG7 | BACT-PSD | NSPS , NESHAP | U | 0 | U | 3 | GRAM / HP-HR | NOX + NMHC FOR ENGINE CLASS (HOURLY AVG. | 0 |  |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Fire Pump Engine | 17.21 | Diesel | 251 | HP | Limited to 100 Hours/year. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.17 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N