## All Pollutants_Small RICE 17.21
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUFPENGINE: Fire pump engine | 17.21 | Diesel | 399 | BHP | A 399 brake HP diesel-fueled emergency fire pump engine with a model year of 2011 or later, and a displacement of <10 liters/cylinder. The engine is an EPA Tier 3 certified engine subject to NSPS IIII. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion | 86 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0799 | BEAUMONT TERMINAL | PHILLIPS 66 PIPELINE LLC | JEFFERSON | TX |  | USA | CHINTAN MEHTA | 832-765-1677 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Beth Akers, 512-239-4620 beth.akers@tceq.texas.gov | 18295, PSDTX1466, GHGPSDTX139 | 5171 | 424710 | 110033444850 | 04/19/2016 &nbsp;ACT | 06/08/2016 &nbsp;ACT | 2016-06-17 | 2016-07-07 | C |  | This marine terminal receives, stores, and distributes various volatile organic liquids (VOLs) and refined petroleum products. | (consolidate and/or void: 1973, 8113, 481, 2365, 56419, 6312, and 6559) | EMERGENCY ENGINES | 17.21 | diesel | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion | 6.79 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0319 | GATEWAY COGENERATION 1, LLC - SMART WATER PROJECT | GATEWAY GREEN ENERGY | PRINCE GEORGE | VA | 23875-3000 | USA | T. EDWARD MCDANIEL | 972-638-8798 | EMCDANIEL@GGEHLLC.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52375-002 | 4911 | 221112 | 110045446718 | 01/11/2012 &nbsp;ACT | 08/27/2012 &nbsp;ACT | 2013-01-16 | 2015-05-29 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Combined cycle electrical power generating facility (160 MW), consisting of two combusion turbines (Rolls Royce Trent 60 WLE) with associated HRSG and no duct burning. |  | FIRE WATER PUMP | 17.21 | diesel (ultra low sulfur) | 1.86 | MMBTU/H | 500 H/Yr operation | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion | 30.5 | T/YR | 12 MO ROLLING AVG | BACT-PSD | NSPS , MACT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | EU-FPENGINE: Diesel fuel fired emergency backup fire pump | 17.21 | diesel fuel | 315 | hp nameplate | This is a diesel fuel fired emergency backup fire mump. It has a capacity of 315 hp, nameplate, and uses diesel fuel ASTM D975 Grade 2-D S15. Ultra low sulfur diesel fuel (15ppmw); 100 hours per year operation for maintenance and readiness testing. NSPS IIII and NESHAP ZZZZ. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion | 15.6 | T/YR | 12-MO. ROLL TIME PERIOD | BACT-PSD | N/A | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Ultra low sulfur diesel fuel (15 ppmw); 100 hour per year operation for maintenance and readiness testing.
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Port and Stb Fwd and Aft Crane Diesel Engines - C.R. Luigs | 17.21 | diesel | 305 | HP |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Good combustion | 3083 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - C.R. Luigs | 17.21 | diesel | 0 |  | Cementing Units: Caterpillar 3412 CDITA 860 hp 2001 Nitrogen Pump: Caterpillar 3406 CDITA 490 hp 2000 | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Good combustion | 628.9 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Cementing and Nitrogen Pump Diesel Engines - Development Driller 1 | 17.21 | Diesel | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Good combustion | 715.5 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Wireline Unit Engines - C.R. Luigs | 17.21 | diesel | 300 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Good combustion | 536.6 | T/12MO ROLLING TOTAL | TONS PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0338 | SAKE PROSPECT DRILLING PROJECT | BHP BILLITON PETROLEUM, INC. |  | FL |  | USA |  |  |  | 4 | OT005 | EPA REGION IV | MS. KATY R. FORNEY | (404) 562-9130 | forney.kathleen@epa.gov |  | OCS-EPA-R4008 | 1381 | 211111 | NA | 03/10/2011 &nbsp;ACT | 05/30/2012 &nbsp;ACT | 2014-02-28 | 2016-05-04 | A | http://www.regulations.gov/#!documentDetail;D=EPA-R04-OAR-2012-0239-0037 | The facility consists of a mobile offshore drilling unit (MODU) using either the Transocean ultra-deepwater C.R. Luigs or the Transocean semisubmersible DD1 to conduct exploratory oil and natural gas drilling in lease blocks within the DeSoto Canyon area of the Gulf of Mexico. | The United States Environmental Protection Agency (EPA) issued this permit pursuant to section 328 of the CAA, 42 U.S.C. Â§ 7627, and the implementing OCS Air Regulations at 40 CFR part 55, which incorporate by reference the PSD Regulations at 40 CFR Â§ 52.21 and the title V Operating Permit Program at 40 CFR part 71. This permit is based upon application materials submitted to EPA by BHP Billiton Petroleum, Inc. (BHPB), dated October 14, 2010, February 9, 2011, September 30, 2011, October 14, 2011, December 21, 2011, January 18, 2012, supplemental submittals in the administrative record for this permit action, and upon the technical analysis performed by EPA. | Wireline Unit Diesel Engines - Development Driller 1 | 17.21 | Diesel | 0 |  | Wireline units including primary, alternative #2, power plant, and hydraulic generator | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion | 536.6 | TONS | PER YEAR 12 MONTH ROLLING TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Fire pump engine | 17.21 | Ultra-low sulfur diesel | 15 | gal/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N | Good Combustion | 9 | TON | 12-MONTH ROLLING BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Emergency diesel engine | 17.21 | diesel | 750 | KW | One (1) 1102 HP (750 KW) emergency diesel engine | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N | Good Combustion | 59.5 | TONS PER YEAR | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Compliance with the CO2e BACT limit shall be demonstrated with an oxygen (O2) concentration monitor in accordance with CO2 calculations provided in 40 CFR Part 75. Calculations shall consist of CO2 emissions only, which account for 99.9% of total CO2e emissions.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | Emergency fire pump engine | 17.21 | diesel | 300 | HP | 223.8 kW. Emergency fire pump engine restricted to 500 hours of operation per rolling 12 months. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N | Good Combustion | 87 | T/YR | PER ROLLING 12-MONTHS | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0103 | CRICKET VALLEY ENERGY CENTER | CRICKET VALLEY ENERGY CENTER LLC | USA | NY | 12522-0407 | USA |  | 845-877-0596 | INFO@CRICKETVALLEY.COM | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-1326-00275/00009 | 4911 | 221112 | 110043340364 | 02/03/2016 &nbsp;ACT | 02/03/2016 &nbsp;ACT | 2017-08-24 | 2017-09-28 | A | http://www.dec.ny.gov/chemical/32249.html | Cricket Valley Energy Center LLC (CVEC) constructed the Cricket Valley Energy Center (the Facility), a nominal net 1,000-megawatt (MW) combined-cycle gas turbine electric generating facility, on a site located in Dover, Dutchess County, New York. The Facility consists of three General Electric (GE) Model 7FA.05 combustion turbine generators (CTGs) operating in combined-cycle mode with supplemental firing of the heat recovery steam generators (HRSGs); natural gas will be the sole fuel fired in the CTGs and duct burners. The Facility will include a natural gas-fired auxiliary boiler, four ultra-low sulfur distillate (ULSD) fired black-start generator engines and a ULSD-fired emergency fire pump engine. In addition to the air emitting equipment, the Facility will include three steam turbine generators (STGs), an air cooled condenser (ACC) and associated auxiliary equipment and systems. Each combined cycle generating unit consisting of the CTG, HRSG and STG will be exhausted through its own stack. Air emissions from the proposed Facility primarily consist of products of combustion from the CTGs, HRSG duct burners, and ancillary combustion sources. Dutchess County is designated as in attainment with respect to the National Ambient Air Quality Standards (NAAQS) for all criteria pollutants with the exception of ozone. Based upon the potential to emit (PTE) estimates, the Facility is subject to Prevention of Significant Deterioration (PSD) requirements for emissions of carbon monoxide (CO); nitrogen oxides (NOx); particulate matter (PM) with a diameter equal to or less than 10 microns (PM10), PM with a diameter equal to or less than 2.5 microns (PM2.5); greenhouse gases (GHG); sulfuric acid mist (H2SO4); and volatile organic compounds (VOC). In accordance with the NYSDECâ€™s Nonattainment New Source Review (NNSR) permitting program, the Facility is also subject to NNSR for emissions of NOx and VOC. |  | Emergency fire pump | 17.21 | ultra low sulfur diesel | 460 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practice and efficient engine design. | 115 | TPY | MO | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0164 | MIDWEST CITY AIR DEPOT | TINKER AIR FORCE BASE LOGISTICS CENTER | OKLAHOMA | OK | 73145 | USA | COL. CHRISTOPHER AZZANO | 405-734-2102 | 72ABW.WORKFLOW@TINKER.AF.MIL | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2009-394-C(M-2)PSD | 9711 | 928110 | 109-00090 | 04/09/2014 &nbsp;ACT | 01/08/2015 &nbsp;ACT | 2015-08-07 | 2016-07-06 | B |  | In February 2011, the U.S. Air Force (USAF) selected the Boeing KC-767 to replace its aging KC-135 tankers and assigned the new aircraft the designation KC-46A. Tinker AFB was selected to perform the programmed depot-level maintenance of the KC-46A aircraft. | Applicant requests authorization to construct facilities to accommodate new workload associated with the KC-46 aircraft. | Diesel-Fueled Fire Pump Engines | 17.21 | Ultra-Low Sulfur Distillate Fuel | 300 | HP | Operate for 100 hours maximum annually | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 44 | TONS PER YEAR | TOTAL FOR 3 ENGINES. | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0612 | THOMAS C. FERGUSON POWER PLANT | LOWER COLORADO RIVER AUTHORITY | LLANO | TX | 78767-7041 | USA | KENNETH TAYLOR | 979-249-8377 | KEN.TAYLOR@LCRA.ORG | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | Melanie Magee, 6PD-R Air Permit Section EPA Region VI (214)665-7161 | PSD-TX-1244-GHG | 4911 | 221122 | 110000456620 | 04/14/2011 &nbsp;ACT | 11/10/2011 &nbsp;ACT | 2012-02-08 | 2013-09-25 | D |  | Install 2 new natural gas-fired combined-cycle combustion turbine units (U1-STKand U2-STK) with a generating capacity of approximately 590 MW. The steam produced from the two new combustion turbines will exhaust to two dedicated Heat Recovery Steam Generators (HRSG) to produce steam. The steam produced from the two HRSGs is routed to the new shared steam turbine unit to produce electricity for sale to the Electric Reliability Council of Texas (ERCOT) power grid. |  | FWP1-STK DIESEL FIRED FIRE WATER PUMP | 17.21 | DIESEL | 617 | HP | 617 HP diesel fired Fire Water Pump. | Carbon Dioxide Equivalent (CO2e) | Other - Method 3a or 3b for CO2 | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 351.4 | tpy | 30-DAY ROLLING AVERAGE | BACT-PSD | NSPS | U | 0 | U | 351.4 | T/YR | 30-DAY ROLLING AVERAGE | 0 |  |  | 0 | 0 | N |  | 617 -horsepower(HP) Diesel Fire Water Pump rated at 43.2 MMBtu/hr and limited to 100 hours of operation per year for non-emergency activities.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Emergency Engine --Diesel Fire Pump (EUFPENGINE) | 17.21 | Diesel | 165 | HP | A 165 hoursepower (hp) diesel-fueled emergency engine manufactured in 2013, iwth a heat input of 1.35 MMBTU/hr. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 0.29 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Pump Engines DFP-16-1 (EQT036) | 17.21 | Diesel | 225 | horsepower | Limit operations to 100 hour/year | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 13 | T/YR | ANNUAL MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 73.96 kg/MM BTU of CO2, 0.003 kg/MM BTU of CH4, and 0.0006 kg/MM BTU of N2O
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Pump Engine DFP-16-2 (EQT037) | 17.21 | Diesel | 225 | horsepower | Limit operations to 100 hr/yr | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 13 | T/YR | ANNUAL MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 73.96 kg/MM BTU of CO2, 0.003 kg/MM BTU of CH4, and 0.0006 kg/MM BTU of N2O
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 13.58 | T/YR | 12 MO. ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Carbon Dioxide Equivalent (CO2e) | Other - recordkeeping | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 91 | TONS/YR | ROLLING 12 MONTH TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*AK-0084 | DONLIN GOLD PROJECT | DONLIN GOLD LLC. | BETHEL CENSUS AREA | AK | 99575 | USA | STAN FOO | 907-273-0200 | SFOO@DONLINGOLD.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | AK DEC DIV. OF AIR QUALITY 410 WILLOUGHBY AVE. SUITE 303 JUNEAU, AK 99801 | AQ0934CPT01 | 1041 | 212221 | Not Entered | 10/15/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2018-06-21 | 2018-06-22 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16763360/d1h2U6BIY-j857LFU-WYmw2 | The Donlin Gold Project is a gold mine located 12 miles north of Crooked Creek, Alaska on the Kuskokwim River, about 280 miles northwest of Anchorage. The deposit has proven and probable reserves estimated at 33.9 million ounces of gold at 2.1 g/t and could produce up to 1.5 million ounces annually. SIC Code 1041; NAICS Code 212221. |  | Fire Pump Diesel Internal Combustion Engines | 17.21 | Diesel | 252 | hp | Three (3) 252 hp fire pump diesel internal combustion engines. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices | 216 | TPY (COMBINED) | YEARLY | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 216 tpy CO2e for EUs 35 - 37 combined. NSPS Subpart IIII engines
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | diesel | 500 | H/YR | A 165 horsepower (hp) diesel-fueled emergency engine manufactured in 2016 with a heat input of 1.35 MMBTU/H. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices. | 55.6 | T/YR | 12-MONTH ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (South Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices. | 85.6 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (North Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices. | 85.6 | T/YR | 12-MONTH ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) FIREWATER PUMP DIESEL ENGINES | 17.21 | DIESEL | 371 | BHP, EACH | THE TWO FIREWATER PUMP ENGINES, IDENTIFIED AS FP01 AND FP02, EXHAUSTING THROUGH TWO (2) VENTS. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD ENGINEERING DESIGN AND FUEL EFFICIENT DESIGN | 172 | TONS | 12 CONSECUTIVE MONTH PERIOD | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LIMIT ONE: COMBINED EMISSION LIMIT: COMPLAINCE DETERMINED AT THE END OF THE MONTH
TX-0824 | JACKSON COUNTY GENERATING FACILITY | SOUTHERN POWER | JACKSON | TX |  | USA | KELLI MCCULLOUGH | 205-257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Marc Sturdivant, (512)239-1313, marc.sturdivant@tceq.texas.gov | GHGPSDTX118 | 4911 | 221112 | Not Found | 08/15/2016 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-07-20 | 2017-11-16 | A |  | simple cycle electric generation |  | Emergency Diesel-Fired Equipment | 17.21 | DIESEL | 160 | HP |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good operating and maintenance practices, efficient design, and low annual capacity | 13 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0758 | ECTOR COUNTY ENERGY CENTER | INVENERGY THERMAL DEVELOPMENT LLC | ECTOR | TX | 79741 | USA | MATTHEW THORNTON | 312-582-1527 | MTHORNTON@INVENERGYLLC.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | EPA Region 6 Permit Writer: Anna Milburn, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | GHGPSDTX1366 | 4911 | 221112 | Not Assigned | 04/18/2014 &nbsp;ACT | 08/01/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | A | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | Invenergy proposes to construct a 330 MW peak power plant (known as the Ector County Energy Center Plant (ECEC)), located in Goldsmith, Ector County, Texas. With this proposed project, Invenergy plans to construct two natural gas-fired simple-cycle turbines, General Electric (GE) Model 7FA.03, and associated equipment, a fire water pump engine, a natural gas-fired dew-point heater, and two circuit breakers. For the purposes of this proposed permitting action, GHG emissions are permitted for the two turbines, the fire water pump engine, the natural gas-fired dew-point heater, and the circuit breakers, as well as for fugitive emissions, and maintenance, startup and shutdown emissions. | Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. | Firewater Pump Engine | 17.21 | Diesel | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N | limited operation | 5 | TPY CO2E | 12-MONTH ROLLING TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Not to exceed 100 hours of non-emergency operation on a 12-month rolling basis. Use of good combustion practices
TX-0757 | INDECK WHARTON ENERGY CENTER | INDECK WHARTON, LLC | WHARTON | TX | 77432 | USA | JAMES SCHNEIDER | 847-520-3212 | JSCHNEIDER@INDECKENERGY.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Jennifer Huser, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | PSD-TX-1374-GHG | 4911 | 221112 | Not Assigned | 04/05/2014 &nbsp;ACT | 05/12/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | A | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | Indeck proposes to construct a peaking power plant, the Indeck Wharton Energy Center, generally located south of Danevang, Texas. To meet the anticipated demand for peak power, Indeck proposes to construct three identical natural gas-fired F-class simple cycle combustion turbines with associated support equipment. Indeck proposes that the three new combustion turbine generators (CTGs) will be either General Electric (GE) 7FA.05 or Siemens SGT6-5000F(5). The GE 7FA.05 has a base-load electric power output of approximately 213 megawatts (MW, net nominal), and the Siemens SGT6-5000F(5) has a base-load electric power output of approximately 225 MW (net nominal). This project also proposes to install one emergency diesel generator, one diesel fire water pump, one natural gas pipeline heater, and other auxiliary equipment. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. | Firewater Pump Engine | 17.21 | ULSD | 175 | hp | Indeck will be equipped with one nominally rated 175-hp diesel-fired pump engine to provide water in the event of a fire. The fire water pump will operate a maximum of 52 hours of non-emergency operation on a 12-month rolling basis for testing and maintenance. The fire water pump engine emissions represent 0.003% of the total facility-wide GHG emissions. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N | Limited Operation | 5.34 | TPY CO2E | 12-MONTH ROLLING TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT for the fire water pump engine will be to limit operation to no more than 52 hours of non-emergency operation per year for the purpose of maintenance, testing, and inspection. Indeck will also monitor hours of operation for the purpose of maintenance, testing, and inspection for each engine on a monthly basis. Compliance will be based on runtime hour meter readings on a 12-month rolling basis.
TX-0753 | GUADALUPE GENERATING STATION | GUADALUPE POWER PARTNERS, L.P. | GUADALUPE | TX | 78124 | USA | BILL SKINNER | 281-252-5221 | BSKINNER@NAVASOTAENERGY.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Melanie Magee, EPA Region 6, Air Permits Section (6PD-R), 1445 Ross Avenue, Dallas, TX 75202 | PSD-TX-1310-GHG | 4911 | 221112 | 110021360329 | 10/24/2014 &nbsp;ACT | 12/02/2014 &nbsp;ACT | 2015-07-20 | 2016-07-06 | B | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | GPP proposes to add two (2) new gas-fired simple-cycle combustion turbines of 227 MW (nominal) electric generating capacity each to the 1,000 MW (nominal) existing major stationary source, Guadalupe Generating Station (GGS), located in Marion, Texas. The proposed project will provide peaking capacity at an existing natural gas fired combined cycle electric generating station. The two new natural gas-fired simple-cycle turbines are proposed to provide a fast ramp up for additional peaking capacity during peak electricity demand periods. In addition, the project also includes the installation of a firewater pump engine, circuit breakers and associated fugitive emissions. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. See CN600132120 and RN100225820 | Fire Water Pump Engine | 17.21 | ULSD | 1.92 | MMBtu/hr (HHV) | Shall not exceed 100 hours of non-emergency operation on a 12-month rolling basis and shall be operated and maintained in accordance with the manufacturer's recommendations. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N | limited operation | 15.71 | TPY CO2E |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Not to exceed 100 hours of non-emergency operation on a 12-month rolling basis. Use of good combustion practices.
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Diesel Fired Well Pump | 17.21 | Diesel | 2.7 | MMBTU/H | 2.7 MMBtu/hr Diesel Fired Well Pump. Installed in 1966. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Limited Operation of 168 hr/yr. | 37.2 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WY-0076 | ROCK SPRINGS FERTILIZER COMPLEX | SIMPLOT PHOSPHATES, LLC | SWEETWATER | WY | 82901 | USA | DARIN HOWE | 3073821519 | DARIN.HOWE@SIMPLOT.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | MD-14824 | 2874 | 325312 | 110040924033 | 11/13/2013 &nbsp;ACT | 07/01/2014 &nbsp;ACT | 2014-07-01 | 2016-01-08 | B |  | Phosphate fertilizer Plant | Installation of an anhydrous ammonia plant with a nominal production capacity of 600 short tons per day (t/day) | Fire Water Pump Engine | 17.21 | Diesel | 200 | HP | limited to 500 hours of operation | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | limited to 500 hours of operation per year | 58 | T/YR | ANNUAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0301 | LAKE CHARLES CHEMICAL COMPLEX ETHYLENE 2 UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | (281) 588-3761 | ERIC.RODRIGUEZ@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-779 | 2869 | 325110 | 110017418061 | 05/02/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2016-09-27 | 2017-04-28 | B |  |  | Complete application date = date of administrative completeness This RBLC entry addresses Ethylene Unit 2 of the Lake Charles Cracker Project. This unit will produce ethylene by thermally cracking ethane in cracking furnaces. | Firewater Pump Nos. 1-3 (EQTs 997, 998, &amp; 999) | 17.21 | Diesel | 500 | HP | Non-emergency use operating time is limited to 100 hr/yr (per engine). | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | NSPS | 10 | TPY | ANNUAL MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT is determined to be compliance with the limitations imposed by 40 CFR 60 Subpart IIII and its associated monitoring, recordkeeping, and reporting requirements; and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage. The CO2e limits are based on a CH4 global warming potential (GWP) of 21 and a N2O GWP of 310. In the event any GWP is revised, the CO2e limits shall be revised accordingly without the need to modify the permit.
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | NSPS | 72 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Genenerator Engine DEG-16-1 (EQT035) | 17.21 | Diesel | 460 | horsepower | Limit operations to 100 hrs/yr | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | NSPS Subpart IIII Limitations and Good Combustion Practices | 26 | T/YR | ANNUAL MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 73.96 kg/MM BTU of CO2, 0.003 kg/MM BTU of CH4, and 0.0006 kg/MM BTU of N2O
PR-0009 | ENERGY ANSWERS ARECIBO PUERTO RICO RENEWABLE ENERGY PROJECT | ENERGY ANSWERS ARECIBO, LLC | ARECIBO | PR |  | USA | MARK GREEN | (347)-351-5248 |  | 2 | OT003 | EPA REGION II | MR. FRANK JON | (212)637-4085 | jon.frank@epa.gov | Ms. Viorica Petriman petriman.viorica@epa.gov | R2-PSD 1 | 4953 | 221119 | FRL-9911-10-Region 2 | 11/11/2012 &nbsp;ACT | 04/10/2014 &nbsp;ACT | 2014-10-14 | 2016-05-05 | A |  | Energy Answers Arecibo is a new resource recovery facility capable of producing up to 77 megawatts (MW) of electrical power while combusting municipal solid waste, as the primary fuel. | This is a PSD permit for a new/greenfield facility. | Emergency Diesel Fire Pump | 17.21 | ULSD Fuel Oil #2 | 0 |  | The Emergency Fire Pump is rated at 335 BHP and limited to 500 hr/yr (emergency operations and testing and maintenance, combined). | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 91.3 | T/YR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Airstrip Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 490 | hp | One 490 hp Airstrip Generator Engine | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 163 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Agitator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 98 | hp | ULSD-fired 98 hp Agitator Generator Engine | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 356 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Incinerator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 102 | hp | ULSD-fired 102 hp Incinerator Generator Engine | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 516 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N