## All Pollutants_Small RICE 17.21
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (South Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | B | Diesel particulate filter, good combustion practices and meeting NSPS Subpart IIII requirements. | 0.15 | G/HP-HR | HOURLY | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUFPENGINE (North Plant): Fire pump engine | 17.21 | Diesel | 300 | HP | A 300 HP diesel-fired emergency fire pump engine with a model year of 2011 or later, and a displacement of <30 liters/cylinder. Equipped with a diesel particulate filter. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | B | Diesel particulate filter, good combustion practices and meeting NSPS Subpart IIII requirements. | 0.15 | G/HP-HR | HOURLY | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*FL-0363 | DANIA BEACH ENERGY CENTER | FLORIDA POWER AND LIGHT COMPANY | BROWARD | FL | 33314 | USA | JOHN HAMPP | 561-691-2894 | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-017-AC | 4911 | 221112 | 110002044065 | 07/27/2017 &nbsp;ACT | 12/04/2017 &nbsp;ACT | 2018-04-03 | 2018-04-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.F.ZIP | 1200 megawatt 2-on-1 combined cycle facility, natural gas-fired, with limited ULSD use. GE 7HA turbines | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.D.ZIP | Emergency Fire Pump Engine (422 hp) | 17.21 | ULSD | 0 |  | Limits equal Subpart IIII limits | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.15 | G/HP-HR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Certified engine, no testing required
NY-0103 | CRICKET VALLEY ENERGY CENTER | CRICKET VALLEY ENERGY CENTER LLC | USA | NY | 12522-0407 | USA |  | 845-877-0596 | INFO@CRICKETVALLEY.COM | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-1326-00275/00009 | 4911 | 221112 | 110043340364 | 02/03/2016 &nbsp;ACT | 02/03/2016 &nbsp;ACT | 2017-08-24 | 2017-09-28 | A | http://www.dec.ny.gov/chemical/32249.html | Cricket Valley Energy Center LLC (CVEC) constructed the Cricket Valley Energy Center (the Facility), a nominal net 1,000-megawatt (MW) combined-cycle gas turbine electric generating facility, on a site located in Dover, Dutchess County, New York. The Facility consists of three General Electric (GE) Model 7FA.05 combustion turbine generators (CTGs) operating in combined-cycle mode with supplemental firing of the heat recovery steam generators (HRSGs); natural gas will be the sole fuel fired in the CTGs and duct burners. The Facility will include a natural gas-fired auxiliary boiler, four ultra-low sulfur distillate (ULSD) fired black-start generator engines and a ULSD-fired emergency fire pump engine. In addition to the air emitting equipment, the Facility will include three steam turbine generators (STGs), an air cooled condenser (ACC) and associated auxiliary equipment and systems. Each combined cycle generating unit consisting of the CTG, HRSG and STG will be exhausted through its own stack. Air emissions from the proposed Facility primarily consist of products of combustion from the CTGs, HRSG duct burners, and ancillary combustion sources. Dutchess County is designated as in attainment with respect to the National Ambient Air Quality Standards (NAAQS) for all criteria pollutants with the exception of ozone. Based upon the potential to emit (PTE) estimates, the Facility is subject to Prevention of Significant Deterioration (PSD) requirements for emissions of carbon monoxide (CO); nitrogen oxides (NOx); particulate matter (PM) with a diameter equal to or less than 10 microns (PM10), PM with a diameter equal to or less than 2.5 microns (PM2.5); greenhouse gases (GHG); sulfuric acid mist (H2SO4); and volatile organic compounds (VOC). In accordance with the NYSDECâ€™s Nonattainment New Source Review (NNSR) permitting program, the Facility is also subject to NNSR for emissions of NOx and VOC. |  | Emergency fire pump | 17.21 | ultra low sulfur diesel | 460 | hp |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.087 | G/BHP-H | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0301 | LAKE CHARLES CHEMICAL COMPLEX ETHYLENE 2 UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | (281) 588-3761 | ERIC.RODRIGUEZ@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-779 | 2869 | 325110 | 110017418061 | 05/02/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2016-09-27 | 2017-04-28 | B |  |  | Complete application date = date of administrative completeness This RBLC entry addresses Ethylene Unit 2 of the Lake Charles Cracker Project. This unit will produce ethylene by thermally cracking ethane in cracking furnaces. | Firewater Pump Nos. 1-3 (EQTs 997, 998, &amp; 999) | 17.21 | Diesel | 500 | HP | Non-emergency use operating time is limited to 100 hr/yr (per engine). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.15 | G/BHP-HR | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.01 | TPY | ANNUAL MAXIMUM | 0.15 | G/BHP-HR |  | 0 | 0 | N |  | BACT is determined to be compliance with the limitations imposed by 40 CFR 60 Subpart IIII and its associated monitoring, recordkeeping, and reporting requirements; and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage.
LA-0301 | LAKE CHARLES CHEMICAL COMPLEX ETHYLENE 2 UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | (281) 588-3761 | ERIC.RODRIGUEZ@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-779 | 2869 | 325110 | 110017418061 | 05/02/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2016-09-27 | 2017-04-28 | B |  |  | Complete application date = date of administrative completeness This RBLC entry addresses Ethylene Unit 2 of the Lake Charles Cracker Project. This unit will produce ethylene by thermally cracking ethane in cracking furnaces. | Firewater Pump Nos. 1-3 (EQTs 997, 998, &amp; 999) | 17.21 | Diesel | 500 | HP | Non-emergency use operating time is limited to 100 hr/yr (per engine). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.15 | G/BHP-HR | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.01 | TPY | ANNUAL MAXIMUM | 0.15 | G/BHP-HR |  | 0 | 0 | N |  | BACT is determined to be compliance with the limitations imposed by 40 CFR 60 Subpart IIII and its associated monitoring, recordkeeping, and reporting requirements; and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage.
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Emergency Diesel Firewater Pump 1 | 17.21 | Diesel | 282 | HP |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | Federal Standards | 0.15 | G/BHP-H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.02 | T/YR | ANNUAL MAXIMUM | 0.15 | G/BHP-H |  | 0 | 0 | N |  | BACT Limit = 0.15 G/BHP-HR
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Emergency Diesel Firewater Pump 1 | 17.21 | Diesel | 282 | HP |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | B | Federal Standards | 0.05 | G/BHP-H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0.02 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.05 G/BHP-HR
LA-0309 | BENTELER STEEL TUBE FACILITY | BENTELER STEEL / TUBE MANUFACTURING CORPORATION | CADDO | LA | 71115 | USA | MYRNA PACHECO PONCE DE LEON | 318-216-4206 | MYRNA.PACHECO@BENTELER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen - 225-219-3395 | PSD-LA-774(M1) | 3312 | 331111 | 110055592318 | 02/09/2015 &nbsp;ACT | 06/04/2015 &nbsp;ACT | 2017-03-09 | 2017-04-28 | A |  | A facility to produce 600,000 metric tons per year of seamless steel pipe from purchased billets. A steel production facility (including an electric arc furnace (EAF)) was added. | Permit PSD-LA-774 was issued on May 17, 2013 for the construction of the hot rolling mill. An EAF was authorized this time. | Firewater Pump Engines | 17.21 | Diesel | 288 | hp (each) |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0309 | BENTELER STEEL TUBE FACILITY | BENTELER STEEL / TUBE MANUFACTURING CORPORATION | CADDO | LA | 71115 | USA | MYRNA PACHECO PONCE DE LEON | 318-216-4206 | MYRNA.PACHECO@BENTELER.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen - 225-219-3395 | PSD-LA-774(M1) | 3312 | 331111 | 110055592318 | 02/09/2015 &nbsp;ACT | 06/04/2015 &nbsp;ACT | 2017-03-09 | 2017-04-28 | A |  | A facility to produce 600,000 metric tons per year of seamless steel pipe from purchased billets. A steel production facility (including an electric arc furnace (EAF)) was added. | Permit PSD-LA-774 was issued on May 17, 2013 for the construction of the hot rolling mill. An EAF was authorized this time. | Firewater Pump Engines | 17.21 | Diesel | 288 | hp (each) |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.15 | G/HP-HR | TEST PROTOCOL WILL SPECIFY AVG TIME. | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Pump Engines DFP-16-1 (EQT036) | 17.21 | Diesel | 225 | horsepower | Limit operations to 100 hour/year | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.15 | G/HP-H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.01 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | 0.15 g/hp-hr
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Pump Engine DFP-16-2 (EQT037) | 17.21 | Diesel | 225 | horsepower | Limit operations to 100 hr/yr | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.15 | G/BHP-HR | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.01 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | 0.15 g/hp-hr
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Genenerator Engine DEG-16-1 (EQT035) | 17.21 | Diesel | 460 | horsepower | Limit operations to 100 hrs/yr | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.2 | G/HP-H | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.01 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | 0.2 g/hp-hr
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | Emergency fire pump engine | 17.21 | diesel | 300 | HP | 223.8 kW. Emergency fire pump engine restricted to 500 hours of operation per rolling 12 months. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.15 | G/BHP-HR |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.025 | T/YR | PER ROLLING 12-MONTHS | 0 |  | SEE NOTES | 0 | 0 | N |  | Additional limit: 0.20 g PM10/kW-H NSPS standard If required Methods 201 or 201A and 202
ID-0018 | LANGLEY GULCH POWER PLANT | IDAHO POWER COMPANY | PAYETTE | ID |  | USA |  | 2083885820 | TMAHLUM@IDAHOPOWER.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2009.0092 | 4911 | 221112 | UNKNOWN | 06/07/2009 &nbsp;ACT | 06/25/2010 &nbsp;ACT | 2010-08-09 | 2010-10-05 | A |  | ONE-ON-ONE COMBINED CYCLE PLANT CONSISTING OF (1) NATURAL GAS-FIRED COMBUSTION TURBINE (CT) AND (1) STEAM TURBINE. THE CT IS EQUIPPED WITH (1) HEAT RECOVERY STEAM GENERATOR (HRSG) AND DUCT BURNER. ANCILLARY EQUIPMENT INCLUDES (1) DIESEL-FIRED EMERGENCY GENERATOR, (1) DIESEL-FIRED FIRE PUMP, (1) WET COOLING TOWER, AND (6) DRY CHEMICAL STORAGE SILOS. |  | FIRE PUMP ENGINE | 17.21 | DIESEL | 235 | KW | COMPRESSION IGNITION INTERNAL COMBUSTION (CI ICE) | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.15 | G/HP-HR |  | BACT-PSD | NSPS | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.075 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.075 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.075 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0324 | PALM BEACH RENEWABLE ENERGY PARK | SOLID WASTE AUTHORITY OF PALM BEACH COUNTY | PALM BEACH | FL | 33412 | USA | MARK HAMMOND | 561-640-4000 | MHAMMOND@SWA.ORG | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Alvaro Linero, P.E. Administrator alvaro.linero@dep.state.fl.us Phone: 850-717-9076 Robert Bull, Engineer robert.bull@dep.state.fl.us Phone: 850-717-9111 Teresa Heron, Engineer teresa.heron@dep.state.fl.us phone: 850-717-9082 | PSD-FL-413 | 4953 | 221119 | 110043792358 | 11/12/2010 &nbsp;ACT | 12/23/2010 &nbsp;ACT | 2011-04-07 | 2011-12-08 | B |  | The existing Palm Beach Renewable Energy Facility (PBREP-1) consists of Class I and Class III landfills, a biosolids pelletizer facility, a compost facility and a waste-to-energy (WTE) plant known as the North County Resource Recovery Facility (NCRRF). The new facility, PBREP-2, will consist of: â€¢Three nominal 1,000 TPD mass burn MWC, each with an estimated maximum continuous rating (MCR) of 416.7 million Btu per hour heat input (mmBtu/hr) and a peak rating of 458.3 mmBtu/hr; â€¢A 100 megawatt (MW) STG with an air cooled condenser; â€¢One ash building and handling system; â€¢Three lime storage silos and one carbon storage silo; and â€¢Two 250 horsepower (hp) diesel fire pumps and one 250 kilowatt (kW) emergency generator. This facility, is located at 7501 North Jog Road (immediately west of the Turnpike) in West Palm Beach. | This project will consist of three 1,000 TPD mass-burn MWC units each with a maximum steam production rate of 320,100 pounds per hour (lb/hr) on a 4-hour average block basis. The project also includes a 90 to100 MW STG; three lime storage silos; one carbon storage silo; two diesel fire pump engines; one emergency generator; and one ash handling system and building. The proposed work will be conducted at the existing PBREP. The project will incorporate the following pollution control equipment and measures: â€¢For each MWC unit, good combustion practices (GCP), spray dryers (SD), fabric filter (FF) baghouses, activated carbon injection (CI), selective catalytic reduction (SCR), as an option selective non-catalytic reduction (SNCR) and use of inherently clean natural gas as a startup, shutdown and flame stabilization fuel. â€¢Use of inherently clean ultra low sulfur distillate (ULSD) fuel oil and GCP in the emergency generator and emergency fire pump engines; and â€¢Reasonable precautions and best management practices (BMP) to minimize fugitive particulate matter (PM)/(PM10)/(PM2.5) emissions from MSW handling and processing; ash (bottom and fly) handling, storage and shipment; lime handling, storage and processing; and activated carbon handling, storage and processing. The project will incorporate continuous emission monitoring systems (CEMS) for CO, SO2, NOX and Hg and continuous opacity monitoring systems (COMS) for visible emissions (VE). | 250 Kw Emergency Generator | 17.21 | ULSD | 0 |  |  | Particulate matter, total (TPM) | Other - Manufacturer Certification | (Particulate Matter (PM)) | PM | P | Federal Standards | 0.15 | G/HP-HR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emergency generator shall comply with the following emission limits and demonstrate compliance in accordance with the procedures given in 40 CFR 60, Subpart IIII. Manufacturer certification can be provided to the Department in lieu of actual stack testing.
VA-0319 | GATEWAY COGENERATION 1, LLC - SMART WATER PROJECT | GATEWAY GREEN ENERGY | PRINCE GEORGE | VA | 23875-3000 | USA | T. EDWARD MCDANIEL | 972-638-8798 | EMCDANIEL@GGEHLLC.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52375-002 | 4911 | 221112 | 110045446718 | 01/11/2012 &nbsp;ACT | 08/27/2012 &nbsp;ACT | 2013-01-16 | 2015-05-29 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Combined cycle electrical power generating facility (160 MW), consisting of two combusion turbines (Rolls Royce Trent 60 WLE) with associated HRSG and no duct burning. |  | FIRE WATER PUMP | 17.21 | diesel (ultra low sulfur) | 1.86 | MMBTU/H | 500 H/Yr operation | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combusion practices | 0.15 | G/HP-HR |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
VA-0319 | GATEWAY COGENERATION 1, LLC - SMART WATER PROJECT | GATEWAY GREEN ENERGY | PRINCE GEORGE | VA | 23875-3000 | USA | T. EDWARD MCDANIEL | 972-638-8798 | EMCDANIEL@GGEHLLC.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52375-002 | 4911 | 221112 | 110045446718 | 01/11/2012 &nbsp;ACT | 08/27/2012 &nbsp;ACT | 2013-01-16 | 2015-05-29 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | Combined cycle electrical power generating facility (160 MW), consisting of two combusion turbines (Rolls Royce Trent 60 WLE) with associated HRSG and no duct burning. |  | FIRE WATER PUMP | 17.21 | diesel (ultra low sulfur) | 1.86 | MMBTU/H | 500 H/Yr operation | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combusion practices | 0.15 | G/HP-HR |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*AK-0084 | DONLIN GOLD PROJECT | DONLIN GOLD LLC. | BETHEL CENSUS AREA | AK | 99575 | USA | STAN FOO | 907-273-0200 | SFOO@DONLINGOLD.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | AK DEC DIV. OF AIR QUALITY 410 WILLOUGHBY AVE. SUITE 303 JUNEAU, AK 99801 | AQ0934CPT01 | 1041 | 212221 | Not Entered | 10/15/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2018-06-21 | 2018-06-22 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16763360/d1h2U6BIY-j857LFU-WYmw2 | The Donlin Gold Project is a gold mine located 12 miles north of Crooked Creek, Alaska on the Kuskokwim River, about 280 miles northwest of Anchorage. The deposit has proven and probable reserves estimated at 33.9 million ounces of gold at 2.1 g/t and could produce up to 1.5 million ounces annually. SIC Code 1041; NAICS Code 212221. |  | Fire Pump Diesel Internal Combustion Engines | 17.21 | Diesel | 252 | hp | Three (3) 252 hp fire pump diesel internal combustion engines. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combusion practices | 0.14 | G/HP-HR | 3-HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Subpart IIII engines
*AK-0084 | DONLIN GOLD PROJECT | DONLIN GOLD LLC. | BETHEL CENSUS AREA | AK | 99575 | USA | STAN FOO | 907-273-0200 | SFOO@DONLINGOLD.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | AK DEC DIV. OF AIR QUALITY 410 WILLOUGHBY AVE. SUITE 303 JUNEAU, AK 99801 | AQ0934CPT01 | 1041 | 212221 | Not Entered | 10/15/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2018-06-21 | 2018-06-22 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16763360/d1h2U6BIY-j857LFU-WYmw2 | The Donlin Gold Project is a gold mine located 12 miles north of Crooked Creek, Alaska on the Kuskokwim River, about 280 miles northwest of Anchorage. The deposit has proven and probable reserves estimated at 33.9 million ounces of gold at 2.1 g/t and could produce up to 1.5 million ounces annually. SIC Code 1041; NAICS Code 212221. |  | Fire Pump Diesel Internal Combustion Engines | 17.21 | Diesel | 252 | hp | Three (3) 252 hp fire pump diesel internal combustion engines. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combusion practices | 0.14 | G/HP-HR | 3-HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Subpart IIII engines
*AK-0084 | DONLIN GOLD PROJECT | DONLIN GOLD LLC. | BETHEL CENSUS AREA | AK | 99575 | USA | STAN FOO | 907-273-0200 | SFOO@DONLINGOLD.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | AK DEC DIV. OF AIR QUALITY 410 WILLOUGHBY AVE. SUITE 303 JUNEAU, AK 99801 | AQ0934CPT01 | 1041 | 212221 | Not Entered | 10/15/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2018-06-21 | 2018-06-22 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16763360/d1h2U6BIY-j857LFU-WYmw2 | The Donlin Gold Project is a gold mine located 12 miles north of Crooked Creek, Alaska on the Kuskokwim River, about 280 miles northwest of Anchorage. The deposit has proven and probable reserves estimated at 33.9 million ounces of gold at 2.1 g/t and could produce up to 1.5 million ounces annually. SIC Code 1041; NAICS Code 212221. |  | Fire Pump Diesel Internal Combustion Engines | 17.21 | Diesel | 252 | hp | Three (3) 252 hp fire pump diesel internal combustion engines. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | good combusion practices | 0.14 | G/HP-HR | 3-HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Subpart IIII engines
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | EU-FPENGINE: Diesel fuel fired emergency backup fire pump | 17.21 | diesel fuel | 315 | hp nameplate | This is a diesel fuel fired emergency backup fire mump. It has a capacity of 315 hp, nameplate, and uses diesel fuel ASTM D975 Grade 2-D S15. Ultra low sulfur diesel fuel (15ppmw); 100 hours per year operation for maintenance and readiness testing. NSPS IIII and NESHAP ZZZZ. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion | 0.15 | G/HP-HR | TEST PROTOCOL WILL SPECIFY AVG. TIME | BACT-PSD | NSPS , NESHAP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ultra low sulfur diesel fuel (15 pppmw); 100 hours per year operation for maintenance and readiness testing; NSPS IIII and NESHAP ZZZZ
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUFPENGINE: Fire pump engine | 17.21 | Diesel | 399 | BHP | A 399 brake HP diesel-fueled emergency fire pump engine with a model year of 2011 or later, and a displacement of <10 liters/cylinder. The engine is an EPA Tier 3 certified engine subject to NSPS IIII. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion | 0.15 | G/HP-HR | HOURLY | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002049328 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | EMERGENCY FIRE PUMP | 17.21 | DIESEL | 350 | HP |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.15 | G/HP-HR | ANNUAL AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0.15 | G/HP-H | ANNUAL AVERAGE | 0 | 0 | N
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002049328 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | EMERGENCY FIRE PUMP | 17.21 | DIESEL | 350 | HP |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.15 | G/HP-HR | ANNUAL AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0.15 | G/HP-H | ANNUAL AVERAGE | 0 | 0 | N
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | One 422-hp emergency fire pump engine | 17.21 | ULSD | 0 |  | BACT limits equal to NSPS Subpart IIII limits. Will use IIII certified engine. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.15 | G/HP-HR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0346 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-011-AC | 4911 | 221112 | 110002044065 | 11/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-01-08 | 2016-05-05 | D | http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | In this project, 24 peaking turbines from the Lauderdale facility are being replaced with five 200 MW combustion turbines at Lauderdale. The turbines will fire primarily natural gas, but may also fire ULSD fuel oil. Triggers PSD for NOx, PM, CO, VOC, and GHG. GHG permit issued by US EPA Region 4. Technical evaluation available at http://arm-permit2k.dep.state.fl.us/nontv/0110037.011.AC.D.ZIP | Emergency fire pump engine (300 HP) | 17.21 | USLD | 29 | MMBTU/H | Emergency engine. BACT = NSPS IIII. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practice | 0.2 | G/HP-HR |  | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT = NSPS IIII; Certified IIII engine meets BACT.
MI-0389 | KARN WEADOCK GENERATING COMPLEX | CONSUMERS ENERGY | BAY | MI | 48732-9601 | USA | JAMES M. WALKER | 5177880428 | JMWALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | FOR TECHNICAL QUESTIONS ABOUT THIS PERMIT, PLEASE CONTACT THE PERMIT ENGINEER - DAVID K. RIDDLE RIDDLED@MICHIGAN.GOV (517-373-7081) | 341-07 | 4911 | 221112 | 26-01700033 | 10/15/2007 &nbsp;ACT | 12/29/2009 &nbsp;ACT | 2010-03-08 | 2010-12-16 | U |  | ELECTRICITY GENERATING FACILITY, EXISTING CAPACITY GREATER THAN 2,000 MW. | AFTER CONSTRUCTION CONSUMERS WILL RETIRE 5 TO 7 COAL-FIRED BOILERS (638 - 958 MW) STATEWIDE. FINAL CONDITIONS WILL BE AT WWW.DEQ.STATE.MI.US/APS/FINALCONDITIONS.SHTML. MATERIAL HANDLING - CONTACT PERMIT ENGINEER FOR TECHNICAL INFORMATION (DAVID RIDDLE, 517-373-7081). INCLUDES 9 EMISSION UNITS. COAL, LIMESTONE, SORBENT AND ASH HANDLING PROCESSES. VARIOUS BACT LIMITS FOR OPACITY, PM AND PM10. BACT FOR THE MATERIAL HANDLING EQUIPMENT CONSISTED OF A COMBINATION OF PASSIVE CONTROL EQUIPMENT SUCH AS WET/CHEMICAL SUPPRESSION SYSTEMS AND ENCLOSED CONVEYORS; AND ACTIVE CONTROL SUCH AS FABRIC FILTERS. ACTIVE CONTROL IS LIMITED TO 0.004 GR/DSCF. | FIRE BOOSTER PUMP | 17.21 | ULTRA LOW SULFUR DIESEL | 40 | KW | OPERATIONAL LIMITS 1 HR/DAY AND 500 HRS/YR FOR PM2.5 NAAQS. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.3 | G/HP-HR | TEST METHOD | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 5 EMERGENCY FIRE WATER PUMP ENGINES | 17.21 | ULTRA LOW SULFUR DIESEL | 350 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR |  | BACT-PSD |  |  | 0 |  | 0.2 | G/KW-H |  | 0 |  |  | 0 | 0 | N
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 5 EMERGENCY FIRE WATER PUMP ENGINES | 17.21 | ULTRA LOW SULFUR DIESEL | 350 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.17 | G/HP-HR |  | BACT-PSD |  |  | 0 |  | 0.23 | G/KW-H |  | 0 |  |  | 0 | 0 | N
MD-0044 | COVE POINT LNG TERMINAL | DOMINION COVE POINT LNG, LP | CALVERT | MD |  | USA | RICHARD B. GANGLE | SYSNULL |  | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9318 | 4911 | 221119 | Not Found | 06/09/2014 &nbsp;ACT | 06/09/2014 &nbsp;ACT | 2015-08-25 | 2018-05-14 | U |  | LIQUIFIED NATURAL GAS PROCESSING FACILITY AND 130 MEGAWATT GENERATING STATIONFACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 124.2 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT= 124/2 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 2,030,988 TONS/YR FACILITY-WIDE FORMALDEHYDE EMISION LIMIT = 6.2 TONS/YR | 5 EMERGENCY FIRE WATER PUMP ENGINES | 17.21 | ULTRA LOW SULFUR DIESEL | 350 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.17 | G/HP-HR |  | BACT-PSD |  |  | 0 |  | 0.23 | G/KW-H |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA LOW SULFUR DIESEL | 477 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR |  | BACT-PSD | NSPS |  | 0 |  | 0.2 | G/KW-H |  | 0 |  |  | 0 | 0 | N |  | NSPS 40 CFR 60 SUBPART IIII
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA LOW SULFUR DIESEL | 477 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR |  | BACT-PSD | NSPS |  | 0 |  | 0.23 | G/KW-H |  | 0 |  |  | 0 | 0 | N |  | NSPS 40 CFR 60 SUBPART IIII
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA LOW SULFUR DIESEL | 477 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR |  | BACT-PSD | NSPS |  | 0 |  | 0.23 | G/KW-H |  | 0 |  |  | 0 | 0 | N |  | NSPS 40 CFR 60 SUBPART IIII
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | DIESEL-FIRED FIRE PUMP ENGINE | 17.21 | ULTRA-LOW SULFUR DIESEL | 300 | HP | ONE DIESEL-FIRED FIRE PUMP ENGINE, RATED AT A NOMINAL 300-HORSEPOWER. SUBJECT TO 40 CFR 63 SUBPART ZZZZ. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS IIII
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | DIESEL-FIRED FIRE PUMP ENGINE | 17.21 | ULTRA-LOW SULFUR DIESEL | 300 | HP | ONE DIESEL-FIRED FIRE PUMP ENGINE, RATED AT A NOMINAL 300-HORSEPOWER. SUBJECT TO 40 CFR 63 SUBPART ZZZZ. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.18 | G/HP-HR |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY GENERATOR | 17.21 | ULTRA-LOW SULFUR DIESEL | 1490 | HP | 40 CFR 60 SUBPART IIII, 40 CFR 63 SUBPART ZZZZ ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.18 | G/HP-HR |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | EMERGENCY GENERATOR | 17.21 | ULTRA-LOW SULFUR DIESEL | 1500 | KW | 40 CFR 60 SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR | N/A | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA-LOW SULFUR DIESEL | 300 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR | N/A | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | EMERGENCY GENERATOR | 17.21 | ULTRA-LOW SULFUR DIESEL | 1500 | KW | 40 CFR 60 SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR | N/A | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA-LOW SULFUR DIESEL | 300 | HP | 40 CFR 60, SUBPART IIII, ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR | N/A | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY GENERATOR | 17.21 | ULTRA-LOW SULFUR DIESEL | 1490 | HP | 40 CFR 60 SUBPART IIII, 40 CFR 63 SUBPART ZZZZ ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS SUBPART IIII
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA-LOW SULFUR DIESEL | 305 | HP | 40 CFR 60, SUBPART IIII, 40 CFR 63 SUBPART ZZZZ, ULTRA LOW-SULFURDIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS SUBPART IIII
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA-LOW SULFUR DIESEL | 305 | HP | 40 CFR 60, SUBPART IIII, 40 CFR 63 SUBPART ZZZZ, ULTRA LOW-SULFURDIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.18 | G/HP-HR |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY GENERATOR | 17.21 | ULTRA-LOW SULFUR DIESEL | 1490 | HP | 40 CFR 60 SUBPART IIII, 40 CFR 63 SUBPART ZZZZ ULTRA LOW-SULFUR DIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.18 | G/HP-HR |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | EMERGENCY DIESEL ENGINE FOR FIRE WATER PUMP | 17.21 | ULTRA-LOW SULFUR DIESEL | 305 | HP | 40 CFR 60, SUBPART IIII, 40 CFR 63 SUBPART ZZZZ, ULTRA LOW-SULFURDIESEL FUEL, GOOD COMBUSTION PRACTICES | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.18 | G/HP-HR |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-HR | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.15 | G/HP-HR | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.03 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and 28 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.15 | G/HP-HR | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.03 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.15 | G/HP-HR | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.03 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | EMERGENCY FIRE PUMP ENGINE | 17.21 | DISTILLATE OIL | 0 |  | 425 HP | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.16 | G/HP-HR |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | AMOUNT OF DIESEL FUEL BURNED SHALL NOT EXCEED 1,128 GALLONS PER 12 CONSECUTIVE MONTH PERIOD
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | EMERGENCY FIRE PUMP ENGINE | 17.21 | DISTILLATE OIL | 0 |  | 425 HP | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.16 | G/HP-HR |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | DIESEL BURNED SHALL NOT EXCEED 1,128 GALLONS PER 12 CONSECUTIVE MONTH PERIOD
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Emergency Engine --Diesel Fire Pump (EUFPENGINE) | 17.21 | Diesel | 165 | HP | A 165 hoursepower (hp) diesel-fueled emergency engine manufactured in 2013, iwth a heat input of 1.35 MMBTU/hr. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.22 | G/HP-HR | TEST PROTOCOL | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | DIESEL-FIRED AUXILIARY (EMERGENCY) ENGINES (TWO) | 17.21 | ULTRA-LOW SULFUR DIESEL | 1500 | KW | TWO DIESEL-FIRED AUXILIARY GENERATORS (EMERGENCY GENERATORS), EACH RATED AT NOMINAL 1,500-KILOWATT (KW) SUBJECT TO 40 CFR 60 SUBPART IIII, 40 CFR 63 SUBPART ZZZZ ULTRA LOW-SULFUR DIESEL FUEL | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS SUBPART IIII.
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | DIESEL-FIRED AUXILIARY (EMERGENCY) ENGINES (TWO) | 17.21 | ULTRA-LOW SULFUR DIESEL | 1500 | KW | TWO DIESEL-FIRED AUXILIARY GENERATORS (EMERGENCY GENERATORS), EACH RATED AT NOMINAL 1,500-KILOWATT (KW) SUBJECT TO 40 CFR 60 SUBPART IIII, 40 CFR 63 SUBPART ZZZZ ULTRA LOW-SULFUR DIESEL FUEL | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.18 | G/HP-HR |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | Emergency diesel fire pump | 17.21 | Ultra Low Sulfur Distillate oil | 0 |  | The fire pump has a maximum heat input rate of 2.63 MMBtu/hr (approximately 250 HP) and is permitted for 100 hrs per year for testing and maintenance | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.099 | LB/H |  | 0 |  |  | 0 | 0 | N
NJ-0081 | PSEG FOSSIL LLC SEWAREN GENERATING STATION | PSEG FOSSIL LLC | MIDDLESEX COUNTY | NJ | 07077-1439 | USA | DOUGLAS GORDON | (973) 430-6092 | DOUGLAS.GORDON@PSEG.COM | 2 | NJ001 | NEW JERSEY DEPT OF ENV PROTECTION, DIVISION OF AIR QUALITY | ALIYA KHAN | (609) 292-2169 | Aliya.Khan@dep.nj.gov | David J. Owen 609-633-1129 - David.Owen@dep.nj.gov | 18068 -(BOP120002) | 4911 | 221112 | 110000801614 | 01/31/2012 &nbsp;ACT | 03/07/2014 &nbsp;ACT | 2014-08-22 | 2016-05-02 | B | http://datamine2.state.nj.us/DEP_OPRA/OpraMain/ | This is a new 625 MW combined cycle project at an existing facility. The project will comprise of two combustion turbines, EITHER GE7FA.05 OR Siemens SGT6 5000F, with two duct burners, two Heat Recovery Steam Generators (HRSG), one steam turbine, one 250 HP fire pump and a 3-cell auxiliary cooling tower. Each turbine will be equipped with Selective Catalytic Reduction System (SCR) for control of NOx emissions and Oxidation Catalyst for control of CO and VOC. The heat input rate of the Siemens turbine will be 2,356 MMBtu/hr(HHV) with a 62.1 duct burner MMBtu/hr(HHV). The heat input rate of each GE turbine will be 2,312 MMBtu/hr(HHV) with a 164.4 duct burner MMBtu/hr(HHV). | Facility-wide Greenhouse Gas (GHG) emissions increase as CO2e = +2,010,399 tpy | Emergency diesel fire pump | 17.21 | Ultra Low Sulfur Distillate oil | 0 |  | The fire pump has a maximum heat input rate of 2.63 MMBtu/hr (approximately 250 HP) and is permitted for 100 hrs per year for testing and maintenance | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.099 | LB/H |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.21 | DIESEL | 182 | HP | UNIT IS 135 KW. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.21 | DIESEL | 182 | HP | UNIT IS 135 KW. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.21 | DIESEL | 182 | HP | UNIT IS 135 KW. | Particulate matter, total (TPM) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | Cummins 6BTA 5.9F-1 Diesel Engine Fire Pump | 17.21 | No. 2 Fuel Oil | 182 | BHP |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.25 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | Cummins 6BTA 5.9F-1 Diesel Engine Fire Pump | 17.21 | No. 2 Fuel Oil | 182 | BHP |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.25 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0317 | OHIO RIVER CLEAN FUELS, LLC | OHIO RIVER CLEAN FUELS, LLC | COLUMBIANA | OH |  | USA | STEPHAN M. DOPUCH | 4402570054 | SDOPUCH@BAARDENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | 02-22896 | 2869 | 325110 | UNKNOWN | 12/21/2007 &nbsp;ACT | 11/20/2008 &nbsp;ACT | 2008-11-28 | 2012-05-18 | A |  | COAL/BIOMASS-TO-LIQUIDS FACILITY. THE PRIMARY INDUSTRIAL PROCESSES: COAL/BIOMASS STORAGE AND HANDLING; COAL GASIFICATION; SYNGAS CLEANING (ACID GASS REMOVAL AND SULFUR RECOVERY PLANT); FISCHER-TROPSCH PROCESS (INDUSTRIAL ORGANIC CHEMICALS); PRODUCT UPGRADE PROCESS (SIMILAR TO PETROLEUM REFINING); LIQUID PRODUCT STORAGE &amp; LOADING; ELECTRIC POWER GENERATION (USE FOR ON SITE ONLY). BIOMASS IS RESTRICTED TO ONLY SAWDUST AND WOOD CHIPS. | NEW INDUSTRY, SIC AND NAICS CODE SELECTED BY FACILITY | FIRE PUMP ENGINES (2) | 17.21 | DIESEL FUEL OIL | 300 | HP | SUBJECT TO NSPS SUBPART IIII. WILL INSTALL NON-RESETTABLE HOUR METER PRIOR TO STARTUP PER 40 CFR 60.4209(A) DIESEL FUEL SHALL MEET THE REQUIREMENTS OF 40 CFR 80.510 AND 60.4207: SULFUR CONTENT OF 15 PPM MAXIMUM, CETANE INDEX OF 40 MINIMUM OR AROMATIC CONTENT OF 35 VOLUME % MAXIMUM | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND GOOD ENGINE DESIGN | 0.4 | G/HP-H | FOR EACH ENGINE | BACT-PSD | NSPS , SIP | U | 0 | N | 0.07 | T/YR | PER ROLLING 12-MONTH PERIOD | 0.4 | G/HP-H | FROM TABLE 4 OF SUBPART IIII | 0 | 0 | N |  | LIMITS FOR EACH ENGINE. SUBJECT TO NSPS SUBPART IIII.
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) FIREWATER PUMP DIESEL ENGINES | 17.21 | DIESEL | 371 | BHP, EACH | THE TWO FIREWATER PUMP ENGINES, IDENTIFIED AS FP01 AND FP02, EXHAUSTING THROUGH TWO (2) VENTS. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices AND USAGE LIMITS | 0.15 | G/HP-HR |  | BACT-PSD |  |  | 0 |  | 500 | HOURS OF OPERATION | YEARLY | 0 |  |  | 0 | 0 | N |  | LIMIT TWO IS FOR EACH FIREWATER PUMP ENGINES
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) FIREWATER PUMP DIESEL ENGINES | 17.21 | DIESEL | 371 | BHP, EACH | THE TWO FIREWATER PUMP ENGINES, IDENTIFIED AS FP01 AND FP02, EXHAUSTING THROUGH TWO (2) VENTS. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices AND USAGE LIMITS | 0.15 | G/HP-HR | 3 HOURS | BACT-PSD |  |  | 0 |  | 500 | HOURS OF OPERATION | YEARLY | 0 |  |  | 0 | 0 | N |  | LIMIT TWO IS FOR EACH FIREWATER PUMP ENGINE
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) FIREWATER PUMP DIESEL ENGINES | 17.21 | DIESEL | 371 | BHP, EACH | THE TWO FIREWATER PUMP ENGINES, IDENTIFIED AS FP01 AND FP02, EXHAUSTING THROUGH TWO (2) VENTS. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices AND USAGE LIMITS | 0.15 | G/HP-HR |  | BACT-PSD |  |  | 0 |  | 500 | HOURS OF OPERATION | YEARLY | 0 |  |  | 0 | 0 | N |  | LIMIT TWO IS FOR EACH FIREWATER PUMP ENGINE
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | diesel | 500 | H/YR | A 165 horsepower (hp) diesel-fueled emergency engine manufactured in 2016 with a heat input of 1.35 MMBTU/H. Powers a fire pump used for back up during an emergency (EUFPENGINE). Restricted to 500 hours/year on a 12-month rolling time period basis. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.22 | G/HP-HR | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0399 | DETROIT EDISON--MONROE | DETROIT EDISON | MONROE | MI | 48161-1970 | USA | LILLIAN WOOLLEY | 313-235-5611 | WOOLLEYL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Julie Brunner at 517-373-7088 with questions related to the permit. Thank you. | 93-09A | 4911 | 221112 | 26-11500020 | 09/29/2010 &nbsp;ACT | 12/21/2010 &nbsp;ACT | 2012-10-17 | 2016-04-14 | D |  | Utility--Coal fired power plant |  | 4 Diesel-fired quench pumps | 17.21 | Diesel fuel | 252 | HP | Each pump engine is 252 HP. They are limited to emergency use and subject to NSPS Subpart IIII. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.4 | G/HP-HR | QP1&QP2 EACH, TEST PROTOCOL | BACT-PSD | NSPS | N | 0 | N | 0.15 | G/HP-H | QP3&QP4 EACH, TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Top ranking option. Note: QP1 = Quench pump#1; QP2= Quench pump#2; QP3=Quench pump#3; QP4 = Quench pump#4.
MI-0399 | DETROIT EDISON--MONROE | DETROIT EDISON | MONROE | MI | 48161-1970 | USA | LILLIAN WOOLLEY | 313-235-5611 | WOOLLEYL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Julie Brunner at 517-373-7088 with questions related to the permit. Thank you. | 93-09A | 4911 | 221112 | 26-11500020 | 09/29/2010 &nbsp;ACT | 12/21/2010 &nbsp;ACT | 2012-10-17 | 2016-04-14 | D |  | Utility--Coal fired power plant |  | 4 Diesel-fired quench pumps | 17.21 | Diesel fuel | 252 | HP | Each pump engine is 252 HP. They are limited to emergency use and subject to NSPS Subpart IIII. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.4 | G/HP-HR | QP1&QP2, EACH; TEST PROTOCOL | BACT-PSD | NSPS , OTHER | N | 0 | N | 0.15 | G/HP-H | QP3&QP4, EACH; TEST PROTOCOL | 0 |  |  | 0 | 0 | N |  | Top ranking option Note: QP1=Quench pump #1; QP2=Quench pump#2; QP3=Quench pump#3; QP4=Quench pump#4.
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Emergency diesel engine | 17.21 | diesel | 750 | KW | One (1) 1102 HP (750 KW) emergency diesel engine | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Emergency diesel engine | 17.21 | diesel | 750 | KW | One (1) 1102 HP (750 KW) emergency diesel engine | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Emergency diesel engine | 17.21 | diesel | 750 | KW | One (1) 1102 HP (750 KW) emergency diesel engine | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0354 | LAUDERDALE PLANT | FLORIDA POWER & LIGHT | BROWARD | FL | 33314 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-013-AC | 4911 | 221112 | 110002044065 | 04/20/2015 &nbsp;ACT | 08/25/2015 &nbsp;ACT | 2016-02-17 | 2016-07-06 | D | https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.F.ZIP | Large natural gas- and oil-fired power facility, consisting of four combined cycle units, and many combustion turbines. Small peaking units being replaced with larger combustion turbines. | Re-affirmed BACT determinations in Permit No. 0110037-011-AC. Also, new GHG BACT determination. Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.013.AC.D.ZIP | Emergency fire pump engine, 300 HP | 17.21 | Diesel | 29 | MMBTU/H | Emergency engine. ULSD only. BACT limits equal NSPS IIII limits. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.15 | G/HP-HR |  | BACT-PSD | NSPS , SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Must use certified engine, or perform stack tests.
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | EMERGENCY FIREWATER PUMP ENGINE | 17.21 | DIESEL | 135 | KW | 135 KW (182 hp) IC Diesel-fired Emergency Firewater Pump Engine | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA Method 5 and 202, or CTM 039 or CTM 040 | (Particulate Matter (PM)) | PM | P | Hour Restriction OF 50 HR/YR | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
CA-1191 | VICTORVILLE 2 HYBRID POWER PROJECT | CITY OF VICTORVILLE | SAN BERNARDINO | CA | 92394 | USA | JOHN B. ROBERTS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 07-02 | 4911 | 221112 | 110040578862 | 06/13/2007 &nbsp;ACT | 03/11/2010 &nbsp;ACT | 2012-11-07 | 2017-12-14 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 563 MW power plant comprised of a hybrid of natural gas-fired combined cycle generating equipment integrated with solar thermal components |  | EMERGENCY FIREWATER PUMP ENGINE | 17.21 | DIESEL | 135 | KW | 135 KW (182 hp) IC Diesel-fired Emergency Firewater Pump Engine | Particulate matter, total (TPM) | Other - EPA Method 5 and 202, or CTM 039 or CTM 040 | (Particulate Matter (PM)) | PM | P | Hour Restriction OF 50 HR/YR | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Fire pump engine | 17.21 | Ultra-low sulfur diesel | 15 | gal/hr |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.11 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.002 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Fire pump engine | 17.21 | Ultra-low sulfur diesel | 15 | gal/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.11 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.002 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Fire pump engine | 17.21 | Ultra-low sulfur diesel | 15 | gal/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.11 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.002 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000310459 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Fire Pump Engine | 17.21 | ULSD | 2.7 | MMBTU/H | â‰¤ 300 hours of operation per 12-month rolling period S in ULSD: â‰¤0.0015% by weight | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR | 1 HR BLOCK AVERAGE | BACT-PSD | NSPS , NESHAP , SIP , OPERATING PERMIT | U | 0 | U | 0.12 | LB/H | 1 HR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000310459 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Fire Pump Engine | 17.21 | ULSD | 2.7 | MMBTU/H | â‰¤ 300 hours of operation per 12-month rolling period S in ULSD: â‰¤0.0015% by weight | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR | 1 HR BLOCK AVERAGE | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 0.12 | LB/H | 1 HR BLOCK AVERAGE | 0 |  |  | 0 | 0 | N
PR-0009 | ENERGY ANSWERS ARECIBO PUERTO RICO RENEWABLE ENERGY PROJECT | ENERGY ANSWERS ARECIBO, LLC | ARECIBO | PR |  | USA | MARK GREEN | (347)-351-5248 |  | 2 | OT003 | EPA REGION II | MR. FRANK JON | (212)637-4085 | jon.frank@epa.gov | Ms. Viorica Petriman petriman.viorica@epa.gov | R2-PSD 1 | 4953 | 221119 | FRL-9911-10-Region 2 | 11/11/2012 &nbsp;ACT | 04/10/2014 &nbsp;ACT | 2014-10-14 | 2016-05-05 | A |  | Energy Answers Arecibo is a new resource recovery facility capable of producing up to 77 megawatts (MW) of electrical power while combusting municipal solid waste, as the primary fuel. | This is a PSD permit for a new/greenfield facility. | Emergency Diesel Fire Pump | 17.21 | ULSD Fuel Oil #2 | 0 |  | The Emergency Fire Pump is rated at 335 BHP and limited to 500 hr/yr (emergency operations and testing and maintenance, combined). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.11 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Opacity of emissions from the emergency diesel fire pump's stack shall not exceed 20% except for one period of no more than six (6) minutes in any sixty (60) minute interval when opacity shall not exceed 27%. The opacity shall be measured annually by using EPA Method 9.
PR-0009 | ENERGY ANSWERS ARECIBO PUERTO RICO RENEWABLE ENERGY PROJECT | ENERGY ANSWERS ARECIBO, LLC | ARECIBO | PR |  | USA | MARK GREEN | (347)-351-5248 |  | 2 | OT003 | EPA REGION II | MR. FRANK JON | (212)637-4085 | jon.frank@epa.gov | Ms. Viorica Petriman petriman.viorica@epa.gov | R2-PSD 1 | 4953 | 221119 | FRL-9911-10-Region 2 | 11/11/2012 &nbsp;ACT | 04/10/2014 &nbsp;ACT | 2014-10-14 | 2016-05-05 | A |  | Energy Answers Arecibo is a new resource recovery facility capable of producing up to 77 megawatts (MW) of electrical power while combusting municipal solid waste, as the primary fuel. | This is a PSD permit for a new/greenfield facility. | Emergency Diesel Fire Pump | 17.21 | ULSD Fuel Oil #2 | 0 |  | The Emergency Fire Pump is rated at 335 BHP and limited to 500 hr/yr (emergency operations and testing and maintenance, combined). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.11 | LB/H |  | 0 |  |  | 0 | 0 | N
PR-0009 | ENERGY ANSWERS ARECIBO PUERTO RICO RENEWABLE ENERGY PROJECT | ENERGY ANSWERS ARECIBO, LLC | ARECIBO | PR |  | USA | MARK GREEN | (347)-351-5248 |  | 2 | OT003 | EPA REGION II | MR. FRANK JON | (212)637-4085 | jon.frank@epa.gov | Ms. Viorica Petriman petriman.viorica@epa.gov | R2-PSD 1 | 4953 | 221119 | FRL-9911-10-Region 2 | 11/11/2012 &nbsp;ACT | 04/10/2014 &nbsp;ACT | 2014-10-14 | 2016-05-05 | A |  | Energy Answers Arecibo is a new resource recovery facility capable of producing up to 77 megawatts (MW) of electrical power while combusting municipal solid waste, as the primary fuel. | This is a PSD permit for a new/greenfield facility. | Emergency Diesel Fire Pump | 17.21 | ULSD Fuel Oil #2 | 0 |  | The Emergency Fire Pump is rated at 335 BHP and limited to 500 hr/yr (emergency operations and testing and maintenance, combined). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0.11 | LB/H |  | 0 |  |  | 0 | 0 | N
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Emergency Fire Pump Engine | 17.21 | ULSD | 0 |  | Sulfur content of diesel fuel shall not exceed 15 ppm, operation of engine shall not exceed 100 hr on a 12-month rolling basis. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY FIRE WATER PUMP | 17.21 | DIESEL | 300 | HP |  | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY GENERATOR | 17.21 | DIESEL |  |  | 1500 KW UNIT | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY GENERATOR | 17.21 | DIESEL |  |  | 1500 KW UNIT | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0400 | WOLVERINE POWER | WOLVERINE POWER SUPPLY COOPERATIVE, INC. | PRESQUE ISLE | MI | 49779 | USA | BRIAN WARNER | 2317755700 X 3336 | BWARNER@WPSCI.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact permit engineer Melissa Byrnes at 517-373-7065 with questions regarding this permit. Thank you. | 317-07 | 4911 | 221112 | 26-14105823 | 09/26/2007 &nbsp;ACT | 06/29/2011 &nbsp;ACT | 2012-10-18 | 2016-04-14 | A |  | Coal-fired power plant. |  | Fire Pump | 17.21 | Diesel | 420 | HP | Maximum operation was based on 500 hours per year. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR | TEST PROTOCOL; BACT/SIP/NSPS | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
FL-0322 | SWEET SORGHUM-TO-ETHANOL ADVANCED BIOREFINERY | SOUTHEAST RENEWABLE FUELS (SRF), LLC | HENDRY COUNTY | FL | 33440 | USA | DON MARKLEY | 954-492-1588 | DMARKLEY@SERENEWABLE.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | Alvaro Linero, P.E. Administrator alvaro.linero@dep.state.fl.us Phone: 850-717-9076 David Read, Engineer david.read@dep.state.fl.us Phone: 850-717-9075 Teresa Heron, Engineer teresa.heron@dep.state.fl.us phone: 850-717-9082 | PSD-FL-412 (0510032-001-AC) | 2869 | 325193 | Not Applicable | 03/19/2010 &nbsp;ACT | 12/23/2010 &nbsp;ACT | 2011-01-31 | 2011-07-06 | A | http://www.dep.state.fl.us/Air/emission/bioenergy/southern_renewables.htm | The SRF facility will be located just East of County Road (CR) 835 at the intersection with Hill Grade Road and approximately 13 miles south southwest of Clewiston/Lake Okeechobee in Hendry County. Hendry County is bounded by Lee County to the west, Glades County to the north, Collier County to the south, Palm Beach County to the east and Broward County to the southeast. Lake Okeechobee is located immediately northeast of Hendry County. The Big Cypress Seminole Indian Reservation is located approximately 18 miles south southeast of the site entrance. Most of Hendry County is agricultural. | The applicant proposes to construct a sweet sorghum-to-ethanol advanced biorefinery with a capacity of 22.11 million gallons per year (MGPY). The sweet sorghum will be grown on adjacent farmland. The sweet sorghum juice will be squeezed from the sorghum stalks, fermented, distilled and blended to make a range of ethanol/gasoline products. The leftover stalk fiber (bagasse) and other parts of the plant (harvest field residue) will be combusted in a cogeneration biomass boiler to make process steam and up to 30 megawatts (MW, gross) of electricity. The applicant also plans to use sweet sorghum molasses in the ethanol process when sweet sorghum is not available. Wood and yard waste will be used as a backup and supplemental fuel for the biomass boiler. | Emergency Diesel Fire Pump, One 600 HP | 17.21 | ULSD | 0 |  |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The fire pumps shall comply with the emission limit and demonstrate compliance in accordance with the procedures given in NSPS 40 CFR 60, Subpart IIII. Manufacturer certification may be provided to the Department in lieu of actual testing. The fire pumps are Stationary Compression Ignition Internal Combustion Engines (Stationary ICE) and shall comply with applicable provisions of 40 CFR 60, Subpart IIII, including emission testing or certification.
*KS-0030 | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | GRANT | KS | 67601 | USA | PAUL REYNOLDS | 620-277-4522 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Mindy Bowman, E-mail address: Mindy.Bowman@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-13309 | 4911 | 221112 | Not Found | 03/07/2017 &nbsp;ACT | 03/31/2016 &nbsp;ACT | 2017-04-06 | 2017-07-19 | C |  | Mid-Kansas Electric Company, LLC (Mid-Kansas Electric) (Source ID: 0670173) operates the Rubart Station located in Grant County, Kansas. The facility currently consist of twelve (12) new spark ignition four-stroke lean burn (4SLB) reciprocating internal combustion engines (RICE) used to generate electricity (the proposed project consist of 24 new 4SLB RICE). The generating capacity of each unit is 10 megawatts (approximately 13,410 BHP). Also located at the station is a diesel fire pump, natural gas emergency generator, heater, circuit breakers and switches. The insignificant activities include a diesel storage tank. | This PSD permit with tracking number C-13309 a modification of PSD permits C-12896 (PSD Administrative Amendment, issued on 5/7/2015), C-12721 (PSD Revisions, issued on 4/28/2015), and C-10021 (original PSD permit for the proposed project, issued on 1/28/2013). | Compression ignition RICE emergency fire pump | 17.21 | Ultra-lowsulfur diesel (ULSD) | 197 | HP | One (1) compression ignition emergency fire pump engine, rated at 197 HP, which shall burn only ultra-low sulfur diesel (ULSD, 15 ppm sulfur or less). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR | EXCLUDES STARTUP, SHUTDOWN & MALFUNCTION | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0030 | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | GRANT | KS | 67601 | USA | PAUL REYNOLDS | 620-277-4522 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Mindy Bowman, E-mail address: Mindy.Bowman@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-13309 | 4911 | 221112 | Not Found | 03/07/2017 &nbsp;ACT | 03/31/2016 &nbsp;ACT | 2017-04-06 | 2017-07-19 | C |  | Mid-Kansas Electric Company, LLC (Mid-Kansas Electric) (Source ID: 0670173) operates the Rubart Station located in Grant County, Kansas. The facility currently consist of twelve (12) new spark ignition four-stroke lean burn (4SLB) reciprocating internal combustion engines (RICE) used to generate electricity (the proposed project consist of 24 new 4SLB RICE). The generating capacity of each unit is 10 megawatts (approximately 13,410 BHP). Also located at the station is a diesel fire pump, natural gas emergency generator, heater, circuit breakers and switches. The insignificant activities include a diesel storage tank. | This PSD permit with tracking number C-13309 a modification of PSD permits C-12896 (PSD Administrative Amendment, issued on 5/7/2015), C-12721 (PSD Revisions, issued on 4/28/2015), and C-10021 (original PSD permit for the proposed project, issued on 1/28/2013). | Compression ignition RICE emergency fire pump | 17.21 | Ultra-lowsulfur diesel (ULSD) | 197 | HP | One (1) compression ignition emergency fire pump engine, rated at 197 HP, which shall burn only ultra-low sulfur diesel (ULSD, 15 ppm sulfur or less). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR | EXCLUDES STARTUP, SHUTDOWN & MALFUNCTION | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0030 | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | GRANT | KS | 67601 | USA | PAUL REYNOLDS | 620-277-4522 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Mindy Bowman, E-mail address: Mindy.Bowman@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-13309 | 4911 | 221112 | Not Found | 03/07/2017 &nbsp;ACT | 03/31/2016 &nbsp;ACT | 2017-04-06 | 2017-07-19 | C |  | Mid-Kansas Electric Company, LLC (Mid-Kansas Electric) (Source ID: 0670173) operates the Rubart Station located in Grant County, Kansas. The facility currently consist of twelve (12) new spark ignition four-stroke lean burn (4SLB) reciprocating internal combustion engines (RICE) used to generate electricity (the proposed project consist of 24 new 4SLB RICE). The generating capacity of each unit is 10 megawatts (approximately 13,410 BHP). Also located at the station is a diesel fire pump, natural gas emergency generator, heater, circuit breakers and switches. The insignificant activities include a diesel storage tank. | This PSD permit with tracking number C-13309 a modification of PSD permits C-12896 (PSD Administrative Amendment, issued on 5/7/2015), C-12721 (PSD Revisions, issued on 4/28/2015), and C-10021 (original PSD permit for the proposed project, issued on 1/28/2013). | Compression ignition RICE emergency fire pump | 17.21 | Ultra-lowsulfur diesel (ULSD) | 197 | HP | One (1) compression ignition emergency fire pump engine, rated at 197 HP, which shall burn only ultra-low sulfur diesel (ULSD, 15 ppm sulfur or less). | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR | EXCLUDES STARTUP, SHUTDOWN & MALFUNCTION | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Airstrip Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 490 | hp | One 490 hp Airstrip Generator Engine | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Airstrip Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 490 | hp | One 490 hp Airstrip Generator Engine | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY FIRE WATER PUMP | 17.21 | DIESEL | 300 | HP |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR |  | BACT-PSD | NSPS |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Incinerator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 102 | hp | ULSD-fired 102 hp Incinerator Generator Engine | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.22 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Incinerator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 102 | hp | ULSD-fired 102 hp Incinerator Generator Engine | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.22 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Agitator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 98 | hp | ULSD-fired 98 hp Agitator Generator Engine | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.3 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Agitator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 98 | hp | ULSD-fired 98 hp Agitator Generator Engine | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.3 | G/HP-HR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Diesel | 250 | hp | 2 units | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.4 | G/HP-HR |  | BACT-PSD | NESHAP | U | 0 | U | 0.0009 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | PM emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Deisel | 150 | hp | 2 units at 75 hp, 1 unit at 150 hp | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 1 | G/HP-HR |  | BACT-PSD | NESHAP | N | 0 | U | 0.0022 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | PM10 emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Diesel | 250 | hp | 2 units | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 1 | G/HP-HR |  | BACT-PSD | NESHAP | U | 0 | U | 0.0022 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | PM10 emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Deisel | 150 | hp | 2 units at 75 hp, 1 unit at 150 hp | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 1 | G/HP-HR |  | BACT-PSD | NESHAP | N | 0 | U | 0.0022 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | PM emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Fire Pump Engine | 17.21 | Diesel | 251 | HP | Limited to 100 Hours/year. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-HR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0.15 | G/HP-HR |  | 0 | 0 | N
LA-0251 | FLOPAM INC. FACILITY | FLOPAM INC. | IBERVILLE | LA | 70764 | USA | GARY RYALS | 912-884-3366 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: DAN NGUYEN (225)219-3181 | PSD-LA-747(M1) | 2869 | 325998 | 110041935779 | 11/18/2010 &nbsp;ACT | 04/26/2011 &nbsp;ACT | 2011-09-01 | 2011-12-12 | A |  | A CHEMICAL MANUFACTURING COMPLEX IS UNDER CONSTRUCTION (PSD-LA-747 - LA0240). EQUIPMENT IS ADDED OR REDESIGNED. (ENGINES, COOLING TOWERS, MATERIAL HANDLING). PERMIT PSD-LA-747(M2) WAS ISSUED JULY 5, 2012 FOR ADDITIONAL DUST FILTERS TO CONTROL PM/PM10 FROM THE PERMITTED POWDER PLANTS. SIMILAR DUST FILTERS WERE DETERMINED AS BACT FOR SAME POWDER PLANTS. NO ADDITIONAL BACT ANALYSIS IS REQUIRED. |  | Small Generator Engine | 17.21 | diesel | 193 | hp |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/HP-H |  | BACT-PSD | NSPS | U | 0 | U | 0.01 | T/YR |  | 0.2 | G/KW-H |  | 0 | 0 | N
LA-0251 | FLOPAM INC. FACILITY | FLOPAM INC. | IBERVILLE | LA | 70764 | USA | GARY RYALS | 912-884-3366 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: DAN NGUYEN (225)219-3181 | PSD-LA-747(M1) | 2869 | 325998 | 110041935779 | 11/18/2010 &nbsp;ACT | 04/26/2011 &nbsp;ACT | 2011-09-01 | 2011-12-12 | A |  | A CHEMICAL MANUFACTURING COMPLEX IS UNDER CONSTRUCTION (PSD-LA-747 - LA0240). EQUIPMENT IS ADDED OR REDESIGNED. (ENGINES, COOLING TOWERS, MATERIAL HANDLING). PERMIT PSD-LA-747(M2) WAS ISSUED JULY 5, 2012 FOR ADDITIONAL DUST FILTERS TO CONTROL PM/PM10 FROM THE PERMITTED POWDER PLANTS. SIMILAR DUST FILTERS WERE DETERMINED AS BACT FOR SAME POWDER PLANTS. NO ADDITIONAL BACT ANALYSIS IS REQUIRED. |  | Fire Pump Engines - 2 units | 17.21 | diesel | 444 | hp | each | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | G/BHP-HR |  | BACT-PSD | NSPS | U | 0 | U | 0.01 | T/YR |  | 0.15 | G/HP-H |  | 0 | 0 | N
OK-0129 | CHOUTEAU POWER PLANT | ASSOCIATED ELECTRIC COOPERATIVE INC | MAYES | OK | 74362 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2007-115-C(M-1)PSD | 4911 | 221112 | 4009700017 | 06/19/2008 &nbsp;ACT | 01/23/2009 &nbsp;ACT | 2009-11-20 | 2010-02-18 | B |  |  |  | EMERGENCY FIRE PUMP (267-HP DIESEL) | 17.21 | LOW SULFUR DIESEL | 267 | HP |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.4 | G/HP-H |  | BACT-PSD | NSPS | U | 0 | U | 0.4 | G/HP-H | NSPS | 0 |  |  | 0 | 0 | N