## All Pollutants_Small RICE 17.21
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
LA-0254 | NINEMILE POINT ELECTRIC GENERATING PLANT | ENTERGY LOUISIANA LLC | JEFFERSON | LA | 70094 | USA | CHRISTEE HERBERT | (504) 576-5699 | CHERBER@ENTERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CHRIS SMITH, (225) 219-3417 | PSD-LA-752 | 4911 | 221112 | 110002049328 | 09/14/2010 &nbsp;ACT | 08/16/2011 &nbsp;ACT | 2011-09-22 | 2011-12-12 | B |  | 1827 MW POWER PLANT (PRE-PROJECT). NATURAL GAS IS PRIMARY FUEL; NO. 2 &amp; NO. 4 FUEL OIL ARE SECONDARY FUELS. PROJECT INVOLVES DECOMMISSIONING OF 2 BOILERS AND THE CONSTRUCTION OF 2 COMBINED CYCLE GAS TURBINES WITH DUCT BURNERS, A NATURAL GAS-FIRED AUXILIARY BOILER, A DIESEL GENERATOR, 2 COOLING TOWERS, A FUEL OIL STORAGE TANK, A DIESEL-FIRED FIREWASTER PUMP, AND AN ANHYDROUS AMMONIA TANK. FUELS FOR THE TURBINES INCLUDE NATURAL GAS, NO. 2 FUEL OIL, AND ULTRA LOW SULFUR DIESEL. | APPLICATION ACCEPTED RECEIVED DATE = DATE OF ADMINISTRATIVE COMPLETENESS BACT FOR GREENHOUSE GASES (CO2E) FROM THE COMBINED CYCLE TURBINE GENERATORS (UNITS 6A & 6B) IS OPERATING PROPERLY AND PERFORMING NECESSARY ROUTINE MAINTENANCE, REPAIR, AND REPLACEMENT TO MAINTAIN THE GROSS HEAT RATE AT OR BELOW 7630 BTU/KW-HR (HHV) (ANNUAL AVERAGE). | EMERGENCY FIRE PUMP | 17.21 | DIESEL | 350 | HP |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION Clean Fuel | 1 | G/HP-H | ANNUAL AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 1 | G/HP-H | ANNUAL AVERAGE | 0 | 0 | N
TX-0799 | BEAUMONT TERMINAL | PHILLIPS 66 PIPELINE LLC | JEFFERSON | TX |  | USA | CHINTAN MEHTA | 832-765-1677 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Beth Akers, 512-239-4620 beth.akers@tceq.texas.gov | 18295, PSDTX1466, GHGPSDTX139 | 5171 | 424710 | 110033444850 | 04/19/2016 &nbsp;ACT | 06/08/2016 &nbsp;ACT | 2016-06-17 | 2016-07-07 | C |  | This marine terminal receives, stores, and distributes various volatile organic liquids (VOLs) and refined petroleum products. | (consolidate and/or void: 1973, 8113, 481, 2365, 56419, 6312, and 6559) | EMERGENCY ENGINES | 17.21 | diesel | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good Combustion | 1.13 | g/hp-hr |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*KS-0036 | WESTAR ENERGY - EMPORIA ENERGY CENTER | WESTAR ENERGY | LYON | KS | 66801 | USA | STEPHANIE HIRNER | 785-575-8447 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; | C-10656 | 4911 | 221112 | Not Found | 10/16/2012 &nbsp;ACT | 03/18/2013 &nbsp;ACT | 2017-08-23 | 2017-08-25 | C |  | The Westar Energy - Emporia Energy Center (Source ID: 1110046) is a fossil fuel power generation facility located in Emporia, Kansas. | This PSD permit with tracking number C-10656 is a modification of PSD permits C-9132 (issued on 5/5/2011) and C-7072 (issued 4/17/2007). | Cummins 6BTA 5.9F-1 Diesel Engine Fire Pump | 17.21 | No. 2 Fuel Oil | 182 | BHP |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion | 0.77 | G/BHP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | EMERGENCY FIRE PUMP ENGINE | 17.21 | DISTILLATE OIL | 0 |  | 425 HP | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.05 | G/HP-H |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | AMOUNT OF DIESEL BURNED SHALL NOT EXCEED 1,128 GALLONS PER 12 MONTH PERIOD
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.141 | G/BHP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.141 | G/BHP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.141 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FIRE PUMP | 17.21 |  | 500 | HP | OPERATION LIMITED TO 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.141 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110059696841 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | RAW WATER PUMP | 17.21 | DIESEL, NO. 2 | 500 | HP | OPERATION NOT TO EXCEED 500 HOURS PER YEAR. INSIGNIFICANT ACTIVITY, WILL NOT BE TESTED. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.141 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0313 | ST. CHARLES POWER STATION | ENTERGY LOUISIANA, LLC | ST. CHARLES | LA | 70068 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-804 | 4911 | 221112 | Not Found | 06/29/2015 &nbsp;ACT | 08/31/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | A |  | The St. Charles Power Station (SCPS) is a new electric power generating facility consisting of two (2) natural gas-fired combined cycle gas turbines, each with a heat recovery stem generator unit equipped with duct burners, and one (1) steam generator turbine. The SCPS will will have a predicted net nominal output of 980 MW at ISO conditions with supplemental duct firing. |  | SCPS Emergency Diesel Firewater Pump 1 | 17.21 | Diesel | 282 | HP |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 0.15 | g/hp-hr | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.47 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 3.0 G/BHP-HR (NMHC + NOx)
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0.19 | g/hp-hr | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.03 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
OH-0317 | OHIO RIVER CLEAN FUELS, LLC | OHIO RIVER CLEAN FUELS, LLC | COLUMBIANA | OH |  | USA | STEPHAN M. DOPUCH | 4402570054 | SDOPUCH@BAARDENERGY.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | 02-22896 | 2869 | 325110 | UNKNOWN | 12/21/2007 &nbsp;ACT | 11/20/2008 &nbsp;ACT | 2008-11-28 | 2012-05-18 | A |  | COAL/BIOMASS-TO-LIQUIDS FACILITY. THE PRIMARY INDUSTRIAL PROCESSES: COAL/BIOMASS STORAGE AND HANDLING; COAL GASIFICATION; SYNGAS CLEANING (ACID GASS REMOVAL AND SULFUR RECOVERY PLANT); FISCHER-TROPSCH PROCESS (INDUSTRIAL ORGANIC CHEMICALS); PRODUCT UPGRADE PROCESS (SIMILAR TO PETROLEUM REFINING); LIQUID PRODUCT STORAGE &amp; LOADING; ELECTRIC POWER GENERATION (USE FOR ON SITE ONLY). BIOMASS IS RESTRICTED TO ONLY SAWDUST AND WOOD CHIPS. | NEW INDUSTRY, SIC AND NAICS CODE SELECTED BY FACILITY | FIRE PUMP ENGINES (2) | 17.21 | DIESEL FUEL OIL | 300 | HP | SUBJECT TO NSPS SUBPART IIII. WILL INSTALL NON-RESETTABLE HOUR METER PRIOR TO STARTUP PER 40 CFR 60.4209(A) DIESEL FUEL SHALL MEET THE REQUIREMENTS OF 40 CFR 80.510 AND 60.4207: SULFUR CONTENT OF 15 PPM MAXIMUM, CETANE INDEX OF 40 MINIMUM OR AROMATIC CONTENT OF 35 VOLUME % MAXIMUM | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES AND GOOD ENGINE DESIGN | 0.39 | g/hp-hr | FOR EACH ENGINE | BACT-PSD | SIP , NSPS | U | 0 | N | 0.07 | T/YR | PER ROLLING 12-MONTH PERIOD | 7.8 | G/HP-H | FOR NMHC AND NOX COMBINED, 5% NMHC | 0 | 0 | N |  | POLLUTANT IS NON METHANE HYDROCARBONS. 7.8 G/HP-H FOR NON-METHANE HYDROCARBONS AND NOX COMBINED LIMIT FROM NSPS SUBPART IIII TABLE 4; 5% CONSIDERED NMHC IN HOURLY LIMIT CALCULATION LIMITS FOR EACH ENGINE.
OK-0164 | MIDWEST CITY AIR DEPOT | TINKER AIR FORCE BASE LOGISTICS CENTER | OKLAHOMA | OK | 73145 | USA | COL. CHRISTOPHER AZZANO | 405-734-2102 | 72ABW.WORKFLOW@TINKER.AF.MIL | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2009-394-C(M-2)PSD | 9711 | 928110 | 109-00090 | 04/09/2014 &nbsp;ACT | 01/08/2015 &nbsp;ACT | 2015-08-07 | 2016-07-06 | B |  | In February 2011, the U.S. Air Force (USAF) selected the Boeing KC-767 to replace its aging KC-135 tankers and assigned the new aircraft the designation KC-46A. Tinker AFB was selected to perform the programmed depot-level maintenance of the KC-46A aircraft. | Applicant requests authorization to construct facilities to accommodate new workload associated with the KC-46 aircraft. | Diesel-Fueled Fire Pump Engines | 17.21 | Ultra-Low Sulfur Distillate Fuel | 300 | HP | Operate for 100 hours maximum annually | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good Combustion Practices. | 0.15 | GRAMS PER HP-HR | TOTAL FOR 3 ENGINES. | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0301 | LAKE CHARLES CHEMICAL COMPLEX ETHYLENE 2 UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | (281) 588-3761 | ERIC.RODRIGUEZ@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-779 | 2869 | 325110 | 110017418061 | 05/02/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2016-09-27 | 2017-04-28 | B |  |  | Complete application date = date of administrative completeness This RBLC entry addresses Ethylene Unit 2 of the Lake Charles Cracker Project. This unit will produce ethylene by thermally cracking ethane in cracking furnaces. | Firewater Pump Nos. 1-3 (EQTs 997, 998, &amp; 999) | 17.21 | Diesel | 500 | HP | Non-emergency use operating time is limited to 100 hr/yr (per engine). | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | NSPS | 0.15 | g/hp-hr | HOURLY MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.005 | TPY | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | NOx + NMHC emissions are limited to 3.0 g/hp-hr. BACT is determined to be compliance with the limitations imposed by 40 CFR 60 Subpart IIII and its associated monitoring, recordkeeping, and reporting requirements; and operating the engine in accordance with the engine manufacturerâ€™s instructions and/or written procedures (consistent with safe operation) designed to maximize combustion efficiency and minimize fuel usage.
OK-0175 | WILDHORSE TERMINAL | WILDHORSE TERMINAL LLC | LINCOLN | OK | 74023 | USA | GREG WARNOCK | 403-860-8760 | GREG_WARNOCK@KEYERA.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2016-1066-C PSD | 4612 | 486110 | Not Found | 09/30/2016 &nbsp;ACT | 06/29/2017 &nbsp;ACT | 2017-07-14 | 2018-05-11 | A |  | The new facility will be designed to receive crude oil via pipeline and tank trucks and store crude in tanks for later transportation via pipeline. No outbound loading stations for tank trucks will be located at the terminal. | FRS Entered as &lsquo;&lsquo;081-00099&lsquo;&lsquo;. Too short for a FRS. Wildhorse Terminal, LLC (WTL or the applicant) has submitted an application to construct a new bulk terminal located in Cushing, Oklahoma. The new facility is classified under NAICS Code 486110 â€“ Pipeline Transportation of Crude Oil. The proposed tanks will be subject to New Source Performance Standards 40 CFR Part 60 (NSPS), Subpart Kb. The facility is a listed Prevention of Significant Deterioration (PSD) major source, a crude oil storage facility exceeding 300,000-barrel (bbl) storage capacity with proposed permitted emissions in excess of 100 TPY. Potential VOC emissions have been estimated at 184.37 TPY. Therefore, the application required a full PSD review. | Emergency Use Engine less than or equal to 500 HP | 17.21 | Diesel | 0 |  | One (1) 275-hp emergency generator, two (2) 176-hp firewater pump engines, and one (1) 156-hp portable stripping engine. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | NSPS | 0.15 | GRAMS PER HP-HR |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 40 CFR Part 60, Subpart IIII.
SC-0113 | PYRAMAX CERAMICS, LLC | PYRAMAX CERAMICS, LLC | ALLENDALE | SC | 29810 | USA | RICHARD DERBAWKA | 7705690079 | R.DERBAWKA@PYRAMAXCERAMICS.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MS. ALYSON HAYES | (803)898-3836 | camitdr@dhec.sc.gov | GEORGE S. ROBINSON (803) 898-4123 | 0160-0023 | 3295 | 327992 | Not Available | 09/16/2011 &nbsp;ACT | 02/08/2012 &nbsp;ACT | 2012-05-09 | 2012-10-17 | A |  | PYRAMAX CERAMICS PLANS TO CONSTRUCT A MANUFACTURING FACILITY FOR THE PRODUCTION OF PROPPANT BEADS FOR USE IN THE OIL AND GAS INDUSTRY. THE MAJOR RAW MATERIAL IS CLAY. THE CLAY IS MIXED WITH CHEMICALS AND THEN FIRED IN A KILN TO PRODUCE CERAMIC BEADS. INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | EMERGENCY ENGINE 1 THRU 8 | 17.21 | DIESEL | 29 | HP | THE CONSTRUCTION PERMIT AUTHORIZES THE CONSTRUCTION OF EIGHT (8) IDENTICAL EMERGENCY ENGINES. THIS PROCESS AND POLLUTANT INFORMATION IS FOR ONE SINGLE ENGINE. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | NSPS | 0.28 | GRAM / HP-HR |  | BACT-PSD | NSPS | Y | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | FACILITY MUST PURCHASE ENGINES CERTIFIED BY THE MANUFACTURER TO MEET NSPS, SUBPART IIII. FACILITY WILL MAINTAIN RECORDS TO SHOW COMPLIANCE WITH NSPS, SUBPART IIII.
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | Emergency fire pump engine | 17.21 | diesel | 300 | HP | 223.8 kW. Emergency fire pump engine restricted to 500 hours of operation per rolling 12 months. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 24A | (Volatile Organic Compounds (VOC)) | VOC | P | NSPS | 0.37 | g/hp-hr |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.06 | T/YR | PER ROLLING 12-MONTHS | 0 |  | SEE NOTES | 0 | 0 | N |  | Additional limit: 0.50 g VOC/kW-h; and 4.0 g NMHC + NOx/kW-h Subpart IIII standard. Method 25A if required
ID-0018 | LANGLEY GULCH POWER PLANT | IDAHO POWER COMPANY | PAYETTE | ID |  | USA |  | 2083885820 | TMAHLUM@IDAHOPOWER.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2009.0092 | 4911 | 221112 | UNKNOWN | 06/07/2009 &nbsp;ACT | 06/25/2010 &nbsp;ACT | 2010-08-09 | 2010-10-05 | A |  | ONE-ON-ONE COMBINED CYCLE PLANT CONSISTING OF (1) NATURAL GAS-FIRED COMBUSTION TURBINE (CT) AND (1) STEAM TURBINE. THE CT IS EQUIPPED WITH (1) HEAT RECOVERY STEAM GENERATOR (HRSG) AND DUCT BURNER. ANCILLARY EQUIPMENT INCLUDES (1) DIESEL-FIRED EMERGENCY GENERATOR, (1) DIESEL-FIRED FIRE PUMP, (1) WET COOLING TOWER, AND (6) DRY CHEMICAL STORAGE SILOS. |  | FIRE PUMP ENGINE | 17.21 | DIESEL | 235 | KW | COMPRESSION IGNITION INTERNAL COMBUSTION (CI ICE) | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | NSPS | 0.15 | g/hp-hr | NOX+NMHC | BACT-PSD | NSPS | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LIMIT APPLIES TO NOX+NMHC COMBINED EMISSIONS.
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | NSPS | 0.3 | g/hp-hr |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*WI-0261 | ENBRIDGE ENERGY - SUPERIOR TERMINAL | ENBRIDGE ENERGY LIMITED PARTNERSHIP | DOUGLAS | WI | 54880-5247 | USA | RHONDA O'LEARY | 218-464-5626 | RHONDA.OLEARY@ENBRIDGE.COM | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov | Kristin.Hart@wisconsin.gov; Ronald.Binzley@wisconsin.gov Megan.Corrado@wisconsin.gov | 13-DCF-129 | 4612 | 486110 | 110000878097 | 04/11/2014 &nbsp;ACT | 06/12/2014 &nbsp;ACT | 2017-06-29 | 2017-07-07 | D | http://dnr.wi.gov/topic/AirPermits/Search.html | Petroleum (Crude Oil) storage facility and pipeline terminal FRS 110000878097 | Wisc. FID 816010580. Also see permit 12-DCF-205. FRS 110000878097 Crude oil (petroleum) pipeline terminal | EG7 - Diesel Emergency Electric Generator w/ tank | 17.21 | Diesel fuel oil | 197 | BHP | 197 BHP / 147 KW; 1.38 MMBTU/hr (est. 125 KWe). Limited to 200 hours / year. Distillate fuel oil storage tank | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | NSPS engine [Tier 3 emergency engine]. EG7 Storage tank, conventional fuel oil storage tank, good operating practices; limiting leakage, spills. (FT01). Engine limited to 200 hours / year (total) and NSPS requirements. | 0.19 | GRAM / HP-HR | NOX, Originally was 3.75 g/hp-hr for NOx + NMHC HOURLY AVG., FOR EG7 | BACT-PSD | NSPS , NESHAP | U | 0 | U | 3 | GRAM / HP-HR | NOX + NMHC FOR ENGINE CLASS (HOURLY AVG. | 0 |  |  | 0 | 0 | N
SC-0159 | US10 FACILITY | MICHELIN NORTH AMERICA, INC. | ANDERSON | SC | 29684 | USA | MIKE ARNTZ | 8648717633 | MIKE.ARNTZ@US.MICHELIN.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MS. ALYSON HAYES | (803)898-3836 | camitdr@dhec.sc.gov |  | 0200-0225-CA | 3011 | 326211 | 1100555885500 | 02/07/2012 &nbsp;ACT | 07/09/2012 &nbsp;ACT | 2013-11-06 | 2014-08-27 | A |  | THE FACILITY PRODUCES COMPONENTS FOR EARTHMOVER TIRES AND THEN IN TURN ASSEMBLES TIRES FROM THESE COMPONENTS. |  | FIRE PUMPS, FIRE1, FIRE2, FIRE3 | 17.21 | DIESEL | 211 | KW | THREE (3) 211 KW/282 BHP (EACH) EMERGENCY DIESEL FIRE PUMPS THAT ARE EXPECTED TO BE OPERATED UP TO 100 HOURS PER YEAR OR LESS FOR TESTING AND MAINTENANCE. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 24A | (Volatile Organic Compounds (VOC)) | VOC | P | NSPS, SUBPART IIII, 40 CFR60.4202 AND 40 CFR60.4205. | 0.15 | g/hp-hr |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | THIS LIMIT IS PER FIRE PUMP, NOT A TOTAL FOR ALL FIRE PUMPS.
SC-0113 | PYRAMAX CERAMICS, LLC | PYRAMAX CERAMICS, LLC | ALLENDALE | SC | 29810 | USA | RICHARD DERBAWKA | 7705690079 | R.DERBAWKA@PYRAMAXCERAMICS.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MS. ALYSON HAYES | (803)898-3836 | camitdr@dhec.sc.gov | GEORGE S. ROBINSON (803) 898-4123 | 0160-0023 | 3295 | 327992 | Not Available | 09/16/2011 &nbsp;ACT | 02/08/2012 &nbsp;ACT | 2012-05-09 | 2012-10-17 | A |  | PYRAMAX CERAMICS PLANS TO CONSTRUCT A MANUFACTURING FACILITY FOR THE PRODUCTION OF PROPPANT BEADS FOR USE IN THE OIL AND GAS INDUSTRY. THE MAJOR RAW MATERIAL IS CLAY. THE CLAY IS MIXED WITH CHEMICALS AND THEN FIRED IN A KILN TO PRODUCE CERAMIC BEADS. INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | INITIAL CONSTRUCTION PERMIT FOR A GREENFIELD FACILITY. | FIRE PUMP | 17.21 | DIESEL | 500 | HP | THE CONSTRUCTION PERMIT AUTHORIZES THE CONSTRUCTION OF ONE (1) FIRE PUMP. THIS PROCESS AND POLLUTANT INFORMATION IS FOR THIS ONE SINGLE FIRE PUMP. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | NSPS, SUBPART IIII. HOURS OF OPERATION LIMITED TO 100 HOURS PER YEAR FOR MAINTENANCE AND TESTING. | 0.15 | g/hp-hr |  | BACT-PSD | NSPS | Y | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | FACILITY MUST PURCHASE ENGINES CERTIFIED BY THE MANUFACTURER TO MEET NSPS, SUBPART IIII. FACILITY TO MAINTAIN RECORDS TO SHOW COMPLIANCE WITH NSPS, SUBPART IIII.
PR-0009 | ENERGY ANSWERS ARECIBO PUERTO RICO RENEWABLE ENERGY PROJECT | ENERGY ANSWERS ARECIBO, LLC | ARECIBO | PR |  | USA | MARK GREEN | (347)-351-5248 |  | 2 | OT003 | EPA REGION II | MR. FRANK JON | (212)637-4085 | jon.frank@epa.gov | Ms. Viorica Petriman petriman.viorica@epa.gov | R2-PSD 1 | 4953 | 221119 | FRL-9911-10-Region 2 | 11/11/2012 &nbsp;ACT | 04/10/2014 &nbsp;ACT | 2014-10-14 | 2016-05-05 | A |  | Energy Answers Arecibo is a new resource recovery facility capable of producing up to 77 megawatts (MW) of electrical power while combusting municipal solid waste, as the primary fuel. | This is a PSD permit for a new/greenfield facility. | Emergency Diesel Fire Pump | 17.21 | ULSD Fuel Oil #2 | 0 |  | The Emergency Fire Pump is rated at 335 BHP and limited to 500 hr/yr (emergency operations and testing and maintenance, combined). | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.15 | G/B-HP-H |  | BACT-PSD |  | U | 0 | U | 0.11 | LB/H |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | INTERNAL COMBUSTION ENGINE - EMERGENCY GENERATOR | 17.21 | DIESEL |  |  | 1500 KW UNIT | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.24 | G/HP-H |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | WAS LISTED AS &lsquo;&lsquo;NONMETHANE HYDROCARBONS&lsquo;&lsquo;. CHANGED TO &lsquo;&lsquo;VOC&lsquo;&lsquo; BY RBLC STAFF ON 2/20/09. COMBINED LIMIT FOR NOX AND NON-METHANE HYDROCARBONS
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Airstrip Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 490 | hp | One 490 hp Airstrip Generator Engine | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 1.13 | g/hp-hr |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Agitator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 98 | hp | ULSD-fired 98 hp Agitator Generator Engine | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 1.13 | g/hp-hr |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0082 | POINT THOMSON PRODUCTION FACILITY | EXXON MOBIL CORPORATION | USA | AK |  | USA | MATT REILE | 907 929 4108 | MATTHEW.R.REILE@EXXONMOBIL.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ1201CPT03 | 1382 | 211111 | 110058932561 | 12/13/2013 &nbsp;ACT | 01/23/2015 &nbsp;ACT | 2015-01-28 | 2016-02-19 | C | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16685549/QXjhK6BJvK3h8EByjhru7Q2 | OIL GAS EXPLORATION AND PRODUCTION FACILITY. | Revise Existing RBLC ID AK-0076 to include pollutants: PM-10 and VOC which now trigger PSD. | Incinerator Generator Engine | 17.21 | Ultra Low Sulfur Diesel | 102 | hp | ULSD-fired 102 hp Incinerator Generator Engine | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 1.13 | g/hp-hr |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Deisel | 150 | hp | 2 units at 75 hp, 1 unit at 150 hp | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 1.134 | G/HP-HR |  | BACT-PSD | NESHAP | U | 0 | U | 0.0025 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | VOC emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
*IN-0295 | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIVISION | STEEL DYNAMICS, INC. - ENGINEERED BAR PRODUCTS DIV | HENDRICKS | IN | 46167 | USA | MIKE BROOKS | 317-892-7000 | MIKE.BROOKS@STEELDYNAMICS.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Kristen Willoughby 317-233-3031 kwilloug@idem.IN.gov Section Chief: Dr. Trip Sinha 317-234-4907 | 063-37891-00037 | 3312 | 331111 | 110056970461 | 11/17/2016 &nbsp;ACT | 02/23/2018 &nbsp;ACT | 2018-08-09 | 2018-08-09 | B | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | Steel Mini Mill |  | Emergency Diesel Generators | 17.21 | Diesel | 250 | hp | 2 units | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 1.134 | G/HP-HR |  | BACT-PSD | NESHAP | U | 0 | U | 0.0025 | LB/HP-HR |  | 0 |  |  | 0 | 0 | N |  | VOC emissions shall be reduced through the implementation of Good Combustion Practices including but not limited to the following: (1) Prepare and maintain a preventative maintenance plan. (2) Change oil and filter every 500 hours of operation or annually, whichever comes first. (3) Inspect air cleaner every 1,000 hours of operation or annually, whichever comes first, and replace as necessary. (4) Inspect all hoses and belts every 500 hours of operation or annually, whichever comes first, and replace as necessary. (5) During periods of startup you must minimize the engine's time spent at idle and minimize the engine's startup time at startup to a period needed for appropriate and safe loading of the engine, not to exceed 30 minutes.
*KS-0030 | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | MID-KANSAS ELECTRIC COMPANY, LLC - RUBART STATION | GRANT | KS | 67601 | USA | PAUL REYNOLDS | 620-277-4522 |  | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Mindy Bowman, E-mail address: Mindy.Bowman@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-13309 | 4911 | 221112 | Not Found | 03/07/2017 &nbsp;ACT | 03/31/2016 &nbsp;ACT | 2017-04-06 | 2017-07-19 | C |  | Mid-Kansas Electric Company, LLC (Mid-Kansas Electric) (Source ID: 0670173) operates the Rubart Station located in Grant County, Kansas. The facility currently consist of twelve (12) new spark ignition four-stroke lean burn (4SLB) reciprocating internal combustion engines (RICE) used to generate electricity (the proposed project consist of 24 new 4SLB RICE). The generating capacity of each unit is 10 megawatts (approximately 13,410 BHP). Also located at the station is a diesel fire pump, natural gas emergency generator, heater, circuit breakers and switches. The insignificant activities include a diesel storage tank. | This PSD permit with tracking number C-13309 a modification of PSD permits C-12896 (PSD Administrative Amendment, issued on 5/7/2015), C-12721 (PSD Revisions, issued on 4/28/2015), and C-10021 (original PSD permit for the proposed project, issued on 1/28/2013). | Compression ignition RICE emergency fire pump | 17.21 | Ultra-lowsulfur diesel (ULSD) | 197 | HP | One (1) compression ignition emergency fire pump engine, rated at 197 HP, which shall burn only ultra-low sulfur diesel (ULSD, 15 ppm sulfur or less). | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 1.14 | G/HP-HR | EXCLUDES STARTUP, SHUTDOWN & MALFUNCTION | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N