## LNG Model Emissions
[19 empty] | Emission Rates (g/s) | [11 empty] | AQRV PM Speciation
Modeled ID | Emission Unit | Configuration | Coordinates (UTM) |  | Coordinates (LC) |  | Base Elevation (m) | Actual Height |  | Modeled Height |  | Temperature |  | Velocity |  | Diameter |  | In-Stack Ratio | NOx |  |  | CO |  | PM10 |  | PM2.5 |  | SO2 @16 ppmvd |  |  | Equip Type | Fuel Type | PMF/SOIL | EC - PM2.5 | EC - PM10 | SOA - PM2.5 | SOA - PM10
|  |  | x | y | x | y |  | (ft) | (m) | (ft) | (m) | (°F) | (°K) | (ft/s) | (m/s) | (ft) | (m) | (-) | 1-hour | 24-hour | Annual | 1-hour | 8-hour | 24-hour | Annual | 24-hour | Annual | 1-hour | 3&24-hour | Annual |  |  | g/s | g/s | g/s | g/s | g/s | Conversion Table
Turbines | [37 empty] | 1 lb = | 453.59 | g
TURB1 | Train 1a Compression Turbine Stack | Vert./no Cap | 589612.041 | 6726290.105 | -19.7781 | 185.0867 | 38 | 210 | 64.008 | 210 | 64.008 | 970 | 794.2611 | 86 | 26.2128 | 19 | 5.7912 | 0.5 | 4.7425 | 4.7425 | 1.0019 | 8.0198 | 8.0198 | 1.0369 | 0.98635 | 1.0369 | 0.98635 | 0.36749 | 0.36749 | 0.34953 | Turbine | Gas | 0 | 0.29849 | 0.29849 | 0.73837 | 0.73837 | 1 hr = | 3600 | sec
TURB2 | Train 1b Compression Turbine Stack | Vert./no Cap | 589704.728 | 6726354.044 | -19.6832 | 185.1481 | 38 | 210 | 64.008 | 210 | 64.008 | 970 | 794.2611 | 86 | 26.2128 | 19 | 5.7912 | 0.5 | 4.7425 | 4.7425 | 1.0019 | 8.0198 | 8.0198 | 1.0369 | 0.98635 | 1.0369 | 0.98635 | 0.36749 | 0.36749 | 0.34953 | Turbine | Gas | 0 | 0.29849 | 0.29849 | 0.73837 | 0.73837
TURB3 | Train 2a Compression Turbine Stack | Vert./no Cap | 589477.149 | 6726485.287 | -19.9077 | 185.2865 | 38 | 210 | 64.008 | 210 | 64.008 | 970 | 794.2611 | 86 | 26.2128 | 19 | 5.7912 | 0.5 | 4.7425 | 4.7425 | 1.0019 | 8.0198 | 8.0198 | 1.0369 | 0.98635 | 1.0369 | 0.98635 | 0.36749 | 0.36749 | 0.34953 | Turbine | Gas | 0 | 0.29849 | 0.29849 | 0.73837 | 0.73837
TURB4 | Train 2b Compression Turbine Stack | Vert./no Cap | 589570.156 | 6726549.36 | -19.8125 | 185.3481 | 38 | 210 | 64.008 | 210 | 64.008 | 970 | 794.2611 | 86 | 26.2128 | 19 | 5.7912 | 0.5 | 4.7425 | 4.7425 | 1.0019 | 8.0198 | 8.0198 | 1.0369 | 0.98635 | 1.0369 | 0.98635 | 0.36749 | 0.36749 | 0.34953 | Turbine | Gas | 0 | 0.29849 | 0.29849 | 0.73837 | 0.73837
TURB5 | Train 3a Compression Turbine Stack | Vert./no Cap | 589343.129 | 6726679.917 | -20.0365 | 185.4858 | 38 | 210 | 64.008 | 210 | 64.008 | 970 | 794.2611 | 86 | 26.2128 | 19 | 5.7912 | 0.5 | 4.7425 | 4.7425 | 1.0019 | 8.0198 | 8.0198 | 1.0369 | 0.98635 | 1.0369 | 0.98635 | 0.36749 | 0.36749 | 0.34953 | Turbine | Gas | 0 | 0.29849 | 0.29849 | 0.73837 | 0.73837
TURB6 | Train 3b Compression Turbine Stack | Vert./no Cap | 589435.876 | 6726744.22 | -19.9415 | 185.5476 | 38 | 210 | 64.008 | 210 | 64.008 | 970 | 794.2611 | 86 | 26.2128 | 19 | 5.7912 | 0.5 | 4.7425 | 4.7425 | 1.0019 | 8.0198 | 8.0198 | 1.0369 | 0.98635 | 1.0369 | 0.98635 | 0.36749 | 0.36749 | 0.34953 | Turbine | Gas | 0 | 0.29849 | 0.29849 | 0.73837 | 0.73837
TRB_GEN1 | Power Generator Turbines | Vert./no Cap | 589851.085 | 6726009.55 | -19.5466 | 184.7981 | 38 | 150 | 45.72 | 150 | 45.72 | 341 | 444.8167 | 48 | 14.6304 | 10 | 3.048 | 0.5 | 1.8413 | 1.8413 | 0.33811 | 0.99641 | 0.99641 | 0.38373 | 0.3403 | 0.38373 | 0.3403 | 0.13586 | 0.13586 | 0.12051 | Turbine | Gas | 0 | 0.11047 | 0.11047 | 0.27326 | 0.27326
TRB_GEN2 | Power Generator Turbines | Vert./no Cap | 589931.338 | 6726064.942 | -19.4644 | 184.8513 | 38 | 150 | 45.72 | 150 | 45.72 | 341 | 444.8167 | 48 | 14.6304 | 10 | 3.048 | 0.5 | 1.8413 | 1.8413 | 0.33811 | 0.99641 | 0.99641 | 0.38373 | 0.3403 | 0.38373 | 0.3403 | 0.13586 | 0.13586 | 0.12051 | Turbine | Gas | 0 | 0.11047 | 0.11047 | 0.27326 | 0.27326
TRB_GEN3 | Power Generator Turbines | Vert./no Cap | 590011.592 | 6726120.339 | -19.3822 | 184.9045 | 38 | 150 | 45.72 | 150 | 45.72 | 341 | 444.8167 | 48 | 14.6304 | 10 | 3.048 | 0.5 | 1.8413 | 1.8413 | 0.33811 | 0.99641 | 0.99641 | 0.38373 | 0.3403 | 0.38373 | 0.3403 | 0.13586 | 0.13586 | 0.12051 | Turbine | Gas | 0 | 0.11047 | 0.11047 | 0.27326 | 0.27326
TRB_GEN4 | Power Generator Turbines | Vert./no Cap | 590091.83 | 6726175.75 | -19.3001 | 184.9577 | 38 | 150 | 45.72 | 150 | 45.72 | 341 | 444.8167 | 48 | 14.6304 | 10 | 3.048 | 0.5 | 1.8413 | 1.8413 | 0.33811 | 0.99641 | 0.99641 | 0.38373 | 0.3403 | 0.38373 | 0.3403 | 0.13586 | 0.13586 | 0.12051 | Turbine | Gas | 0 | 0.11047 | 0.11047 | 0.27326 | 0.27326
Diesel Equipment
Aux_COMP | Auxiliary Air Compressor (224 kW)1 | Vert./no Cap | 589576.441 | 6726013.478 | -19.822 | 184.8101 | 38 | 10 | 3.048 | 10 | 3.048 | 883 | 745.9278 | 115 | 35.052 | 0.665 | 0.20269 | 0.5 | 0.0021281 | 0.037285 | 0.0021281 | 0.27187 | 0.27187 | 0.0018643 | 0.00010641 | 0.0018643 | 0.00010641 | 0.0022123 | 0.038759 | 0.0022123 | Compressor | Diesel | 0 | 0.0016061 | 0.0016137 | 0.00025818 | 0.00025052
FPUMP | Firewater Pump (429 kW)1 | Vert./no Cap | 590146.727 | 6726056.224 | -19.2485 | 184.8362 | 38 | 10 | 3.048 | 10 | 3.048 | 908 | 759.8167 | 157 | 47.8536 | 0.665 | 0.20269 | 0.5 | 0.032478 | 0.56901 | 0.032478 | 0.5191 | 0.5191 | 0.029948 | 0.0017094 | 0.029948 | 0.0017094 | 0.0042402 | 0.074289 | 0.0042402 | Pump | Diesel | 0 | 0.0258 | 0.025924 | 0.0041475 | 0.0040244
Flares
FLARE_1D | Dry Flare Pilot/Purge | Vert./no Cap | 589999.686 | 6725837.07 | -19.4025 | 184.6206 | 38 | 0 | 0 | 7.5555 | 2.3029 | 1831.73 | 1273 | 65.6168 | 20 | 1.4635 | 0.44608 | 0.5 | 0.06126 | 0.06126 | 0.06126 | 0.27927 | 0.27927 | 0.025423 | 0.025423 | 0.025423 | 0.025423 | 0.0021747 | 0.0021747 | 0.0021747 | Flare | Gas | 0 | 0.0063557 | 0.0063557 | 0.019067 | 0.019067
FLARE_2D | Dry Flare Pilot/Purge | Vert./no Cap | 590097.738 | 6725906.294 | -19.3021 | 184.6872 | 38 | 0 | 0 | 7.5555 | 2.3029 | 1831.73 | 1273 | 65.6168 | 20 | 1.4635 | 0.44608 | 0.5 | 0.06126 | 0.06126 | 0.06126 | 0.27927 | 0.27927 | 0.025423 | 0.025423 | 0.025423 | 0.025423 | 0.0021747 | 0.0021747 | 0.0021747 | Flare | Gas | 0 | 0.0063557 | 0.0063557 | 0.019067 | 0.019067
FLARE_1W | Wet Flare Pilot/Purge | Vert./no Cap | 589999.686 | 6725837.07 | -19.4025 | 184.6206 | 38 | 0 | 0 | 4.3451 | 1.3244 | 1831.73 | 1273 | 65.6168 | 20 | 0.82049 | 0.25009 | 0.5 | 0.019278 | 0.019278 | 0.019278 | 0.087883 | 0.087883 | 0.0080002 | 0.0080002 | 0.0080002 | 0.0080002 | 0.00070875 | 0.00070875 | 0.00070875 | Flare | Gas | 0 | 0.0020001 | 0.0020001 | 0.0060002 | 0.0060002
FLARE_2W | Wet Flare Pilot/Purge | Vert./no Cap | 590097.738 | 6725906.294 | -19.3021 | 184.6872 | 38 | 0 | 0 | 4.3451 | 1.3244 | 1831.73 | 1273 | 65.6168 | 20 | 0.82049 | 0.25009 | 0.5 | 0.019278 | 0.019278 | 0.019278 | 0.087883 | 0.087883 | 0.0080002 | 0.0080002 | 0.0080002 | 0.0080002 | 0.00070875 | 0.00070875 | 0.00070875 | Flare | Gas | 0 | 0.0020001 | 0.0020001 | 0.0060002 | 0.0060002
DRY_MAX1 | Dry Flare Maximum Case1 | Vert./no Cap | 589999.686 | 6725837.07 | -19.4025 | 184.6206 | 38 | 0 | 0 | 567.0035 | 172.8227 | 1831.73 | 1273 | 65.6168 | 20 | 133.9765 | 40.836 | 0.5 | 29.3379 | 10.7083 | 29.3379 | 1171.6179 | 146.4522 | 4.444 | 12.1753 | 4.444 | 12.1753 | 1.0752 | 3.1395 | 1.0752 | Flare | Gas | 0 | 1.111 | 1.111 | 3.333 | 3.333
DRY_MAX2 | Dry Flare Maximum Case1 | Vert./no Cap | 590097.738 | 6725906.294 | -19.3021 | 184.6872 | 38 | 0 | 0 | 567.0035 | 172.8227 | 1831.73 | 1273 | 65.6168 | 20 | 133.9765 | 40.836 | 0.5 | 29.3379 | 10.7083 | 29.3379 | 1171.6179 | 146.4522 | 4.444 | 12.1753 | 4.444 | 12.1753 | 1.0752 | 3.1395 | 1.0752 | Flare | Gas | 0 | 1.111 | 1.111 | 3.333 | 3.333
WET_MAX1 | Wet Flare Maximum Case1 | Vert./no Cap | 589999.686 | 6725837.07 | -19.4025 | 184.6206 | 38 | 0 | 0 | 283.1351 | 86.2996 | 1831.73 | 1273 | 65.6168 | 20 | 64.7971 | 19.7502 | 0.5 | 6.8562 | 2.5025 | 6.8562 | 273.8046 | 34.2256 | 1.0385 | 2.8453 | 1.0385 | 2.8453 | 0.25135 | 0.73394 | 0.25135 | Flare | Gas | 0 | 0.25964 | 0.25964 | 0.77891 | 0.77891
WET_MAX2 | Wet Flare Maximum Case1 | Vert./no Cap | 590097.738 | 6725906.294 | -19.3021 | 184.6872 | 38 | 0 | 0 | 283.1351 | 86.2996 | 1831.73 | 1273 | 65.6168 | 20 | 64.7971 | 19.7502 | 0.5 | 6.8562 | 2.5025 | 6.8562 | 273.8046 | 34.2256 | 1.0385 | 2.8453 | 1.0385 | 2.8453 | 0.25135 | 0.73394 | 0.25135 | Flare | Gas | 0 | 0.25964 | 0.25964 | 0.77891 | 0.77891
LP_FLARE | LP Flare Pilot/Purge | Vert./no Cap | 589339.797 | 6726051.771 | -20.0584 | 184.8556 | 38 | 199 | 60.6552 | 208.0814 | 63.4232 | 1831.73 | 1273 | 65.6168 | 20 | 1.774 | 0.54073 | 0.5 | 0.089962 | 0.089962 | 0.089962 | 0.41012 | 0.41012 | 0.037334 | 0.037334 | 0.037334 | 0.037334 | 0.0063586 | 0.0063586 | 0.0063586 | Flare | Gas | 0 | 0.0093336 | 0.0093336 | 0.028001 | 0.028001
LP_MAX | LP Flare Maximum Flow1 (Maintenance) | Vert./no Cap | 589339.797 | 6726051.771 | -20.0584 | 184.8556 | 38 | 199 | 60.6552 | 278.9416 | 85.0214 | 1831.73 | 1273 | 65.6168 | 20 | 17.2606 | 5.261 | 0.5 | 0.14782 | 8.9926 | 0.14782 | 39.2327 | 39.2327 | 3.5468 | 0.058303 | 3.5468 | 0.058303 | 0.005672 | 0.34505 | 0.005672 | Flare | Gas | 0 | 0.88669 | 0.88669 | 2.6601 | 2.6601
TH_OX | Thermal Oxidizer | Vert./no Cap | 589545.886 | 6725947.886 | -19.8546 | 184.7452 | 38 | 47 | 14.3256 | 47 | 14.3256 | 1800 | 1255.3722 | 8.9 | 2.7127 | 5 | 1.524 | 0.5 | 0.041648 | 0.041648 | 0.041648 | 0.062361 | 0.062361 | 0.0056422 | 0.0056422 | 0.0056422 | 0.0056422 | 0.0020665 | 0.0020665 | 0.0020665 | Heater | Gas | 0 | 0.0014106 | 0.0014106 | 0.0042317 | 0.0042317
Total Emissions (Without Maximum Flare) | [18 empty] | 36.2953 | 45.7118 | 7.8392 | 93.3349 | 93.3349 | 11.4445 | 7.4492 | 11.4445 | 7.4492 | 2.7747 | 3.2207 | 2.6055
Total Emissions (With Maximum Flare) | [18 empty] | 108.6835 | 72.1335 | 80.2274 | 2984.1799 | 454.6905 | 22.4095 | 37.4905 | 22.4095 | 37.4905 | 5.4277 | 10.9675 | 5.2585
NOTES
500 | hours Intermittent Diesel Equipment has been modeled with an annual value based on operating only 500 hours/year.
500 | hours Maximum Flaring Events have been modeled with an annual value based on operating only 500 hours/year.
144 | hours Maximum LP Flaring Events have been modeled with an annual value based on operating only 144 hours/year.
8760 | hours Annual hours
0.5 | hours Per day maximum flare operation
1 | Intermittent equipment 1-hr NOx and SO2 emissions can be annualized

## LNG Potential to Emit
PTE SUMMARY
Model ID | Source Description | Annual Operating Hours | Potential to Emit (PTE) Emission Rates
|  |  | NOx |  | CO |  |  | VOC |  | PM10 |  |  | PM2.5 |  |  | SO2 @ 16 ppmvd |  |  |  | CO2 |  | CH4 |  | N2O |  | CO2e | CO2e | HAPs (Formaldehyde) |  | HAPs (Total)
|  |  | lb/hr | tpy | lb/hr | lb/8-hr | tpy | lb/hr | tpy | lb/hr | lb/day | tpy | lb/hr | lb/day | tpy | lb/hr | lb/day | tpy | lb/hr | tonnesyr | lb/hr | tonnes/yr | lb/hr | tonnes/yr | lb/hr | tonnes/yr | tpy | lb/hr | tpy | lb/hr | tpy
TURB1 | Train 1a Compression Turbine Stack | 8760 | 37.6395 | 35.4238 | 63.6506 | 509.2045 | 54.0406 | 3.2985 | 13.7252 | 8.2292 | 197.5015 | 34.288 | 8.2292 | 197.5015 | 34.288 | 2.9166 | 69.9992 | 12.1505 | 136862.0089 | 517328.6328 | 2.5794 | 9.7499 | 0.25794 | 0.97499 | 137003.3591 | 517862.9262 | 570845.4822 | 0.79023 | 3.4612 | 1.1434 | 5.0082
TURB2 | Train 1b Compression Turbine Stack | 8760 | 37.6395 | 35.4238 | 63.6506 | 509.2045 | 54.0406 | 3.2985 | 13.7252 | 8.2292 | 197.5015 | 34.288 | 8.2292 | 197.5015 | 34.288 | 2.9166 | 69.9992 | 12.1505 | 136862.0089 | 517328.6328 | 2.5794 | 9.7499 | 0.25794 | 0.97499 | 137003.3591 | 517862.9262 | 570845.4822 | 0.79023 | 3.4612 | 1.1434 | 5.0082
TURB3 | Train 2a Compression Turbine Stack | 8760 | 37.6395 | 35.4238 | 63.6506 | 509.2045 | 54.0406 | 3.2985 | 13.7252 | 8.2292 | 197.5015 | 34.288 | 8.2292 | 197.5015 | 34.288 | 2.9166 | 69.9992 | 12.1505 | 136862.0089 | 517328.6328 | 2.5794 | 9.7499 | 0.25794 | 0.97499 | 137003.3591 | 517862.9262 | 570845.4822 | 0.79023 | 3.4612 | 1.1434 | 5.0082
TURB4 | Train 2b Compression Turbine Stack | 8760 | 37.6395 | 35.4238 | 63.6506 | 509.2045 | 54.0406 | 3.2985 | 13.7252 | 8.2292 | 197.5015 | 34.288 | 8.2292 | 197.5015 | 34.288 | 2.9166 | 69.9992 | 12.1505 | 136862.0089 | 517328.6328 | 2.5794 | 9.7499 | 0.25794 | 0.97499 | 137003.3591 | 517862.9262 | 570845.4822 | 0.79023 | 3.4612 | 1.1434 | 5.0082
TURB5 | Train 3a Compression Turbine Stack | 8760 | 37.6395 | 35.4238 | 63.6506 | 509.2045 | 54.0406 | 3.2985 | 13.7252 | 8.2292 | 197.5015 | 34.288 | 8.2292 | 197.5015 | 34.288 | 2.9166 | 69.9992 | 12.1505 | 136862.0089 | 517328.6328 | 2.5794 | 9.7499 | 0.25794 | 0.97499 | 137003.3591 | 517862.9262 | 570845.4822 | 0.79023 | 3.4612 | 1.1434 | 5.0082
TURB6 | Train 3b Compression Turbine Stack | 8760 | 37.6395 | 35.4238 | 63.6506 | 509.2045 | 54.0406 | 3.2985 | 13.7252 | 8.2292 | 197.5015 | 34.288 | 8.2292 | 197.5015 | 34.288 | 2.9166 | 69.9992 | 12.1505 | 136862.0089 | 517328.6328 | 2.5794 | 9.7499 | 0.25794 | 0.97499 | 137003.3591 | 517862.9262 | 570845.4822 | 0.79023 | 3.4612 | 1.1434 | 5.0082
TRB_GEN1 | Power Generator Turbines | 8760 | 14.614 | 11.9923 | 7.9082 | 63.2657 | 7.281 | 1.2807 | 4.6334 | 3.0455 | 73.0924 | 11.8298 | 3.0455 | 73.0924 | 11.8298 | 1.0783 | 25.8787 | 4.1893 | 50650.6409 | 178485.3504 | 0.95459 | 3.3638 | 0.095459 | 0.33638 | 50702.9525 | 178669.6888 | 196949.3847 | 0.27264 | 1.1942 | 0.39449 | 1.7279
TRB_GEN2 | Power Generator Turbines | 8760 | 14.614 | 11.9923 | 7.9082 | 63.2657 | 7.281 | 1.2807 | 4.6334 | 3.0455 | 73.0924 | 11.8298 | 3.0455 | 73.0924 | 11.8298 | 1.0783 | 25.8787 | 4.1893 | 50650.6409 | 178485.3504 | 0.95459 | 3.3638 | 0.095459 | 0.33638 | 50702.9525 | 178669.6888 | 196949.3847 | 0.27264 | 1.1942 | 0.39449 | 1.7279
TRB_GEN3 | Power Generator Turbines | 8760 | 14.614 | 11.9923 | 7.9082 | 63.2657 | 7.281 | 1.2807 | 4.6334 | 3.0455 | 73.0924 | 11.8298 | 3.0455 | 73.0924 | 11.8298 | 1.0783 | 25.8787 | 4.1893 | 50650.6409 | 178485.3504 | 0.95459 | 3.3638 | 0.095459 | 0.33638 | 50702.9525 | 178669.6888 | 196949.3847 | 0.27264 | 1.1942 | 0.39449 | 1.7279
TRB_GEN4 | Power Generator Turbines | 8760 | 14.614 | 11.9923 | 7.9082 | 63.2657 | 7.281 | 1.2807 | 4.6334 | 3.0455 | 73.0924 | 11.8298 | 3.0455 | 73.0924 | 11.8298 | 1.0783 | 25.8787 | 4.1893 | 50650.6409 | 178485.3504 | 0.95459 | 3.3638 | 0.095459 | 0.33638 | 50702.9525 | 178669.6888 | 196949.3847 | 0.27264 | 1.1942 | 0.39449 | 1.7279
Aux_COMP | Auxiliary Air Compressor (224 kW) | 500 | 0.29592 | 0.07398 | 2.1577 | 17.262 | 0.53944 | 0.14056 | 0.03514 | 0.014796 | 0.3551 | 0.003699 | 0.014796 | 0.3551 | 0.003699 | 0.30762 | 7.3829 | 0.076905 | 342.4097 | 77.658 | 0.013889 | 0.00315 | 0.0027778 | 0.00063 | 343.5847 | 77.9245 | 85.8969 | 0.002478 | 0.0006195 | 0.0084879 | 0.002122
FPUMP | Firewater Pump (429 kW) | 500 | 4.5161 | 1.129 | 4.1199 | 32.9593 | 1.03 | 0.23769 | 0.059422 | 0.23769 | 5.7045 | 0.059422 | 0.23769 | 5.7045 | 0.059422 | 0.58961 | 14.1506 | 0.1474 | 656.2852 | 148.8445 | 0.026621 | 0.0060375 | 0.0053241 | 0.0012075 | 658.5373 | 149.3553 | 164.6358 | 0.0047495 | 0.0011874 | 0.016268 | 0.0040671
FLARE_1D | Dry Flare Pilot/Purge | 8760 | 0.4862 | 2.1296 | 2.2165 | 17.732 | 9.7083 | 4.719 | 20.6692 | 0.20177 | 4.8426 | 0.88377 | 0.20177 | 4.8426 | 0.88377 | 0.01726 | 0.41424 | 0.075598 | 836.3789 | 3323.36 | 0.015763 | 0.062634 | 0.0015763 | 0.0062634 | 837.2427 | 3326.7924 | 3667.1565 | 0.0081945 | 0.035892 | 0.020714 | 0.090728
FLARE_2D | Dry Flare Pilot/Purge | 8760 | 0.4862 | 2.1296 | 2.2165 | 17.732 | 9.7083 | 4.719 | 20.6692 | 0.20177 | 4.8426 | 0.88377 | 0.20177 | 4.8426 | 0.88377 | 0.01726 | 0.41424 | 0.075598 | 836.3789 | 3323.36 | 0.015763 | 0.062634 | 0.0015763 | 0.0062634 | 837.2427 | 3326.7924 | 3667.1565 | 0.0081945 | 0.035892 | 0.020714 | 0.090728
| Dry Flare Pilot/Purge (Not Modeled) | 8760
FLARE_1W | Wet Flare Pilot/Purge | 8760 | 0.153 | 0.67014 | 0.6975 | 5.58 | 3.0551 | 1.485 | 6.5043 | 0.063495 | 1.5239 | 0.27811 | 0.063495 | 1.5239 | 0.27811 | 0.0056251 | 0.135 | 0.024638 | 263.1962 | 1045.8126 | 0.0049604 | 0.01971 | 0.00049604 | 0.001971 | 263.468 | 1046.8927 | 1154.0003 | 0.0025787 | 0.011295 | 0.0065184 | 0.028551
FLARE_2W | Wet Flare Pilot/Purge | 8760 | 0.153 | 0.67014 | 0.6975 | 5.58 | 3.0551 | 1.485 | 6.5043 | 0.063495 | 1.5239 | 0.27811 | 0.063495 | 1.5239 | 0.27811 | 0.0056251 | 0.135 | 0.024638 | 263.1962 | 1045.8126 | 0.0049604 | 0.01971 | 0.00049604 | 0.001971 | 263.468 | 1046.8927 | 1154.0003 | 0.0025787 | 0.011295 | 0.0065184 | 0.028551
| Wet Flare Pilot/Purge (Not Modeled) | 8760
DRY_MAX1 | Dry Flare Maximum Case | 500 | 2039.728 | 1019.864 | 9298.76 | 9298.76 | 4649.38 | 19797.36 | 9898.68 | 846.4904 | 846.4904 | 423.2452 | 846.4904 | 846.4904 | 423.2452 | 74.7509 | 74.7509 | 37.3754 | 3508814.3757 | 1591587.76 | 66.1292 | 29.996 | 6.6129 | 2.9996 | 3512438.2548 | 1593231.5408 | 1756235.0597 | 34.3778 | 17.1889 | 86.9005 | 43.4502
DRY_MAX2 | Dry Flare Maximum Case | 500 | 2039.728 | 1019.864 | 9298.76 | 9298.76 | 4649.38 | 19797.36 | 9898.68 | 846.4904 | 846.4904 | 423.2452 | 846.4904 | 846.4904 | 423.2452 | 74.7509 | 74.7509 | 37.3754 | 3508814.3757 | 1591587.76 | 66.1292 | 29.996 | 6.6129 | 2.9996 | 3512438.2548 | 1593231.5408 | 1756235.0597 | 34.3778 | 17.1889 | 86.9005 | 43.4502
| Dry Flare Maximum Case (Not Modeled) | 500
WET_MAX1 | Wet Flare Maximum Case | 500 | 476.68 | 238.34 | 2173.1 | 2173.1 | 1086.55 | 4626.6 | 2313.3 | 197.823 | 197.823 | 98.9115 | 197.823 | 197.823 | 98.9115 | 17.4752 | 17.4752 | 8.7376 | 820002.2928 | 371950.6 | 15.4542 | 7.01 | 1.5454 | 0.701 | 820849.1854 | 372334.748 | 410428.3161 | 8.034 | 4.017 | 20.3085 | 10.1542
WET_MAX2 | Wet Flare Maximum Case | 500 | 476.68 | 238.34 | 2173.1 | 2173.1 | 1086.55 | 4626.6 | 2313.3 | 197.823 | 197.823 | 98.9115 | 197.823 | 197.823 | 98.9115 | 17.4752 | 17.4752 | 8.7376 | 820002.2928 | 371950.6 | 15.4542 | 7.01 | 1.5454 | 0.701 | 820849.1854 | 372334.748 | 410428.3161 | 8.034 | 4.017 | 20.3085 | 10.1542
| Wet Flare Maximum Case (Not Modeled) | 500
LP_FLARE | LP Flare Pilot/Purge | 8760 | 0.714 | 3.1273 | 3.255 | 26.04 | 14.2569 | 6.93 | 30.3534 | 0.29631 | 7.1115 | 1.2978 | 0.29631 | 7.1115 | 1.2978 | 0.050466 | 1.2112 | 0.22104 | 1228.2488 | 4880.4588 | 0.023148 | 0.09198 | 0.0023148 | 0.009198 | 1229.5173 | 4885.4993 | 5385.3347 | 0.012034 | 0.052708 | 0.030419 | 0.13324
LP_MAX | LP Flare Maximum Flow (Maintenance) | 144 | 71.3717 | 5.1388 | 311.3778 | 2491.0222 | 22.4192 | 658.35 | 47.4012 | 28.1496 | 675.5894 | 2.0268 | 28.1496 | 675.5894 | 2.0268 | 2.7385 | 65.7248 | 0.19717 | 121772.395 | 7621.5384 | 2.1991 | 0.14364 | 0.21991 | 0.014364 | 121892.9051 | 7629.4099 | 8409.9748 | 1.1432 | 0.082311 | 2.8898 | 0.20807
TH_OX | Thermal Oxidizer | 8760 | 0.33055 | 1.4478 | 0.49494 | 3.9595 | 2.1678 | 0.032407 | 0.14194 | 0.04478 | 1.0747 | 0.19614 | 0.04478 | 1.0747 | 0.19614 | 0.016401 | 0.39362 | 0.071836 | 703.0262 | 2793.4817 | 0.01325 | 0.052648 | 0.001325 | 0.0052648 | 703.7523 | 2796.3667 | 3082.463 | 0.00044191 | 0.0019356 | 0.011087 | 0.048562
| Tank Emissions | 8760 | [6 empty] | 0.0015
| Fugitive Emissions | 8760 | [5 empty] | 4.1 | 17.958 | [11 empty] | 24.4 | 96.9536 |  |  | 610 | 2423.8411 | 2671.8242
| Mobile Equipment Emissions (Normal Operation) | 8760 |  | 3.259 |  |  | 3.2583 |  | 0.33304 |  |  | 0.19328 |  |  | 0.16899 |  |  | 0.018136 |  | 2159.6627 |  | 0.12735 |  | 0.0087667 |  | 2165.459 | 2387.0071 |  |  |  | 0.06986
| Non-Road/Portable Equipment Emissions (Normal Operation) | 8760 |  | 7.5904 |  |  | 3.2176 |  | 2.4298 |  |  | 0.69429 |  |  | 0.69429
| Marine Terminal Emissions (Normal Operation) | 8760 | 279.3093 | 379.5928 | 457.6916 | 3661.533 | 630.3831 | 59.1747 | 116.5816 | 13.3265 | 319.8368 | 14.0123 | 12.2573 | 294.1759 | 12.9756 | 18.2836 | 438.8065 | 1.1741 | [7 empty] | 81247.8049 | 89560.2678 |  |  | 0.30566 | 0.32664
Total Emissions (Without Maximum Flare) |  |  | 642.109 | 667.4708 | 1198.4612 | 9587.6899 | 1056.1668 | 766.2873 | 370.5269 | 104.1577 | 2499.7836 | 273.855 | 103.0884 | 2474.1227 | 272.7941 | 43.8449 | 1052.2782 | 91.7672 | 1150676.1323 | 3844333.1878 | 46.0121 | 169.4978 | 2.1653 | 7.2514 | 1152471.6826 | 3931979.3435 | 4334260.1501 | 7.0164 | 25.777 | 11.7547 | 37.9917
Total Emissions (With Maximum Flare) |  |  | 5674.925 | 3183.8788 | 24142.1812 | 32531.4099 | 12528.0268 | 49614.2073 | 24794.4869 | 2192.7843 | 4588.4103 | 1318.1684 | 2191.7151 | 4562.7494 | 1317.1074 | 228.2972 | 1236.7304 | 183.9933 | 9808309.4692 | 7771409.9078 | 209.179 | 243.5098 | 18.4819 | 14.6526 | 9819046.5632 | 7863111.9211 | 8667586.9017 | 91.84 | 68.1888 | 226.1726 | 145.2006
Total Emissions (W/O Maximum Flare, W/O Marine Terminal) |  |  |  | 277.0285 |  |  | 419.3078 |  | 251.1825 |  |  | 258.9552 |  |  | 258.9552 |  |  | 90.575 | [8 empty] | 4242312.8752
Total Emissions (W/ Maximum Flare, W/O Marine Terminal) |  |  |  | 2793.4365 |  |  | 11891.1678 |  | 24675.1425 |  |  | 1303.2685 |  |  | 1303.2685 |  |  | 182.8011 | [7 empty] | 7781864.1162 | 8575639.6268
Total Emissions (W/ Maximum Flare, W/O Marine Terminal, W/O Fugitive) |  |  |  | 2793.4365 |  |  | 11891.1678 |  | 24657.1845 |  |  | 1303.2685 |  |  | 1303.2685 |  |  | 182.8011 | [8 empty] | 8572967.8026
8 | CO Standard Requirement
24 | Intermittent unit hours/day operation
24 | Non-intermittent unit hours/day operation
0.5 | Flare hours/day operation

## LNG Fuel
LNG Fuel Gas Specification
| Component | % By Volume | MW
| N2 - Nitrogen | 0.6872
| CO2 - Carbon Dioxide | 0.005
H2O - Water
| O2 - Oxygen | 0.001
Ar - Argon
H2 - Hydrogen
| CH4 - Methane | 91.1475
| C2H6 - Ethane | 5.8251
| C3H8 - Propane | 1.8872
| C4H10 - IsoButane | 0.1374
| C4H10 - Normal Butane | 0.2056
| C5H12 - IsoPentane | 0.0463
| C5H12 - N-Pentane | 0.0443
| C6H14 - 2-Methylpentane | 0.0017
| C6H14 - Hexane | 0.0023
| C6H12 -Methylcyclopentane | 0.0013
| C6H12 - Cyclohexane | 0.0012
| C7H16 - Heptane | 0.0041
| C7H14 - Methylcyclohexane | 0.0011
| C8H18 - Octane | 0.001
| C9H20 - Nonane | 0.0003
| C10H22 - Decane | 0.0001
C10H18 - Heavy Oil
C12H26 - Distillate
C6H6 - Benzene
C7H8 - Toluene
C8H10 - Xylene
C8H8 - Styrene
Hg - Mercury
C2H4 - Ethylene
C2H2 - Acetylene
C3H6 - Propylene
C4H8 - Butylene
C4H6 - Butadienes
C6H12 - Hexene
CH3OH - Methanol
C2H5OH - Ethyl Alcohol
CO - Carbon Monoxide
NO - Nitric Oxide
NO2 - Nitrogen Dioxide
NH3 - Ammonia
| H2S - Hydrogen Sulfide | 0.0016 | 64.066
COS - Carbonyl Sulfide
C2H6S2 - DiMethyl DiSulfide
SO2
Properties
Temp
| MW | 17.68
Fuel Heating Value at 82ºF:
Net (Btu/lbm)
| Net (Btu/scf) | 981
Gross (Btu/lbm)
| Gross (Btu/scf) | 1087
scf defined at 14.676 psia, 60F
REFERENCE CB&I/CHIYODA CALCULATION GAS ANALYSIS SHEETS
Notes:
1 | Normal maximum sulfur based on 16 ppmv for total sulfur being equal to the pipeline specification of 1 grain/100 scf. This assumes all H2S and other mercaptans are included in Sulfur value
LNG Diesel Fuel Specification
| Sulfur Content (H2S) | 15 | ppm | Assume ULSD required
| Specific Gravity | 0.855 |  | average value at 60oF
| Density | 7.1307 | lb/gal
| LHV | 0.13113 | MMBtu/gal
| LHV | 18390 | Btu/lb
| HHV | 0.14425 | MMBtu/gal | Assumed 10% higher than LHV
| HHV | 20229 | Btu/lb
| lb SO2/gal Fuel | 0.00020134

## LNG Turbines
LNG Fuel Gas-Driven Turbines |  |  |  | Reference: CB&I/Chiyoda Calculation USAL-CB-SCCAL-00-000014-500
Reference: CB&I/Chiyoda Calculation USAL-CB-SCCAL-00-000015-500
| EMISSION FACTORS | Standard Factors |  | Special/Vendor
|  | AP42 Table 3.1-1 and 3.1-2a | 40 CFR Part 98 (Natural Gas) |  |  | Ambient Temp Basis (F) | Load % Basis | Compression Turbine Vendor | Ambient Temp Basis (F) | Load % Basis | Power Generation Turbine Vendor
| NOx (lb/MMBtu) | 0.34102 |  | Short-Term ppmvd @ 15% NOx |  | -30 | 100% | 9 | -30 | 100% | 9
| CO (lb/MMBtu) | 0.087386 |  | Short-Term ppmvd @ 15% CO |  | -30 | 100% | 25 | -30 | 100% | 8
| VOC (lb/MMBtu) | 0.0022379 |  | Annual ppmvd @ 15% NOx |  | 40 | 100% | 9 | 40 | 100% | 9
| PM10 (lb/MMBtu) | 0.0070335 |  | Annual ppmvd @ 15% CO |  | 40 | 100% | 25 | 40 | 100% | 5
| PM2.5 (lb/MMBtu) | 0.0070335
| CO2 (kg CO2/MMBtu) |  | 53.06
| CH4 (kg CH4/MMBtu) |  | 0.001
| N2O (kg N2O/MMBtu) |  | 0.0001
Notes:
1.) Emission Factors have been convert to AlaskaLNG fuel gas HHV by ratio of project fuel gas/1020 (btu/scf)
| EMISSIONS CALCULATIONS | Compressor Turbines |  | Power Generation Turbines with CO Catalyst and HRSG |  | References/ Comments
| Turbine Parameters | Short-Term | Annual | Short-Term | Annual |  |  |  | Conversion Table
| Total Installed | 6 | 6 | 4 | 4 | From CB&I/Chiyoda Calculation |  |  | 1 lb = | 453.59 | g
| Ambient Temperature Basis (F) | -30 | 40 | -30 | 40 |  |  |  | 1 lbmol = | 378.49 | scf
| Load % Basis | 100% | 100% | 100% | 100% |  |  |  | 1 MMBtu= | 1000000 | Btu
| Operation (hr/yr) | 8760 | 8760 | 8760 | 8760 |  |  |  | 1 hr = | 60 | min
| Device Power (hp) | 155759.6889 | 152876.4919 | 60603.4598 | 53756.2022 |  |  |  | 1 ft3 = | 0.028317 | m3
| Device Power (kW) | 116150 | 114000 | 45192 | 40086 | From CB&I/Chiyoda Calculation -Output |  |  | 1 min = | 60 | sec
| Turbine Heat Input HHV (MMBtu/hr) | 1170 | 1113 | 433 | 384 | From CB&I/Chiyoda Calculation |  |  | 1 kJ = | 0.94782 | MMBtu
| Fuel Flow Rate (lbmol/hr) | 2845.3407 | 2706.2829 | 1051.9221 | 933.0709 | From CB&I/Chiyoda Calculation |  |  | 1 scf = | 28.32 | L
| Exhaust Flow MW (lb/lbmol) | 28.55 | 28.5 | 28.51 | 28.54 | From CB&I/Chiyoda Calculation |  |  | 1 g = | 1000000 | ug
| Exhaust Flow Rate WET (lb/hr) | 2524290 | 2477111 | 1027143 | 924064 | From CB&I/Chiyoda Calculation |  |  | 1 ton = | 2000 | lb
| Exhaust Flow Rate (lbmol/hr) | 88416.4623 | 86916.1754 | 36027.464 | 32377.8556 |  |  |  | 1 hp = | 0.7457 | kW
| Exhaust H2O Concentration | 6.72% | 7.1% | 6.94% | 6.44% | From CB&I/Chiyoda Calculation |  |  | 1 kg = | 2.2046 | lb
| Exhaust Flow Rate DRY (lbmol/hr) | 82474.8761 | 80745.127 | 33527.158 | 30292.7217 |  |  |  | 1 mol = | 1000000 | ppm
| Exhaust O2 Concentration DRY | 14.4% | 14.59% | 14.69% | 15.22% | From CB&I/Chiyoda Calculation |  |  | 1 tonnes = | 1000 | kg
| Exhaust Flow Rate (acfh) | 92314463.5685 | 90748033.7719 | 21070109.2865 | 18935691.8355
| Turbine Emission Factors | [7 empty] | Heat Release Equivalents
| NOx (ppmvd @15% O2) | 9 | 2 | 9 | 2 | Adjusted to Actual O2 Amount |  |  | 1 | CO2
| CO (ppmvd @15% O2) | 25 | 5 | 8 | 2 | Adjusted to Actual O2 Amount |  |  | 25 | CH4
| VOC (ppmvd @15% O2) | 2 | 2 | 2 | 2 |  |  |  | 298 | N2O
| PM10 (lb/MMBtu) | 0.0070335 | 0.0070335 | 0.0070335 | 0.0070335
| PM2.5 (lb/MMBtu) | 0.0070335 | 0.0070335 | 0.0070335 | 0.0070335 |  |  |  | Molecular Weight
| SO2 | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | Based on Mass Balance of Sulfur |  |  | NO2 | 46.01
| CO2 (kg CO2/MMBtu) | 53.06 | 53.06 | 53.06 | 53.06 |  |  |  | CO | 28.01
| CH4 (kg CH4/MMBtu) | 0.001 | 0.001 | 0.001 | 0.001 |  |  |  | VOCs | 18.1444 | Assumes 90% Methane, 6% Ethane, 3% Propane, and 1% Butane
| N2O (kg N2O/MMBtu) | 0.0001 | 0.0001 | 0.0001 | 0.0001
Turbine Emission Calculations (Maximum 1-hour)
| NOx (lb/hr) | 37.6395 | 7.9521 | 14.614 | 2.6835
| CO (lb/hr) | 63.6506 | 12.1027 | 7.9082 | 1.6337
| VOC (lb/hr) | 3.2985 | 3.136 | 1.2807 | 1.0583 |  |  |  | Turbine Emissions when SCR and Ox Cat
| PM10 (lb/hr) | 8.2292 | 7.8283 | 3.0455 | 2.7009 |  |  |  | is being Bypassed for 40 hours per year.
| PM2.5 (lb/hr) | 8.2292 | 7.8283 | 3.0455 | 2.7009 |  |  | Turbine Type | Compressor (1-6) | Power Generation (7-10)
| SO2 @ 16 ppm (lb/hr) | 2.9166 | 2.7741 | 1.0783 | 0.95645 |  |  | NOx (lb/hr) | 37.64 | 14.61
| CO2 (lb/hr) | 136862.0089 | 130194.3726 | 50650.6409 | 44918.8132 |  |  | CO (lb/hr) | 63.65 | 7.91
| CH4 (lb/hr) | 2.5794 | 2.4537 | 0.95459 | 0.84657 |  |  | VOC (lb/hr) | 2.62 | 0.97
| N2O (lb/hr) | 0.25794 | 0.24537 | 0.095459 | 0.084657
| CO2e (lb/hr) | 137003.3591 | 130328.8364 | 50702.9525 | 44965.205
| CO2e (lb/MMBtu) | 117.0969 | 117.0969 | 117.0969 | 117.0969
Total Emission Calculations (Annual)
| NOx (tpy) | 164.861 | 35.4238 | 64.0094 | 11.9923
| CO (tpy) | 278.7895 | 54.0406 | 34.6379 | 7.281
| VOC (tpy) | 14.4476 | 13.7252 | 5.6095 | 4.6334
| PM10 (tpy) | 36.044 | 34.288 | 13.3394 | 11.8298
| PM2.5 (tpy) | 36.044 | 34.288 | 13.3394 | 11.8298
| SO2 @ 16 ppm (tpy) | 12.7749 | 12.1505 | 4.7229 | 4.1893
| CO2 (tonnes/yr) | 543822.552 | 517328.6328 | 201260.8248 | 178485.3504
| CH4 (tonnes/yr) | 10.2492 | 9.7499 | 3.7931 | 3.3638
| N2O (tonnes/yr) | 1.0249 | 0.97499 | 0.37931 | 0.33638
| CO2e (tonnes/yr) | 544384.2082 | 517862.9262 | 201468.6856 | 178669.6888
| CO2e tpy | 600074.7127 | 570840.3036 | 222078.9321 | 196947.598
Stack Parameters
| Stack Height (ft) | 210 | 210 | 150 | 150 | From CB&I/Chiyoda Calculation
| Exhaust Temp Ambient Temp Basis (F) | -30 | -30 | -- | --
| Exhaust Temp Load % Basis | 100% | 100% | -- | --
| Exhaust Temperature (F) | 970 | 970 | 341 | 341 | From CB&I/Chiyoda Calculation with HRSG
| Exhaust Velocity Ambient Temp Basis (F) | 71 | 71 | 70 | 70
| Exhaust Velocity Load % Basis | 100% | 100% | 60% | 60%
| Exhaust Velocity (ft/s) | 86 | 86 | 48 | 48 | From CB&I/Chiyoda Calculation with HRSG adjustment
| Stack Diameter (ft) | 19 | 19 | 10 | 10 | From CB&I/Chiyoda Calculation
| NO2/NOx Ratio | 0.5 | 0.5 | 0.5 | 0.5 | EPA's ISR Guidance (Date: 3-1-2011)

## LNG Diesel Equip
LNG Diesel-Driven Intermittent Equipment |  |  |  | Reference: CB&I/Chiyoda Calculation 194210-USAL-CB-SCCAL-00-000025-000
Reference: CB&I/Chiyoda Calculation 194210-USAL-CB-SCCAL-00-000018-000
|  | Emergency |  |  |  | Non-Emergency
| EMISSION FACTORS | Standard Factors
|  | 40 CFR Part 89.112 Tier 3 130<kW<225 | 40 CFR Part 89.112 Tier 3 225<kW<450 | 40 CFR Part 60 Subpart IIII 175<hp<300 | 40 CFR Part 60 Subpart IIII 300<hp<600 | 40 CFR 1039 Subpart B Tier 4 130<kW<560 | 40 CFR 1039 Subpart B Tier 4 kW > 560 | 40 CFR Part 98 (Petroleum)
| NOx (g/hp-hr) (95% of NOx+NMHC) | 2.8337 | 2.8337 | 2.85 | 2.85 | 0.29828 | 2.6099
| CO (g/hp-hr) | 2.6099 | 2.6099 | 2.6 | 2.6 | 2.6099 | 2.6099
| VOC (g/hp-hr) (5% of NOx+NMHC) | 0.14914 | 0.14914 | 0.15 | 0.15 | 0.14168 | 0.14168
| PM10 (g/hp-hr) | 0.14914 | 0.14914 | 0.15 | 0.15 | 0.014914 | 0.029828
| PM2.5 (g/hp-hr) | 0.14914 | 0.14914 | 0.15 | 0.15 | 0.014914 | 0.029828
| CO2 (kg CO2/MMBtu) | [6 empty] | 73.96
| CH4 (kg CH4/MMBtu) | [6 empty] | 0.003
| N2O (kg N2O/MMBtu) | [6 empty] | 0.0006
Conversion Table
[8 empty] | ULSD S Content | 0.0015 | percent by weight
| EMISSIONS CALCULATIONS | Auxiliary Air Compressor | Firewater Pump | References/ Comments |  |  |  | 1 gal diesel | 7.05 | lb
| Total Installed | 1 | 1 | From CB&I/Chiyoda Calculation |  |  |  | lb SO2/ lb S | 1.9981 | unitless
| Load | 100% | 100% | Ambient Temp does not affect emissions |  |  |  | 1 lb = | 453.59 | g
| Operation (hr/yr) | 500 | 500 | Intermittent Assumption |  |  |  | 1 lbmol = | 378.49 | scf
| Rated Power (hp) | 300 | 575 | From Chiyoda Calculation |  |  |  | 1 MMBtu= | 1000000 | Btu
| Rated Power (kW) | 224 | 429 | From Chiyoda Calculation |  |  |  | 1 hr = | 60 | min
| BSFC (Btu/hp-hr) | 7000 | 7000 | AP42 Table 3.3-1 |  |  |  | 1 ft3 = | 0.028317 | m3
| Rated Duty (MMBtu/hr) | 2.1 | 4.025 | For HAPs calculation and CO2e |  |  |  | 1 min = | 60 | sec
| Fuel Flow Rate (gal/hr) | 14.5584 | 27.9035 | Used ULSD HHV |  |  |  | 1 kJ = | 0.94782 | MMBtu
| Emission Factors | [6 empty] | 1 scf = | 28.32 | L
| Not-to-Exceed Factor | 50% | 25% | See 40 CFR 1039.101(e)(3) for when to use 50% not to exceed factor of safety |  |  |  | 1 g = | 1000000 | ug
| NOx (g/hp-hr) | 0.44742 | 3.5625 |  |  |  |  | 1 ton = | 2000 | lb
| CO (g/hp-hr) | 3.2624 | 3.25 |  |  |  |  | 1 hp = | 0.7457 | kW
| VOC (g/hp-hr) | 0.21252 | 0.1875 |  |  |  |  | 1 kg = | 2.2046 | lb
| PM10 (g/hp-hr) | 0.022371 | 0.1875 |  |  |  |  | 1 mol = | 1000000 | ppm
| PM2.5 (g/hp-hr) | 0.022371 | 0.1875 |  |  |  |  | 1 tonnes = | 1000 | kg
| SO2 | No Emission Factor | No Emission Factor | Based on Mass Balance of Sulfur
| CO2 (kg CO2/MMBtu) | 73.96 | 73.96 |  |  |  |  | Heat Release Equivalents
| CH4 (kg CH4/MMBtu) | 0.003 | 0.003 |  |  |  |  | 1 | CO2
| N2O (kg N2O/MMBtu) | 0.0006 | 0.0006 |  |  |  |  | 25 | CH4
| Emission Calculations (Maximum 1-hour) | [6 empty] | 298 | N2O
| NOx (lb/hr) | 0.29592 | 4.5161
| CO (lb/hr) | 2.1577 | 4.1199
| VOC (lb/hr) | 0.14056 | 0.23769
| PM10 (lb/hr) | 0.014796 | 0.23769
| PM2.5 (lb/hr) | 0.014796 | 0.23769
| SO2 (lb/hr) | 0.30762 | 0.58961
| CO2 (lb/hr) | 342.4097 | 656.2852
| CH4 (lb/hr) | 0.013889 | 0.026621
| N2O (lb/hr) | 0.0027778 | 0.0053241
| CO2e (lb/hr) | 343.5847 | 658.5373
| CO2e (lb/MMBtu) | 163.6117 | 163.6117
Emission Calculations (Annual)
| NOx (tpy) | 0.07398 | 1.129
| CO (tpy) | 0.53944 | 1.03
| VOC (tpy) | 0.03514 | 0.059422
| PM10 (tpy) | 0.003699 | 0.059422
| PM2.5 (tpy) | 0.003699 | 0.059422
| SO2 (tpy) | 0.076905 | 0.1474
| CO2 (tonnes/yr) | 77.658 | 148.8445
| CH4 (tonnes/yr) | 0.00315 | 0.0060375
| N2O (tonnes/yr) | 0.00063 | 0.0012075
| CO2e (tonnes/yr) | 77.9245 | 149.3553
| CO2e (tpy) | 85.8962 | 164.6343
Stack Parameters
| Stack Height (ft) | 10 | 10 | From CB&I/Chiyoda Calculation
| Exhaust Temperature (F) | 883 | 908 | From CB&I/Chiyoda Calculation
| Exhaust Velocity (ft/s) | 115 | 157 | From CB&I/Chiyoda Calculation
| Stack Diameter (ft) | 0.665 | 0.665 | From CB&I/Chiyoda Calculation
| NO2/NOx Ratio | 0.5 | 0.5 | EPA's ISR Guidance (Date: 3-1-2011)

## LNG Flares
LNG Flares |  |  |  | Reference: CB&I/Chiyoda Calculation 194210-USAL-CB-SCCAL-00-000027-000
Reference: CB&I/Chiyoda Calculation 194210-USAL-CB-SCCAL-00-000026-000
Reference: CB&I/Chiyoda Calculation 194210-USAL-CB-SCCAL-00-000019-000
| EMISSION FACTORS | Standard Factors
|  | AP42 Tables 13.5-1 and 13.5-2 | 40 CFR Part 98 (Natural Gas)
| NOx (lb/MMBtu) | 0.068
| CO (lb/MMBtu) | 0.31
| VOC (lb/MMBtu) | 0.66
| PM10 (µg/L Exhaust) | 40
| PM2.5 (µg/L Exhaust) | 40
| CO2 (kg CO2/MMBtu) |  | 53.06
| CH4 (kg CH4/MMBtu) |  | 0.001
| N2O (kg N2O/MMBtu) |  | 0.0001
| MODELING PARAMETERS CALCULATION | Dry Flare Purge/Pilot/Valve Passing | Wet Flare Purge/Pilot | LP Flare Purge/Pilot/Comp Seal Gas | Dry Flare Maximum | Wet Flare Maximum | LP Flare Maximum | References/ Comments
Exhaust Flow Calculation
| Fuel Flow Rate (scfh) | 6373 | 2077 | 18634 | 55201793 | 12905048 | 992915.5 | From CB&I/Chiyoda Calculation (Wet/dry Purge/Pilot divided by 2)
| Fuel Flow Rate (lbmol/hr) | 16.838 | 5.4876 | 49.2325 | 145847.4279 | 34096.1399 | 2623.3599
| Fuel MW(lb/lbmol) | 18.5 | 17.68 | 23.1 | 17.68 | 17.68 | 25.7 | All cases not based on fuel gas from CB&I/Chiyoda Calculation
| Fuel Flow Rate (lb/hr) | 311.5023 | 97.0207 | 1137.2702 | 2578582.5259 | 602819.7539 | 67420.3502
| Fuel Flow HHV (MMBtu/hr) | 7.15 | 2.25 | 10.5 | 59992 | 14020 | 997.5 | From CB&I/Chiyoda Calculation (Wet/dry Purge/Pilot divided by 2)
| Fd Factor (dscf/MMBtu) | 8710 | 8710 | 8710 | 8710 | 8710 | 8710 | Method 19 for gas fuel
| Exhaust O2 Concentration | 3% | 3% | 3% | 3% | 3% | 3% | Assumed Dry Oxygen Concentration
| Exhaust Flow (dscfh) (@HHV) | 72713.9022 | 22881.9972 | 106782.6536 | 610105233.9665 | 142580267.0391 | 10144352.095
| Exhaust Water Concentration | 10% | 10% | 10% | 10% | 10% | 10% | Assumed Water Content
| Exhaust Flow (scfh) (@HHV) | 80793.2247 | 25424.4413 | 118647.3929 | 677894704.4072 | 158422518.9323 | 11271502.3277
| Ratio of Exhaust to Fuel | 12.6774 | 12.2409 | 6.3673 | 12.2803 | 12.276 | 11.3519
| Exhaust Flow (L/h) (@HHV) | 2288064.1236 | 720020.1788 | 3360094.1676 | 19197978028.8119 | 4486525736.1639 | 319208945.9218
Effective Height and Diameter Calculation
| Heat Release Rate (MMBtu/hr) | 6.4605 | 2.0306 | 9.4929 | 54141.8142 | 12664.4751 | 898.6486 | Based on LHV From CB&I/Chiyoda Calculation
| Buoyancy flux | 7.5071 | 2.3595 | 11.0307 | 62912.7881 | 14716.1201 | 1044.2297 | SCREEN3 Model User's Guide
| Actual Stack Height (m) | 0 | 0 | 60.6552 | 0 | 0 | 60.6552 | From CB&I/Chiyoda Calculation converted to m
| GEP stack height (m) | 65 | 65 | 65 | 65 | 65 | 65 | EPA GEP Stack Height Guideline
| Effective Stack Height (m) | 2.3029 | 1.3244 | 63.4232 | 172.8227 | 86.2996 | 85.0214 | SCREEN3 Model User's Guide
| Effective Stack Diameter (m) | 0.44608 | 0.25009 | 0.54073 | 40.836 | 19.7502 | 5.261 | SCREEN3 Model User's Guide
Note:
1.) Method 19 used to develop Exhaust Flow Rate for PM calculation. Assumed typical Boiler Exhaust parameters of 3% O2 and 10% H2O
| EMISSIONS CALCULATIONS | Dry Flare Purge/Pilot/Valve Passing | Wet Flare Purge/Pilot | LP Flare Purge/Pilot/Comp Seal Gas | Dry Flare Maximum | Wet Flare Maximum | LP Flare Maximum | References/ Comments
| Total Installed | 3 | 3 | 1 | 3 | 3 | 1 | From CB&I/Chiyoda Calculation (2 op, 1 spare) | Conversion Table
| Load | 100% | 100% | 100% | 100% | 100% | 100% | Ambient Temp does not affect emissions | 1 lb = | 453.59 | g
| Operation (hr/yr) | 8760 | 8760 | 8760 | 500 | 500 | 144 | Maximum Case Intermittent | 1 lbmol = | 378.49 | scf
| Rated Duty HHV (MMBtu/hr) | 7.15 | 2.25 | 10.5 | 59992 | 14020 | 997.5 | From CB&I/Chiyoda Calculation for HAPs Calculation | 1 MMBtu= | 1000000 | Btu
| Emission Factors | [7 empty] | 1 hr = | 60 | min
| NOx (lb/MMBtu) | 0.068 | 0.068 | 0.068 | 0.068 | 0.068 | 0.068 | Based on HHV | 1 ft3 = | 0.028317 | m3
| CO (lb/MMBtu) | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | 0.31 | Based on HHV | 1 min = | 60 | sec
| VOC (lb/MMBtu) | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | Based on HHV | 1 kJ = | 0.94782 | MMBtu
| PM10 (µg/L Exhaust) | 40 | 40 | 40 | 40 | 40 | 40 |  | 1 scf = | 28.32 | L
| PM2.5 (µg/L Exhaust) | 40 | 40 | 40 | 40 | 40 | 40 |  | 1 g = | 1000000 | ug
| SO2 | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | No Emission Factor | Based on Mass Balance of Sulfur | 1 ton = | 2000 | lb
| CO2 (kg CO2/MMBtu) | 53.06 | 53.06 | 53.06 | 53.06 | 53.06 | 53.06 | Based on HHV | 1 hp = | 0.7457 | kW
| CH4 (kg CH4/MMBtu) | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | Based on HHV | 1 kg = | 2.2046 | lb
| N2O (kg N2O/MMBtu) | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | Based on HHV | 1 m = | 0.3048 | ft
| CO2e (lb/Mmbtu) | 117.0969 | 117.0969 | 117.0969 | 117.0969 | 117.0969 | 117.0969 |  | 1 mol = | 1000000 | ppm
| Additional Warm Vessel Arrival Inert Gas Emissions (Annual) | [7 empty] | 1 tonnes = | 1000 | kg
| NOx (tpy) | [5 empty] | 0.255 | From CB&I/Chiyoda Calculation
| CO (tpy) | [5 empty] | 0.155 | From CB&I/Chiyoda Calculation | Heat Release Equivalents
| SO2 (tpy) | [5 empty] | 0.00356 | From CB&I/Chiyoda Calculation | 1 | CO2
| CO2 (tpy) | [5 empty] | 366.3907 | From CB&I/Chiyoda Calculation | 25 | CH4
| Emission Calculations (Maximum 1-hour) | [7 empty] | 298 | N2O
| NOx (lb/hr) | 0.4862 | 0.153 | 0.714 | 4079.456 | 953.36 | 71.3717
| CO (lb/hr) | 2.2165 | 0.6975 | 3.255 | 18597.52 | 4346.2 | 311.3778
| VOC (lb/hr) | 4.719 | 1.485 | 6.93 | 39594.72 | 9253.2 | 658.35
| PM10 (lb/hr) | 0.20177 | 0.063495 | 0.29631 | 1692.9807 | 395.6459 | 28.1496
| PM2.5 (lb/hr) | 0.20177 | 0.063495 | 0.29631 | 1692.9807 | 395.6459 | 28.1496
| SO2 @ 16 ppm (lb/hr) | 0.01726 | 0.0056251 | 0.050466 | 149.5018 | 34.9505 | 2.7385
| CO2 (lb/hr) | 836.3789 | 263.1962 | 1228.2488 | 7017628.7514 | 1640004.5855 | 121772.395
| CH4 (lb/hr) | 0.015763 | 0.0049604 | 0.023148 | 132.2584 | 30.9085 | 2.1991
| N2O (lb/hr) | 0.0015763 | 0.00049604 | 0.0023148 | 13.2258 | 3.0908 | 0.21991
| CO2e (lb/hr) | 837.2427 | 263.468 | 1229.5173 | 7024876.5097 | 1641698.3709 | 121892.9051
Emission Calculations (Annual)
| NOx (tpy) | 2.1296 | 0.67014 | 3.1273 | 1019.864 | 238.34 | 5.1388
| CO (tpy) | 9.7083 | 3.0551 | 14.2569 | 4649.38 | 1086.55 | 22.4192
| VOC (tpy) | 20.6692 | 6.5043 | 30.3534 | 9898.68 | 2313.3 | 47.4012
| PM10 (tpy) | 0.88377 | 0.27811 | 1.2978 | 423.2452 | 98.9115 | 2.0268
| PM2.5 (tpy) | 0.88377 | 0.27811 | 1.2978 | 423.2452 | 98.9115 | 2.0268
| SO2 @ 16 ppm (tpy) | 0.075598 | 0.024638 | 0.22104 | 37.3754 | 8.7376 | 0.19717
| CO2 (tonnes/yr) | 3323.36 | 1045.8126 | 4880.4588 | 1591587.76 | 371950.6 | 7621.5384
| CH4 (tonnes/yr) | 0.062634 | 0.01971 | 0.09198 | 29.996 | 7.01 | 0.14364
| N2O (tonnes/yr) | 0.0062634 | 0.001971 | 0.009198 | 2.9996 | 0.701 | 0.014364
| CO2e (tonnes/yr) | 3326.7924 | 1046.8927 | 4885.4993 | 1593231.5408 | 372334.748 | 7629.4099
| CO2e (tpy) | 3667.1232 | 1153.9898 | 5385.2859 | 1756219.1274 | 410424.5927 | 8776.2892
Stack Parameters
| Stack Height (m) | 2.3029 | 1.3244 | 63.4232 | 172.8227 | 86.2996 | 85.0214
| Exhaust Temperature (K) | 1273 | 1273 | 1273 | 1273 | 1273 | 1273
| Exhaust Velocity (m/s) | 20 | 20 | 20 | 20 | 20 | 20
| Stack Diameter (m) | 0.44608 | 0.25009 | 0.54073 | 40.836 | 19.7502 | 5.261
| NO2/NOx Ratio | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | EPA's ISR Guidance (Date: 3-1-2011)

## LNG Thermal Oxidizer
LNG Fuel Gas Heaters |  |  |  | Reference: CB&I/Chiyoda Calculation 194210-USAL-CB-SCCAL-00-000021-000
| EMISSION FACTORS | Standard Factors
|  | TCEQ Vapor Oxidizers Emission Factors | 40 CFR Part 98 (Natural Gas)
| NOx (lb/MMBtu) | 0.1
| CO (lb/MMBtu) | 0.082353
| VOC (lb/MMBtu) | 0.0053922
| PM10 (lb/MMBtu) | 0.007451
| PM2.5 (lb/MMBtu) | 0.007451
| CO2 (kg CO2/MMBtu) |  | 53.06
| CH4 (kg CH4/MMBtu) |  | 0.001
| N2O (kg N2O/MMBtu) |  | 0.0001
Notes:
1.) Emission Factor for CO has been based on AP42 Section 1.4, to ensure CO emissions are not underestimated (TCEQ references AP42 Section 1.4 for VOC and PM emissions)
| EMISSIONS CALCULATIONS | Thermal Oxidizer | References/ Comments
| Total Installed | 1 | From CB&I/Chiyoda Calculation |  | Conversion Table
| Load | 100% | From CB&I/Chiyoda Calculation |  | 1 lb = | 453.59 | g
| Operation (hr/yr) | 8760 |  |  | 1 lbmol = | 378.49 | scf
| Rated Duty LHV (MMBtu/hr) | 5.55 | From CB&I/Chiyoda Calculation |  | 1 MMBtu= | 1000000 | Btu
| Rated Duty HHV (MMBtu/hr) | 6.01 | From CB&I/Chiyoda Calculation |  | 1 hr = | 60 | min
| Fuel Flow Rate (lbmol/hr) | 16 | From CB&I/Chiyoda Calculation |  | 1 ft3 = | 0.028317 | m3
| Emission Factors |  |  |  | 1 min = | 60 | sec
| NOx (lb/MMBtu) | 0.055 | Based on HHV |  | 1 kJ = | 0.94782 | MMBtu
| CO (lb/MMBtu) | 0.082353 | Based on HHV |  | 1 scf = | 28.32 | L
| VOC (lb/MMBtu) | 0.0053922 | Based on HHV |  | 1 g = | 1000000 | ug
| PM10 (lb/MMBtu) | 0.007451 | Based on HHV |  | 1 ton = | 2000 | lb
| PM2.5 (lb/MMBtu) | 0.007451 | Based on HHV |  | 1 hp = | 0.7457 | kW
| SO2 | No Emission Factor | Based on Mass Balance of Sulfur |  | 1 kg = | 2.2046 | lb
| CO2 (kg CO2/MMBtu) | 53.06 | Based on HHV |  | 1 m = | 0.3048 | ft
| CH4 (kg CH4/MMBtu) | 0.001 | Based on HHV |  | 1 mol = | 1000000 | ppm
| N2O (kg N2O/MMBtu) | 0.0001 | Based on HHV |  | 1 tonnes = | 1000 | kg
| CO2e (lb/Mmbtu) | 117.0969
| Emission Calculations (Maximum 1-hour) |  |  |  | Heat Release Equivalents
| NOx (lb/hr) | 0.33055 |  |  | 1 | CO2
| CO (lb/hr) | 0.49494 | 0.044816 |  | 25 | CH4
| VOC (lb/hr) | 0.032407 |  |  | 298 | N2O
| PM10 (lb/hr) | 0.04478
| PM2.5 (lb/hr) | 0.04478 |  |  | Molecular Weight
| SO2 @ 16 ppm (lb/hr) | 0.016401 |  |  | NO2 | 46.01
| CO2 (lb/hr) | 703.0262 |  |  | CO | 28.01
| CH4 (lb/hr) | 0.01325
| N2O (lb/hr) | 0.001325
| CO2e (lb/hr) | 703.7523
Emission Calculations (Annual)
| NOx (tpy) | 1.4478
| CO (tpy) | 2.1678
| VOC (tpy) | 0.14194
| PM10 (tpy) | 0.19614
| PM2.5 (tpy) | 0.19614
| SO2 @ 16 ppm (tpy) | 0.071836
| CO2 (tonnes/yr) | 2793.4817
| CH4 (tonnes/yr) | 0.052648
| N2O (tonnes/yr) | 0.0052648
| CO2e (tonnes/yr) | 2796.3667
| CO2e (lb/MMBtu) | 3082.4351
Stack Parameters
| Stack Height (ft) | 47 | From CB&I/Chiyoda Calculation
| Exhaust Temperature (F) | 1800 | From CB&I/Chiyoda Calculation
| Exhaust Velocity (ft/s) | 8.9 | From CB&I/Chiyoda Calculation
| Stack Diameter (ft) | 5 | From CB&I/Chiyoda Calculation
| NO2/NOx Ratio | 0.5 | EPA's ISR Guidance (Date: 3-1-2011)

## LNG Misc
LNG Miscellaneous Emissions |  |  |  | Reference: CB&I/Chiyoda Calculation 194210-USAL-CB-SCCAL-00-000023-000
Reference: CB&I/Chiyoda Calculation 194210-USAL-CB-SCCAL-00-000024-000
| EMISSIONS CALCULATIONS | Tank | Fugitive | References/ Comments
| Methane (lb/hr) |  | 24.4 | From CB&I/Chiyoda Calculation
| NMHC (lb/hr) |  | 4.1 | From CB&I/Chiyoda Calculation
| CO2e (lb/hr) |  | 610
| Emissions Calculation (Annual) |  |  |  | Conversion Table
| Operation (hr/yr) | 8760 | 8760 | From CB&I/Chiyoda Calculation | 1 lb = | 453.59 | g
| Methane (tonnes/yr) |  | 96.9536 |  | 1 lbmol = | 378.49 | scf
| CO2e (tonnes/yr) |  | 2423.8411 |  | 1 MMBtu= | 1000000 | Btu
| NMHC (tpy) | 0.0015 | 17.958 |  | 1 hr = | 60 | min
|  | Tank emissions from BACT Analysis |  |  | 1 ft3 = | 0.028317 | m3
[5 empty] | 1 min = | 60 | sec
[5 empty] | 1 kJ = | 0.94782 | MMBtu
[5 empty] | 1 scf = | 28.32 | L
[5 empty] | 1 g = | 1000000 | ug
[5 empty] | 1 ton = | 2000 | lb
[5 empty] | 1 hp = | 0.7457 | kW
[5 empty] | 1 kg = | 2.2046 | lb
[5 empty] | 1 mol = | 1000000 | ppm
[5 empty] | 1 tonnes = | 1000 | kg
Heat Release Equivalents
[5 empty] | 1 | CO2
[5 empty] | 25 | CH4
[5 empty] | 298 | N2O

## LNG HAP Emission Unit Inventory
Emission Unit ID | Emission Unit Tag No. | Description | Source Category | Turbine ISO Power | Turbine ISO Heat Rate | Turbine 10o F MMBtu/hr (HHV) | Load Basis for CT EF | Fuel/Service | Control Type | CE% | hrs/yr | Load Basis for Calc
TURB1 |  | Train 1a Compression Turbine Stack | CT |  |  | 1113 | >80% | NG |  |  | 8760 | 100% load
TURB2 |  | Train 1b Compression Turbine Stack | CT |  |  | 1113 | >80% | NG |  |  | 8760 | 100% load
TURB3 |  | Train 2a Compression Turbine Stack | CT |  |  | 1113 | >80% | NG |  |  | 8760 | 100% load
TURB4 |  | Train 2b Compression Turbine Stack | CT |  |  | 1113 | >80% | NG |  |  | 8760 | 100% load
TURB5 |  | Train 3a Compression Turbine Stack | CT |  |  | 1113 | >80% | NG |  |  | 8760 | 100% load
TURB6 |  | Train 3b Compression Turbine Stack | CT |  |  | 1113 | >80% | NG |  |  | 8760 | 100% load
TRB_GEN1 |  | Power Generator Turbines | CT |  |  | 384 | >80% | NG |  |  | 8760 | 100% load
TRB_GEN2 |  | Power Generator Turbines | CT |  |  | 384 | >80% | NG |  |  | 8760 | 100% load
TRB_GEN3 |  | Power Generator Turbines | CT |  |  | 384 | >80% | NG |  |  | 8760 | 100% load
TRB_GEN4 |  | Power Generator Turbines | CT |  |  | 384 | >80% | NG |  |  | 8760 | 100% load
Aux_COMP |  | Auxiliary Air Compressor (224 kW) | ICE |  |  | 2.1 | <600hp | D |  |  | 500 | 100% load
FPUMP |  | Firewater Pump (429 kW) | ICE |  |  | 4.025 | <600hp | D |  |  | 500 | 100% load
FLARE_1D |  | Dry Flare Pilot/Purge | Flare |  |  | 7.15 | 0 | NG |  |  | 8760 | 100% load
FLARE_2D |  | Dry Flare Pilot/Purge | Flare |  |  | 7.15 | 0 | NG |  |  | 8760 | 100% load
|  | Dry Flare Pilot/Purge (Not Modeled) | Flare |  |  | 0 | 0 | NG |  |  | 0 | 100% load
FLARE_1W |  | Wet Flare Pilot/Purge | Flare |  |  | 2.25 | 0 | NG |  |  | 8760 | 100% load
FLARE_2W |  | Wet Flare Pilot/Purge | Flare |  |  | 2.25 | 0 | NG |  |  | 8760 | 100% load
|  | Wet Flare Pilot/Purge (Not Modeled) | Flare |  |  | 0 | 0 | NG |  |  | 0 | 100% load
DRY_MAX1 |  | Dry Flare Maximum Case | Flare |  |  | 59992 | 0 | NG |  |  | 500 | 100% load
DRY_MAX2 |  | Dry Flare Maximum Case | Flare |  |  | 59992 | 0 | NG |  |  | 500 | 100% load
|  | Dry Flare Maximum Case (Not Modeled) | Flare |  |  | 0 | 0 | NG |  |  | 0 | 100% load
WET_MAX1 |  | Wet Flare Maximum Case | Flare |  |  | 14020 | 0 | NG |  |  | 500 | 100% load
WET_MAX2 |  | Wet Flare Maximum Case | Flare |  |  | 14020 | 0 | NG |  |  | 500 | 100% load
|  | Wet Flare Maximum Case (Not Modeled) | Flare |  |  | 0 | 0 | NG |  |  | 0 | 100% load
LP_FLARE |  | LP Flare Pilot/Purge | Flare |  |  | 10.5 | 0 | NG |  |  | 8760 | 100% load
LP_MAX |  | LP Flare Maximum Flow | Flare |  |  | 997.5 | 0 | NG |  |  | 144 | 100% load
TH_OX |  | Thermal Oxidizer | Heater |  |  | 6.01 | 0 | NG |  |  | 8760 | 100% load
Note on K1: kmalmquist: Control Efficiency

## LNG HAPs Calc
| Emission Unit Tag No. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Total
| Emission Unit ID | TURB1 | TURB2 | TURB3 | TURB4 | TURB5 | TURB6 | TRB_GEN1 | TRB_GEN2 | TRB_GEN3 | TRB_GEN4 | Aux_COMP | FPUMP | FLARE_1D | FLARE_2D | 0 | FLARE_1W | FLARE_2W | 0 | DRY_MAX1 | DRY_MAX2 | 0 | WET_MAX1 | WET_MAX2 | 0 | LP_FLARE | LP_MAX | TH_OX
| CT Mfg / Model | Train 1a Compression Turbine Stack | Train 1b Compression Turbine Stack | Train 2a Compression Turbine Stack | Train 2b Compression Turbine Stack | Train 3a Compression Turbine Stack | Train 3b Compression Turbine Stack | Power Generator Turbines | Power Generator Turbines | Power Generator Turbines | Power Generator Turbines | Auxiliary Air Compressor (224 kW) | Firewater Pump (429 kW) | Dry Flare Pilot/Purge | Dry Flare Pilot/Purge | Dry Flare Pilot/Purge (Not Modeled) | Wet Flare Pilot/Purge | Wet Flare Pilot/Purge | Wet Flare Pilot/Purge (Not Modeled) | Dry Flare Maximum Case | Dry Flare Maximum Case | Dry Flare Maximum Case (Not Modeled) | Wet Flare Maximum Case | Wet Flare Maximum Case | Wet Flare Maximum Case (Not Modeled) | LP Flare Pilot/Purge | LP Flare Maximum Flow | Thermal Oxidizer
| Source Category | CT | CT | CT | CT | CT | CT | CT | CT | CT | CT | ICE | ICE | Flare | Flare | Flare | Flare | Flare | Flare | Flare | Flare | Flare | Flare | Flare | Flare | Flare | Flare | Heater
| ISO Power (kW) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| ISO Heat Rate (MMBtu/hr) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 10oF Heat Consumption (MMBtu/hr) | 1113 | 1113 | 1113 | 1113 | 1113 | 1113 | 384 | 384 | 384 | 384 | 2.1 | 4.025 | 7.15 | 7.15 | 0 | 2.25 | 2.25 | 0 | 59992 | 59992 | 0 | 14020 | 14020 | 0 | 10.5 | 997.5 | 6.01
| Load Basis for CT EF | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >80% | >80% | <600hp | <600hp | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Fuel | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | D | D | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG | NG
| hrs/yr | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 500 | 500 | 8760 | 8760 | 0 | 8760 | 8760 | 0 | 500 | 500 | 0 | 500 | 500 | 0 | 8760 | 144 | 8760
2 | 1,1,2,2-Tetrachloroethane | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | 1,1,2-Trichloroethane | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | 1,3-Butadiene | 0.0020962 | 0.0020962 | 0.0020962 | 0.0020962 | 0.0020962 | 0.0020962 | 0.00072323 | 0.00072323 | 0.00072323 | 0.00072323 | 2.0528e-05 | 3.9344e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.01553
5 | 1,3-Dichloropropene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | 1,4-Dichlorobenzene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | 2,2,4-Trimethylpentane | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | Acetaldehyde | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.195 | 0.067277 | 0.067277 | 0.067277 | 0.067277 | 0.00040268 | 0.00077179 | 0.0013202 | 0.0013202 | 0 | 0.00041546 | 0.00041546 | 0 | 0.63227 | 0.63227 | 0 | 0.14776 | 0.14776 | 0 | 0.0019388 | 0.0030277 | 0 | 3.0088
9 | Acrolein | 0.0312 | 0.0312 | 0.0312 | 0.0312 | 0.0312 | 0.0312 | 0.010764 | 0.010764 | 0.010764 | 0.010764 | 4.8563e-05 | 9.3078e-05 | 0.00030703 | 0.00030703 | 0 | 9.6618e-05 | 9.6618e-05 | 0 | 0.14704 | 0.14704 | 0 | 0.034363 | 0.034363 | 0 | 0.00045088 | 0.00070412 | 0 | 0.59516
10 | Antimony | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | Arsenic | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Benzene | 0.058499 | 0.058499 | 0.058499 | 0.058499 | 0.058499 | 0.058499 | 0.020183 | 0.020183 | 0.020183 | 0.020183 | 0.00048983 | 0.00093883 | 0.0048818 | 0.0048818 | 0 | 0.0015362 | 0.0015362 | 0 | 2.3379 | 2.3379 | 0 | 0.54637 | 0.54637 | 0 | 0.007169 | 0.011195 | 5.4195e-05 | 6.233
13 | Beryllium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | Biphenyl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Cadmium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Carbon Tetrachloride | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | Chlorobenzene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | Chloroform | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | Chromium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | Cobalt | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | Dibutylphthalate | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | Ethylbenzene | 0.156 | 0.156 | 0.156 | 0.156 | 0.156 | 0.156 | 0.053821 | 0.053821 | 0.053821 | 0.053821 | 0 | 0 | 0.044335 | 0.044335 | 0 | 0.013952 | 0.013952 | 0 | 21.2325 | 21.2325 | 0 | 4.962 | 4.962 | 0 | 0.065107 | 0.10167 | 0 | 53.8235
23 | Ethylene Dibromide | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | Ethylene Dichloride | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | Formaldehyde | 3.4612 | 3.4612 | 3.4612 | 3.4612 | 3.4612 | 3.4612 | 1.1942 | 1.1942 | 1.1942 | 1.1942 | 0.0006195 | 0.0011874 | 0.035892 | 0.035892 | 0 | 0.011295 | 0.011295 | 0 | 17.1889 | 17.1889 | 0 | 4.017 | 4.017 | 0 | 0.052708 | 0.082311 | 0.0019356 | 68.1888
26 | HCl | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | Lead | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2904e-05 | 1.2904e-05
28 | Manganese | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | Mercury | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
30 | Methanol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
31 | Methylene Chloride | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
32 | n-Hexane | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00089039 | 0.00089039 | 0 | 0.00028019 | 0.00028019 | 0 | 0.42641 | 0.42641 | 0 | 0.099652 | 0.099652 | 0 | 0.0013076 | 0.0020419 | 0.046454 | 1.1043
33 | Nickel | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
34 | PAHs | 0.010725 | 0.010725 | 0.010725 | 0.010725 | 0.010725 | 0.010725 | 0.0037002 | 0.0037002 | 0.0037002 | 0.0037002 | 8.82e-05 | 0.00016905 | 0.00042984 | 0.00042984 | 0 | 0.00013526 | 0.00013526 | 0 | 0.20585 | 0.20585 | 0 | 0.048108 | 0.048108 | 0 | 0.00063124 | 0.00098576 | 0 | 0.59008
35 | Phenol | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
36 | Phosphorus | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
37 | POM (Total) | 0.0063374 | 0.0063374 | 0.0063374 | 0.0063374 | 0.0063374 | 0.0063374 | 0.0021865 | 0.0021865 | 0.0021865 | 0.0021865 | 8.8338e-05 | 0.00016931 | 3.3111e-07 | 3.3111e-07 | 0 | 1.042e-07 | 1.042e-07 | 0 | 0.00015857 | 0.00015857 | 0 | 3.7058e-05 | 3.7058e-05 | 0 | 4.8625e-07 | 7.5934e-07 | 1.8027e-05 | 0.04744
38 | POM 2-Methylnaphthalene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.1861e-07 | 6.1861e-07
39 | POM 3-Methylcholanthrene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7383e-08 | 4.7383e-08
40 | POM 7,12-Dimethylbenz(a)anthracene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.1328e-07 | 4.1328e-07
41 | POM Acenaphthene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.455e-07 | 1.4289e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7383e-08 | 2.2218e-06
42 | POM Acenaphthylene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6565e-06 | 5.0916e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7383e-08 | 7.7955e-06
43 | POM Anthracene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8175e-07 | 1.8817e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3177e-08 | 2.9266e-06
44 | POM Benz(a)anthracene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.82e-07 | 1.6905e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7383e-08 | 2.6199e-06
45 | POM Benzo(a)pyrene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.87e-08 | 1.8917e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1589e-08 | 3.1946e-07
46 | POM Benzo(b)fluoranthene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2028e-08 | 9.9719e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7383e-08 | 1.9913e-07
47 | POM Benzo(g,h,i)perylene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5673e-07 | 4.9206e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1589e-08 | 7.8037e-07
48 | POM Benzo(k)fluoranthene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.1375e-08 | 1.5597e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7383e-08 | 2.8473e-07
49 | POM Chrysene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8533e-07 | 3.5521e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7383e-08 | 5.8791e-07
50 | POM Dibenz(a,h)anthracene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.0608e-07 | 5.8664e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.1589e-08 | 9.2431e-07
51 | POM Fluoranthene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.9953e-06 | 7.6576e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.6339e-08 | 1.1729e-05
52 | POM Fluorene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5435e-05 | 2.9584e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.1074e-08 | 4.509e-05
53 | POM Indeno(1,2,3-c,d)pyrene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9688e-07 | 3.7734e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7383e-08 | 6.216e-07
54 | POM Naphthalene | 0.0063374 | 0.0063374 | 0.0063374 | 0.0063374 | 0.0063374 | 0.0063374 | 0.0021865 | 0.0021865 | 0.0021865 | 0.0021865 | 4.452e-05 | 8.533e-05 | 0.00033773 | 0.00033773 | 0 | 0.00010628 | 0.00010628 | 0 | 0.16174 | 0.16174 | 0 | 0.037799 | 0.037799 | 0 | 0.00049597 | 0.00077453 | 1.5742e-05 | 0.44816
55 | POM Phenanthrene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.5435e-05 | 2.9584e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.3961e-07 | 4.5458e-05
56 | POM Pyrene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5095e-06 | 4.8099e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2899e-07 | 7.4484e-06
57 | Propional[dehyde] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
58 | Propylene Oxide | 0.14137 | 0.14137 | 0.14137 | 0.14137 | 0.14137 | 0.14137 | 0.048776 | 0.048776 | 0.048776 | 0.048776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0433
59 | Selenium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
60 | Styrene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
61 | Tetrachloroethylene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
62 | Toluene | 0.63374 | 0.63374 | 0.63374 | 0.63374 | 0.63374 | 0.63374 | 0.21865 | 0.21865 | 0.21865 | 0.21865 | 0.00021473 | 0.00041156 | 0.0017808 | 0.0017808 | 0 | 0.00056038 | 0.00056038 | 0 | 0.85283 | 0.85283 | 0 | 0.1993 | 0.1993 | 0 | 0.0026151 | 0.0040839 | 8.7745e-05 | 6.7934
63 | Trichloroethylene | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
64 | Vinyl Chloride | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
65 | Vinylidene Chloride | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
66 | Xylenes(m,p,o) | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.312 | 0.10764 | 0.10764 | 0.10764 | 0.10764 | 0.00014962 | 0.00028678 | 0.00089039 | 0.00089039 | 0 | 0.00028019 | 0.00028019 | 0 | 0.42641 | 0.42641 | 0 | 0.099652 | 0.099652 | 0 | 0.0013076 | 0.0020419 | 0 | 3.3608
67 | CDD/CDF | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| SOURCE TOTAL (tpy) | 5.0082 | 5.0082 | 5.0082 | 5.0082 | 5.0082 | 5.0082 | 1.7279 | 1.7279 | 1.7279 | 1.7279 | 0.002122 | 0.0040671 | 0.090728 | 0.090728 | 0 | 0.028551 | 0.028551 | 0 | 43.4502 | 43.4502 | 0 | 10.1542 | 10.1542 | 0 | 0.13324 | 0.20807 | 0.048562 | 144.8041
|  |  | FACILITY TOTAL | 144.8041
|  |  | CT TOTAL (All Fuels) | 36.9606
|  |  | HEATER TOTAL (All Fuels) | 0.048562
|  |  | ICE TOTAL (All fuels) | 0.0061891
|  |  | SUM CTs & ICE (All Fuels) | 36.9606
|  |  | FLARE TOTAL | 107.7888
|  |  | INCINERATOR TOTAL | 0
|  |  | BURNER TOTAL | 0
|  |  | TANK TOTAL | 0
|  |  | FUGITIVE TOTAL | 0

## LNG Emission Factor Summary
| Short-Term Maximum |  | Short-Term Maximum |  | Annual
| Compressor Turbine |  | Power Generator Turbine |  | Power Generator Turbine |  | Auxiliary Air Compressor |  | Diesel Firewater Pump |  | Flares |  | Thermal Oxidizer
Pollutant | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units | Emission Factor | Units
NOx | 9 | ppmvd @15% O2 | 9 | ppmvd @15% O2 | 9 | ppmvd @15% O2 | 0.37285 | g/hp-hr | 3.5625 | g/hp-hr | 0.068 | lb/MMBtu | 0.1 | lb/MMBtu
CO | 25 | ppmvd @15% O2 | 8 | ppmvd @15% O2 | 5 | ppmvd @15% O2 | 3.2624 | g/hp-hr | 3.25 | g/hp-hr | 0.31 | lb/MMBtu | 0.082353 | lb/MMBtu
VOC | 0.0022174 | lb/MMBtu | 0.0022174 | lb/MMBtu | 0.0022174 | lb/MMBtu | 0.1771 | g/hp-hr | 0.1875 | g/hp-hr | 0.66 | lb/MMBtu | 0.0053922 | lb/MMBtu
PM10 | 0.0069688 | lb/MMBtu | 0.0069688 | lb/MMBtu | 0.0069688 | lb/MMBtu | 0.018642 | g/hp-hr | 0.1875 | g/hp-hr | 40 | µg/L | 0.007451 | lb/MMBtu
PM2.5 | 0.0069688 | lb/MMBtu | 0.0069688 | lb/MMBtu | 0.0069688 | lb/MMBtu | 0.018642 | g/hp-hr | 0.1875 | g/hp-hr | 40 | µg/L | 0.007451 | lb/MMBtu
Fuel Sulfur Normal Operation | 16 | ppmv | 16 | ppmv | 16 | ppmv | 16 | ppmv | 15 | ppmv | 16 | ppmv | 16 | ppmv
CO2 | 53.06 | kg/MMBtu | 53.06 | kg/MMBtu | 53.06 | kg/MMBtu | 73.96 | kg/MMBtu | 73.96 | kg/MMBtu | 53.06 | kg/MMBtu | 53.06 | kg/MMBtu
CH4 | 0.001 | kg/MMBtu | 0.001 | kg/MMBtu | 0.001 | kg/MMBtu | 0.003 | kg/MMBtu | 0.003 | kg/MMBtu | 0.001 | kg/MMBtu | 0.001 | kg/MMBtu
N2O | 0.0001 | kg/MMBtu | 0.0001 | kg/MMBtu | 0.0001 | kg/MMBtu | 0.0006 | kg/MMBtu | 0.0006 | kg/MMBtu | 0.0001 | kg/MMBtu | 0.0001 | kg/MMBtu
1,1,2,2-Tetrachloroethane
1,1,2-Trichloroethane
1,3-Butadiene | 4.3e-07 | lb/MMBtu | 4.3e-07 | lb/MMBtu | 4.3e-07 | lb/MMBtu | 3.91e-05 | lb/MMBtu | 3.91e-05 | lb/MMBtu
1,3-Dichloropropene
1,4-Dichlorobenzene
2,2,4-Trimethylpentane
Acetaldehyde | 4e-05 | lb/MMBtu | 4e-05 | lb/MMBtu | 4e-05 | lb/MMBtu | 0.000767 | lb/MMBtu | 0.000767 | lb/MMBtu | 4.2157e-05 | lb/MMBtu
Acrolein | 6.4e-06 | lb/MMBtu | 6.4e-06 | lb/MMBtu | 6.4e-06 | lb/MMBtu | 9.25e-05 | lb/MMBtu | 9.25e-05 | lb/MMBtu | 9.8039e-06 | lb/MMBtu
Antimony
Arsenic
Benzene | 1.2e-05 | lb/MMBtu | 1.2e-05 | lb/MMBtu | 1.2e-05 | lb/MMBtu | 0.000933 | lb/MMBtu | 0.000933 | lb/MMBtu | 0.00015588 | lb/MMBtu | 2.0588e-06 | lb/MMBtu
Beryllium
Biphenyl
Cadmium
Carbon Tetrachloride
Chlorobenzene
Chloroform
Chromium
Cobalt
Dibutylphthalate
Ethylbenzene | 3.2e-05 | lb/MMBtu | 3.2e-05 | lb/MMBtu | 3.2e-05 | lb/MMBtu |  |  |  |  | 0.0014157 | lb/MMBtu
Ethylene Dibromide
Ethylene Dichloride
Formaldehyde | 0.00071 | lb/MMBtu | 0.00071 | lb/MMBtu | 0.00071 | lb/MMBtu | 0.00118 | lb/MMBtu | 0.00118 | lb/MMBtu | 0.0011461 | lb/MMBtu | 7.3529e-05 | lb/MMBtu
HCl
Lead | [12 empty] | 4.902e-07 | lb/MMBtu
Manganese
Mercury
Methanol
Methylene Chloride
n-Hexane | [10 empty] | 2.8431e-05 | lb/MMBtu | 0.0017647 | lb/MMBtu
Nickel
PAHs | 2.2e-06 | lb/MMBtu | 2.2e-06 | lb/MMBtu | 2.2e-06 | lb/MMBtu | 0.000168 | lb/MMBtu | 0.000168 | lb/MMBtu | 1.3725e-05 | lb/MMBtu
Phenol
Phosphorus
POM 2-Methylnaphthalene | [12 empty] | 2.35e-08 | lb/MMBtu
POM 3-Methylcholanthrene | [12 empty] | 1.8e-09 | lb/MMBtu
POM 7,12-Dimethylbenz(a)anthracene | [12 empty] | 1.57e-08 | lb/MMBtu
POM Acenaphthene | [6 empty] | 1.42e-06 | lb/MMBtu | 1.42e-06 | lb/MMBtu |  |  | 1.8e-09 | lb/MMBtu
POM Acenaphthylene | [6 empty] | 5.06e-06 | lb/MMBtu | 5.06e-06 | lb/MMBtu |  |  | 1.8e-09 | lb/MMBtu
POM Anthracene | [6 empty] | 1.87e-06 | lb/MMBtu | 1.87e-06 | lb/MMBtu |  |  | 2.4e-09 | lb/MMBtu
POM Benz(a)anthracene | [6 empty] | 1.68e-06 | lb/MMBtu | 1.68e-06 | lb/MMBtu |  |  | 1.8e-09 | lb/MMBtu
POM Benzo(a)pyrene | [6 empty] | 1.88e-07 | lb/MMBtu | 1.88e-07 | lb/MMBtu |  |  | 1.2e-09 | lb/MMBtu
POM Benzo(b)fluoranthene | [6 empty] | 9.91e-08 | lb/MMBtu | 9.91e-08 | lb/MMBtu |  |  | 1.8e-09 | lb/MMBtu
POM Benzo(g,h,i)perylene | [6 empty] | 4.89e-07 | lb/MMBtu | 4.89e-07 | lb/MMBtu |  |  | 1.2e-09 | lb/MMBtu
POM Benzo(k)fluoranthene | [6 empty] | 1.55e-07 | lb/MMBtu | 1.55e-07 | lb/MMBtu |  |  | 1.8e-09 | lb/MMBtu
POM Chrysene | [6 empty] | 3.53e-07 | lb/MMBtu | 3.53e-07 | lb/MMBtu |  |  | 1.8e-09 | lb/MMBtu
POM Dibenz(a,h)anthracene | [6 empty] | 5.83e-07 | lb/MMBtu | 5.83e-07 | lb/MMBtu |  |  | 1.2e-09 | lb/MMBtu
POM Fluoranthene | [6 empty] | 7.61e-06 | lb/MMBtu | 7.61e-06 | lb/MMBtu |  |  | 2.9e-09 | lb/MMBtu
POM Fluorene | [6 empty] | 2.94e-05 | lb/MMBtu | 2.94e-05 | lb/MMBtu |  |  | 2.7e-09 | lb/MMBtu
POM Indeno(1,2,3-c,d)pyrene | [6 empty] | 3.75e-07 | lb/MMBtu | 3.75e-07 | lb/MMBtu |  |  | 1.8e-09 | lb/MMBtu
POM Naphthalene | 1.3e-06 | lb/MMBtu | 1.3e-06 | lb/MMBtu | 1.3e-06 | lb/MMBtu | 8.48e-05 | lb/MMBtu | 8.48e-05 | lb/MMBtu | 1.0784e-05 | lb/MMBtu | 5.98e-07 | lb/MMBtu
POM Phenanthrene | [6 empty] | 2.94e-05 | lb/MMBtu | 2.94e-05 | lb/MMBtu |  |  | 1.67e-08 | lb/MMBtu
POM Pyrene | [6 empty] | 4.78e-06 | lb/MMBtu | 4.78e-06 | lb/MMBtu |  |  | 4.9e-09 | lb/MMBtu
Propional[dehyde]
Propylene Oxide | 2.9e-05 | lb/MMBtu | 2.9e-05 | lb/MMBtu | 2.9e-05 | lb/MMBtu
Selenium
Styrene
Tetrachloroethylene
Toluene | 0.00013 | lb/MMBtu | 0.00013 | lb/MMBtu | 0.00013 | lb/MMBtu | 0.000409 | lb/MMBtu | 0.000409 | lb/MMBtu | 5.6863e-05 | lb/MMBtu | 3.3333e-06 | lb/MMBtu
Trichloroethylene
Vinyl Chloride
Vinylidene Chloride
Xylenes(m,p,o) | 6.4e-05 | lb/MMBtu | 6.4e-05 | lb/MMBtu | 6.4e-05 | lb/MMBtu | 0.000285 | lb/MMBtu | 0.000285 | lb/MMBtu | 2.8431e-05 | lb/MMBtu
CDD/CDF

## LNG Annual Fuel Consumption
Gas-Fired Equipment (Fuel Gas Users) | Rated Duty (HHV) | Daily Average Fuel Flow
| MMBtu/hr | MMSCFD | LNG Fuel
Train 1a Compression Turbine | 1113 | 24.5741 | Gross (Btu/lb) | 23331.1516
Train 1b Compression Turbine | 1113 | 24.5741 | Gross (Btu/scf) | 1087
Train 2a Compression Turbine | 1113 | 24.5741 | Gross (MMBtu/gal) | 0.14425
Train 2b Compression Turbine | 1113 | 24.5741 | Gross (Btu/lb) | 20229
Train 3a Compression Turbine | 1113 | 24.5741
Train 3b Compression Turbine | 1113 | 24.5741 | Heat Release Equivalents
Power Generator Turbines | 384 | 8.4784 | 1 | CO2
Power Generator Turbines | 384 | 8.4784 | 25 | CH4
Power Generator Turbines | 384 | 8.4784 | 298 | N2O
Power Generator Turbines | 384 | 8.4784
Dry Flare Pilot/Purge | 7.15 | 0.15787 | GHG Emissions from 40 CFR 98
Dry Flare Pilot/Purge | 7.15 | 0.15787 |  | Gas | Diesel
Dry Flare Pilot/Purge (Not Modeled) | 0 | 0 | CO2 | 53.06 | 73.96 | kg/MMBtu
Wet Flare Pilot/Purge | 2.25 | 0.049678 | CH4 | 0.001 | 0.003 | kg/MMBtu
Wet Flare Pilot/Purge | 2.25 | 0.049678 | N2O | 0.0001 | 0.0006 | kg/MMBtu
Wet Flare Pilot/Purge (Not Modeled) | 0 | 0
LP Flare Pilot/Purge | 10.5 | 0.23183 | Conversion Table
Thermal Oxidizer | 6.01 | 0.1327 | 1 tonnes = | 1000 | kg
Total Fuel Gas Consumption | 8249.31 | 182.1375 | 1 yr = | 8760 | hr
Liquid-Driven Equipment (Diesel Users) | Rated Duty (HHV) | Daily Average Diesel Flow | 1 yr = | 500 | hr
| MMBtu/hr | gal/day | 1 yr = | 144 | hr
Auxiliary Air Compressor (224 kW) | 2.1 | 349.4008
Firewater Pump (429 kW) | 4.025 | 669.685
Mobile Equipment Emissions (Normal Operation) | 6.531 | 1086.6411
Non-Road/Portable Equipment Emissions (Normal Operation) | 27.324 | 4546.2042
Marine Terminal Emissions (Normal Operation) | 6120.2511 | 1018295.6817
Total Diesel Consumption | 6160.2311 | 1024947.6128
Additional GHG Emission Sources not from Fuel Gas or Diesel Consumption
Dry Flare Maximum Case
Wet Flare Maximum Case
LP Flare Maximum Flow (Maintenance)
Tank Emissions
Fugitive Emissions

## AQRV Speciation
AQRV Speciation Table
Equipment and Fuel Type | PMF Ratio | EC % Filterable |  | SOA % Condensable |  | Reference
|  | PM2.5 | PM10 | PM2.5 | PM10
Mobile Source ¦ Diesel | 0 | 9.98% | 10.85% | 90.02% | 89.15% | EPA-420-R-15-022 Speciation of Total Organic Gas and Particulate Matter Emissions from On-road Vehicles in MOVES2014 Table C-10 and Table D-1
Turbine¦Gas | 0 | 28.79% | 28.79% | 71.21% | 71.21% | AP42 Table 3.1-2a
Turbine¦Diesel | 0 | 37.39% | 37.39% | 62.61% | 62.61% | AP42 Table 3.1-2a
Generator¦Gas | 0 | 48.94% | 48.94% | 51.06% | 51.06% | AP42 Table 3.2-3
Generator¦Diesel | 0 | 86.15% | 86.56% | 13.85% | 13.44% | AP42 Table 3.4-2
Compressor¦Gas | 0 | 48.94% | 48.94% | 51.06% | 51.06% | AP42 Table 3.2-3
Compressor¦Diesel | 0 | 86.15% | 86.56% | 13.85% | 13.44% | AP42 Table 3.4-2 (Smaller than 600 hp, but no condensable info in AP42 3.3)
Heater¦Gas | 0 | 25% | 25% | 75% | 75% | AP42 Table 1.4-2
Heater¦Diesel | 0 | 38.97% | 45.38% | 61.03% | 54.62% | AP42 Table 1.3-2 and Table 1.3-7
Boiler¦Gas | 0 | 25% | 25% | 75% | 75% | AP42 Table 1.4-2
Boiler¦Diesel | 0 | 38.97% | 45.38% | 61.03% | 54.62% | AP42 Table 1.3-2 and Table 1.3-7
Pump¦Gas | 0 | 48.94% | 48.94% | 51.06% | 51.06% | AP42 Table 3.2-3
Pump¦Diesel | 0 | 86.15% | 86.56% | 13.85% | 13.44% | AP42 Table 3.4-2 (Smaller than 600 hp, but no condensable info in AP42 3.3)
Flare¦Gas | 0 | 25% | 25% | 75% | 75% | AP42 Table 1.4-2 (pilot/purge fuel gas, assumed as external combustion source)
Cooling Tower¦N/A | 0 | 0% | 0% | 100% | 100% | The particulates from cooling towers are hygroscopic particles which are likely organic - therefore assumed 100% SOA.
Tank¦N/A | 0 | 0% | 0% | 0% | 0% | No EC, SOA or PMF Emissions assumed from tank emissions

## Mobile Equip Assumptions (hidden)
Assumptions
• During commissioning of a piece of equipment, assume only operate half of the hours in 1 month
• During maintainence of a piece of equipment, assume only operate half of the hours in 1 month
• During start-up of Trains 1&2 compressors, use CGF gas
• Power Generators use CGF gas until Trains 1&2 completely started-up
• Two Power Generators in operation after sealift 1, four after sealift 2 and commisioning of T 1&2, and six after all sealift 3.
• Each essential and emergency generator is tested for 5 hr/month.
• Essential and emergency generators start with Hookup of Sealift 1.
• First Fills for tanks occurs just before use. More specifically, this means that the TEG storage tanks and common heating/cooling medium tanks will operate on Sealift 1
as well as the diesel tanks. MeOH and Amine storage tanks come on line with sealift 2; all train tanks come online as the train is put in service
• All water tanks assumed to not have vent emissions that require recording
• Diesel Air compressors and Fire Water Pump will be tested for 5 hr/month. These items are for emergency use only, which is not reflected in these sheets.
• Auxilliary heater operates at 40% of design for the first year after sealift one. After sealift one and comissioning of Trains 1 & 2 the heater will not operate.
• Garbage and Food delivery trucks will operate daily, assuming 5hrs of operation a day
• Water delivery was asssumed to be by pipeline only; No truck delivery was assumed
• Each of the following trucks were assumed to operate 10hrs/month:
Miscelaneous Parts Delivery Truck
Electrical and Controls Delivery Truck
Azimuth and Elevation Drive Delivery Truck (i.e. communications)
Hazardous Waste Truck
• Each of the following trucks were assumed to operate 20hrs/month:
Special Maintenance Personnel Truck
Vacuum Truck (after commisioning)
• During commissioning, the vacuum truck will operate 12hr/day for 7 days a week
• Delivery Truck size was based on the maximum vehicle weight limit as defined in AAC 25.013. a Kenworth T800 was assumed to have an empty weight of 25,000 lb.
• All chemical delivery trucks were defined together. The delivery truck size was assumed to be 9000 US gal (unless noted), and first fill quantities are:
[5 empty] | Sea Lift 1 (month 48) | Sea Lift 2 (month 60) | Sea Lift 3 (month 72)
| TEG: | 363 trucks SL1 (heating/cooling medium) |  |  | 121
| TEG: | 42 trucks, sea lift 2;24 trucks SL3 |  |  |  | 14 | 8
| Amine: | 312 trucks seal lift 2, 285 trucks SL3 |  |  |  | 104 | 95
| Propane: | 60 trucks sea lift 2 |  |  |  | 20
| Liquid N2: | 4 trucks sea lift 1 (6000 gal) |  |  | 2
| Diesel: | 57 trucks sea lift 1 |  |  | 19
| Chemical Injectants: |  | 6 trucks sea lift 1 |  | 2
| Hydraulic Fluid: |  | 9 trucks sea lift 1 |  | 3
| Lube oil: | 12 trucks each sea lift |  |  | 4 | 4 | 4
[5 empty] | 151 | 142 | 107
• All chemical delivery trucks were defined together. The delivery truck size was assumed to be 9000 US gal (unless noted), and delivery quantities are:
[5 empty] | Jan | Feb | Mar | April | May | June | July | Aug | Sept | Oct | Nov | Dec
| TEG: | 6 trucks every 2 months |  |  | Jan: 6; Mar: 6; May: 6; July: 6; Sept: 6; Nov: 6
| Amine: | 15 trucks a year |  |  | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 1 | 1 | 1 | 1 | 1
| Propane: | 1 trucks a year (6000 gal) | bar: Jan
| Liquid N2: | 2 trucks every 2 months (6000 gal) |  |  | Feb: 2; April: 2; June: 2; Aug: 2; Oct: 2; Dec: 2
| Diesel: | 1 truck every week |  |  | 4 | 5 | 4 | 4 | 4 | 5 | 4 | 5 | 4 | 4 | 4 | 5
| Chemical Injectants: |  | 1 trucks every other month | bar: Feb; April; June; Aug; Oct; Dec
Hydraulic Fluid:
| Lube oil: | 8 trucks every 2 months |  |  | Feb: 8; April: 8; June: 8; Aug: 8; Oct: 8; Dec: 8
[5 empty] | 12 | 18 | 11 | 17 | 11 | 18 | 11 | 17 | 11 | 16 | 11 | 17
(ABOVE quatities based on USAG-WD-PEUTL-000002 Inventory List Base Case Rev 0.xls)
Therefore, for normal operation assume 18 chemical trucks a month, at 12 hrs each (once all trains running)
| (6 after sea lift 1) |  |  | sea lift 1: | 4.3333 | 6.3333 | 3.3333 | 6 | 3.3333 | 6.3333 | 3.3333 | 6.3333 | 3.3333 | 6 | 3.3333 | 6.3333
| (12 after sea lift 2) |  |  | sea lift 2: | 8.1667 | 12.6667 | 7.1667 | 12 | 7.1667 | 12.6667 | 7.1667 | 12.1667 | 7.1667 | 11.5 | 7.1667 | 12.1667
• Flaring/venting for startup occurs 4 times a year per train, except during commissioning which was assumed to be 8 times/yr/train for the first year. Each event was assumed to take 24 hrs.
• Cooling Medium Expansion Drums and Sumps open to atmosphere were assumed to have a working volume of 50%, and to have 1 turnover a year each, to approximate actual operation.
• Truck horsepower was assumed to be 400HP as an average, if more detailed vehicle information was unavailable
• All diesel is arctic diesel
• Turbine emissions and stack parameters account for waste heat recovery and supplimental firing where applicable
• Turbine HP represents average over the year with respect to ambient temperature (derated)
AAC Vehicle weight: |  |  | http://www.legis.state.ak.us/basis/folioproxy.asp?url=http://wwwjnu01.legis.state.ak.us/cgi-bin/folioisa.dll/aac/query=[JUMP:'Title17Chap25!2C+a!2E+1']/doc/{@1}?firsthit
Description:
1998 Kenworth T800; 400 miles, empty weight 25,500 lbs, 525 hp, N14 Cummins, 18 speed, 17 aluminum east box, 20k and 40k, axles, 433 ratio, air ride, axle interlock, 240" wheel base, all aluminum wheels, all new tires, 2 steerable lift axles, new brakes, roll tarp, suspension updates, new S.S. drop visor, L.E.D. lights and S.S. trip, new bumper, paint light bar and more. Asking $67,900. Located in Eau Claire, WI. For more information, please call 715-833-0313 or 715-830-0031.
http://www.activefarming.org/node/6478

## Onsite Opper. Eqt and Vehic (hidden)
GTP
| Co-current construction and operation | Onsite Operations Equipment Projection
| Operations Equipment Description | HP | D | G | P | Sales Gas | CGF Gas | Hrs/Month | Month After Construction Start (number of equipment per month in chart)
[9 empty] | 2014 -3Q,4Q | [5 empty] | 2015 | [11 empty] | 2016 | [11 empty] | 2017 | [11 empty] | 2018 | [11 empty] | 2019 | [11 empty] | 2020 | [11 empty] | 2021 | [11 empty] | 2022
Item Number | [8 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 1-12 | 2-13 | 3-14 | 4-15 | 5-16 | 6-17 | 7-18 | 8-19 | 9-20 | 10-21 | 11-22 | 12-23 | 13-24 | 14-25 | 15-26 | 16-27 | 17-28 | 18-29 | 19-30 | 20-31 | 21-32 | 22-33 | 23-34 | 24-35 | 25-36 | 26-37 | 27-38 | 28-39 | 29-40 | 30-41 | 31-42 | 32-43 | 33-44 | 34-45 | 35-46 | 36-47 | 37-48 | 38-49 | 39-50 | 40-51 | 41-52 | 42-53 | 43-54 | 44-55 | 45-56 | 46-57 | 47-58 | 48-59 | 49-60 | 50-61 | 51-62 | 52-63 | 53-64 | 54-65 | 55-66 | 56-67 | 57-68 | 58-69 | 59-70 | 60-71 | 61-72 | 62-73 | 63-74 | 64-75 | 65-76 | 66-77 | 67-78 | 68-79 | 69-80 | 70-81 | 71-82 | 72-83 | 73-84 | 74-85 | 75-86 | 76-87 | 77-88 | 78-89 | 79-90 | 80-91 | 81-92 | 82-93 | 83-94 | 84-95 | 85-96 | 86-97 | 87-98 | 88-99 | 89-100 | 90-101 | 91-102 | 1-75 (entire construction)
| Vehicles with Onroad Engines for Emissions Estimates | [7 empty] | 2022 1-12: 0; 2022 2-13: 0; 2022 3-14: 0; 2022 4-15: 0; 2022 5-16: 0; 2022 6-17: 0; 2022 7-18: 0; 2022 8-19: 0; 2022 9-20: 0; 2022 10-21: 0; 2022 11-22: 0; 2022 12-23: 0; 2022 13-24: 0; 2022 14-25: 0; 2022 15-26: 0; 2022 16-27: 0; 2022 17-28: 0; 2022 18-29: 0; 2022 19-30: 0; 2022 20-31: 0; 2022 21-32: 0; 2022 22-33: 0; 2022 23-34: 0; 2022 24-35: 0; 2022 25-36: 0; 2022 26-37: 0; 2022 27-38: 0; 2022 28-39: 0; 2022 29-40: 0; 2022 30-41: 0; 2022 31-42: 0; 2022 32-43: 0; 2022 33-44: 0; 2022 34-45: 0; 2022 35-46: 0; 2022 36-47: 0; 2022 37-48: 0; 2022 38-49: 0; 2022 39-50: 0; 2022 40-51: 0; 2022 41-52: 0; 2022 42-53: 0; 2022 43-54: 0; 2022 44-55: 0; 2022 45-56: 0; 2022 46-57: 0; 2022 47-58: 0; 2022 48-59: 0; 2022 49-60: 0; 2022 50-61: 0; 2022 51-62: 0; 2022 52-63: 0; 2022 53-64: 0; 2022 54-65: 0; 2022 55-66: 0; 2022 56-67: 0; 2022 57-68: 0; 2022 58-69: 0; 2022 59-70: 0; 2022 60-71: 0; 2022 61-72: 0; 2022 62-73: 0; 2022 63-74: 0; 2022 64-75: 0; 2022 65-76: 0; 2022 66-77: 0; 2022 67-78: 0; 2022 68-79: 0; 2022 69-80: 0; 2022 70-81: 0; 2022 71-82: 0; 2022 72-83: 0; 2022 73-84: 0; 2022 74-85: 0; 2022 75-86: 0; 2022 76-87: 0; 2022 77-88: 0; 2022 78-89: 0; 2022 79-90: 0; 2022 80-91: 0; 2022 81-92: 0; 2022 82-93: 0; 2022 83-94: 0; 2022 84-95: 0; 2022 85-96: 0; 2022 86-97: 0; 2022 87-98: 0; 2022 88-99: 0; 2022 89-100: 0; 2022 90-101: 0; 2022 91-102: 0 | 0
21 | General Materials Delivery Truck for general construction | 400 | x |  |  |  |  | 10 | [38 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 37
22 | Delivery Truck- Food | 400 | x |  |  |  |  | 150 | [38 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 37
23 | Delivery Truck - Chemicals | 400 | x |  |  |  |  | 12 | 2017 39: 17; 2017 40: 17; 2017 41: 17; 2017 42: 17; 2018 43: 17; 2018 44: 17; 2018 45: 17; 2018 46: 17; 2018 47: 35; 2018 48: 186; 2018 49: 35; 2018 50: 35; 2018 51: 35; 2018 52: 35; 2018 53: 35; 2018 54: 35; 2019 55: 35; 2019 56: 35; 2019 57: 35; 2019 58: 35; 2019 59: 35; 2019 60: 194; 2019 61: 52; 2019 62: 52; 2019 63: 52; 2019 64: 52; 2019 65: 52; 2019 66: 52; 2020 67: 52; 2020 68: 52; 2020 69: 52; 2020 70: 52; 2020 71: 159; 2020 72: 52; 2020 73: 52; 2020 74: 52; 2020 75: 52; 2020 76: 52; 2020 77: 52; 2020 78: 52; 2021 79: 52; 2021 80: 52; 2021 81: 52; 2021 82: 52; 2021 83: 52; 2021 84: 52; 2021 85: 52; 2021 86: 52; 2021 87: 52; 2021 88: 52; 2021 89: 52; 2021 90: 52; 2022 91: 52; 2022 92: 52; 2022 93: 52; 2022 94: 52; 2022 95: 52; 2022 96: 52; 2022 97: 52; 2022 98: 52; 2022 99: 52; 2022 100: 52; 2022 101: 52; 2022 102: 52
24 | Delivery Truck - Misc. Parts | 400 | x |  |  |  |  | 10 | [38 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 37
25 | Special Maintenance Personnel Truck | 400 | x |  |  |  |  | 20 | [38 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 37
26 | Electrical and Control Systems Delivery Truck | 400 | x |  |  |  |  | 10 | [38 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 37
27 | Azimuth and Elevation Drive (Communications) Delivery Truck | 400 | x |  |  |  |  | 10 | [38 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 12 | 37
28 | Water Delivery Trucks | 400 | x |  |  |  |  | 0 | [38 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29a | Vacuum Truck (commisioning) | 300 | x |  |  |  |  | 360 | bar: 2017 39 to 2020 72
29b | Vacuum Truck | 300 | x |  |  |  |  | 20 | bar: 2020 73 to 2022 102
30 | Garbage Trucks | 400 | x |  |  |  |  | 150 | bar: 2017 39 to 2022 102
31 | Hazardous Waste Trucks | 400 | x |  |  |  |  | 10 | bar: 2017 39 to 2022 102
| Total | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 44 | 195 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 44 | 203 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 168 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 18 | [61 empty] | 222
Note:
1. abbreviation:
| HP=horsepower G=gasoline D=diesel P=propane Sales Gas CGF Gas = Plant Inlet gas | [7 empty] | 2022 4-15: max =; 2022 5-16: 12
| 2. max numbers of equipment and vehicles per month = |  |  | 203
3. It is assumed the numbers of worker passenger vehicles are the numbers of workers divided by 1.5.

## Mobile Eqt and Vehic (hidden)
GTP
Mobile Equipment and Vehicle Projection for Operations
Co-current construction and operation
Onsite Mobile Equipment and Vehicles Emission Sources
Mobile Equipment Description | HP | D | G | P | Sales Gas | CGF Gas | Hrs/Month | Month After Construction Start (number of equipment operating per month in chart)
[8 empty] | 2014 -3Q,4Q | [5 empty] | 2015 | [11 empty] | 2016 | [11 empty] | 2017 | [11 empty] | 2018 | [11 empty] | 2019 | [11 empty] | 2020 | [11 empty] | 2021 | [11 empty] | 2022
[8 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65 | 66 | 67 | 68 | 69 | 70 | 71 | 72 | 73 | 74 | 75 | 76 | 77 | 78 | 79 | 80 | 81 | 82 | 83 | 84 | 85 | 86 | 87 | 88 | 89 | 90 | 91 | 92 | 93 | 94 | 95 | 96 | 97 | 98 | 99 | 100 | 101 | 102 | 1-12 | 2-13 | 3-14 | 4-15 | 5-16 | 6-17 | 7-18 | 8-19 | 9-20 | 10-21 | 11-22 | 12-23 | 13-24 | 14-25 | 15-26 | 16-27 | 17-28 | 18-29 | 19-30 | 20-31 | 21-32 | 22-33 | 23-34 | 24-35 | 25-36 | 26-37 | 27-38 | 28-39 | 29-40 | 30-41 | 31-42 | 32-43 | 33-44 | 34-45 | 35-46 | 36-47 | 37-48 | 38-49 | 39-50 | 40-51 | 41-52 | 42-53 | 43-54 | 44-55 | 45-56 | 46-57 | 47-58 | 48-59 | 49-60 | 50-61 | 51-62 | 52-63 | 53-64 | 54-65 | 55-66 | 56-67 | 57-68 | 58-69 | 59-70 | 60-71 | 61-72 | 62-73 | 63-74 | 64-75 | 65-76 | 66-77 | 67-78 | 68-79 | 69-80 | 70-81 | 71-82 | 72-83 | 73-84 | 74-85 | 75-86 | 76-87 | 77-88 | 78-89 | 79-90 | 80-91 | 81-92 | 82-93 | 83-94 | 84-95 | 85-96 | 86-97 | 87-98 | 88-99 | 89-100 | 90-101 | 91-102 | 1-75 (entire construction)
Air Compressor -900CFM (Sullair; caterpillar C-9 ATAAC engine) | 300 | X |  |  |  |  | 120 | [36 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 6 | 8 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 24 | 78
Dump Truck - Mack B70 (10 tires, 12 gph, 6 cylinders) |  | X |  |  |  |  | 300 | 2017 41: 4; 2017 42: 4; 2018 43: 4; 2018 44: 4; 2018 45: 4; 2018 53: 4; 2018 54: 4; 2019 55: 4; 2019 56: 4; 2019 57: 4; 2019 65: 4; 2019 66: 4; 2020 67: 4; 2020 68: 4; 2020 69: 4; 2020 77: 4; 2020 78: 4; 2021 79: 4; 2021 80: 4; 2021 81: 4; 2021 89: 4; 2021 90: 4; 2022 91: 4; 2022 92: 4; 2022 93: 4; 2022 101: 4; 2022 102: 4
Motor Grader - Cat 16G (6 tires, 7gph, 6-cylinder engine) | 250 | X |  |  |  |  | 300 | bar: 2017 37 to 2022 102
Backhoe (CAT 966F) | 220 | X |  |  |  |  | 60 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Crane (small) - 50/60 ton , Grove, RT700E (Cummins QSB engine) | 240 | X |  |  |  |  | 120 | [36 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 6 | 8 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 24 | 78
Crane (large) - 200 ton, Manitowoc 888 (Cummins M11 engine) | 330 | X |  |  |  |  | 60 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Crane (large) - 90 ton, Grove 890E (Cummins QSB engine) | 275 | X |  |  |  |  | 60 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Dozer - Cat D9, 475 HP | 475 | X |  |  |  |  | 300 | [40 empty] | 1 | 1 | 1 | 1 | 1 | [7 empty] | 1 | 1 | 1 | 1 | 1 | [7 empty] | 1 | 1 | 1 | 1 | 1 | [7 empty] | 1 | 1 | 1 | 1 | 1 | [7 empty] | 1 | 1 | 1 | 1 | 1 | [7 empty] | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 4 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 6 | 6 | 5 | 15
Boom Truck (National Crane 800D) | 350 | X |  |  |  |  | 60 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Loader - Cat 988H, 501HP | 501 | X |  |  |  |  | 300 | [39 empty] | 4 | 4 | 4 | 4 | 4 | 4 | [6 empty] | 4 | 4 | 4 | 4 | 4 | 4 | [6 empty] | 4 | 4 | 4 | 4 | 4 | 4 | [6 empty] | 4 | 4 | 4 | 4 | 4 | 4 | [6 empty] | 4 | 4 | 4 | 4 | 4 | 4 | [6 empty] | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 12 | 16 | 20 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 24 | 24 | 24 | 24 | 24 | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 24 | 24 | 24 | 24 | 24 | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 24 | 24 | 24 | 24 | 24 | 28 | 28 | 28 | 28 | 28 | 28 | 24 | 24 | 24 | 24 | 24 | 24 | 28 | 28 | 28 | 24 | 72
Groundthaw Heater (E3000) | 151 | X |  |  |  |  | 360 | 2017 40: 4; 2017 41: 4; 2017 42: 4; 2018 43: 4; 2018 44: 4; 2018 45: 4; 2018 52: 4; 2018 53: 4; 2018 54: 4; 2019 55: 4; 2019 56: 4; 2019 57: 4; 2019 64: 4; 2019 65: 4; 2019 66: 4; 2020 67: 4; 2020 68: 4; 2020 69: 4; 2020 76: 4; 2020 77: 4; 2020 78: 4; 2021 79: 4; 2021 80: 4; 2021 81: 4; 2021 88: 4; 2021 89: 4; 2021 90: 4; 2022 91: 4; 2022 92: 4; 2022 93: 4; 2022 100: 4; 2022 101: 4; 2022 102: 4; 2022 29-40: 4; 2022 88-99: 28; 2022 89-100: 28; 2022 90-101: 28
Tioga Heaters (600,000 Btu/hr heater) | 236 | X |  |  |  |  | 360 | [39 empty] | 26 | 26 | 26 | 26 | 26 | 26 | [6 empty] | 26 | 26 | 26 | 26 | 26 | 26 | [6 empty] | 26 | 26 | 26 | 26 | 26 | 26 | [6 empty] | 26 | 26 | 26 | 26 | 26 | 26 | [6 empty] | 26 | 26 | 26 | 26 | 26 | 26 | [6 empty] | 26 | 26 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 78 | 104 | 130 | 156 | 156 | 156 | 156 | 156 | 156 | 156 | 182 | 182 | 182 | 182 | 182 | 182 | 156 | 156 | 156 | 156 | 156 | 156 | 182 | 182 | 182 | 182 | 182 | 182 | 156 | 156 | 156 | 156 | 156 | 156 | 182 | 182 | 182 | 182 | 182 | 182 | 156 | 156 | 156 | 156 | 156 | 156 | 182 | 182 | 182 | 182 | 182 | 182 | 156 | 156 | 156 | 156 | 156 | 156 | 182 | 182 | 182 | 156 | 468
Light Plants (Genie TML-4000) | 15 | X |  |  |  |  | 120 | [36 empty] | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 50 | 75 | 100 | 150 | 175 | 200 | 225 | 250 | 275 | 300 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 325 | 300 | 975
Forklift - 15 Ton (Cat P30000) | 148 | X |  |  |  |  | 120 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Forklift - Cat (2P5000) | 61 | X |  |  |  |  | 120 | [36 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 9 | 12 | 18 | 21 | 24 | 27 | 30 | 33 | 36 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 39 | 36 | 117
Snowblower/ Grader - 16' (Kodiak Northwest) | 500 | X |  |  |  |  | 300 | 2017 40: 4; 2017 41: 4; 2017 42: 4; 2018 43: 4; 2018 44: 4; 2018 45: 4; 2018 52: 4; 2018 53: 4; 2018 54: 4; 2019 55: 4; 2019 56: 4; 2019 57: 4; 2019 64: 4; 2019 65: 4; 2019 66: 4; 2020 67: 4; 2020 68: 4; 2020 69: 4; 2020 76: 4; 2020 77: 4; 2020 78: 4; 2021 79: 4; 2021 80: 4; 2021 81: 4; 2021 88: 4; 2021 89: 4; 2021 90: 4; 2022 91: 4; 2022 92: 4; 2022 93: 4; 2022 100: 4; 2022 101: 4; 2022 102: 4
Generator - 100 kW | 135 | X |  |  |  |  | 60 | 2017 37: 4; 2017 38: 4; 2017 39: 4; 2017 40: 4; 2017 41: 4; 2017 42: 4; 2018 43: 4; 2018 44: 4; 2018 45: 4; 2018 46: 4; 2018 47: 4; 2018 48: 4; 2018 49: 4; 2018 50: 4; 2018 51: 4; 2018 52: 4; 2018 53: 4; 2018 54: 4; 2019 55: 4; 2019 56: 4; 2019 57: 4; 2019 58: 4; 2019 59: 4; 2019 60: 4; 2019 61: 4; 2019 62: 4; 2019 63: 4; 2019 64: 4; 2019 65: 4; 2019 66: 4; 2020 67: 4; 2020 68: 4; 2020 69: 4; 2020 70: 4; 2020 71: 4; 2020 72: 4; 2020 73: 4; 2020 74: 4; 2020 75: 4; 2020 76: 4; 2020 77: 4; 2020 78: 4; 2021 79: 4; 2021 80: 4; 2021 81: 4; 2021 82: 4; 2021 83: 4; 2021 84: 4; 2021 85: 4; 2021 86: 4; 2021 87: 4; 2021 88: 4; 2021 89: 4; 2021 90: 4; 2022 91: 4; 2022 92: 4; 2022 93: 4; 2022 94: 4; 2022 95: 4; 2022 96: 4; 2022 97: 4; 2022 98: 4; 2022 99: 4; 2022 100: 4; 2022 101: 4; 2022 102: 4
Generator - 50 kW | 67 | X |  |  |  |  | 60 | 2017 37: 20; 2017 38: 20; 2017 39: 20; 2017 40: 20; 2017 41: 20; 2017 42: 20; 2018 43: 20; 2018 44: 20; 2018 45: 20; 2018 46: 20; 2018 47: 20; 2018 48: 20; 2018 49: 20; 2018 50: 20; 2018 51: 20; 2018 52: 20; 2018 53: 20; 2018 54: 20; 2019 55: 20; 2019 56: 20; 2019 57: 20; 2019 58: 20; 2019 59: 20; 2019 60: 20; 2019 61: 20; 2019 62: 20; 2019 63: 20; 2019 64: 20; 2019 65: 20; 2019 66: 20; 2020 67: 20; 2020 68: 20; 2020 69: 20; 2020 70: 20; 2020 71: 20; 2020 72: 20; 2020 73: 20; 2020 74: 20; 2020 75: 20; 2020 76: 20; 2020 77: 20; 2020 78: 20; 2021 79: 20; 2021 80: 20; 2021 81: 20; 2021 82: 20; 2021 83: 20; 2021 84: 20; 2021 85: 20; 2021 86: 20; 2021 87: 20; 2021 88: 20; 2021 89: 20; 2021 90: 20; 2022 91: 20; 2022 92: 20; 2022 93: 20; 2022 94: 20; 2022 95: 20; 2022 96: 20; 2022 97: 20; 2022 98: 20; 2022 99: 20; 2022 100: 20; 2022 101: 20; 2022 102: 20
Manlifts - 80' Gemie (Z80/60) | 78 | X |  |  |  |  | 60 | 2017 37: 2; 2017 38: 2; 2017 39: 2; 2017 40: 2; 2017 41: 2; 2017 42: 2; 2018 43: 2; 2018 44: 2; 2018 45: 2; 2018 46: 2; 2018 47: 2; 2018 48: 2; 2018 49: 2; 2018 50: 2; 2018 51: 2; 2018 52: 2; 2018 53: 2; 2018 54: 2; 2019 55: 2; 2019 56: 2; 2019 57: 2; 2019 58: 2; 2019 59: 2; 2019 60: 2; 2019 61: 2; 2019 62: 2; 2019 63: 2; 2019 64: 2; 2019 65: 2; 2019 66: 2; 2020 67: 2; 2020 68: 2; 2020 69: 2; 2020 70: 2; 2020 71: 2; 2020 72: 2; 2020 73: 2; 2020 74: 2; 2020 75: 2; 2020 76: 2; 2020 77: 2; 2020 78: 2; 2021 79: 2; 2021 80: 2; 2021 81: 2; 2021 82: 2; 2021 83: 2; 2021 84: 2; 2021 85: 2; 2021 86: 2; 2021 87: 2; 2021 88: 2; 2021 89: 2; 2021 90: 2; 2022 91: 2; 2022 92: 2; 2022 93: 2; 2022 94: 2; 2022 95: 2; 2022 96: 2; 2022 97: 2; 2022 98: 2; 2022 99: 2; 2022 100: 2; 2022 101: 2; 2022 102: 2
Manlift - 45' Genie (Z45, Perkins 404D-22 4 cylinder engine) | 51 | X |  |  |  |  | 60 | 2017 37: 4; 2017 38: 4; 2017 39: 4; 2017 40: 4; 2017 41: 4; 2017 42: 4; 2018 43: 4; 2018 44: 4; 2018 45: 4; 2018 46: 4; 2018 47: 4; 2018 48: 4; 2018 49: 4; 2018 50: 4; 2018 51: 4; 2018 52: 4; 2018 53: 4; 2018 54: 4; 2019 55: 4; 2019 56: 4; 2019 57: 4; 2019 58: 4; 2019 59: 4; 2019 60: 4; 2019 61: 4; 2019 62: 4; 2019 63: 4; 2019 64: 4; 2019 65: 4; 2019 66: 4; 2020 67: 4; 2020 68: 4; 2020 69: 4; 2020 70: 4; 2020 71: 4; 2020 72: 4; 2020 73: 4; 2020 74: 4; 2020 75: 4; 2020 76: 4; 2020 77: 4; 2020 78: 4; 2021 79: 4; 2021 80: 4; 2021 81: 4; 2021 82: 4; 2021 83: 4; 2021 84: 4; 2021 85: 4; 2021 86: 4; 2021 87: 4; 2021 88: 4; 2021 89: 4; 2021 90: 4; 2022 91: 4; 2022 92: 4; 2022 93: 4; 2022 94: 4; 2022 95: 4; 2022 96: 4; 2022 97: 4; 2022 98: 4; 2022 99: 4; 2022 100: 4; 2022 101: 4; 2022 102: 4
Zoom Boom - Telehandler (used on warehouse), GTH-1056 | 125 | X |  |  |  |  | 300 | 2017 37: 2; 2017 38: 2; 2017 39: 2; 2017 40: 2; 2017 41: 2; 2017 42: 2; 2018 43: 2; 2018 44: 2; 2018 45: 2; 2018 46: 2; 2018 47: 2; 2018 48: 2; 2018 49: 2; 2018 50: 2; 2018 51: 2; 2018 52: 2; 2018 53: 2; 2018 54: 2; 2019 55: 2; 2019 56: 2; 2019 57: 2; 2019 58: 2; 2019 59: 2; 2019 60: 2; 2019 61: 2; 2019 62: 2; 2019 63: 2; 2019 64: 2; 2019 65: 2; 2019 66: 2; 2020 67: 2; 2020 68: 2; 2020 69: 2; 2020 70: 2; 2020 71: 2; 2020 72: 2; 2020 73: 2; 2020 74: 2; 2020 75: 2; 2020 76: 2; 2020 77: 2; 2020 78: 2; 2021 79: 2; 2021 80: 2; 2021 81: 2; 2021 82: 2; 2021 83: 2; 2021 84: 2; 2021 85: 2; 2021 86: 2; 2021 87: 2; 2021 88: 2; 2021 89: 2; 2021 90: 2; 2022 91: 2; 2022 92: 2; 2022 93: 2; 2022 94: 2; 2022 95: 2; 2022 96: 2; 2022 97: 2; 2022 98: 2; 2022 99: 2; 2022 100: 2; 2022 101: 2; 2022 102: 2
Tractor Trailer |  | X |  |  |  |  | 120 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Flatbed Truck (2 ton) (approx. F-450) | 385 | X |  |  |  |  | 180 | 2017 37: 1; 2017 38: 1; 2017 39: 1; 2017 40: 1; 2017 41: 1; 2017 42: 1; 2018 43: 1; 2018 44: 1; 2018 45: 1; 2018 46: 1; 2018 47: 1; 2018 48: 2; 2018 49: 2; 2018 50: 2; 2018 51: 2; 2018 52: 2; 2018 53: 2; 2018 54: 2; 2019 55: 2; 2019 56: 2; 2019 57: 2; 2019 58: 2; 2019 59: 2; 2019 60: 2; 2019 61: 2; 2019 62: 2; 2019 63: 2; 2019 64: 2; 2019 65: 2; 2019 66: 2; 2020 67: 2; 2020 68: 2; 2020 69: 2; 2020 70: 2; 2020 71: 2; 2020 72: 2; 2020 73: 2; 2020 74: 2; 2020 75: 2; 2020 76: 2; 2020 77: 2; 2020 78: 2; 2021 79: 2; 2021 80: 2; 2021 81: 2; 2021 82: 2; 2021 83: 2; 2021 84: 2; 2021 85: 2; 2021 86: 2; 2021 87: 2; 2021 88: 2; 2021 89: 2; 2021 90: 2; 2022 91: 2; 2022 92: 2; 2022 93: 2; 2022 94: 2; 2022 95: 2; 2022 96: 2; 2022 97: 2; 2022 98: 2; 2022 99: 2; 2022 100: 2; 2022 101: 2; 2022 102: 2
Fuel Truck (Kenworth T800) | 400 | X |  |  |  |  | 360 | 2017 37: 1; 2017 38: 1; 2017 39: 1; 2017 40: 1; 2017 41: 1; 2017 42: 1; 2018 43: 1; 2018 44: 1; 2018 45: 1; 2018 46: 1; 2018 47: 1; 2018 48: 1; 2018 49: 1; 2018 50: 2; 2018 51: 2; 2018 52: 2; 2018 53: 2; 2018 54: 2; 2019 55: 2; 2019 56: 2; 2019 57: 2; 2019 58: 2; 2019 59: 2; 2019 60: 2; 2019 61: 2; 2019 62: 2; 2019 63: 2; 2019 64: 2; 2019 65: 2; 2019 66: 2; 2020 67: 2; 2020 68: 2; 2020 69: 2; 2020 70: 2; 2020 71: 2; 2020 72: 2; 2020 73: 2; 2020 74: 2; 2020 75: 2; 2020 76: 2; 2020 77: 2; 2020 78: 2; 2021 79: 2; 2021 80: 2; 2021 81: 2; 2021 82: 2; 2021 83: 2; 2021 84: 2; 2021 85: 2; 2021 86: 2; 2021 87: 2; 2021 88: 2; 2021 89: 2; 2021 90: 2; 2022 91: 2; 2022 92: 2; 2022 93: 2; 2022 94: 2; 2022 95: 2; 2022 96: 2; 2022 97: 2; 2022 98: 2; 2022 99: 2; 2022 100: 2; 2022 101: 2; 2022 102: 2
Bobcat (2500 lb capacity, 75 hp, Kubota S250 ) | 75 | X |  |  |  |  | 360 | 2017 40: 4; 2017 41: 4; 2017 42: 4; 2018 43: 4; 2018 44: 4; 2018 45: 4; 2018 52: 4; 2018 53: 4; 2018 54: 4; 2019 55: 4; 2019 56: 4; 2019 57: 4; 2019 64: 4; 2019 65: 4; 2019 66: 4; 2020 67: 4; 2020 68: 4; 2020 69: 4; 2020 76: 4; 2020 77: 4; 2020 78: 4; 2021 79: 4; 2021 80: 4; 2021 81: 4; 2021 88: 4; 2021 89: 4; 2021 90: 4; 2022 91: 4; 2022 92: 4; 2022 93: 4; 2022 100: 4; 2022 101: 4; 2022 102: 4
Welding Machines (in shop) (Lincoln Electric) | 36 | X |  |  |  |  | 180 | [36 empty] | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 8 | 12 | 16 | 24 | 28 | 32 | 36 | 40 | 44 | 48 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 48 | 156
Water Truck - dust control (West Mark DST-S4000) | 350 | X |  |  |  |  | 300 | 2017 37: 2; 2017 38: 2; 2017 39: 2; 2018 46: 2; 2018 47: 2; 2018 48: 2; 2018 49: 2; 2018 50: 2; 2018 51: 2; 2019 58: 2; 2019 59: 2; 2019 60: 2; 2019 61: 2; 2019 62: 2; 2019 63: 2; 2020 70: 2; 2020 71: 2; 2020 72: 2; 2020 73: 2; 2020 74: 2; 2020 75: 2; 2021 82: 2; 2021 83: 2; 2021 84: 2; 2021 85: 2; 2021 86: 2; 2021 87: 2; 2022 94: 2; 2022 95: 2; 2022 96: 2; 2022 97: 2; 2022 98: 2; 2022 99: 2
Grey and Black Water Truck (Kenworth T800) | 400 | X |  |  |  |  | 180 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Solid Waste Truck - Refuse (Kenworth T800) | 400 | X |  |  |  |  | 300 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 24 | 66
Vehicles with Onroad Engines for Emissions Estimates | [7 empty] | 2017 42: Vehicles with Onroad Engines for Emissions Estimates; 2022 91: Vehicles with Onroad Engines for Emissions Estimates; 2022 38-49: 0; 2022 39-50: 0; 2022 40-51: 0; 2022 41-52: 0; 2022 42-53: 0; 2022 43-54: 0; 2022 44-55: 0; 2022 45-56: 0; 2022 46-57: 0; 2022 47-58: 0; 2022 48-59: 0; 2022 49-60: 0; 2022 50-61: 0; 2022 51-62: 0; 2022 52-63: 0; 2022 53-64: 0; 2022 54-65: 0; 2022 55-66: 0; 2022 56-67: 0; 2022 57-68: 0; 2022 58-69: 0; 2022 59-70: 0; 2022 60-71: 0; 2022 61-72: 0; 2022 62-73: 0; 2022 63-74: 0; 2022 64-75: 0; 2022 65-76: 0; 2022 66-77: 0; 2022 67-78: 0; 2022 68-79: 0; 2022 69-80: 0; 2022 70-81: 0; 2022 71-82: 0; 2022 72-83: 0; 2022 73-84: 0; 2022 74-85: 0; 2022 75-86: 0; 2022 76-87: 0; 2022 77-88: 0; 2022 78-89: 0; 2022 79-90: 0; 2022 80-91: 0; 2022 81-92: 0; 2022 82-93: 0; 2022 83-94: 0; 2022 84-95: 0; 2022 85-96: 0; 2022 86-97: 0; 2022 87-98: 0; 2022 88-99: 0; 2022 89-100: 0; 2022 90-101: 0; 2022 91-102: 0 | 0
Passenger Van, 16 person (Ford E-350 series, or GM chevy 3500) | 320 | X |  |  |  |  | 180 | [36 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 6 | 8 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 52 | 48 | 120
Passenger Bus, 20 person (Blue Bird; 6.8 L engine) | 360 | X |  |  |  |  | 120 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Staff & Security Truck (3/4 ton crew cab) | 300 | X |  |  |  |  | 360 | [36 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 6 | 8 | 12 | 14 | 16 | 18 | 20 | 22 | 24 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 26 | 24 | 78
Pickup Truck - Standard Bed (V8 engine) | 360 | X |  |  |  |  | 360 | [36 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 10 | 15 | 20 | 30 | 35 | 40 | 45 | 50 | 55 | 60 | 70 | 75 | 80 | 85 | 90 | 95 | 100 | 105 | 110 | 115 | 120 | 125 | 135 | 140 | 145 | 150 | 155 | 160 | 165 | 170 | 175 | 180 | 185 | 190 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 195 | 180 | 405
Pickup Truck - Service Bed (Silverado HD2500) | 397 | X |  |  |  |  | 360 | 2017 37: 5; 2017 38: 5; 2017 39: 5; 2017 40: 5; 2017 41: 5; 2017 42: 5; 2018 43: 5; 2018 44: 5; 2018 45: 5; 2018 46: 5; 2018 47: 5; 2018 48: 5; 2018 49: 10; 2018 50: 10; 2018 51: 10; 2018 52: 10; 2018 53: 10; 2018 54: 10; 2019 55: 10; 2019 56: 10; 2019 57: 10; 2019 58: 10; 2019 59: 10; 2019 60: 10; 2019 61: 15; 2019 62: 15; 2019 63: 15; 2019 64: 15; 2019 65: 15; 2019 66: 15; 2020 67: 15; 2020 68: 15; 2020 69: 15; 2020 70: 15; 2020 71: 15; 2020 72: 15; 2020 73: 15; 2020 74: 15; 2020 75: 15; 2020 76: 15; 2020 77: 15; 2020 78: 15; 2021 79: 15; 2021 80: 15; 2021 81: 15; 2021 82: 15; 2021 83: 15; 2021 84: 15; 2021 85: 15; 2021 86: 15; 2021 87: 15; 2021 88: 15; 2021 89: 15; 2021 90: 15; 2022 91: 15; 2022 92: 15; 2022 93: 15; 2022 94: 15; 2022 95: 15; 2022 96: 15; 2022 97: 15; 2022 98: 15; 2022 99: 15; 2022 100: 15; 2022 101: 15; 2022 102: 15; 2022 26-37: 5; 2022 27-38: 10; 2022 28-39: 15; 2022 29-40: 20; 2022 30-41: 30; 2022 31-42: 35; 2022 32-43: 40; 2022 33-44: 45; 2022 34-45: 50; 2022 35-46: 55; 2022 36-47: 60; 2022 37-48: 70 | 405
Ambulence (GM ambulence) | 260 | X |  |  |  |  | 12 | [36 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 | 4 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 12 | 39
Total | [7 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 22 | 22 | 22 | 27 | 27 | 27 | 27 | 27 | 22 | 22 | 22 | 32 | 32 | 32 | 32 | 37 | 37 | 37 | 37 | 37 | 32 | 32 | 32 | 42 | 42 | 42 | 42 | 47 | 47 | 47 | 47 | 47 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 47 | 47 | 47 | 47 | 47 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 47 | 47 | 47 | 47 | 47 | 42 | 42 | 42 | 42 | 42 | 42 | 42 | 47 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 42 | 63 | 84 | 128 | 150 | 172 | 194 | 215 | 236 | 257 | 288 | 223 | 228 | 233 | 239 | 244 | 249 | 254 | 259 | 263 | 268 | 273 | 283 | 288 | 293 | 298 | 304 | 309 | 314 | 319 | 324 | 328 | 333 | 338 | 343 | 343 | 343 | 343 | 344 | 344 | 344 | 344 | 344 | 343 | 343 | 343 | 343 | 343 | 343 | 343 | 344 | 344 | 344 | 344 | 344 | 343 | 343 | 343 | 343 | 343 | 343 | 343 | 344 | 344 | 317 | 1254
Note:
1. abbreviation: | [7 empty] | 2022 4-15: max =; 2022 5-16: #REF!
HP=horsepower G=gasoline D=diesel P=propane Sales Gas CGF Gas = Plant Inlet gas
2. max numbers of equipment and vehicles per month = |  |  | 47
3. It is assumed the numbers of worker passenger vehicles are the numbers of workers divided by 1.5.

## Mobile Trip Assumptions (hidden)
Vehicle Classification | Vehicle Descriptions | Total Hours per Year | Total Assumed Miles Driven
Single Unit Short-Haul Truck | General Materials Delivery Truck | 120 | 1200
| Delivery Truck- Food | 1800 | 18000
| Delivery Truck - Chemicals | 7488 | 74880
| Delivery Truck - Misc. Parts | 120 | 1200
| Electrical and Control Systems Delivery Truck | 120 | 1200
| Azimuth and Elevation Drive (Communications) Delivery Truck | 120 | 1200
| Water Delivery Trucks | 0 | 0
| Flatbed Truck (2 ton) (approx. F-450) | 4320 | 43200
| Tractor Trailer | 1440 | 14400
| Garbage Trucks | 1800 | 18000
| Hazardous Waste Trucks | 120 | 1200
| Dump Truck - Mack B70 (10 tires, 12 gph, 6 cylinders) | 6000 | 60000
| Solid Waste Truck - Refuse (Kenworth T800) | 7200 | 72000
Light Commercial Truck | Vacuum Truck | 240 | 2400
| Ambulence (GM ambulence) | 144 | 1440
| Fuel Truck (Kenworth T800) | 8640 | 86400
| Water Truck - dust control (West Mark DST-S4000) | 3600 | 36000
| Grey and Black Water Truck (Kenworth T800) | 2160 | 21600
| Snowblower/ Grader - 16' (Kodiak Northwest) | 4320 | 43200
Intercity Bus | Passenger Van, 16 person (Ford E-350 series, or GM chevy 3500) | 8640 | 86400
| Passenger Bus, 20 person (Blue Bird; 6.8 L engine) | 1440 | 14400
Passenger Truck | Special Maintenance Personnel Truck | 240 | 2400
| Staff & Security Truck (3/4 ton crew cab) | 8640 | 86400
| Pickup Truck - Standard Bed (V8 engine) | 64800 | 648000
| Pickup Truck - Service Bed (Silverado HD2500) | 64800 | 648000
|  | Total Miles | 1983120
|  | Total Gal Diesel/yr | 396624
|  | MMBtu/hr | 6.531
Notes:
Based only on 1 year of normal operation, post-construction (year 2021)
Idling assumed to be included in total operating hours
Vehicle Classification assumed based on DOT-HPMF Vehicle Classes
Fuel Consumption based on 5 miles per gallon for all vehicles
|  | Time-Weighted Average Speed= | 10 | mph
|  | Fuel Consumption Assumption= | 5 | miles/gal
|  | Gross Diesel Heat of Combustion= | 0.14425 | MMBtu/gal

## Mobile Emissions
Mobile Emissions ton/year
Moves Vehicle Class | Total Miles Per Year | MOVES | [10 empty] | Ton/year
EFs (g/mi) 1
|  | VOC | NOx | CO | SO2 | PM10 | PM2.5 | CO2 | CH4 | N2O | CO2e4 | HAPs2 | VOC | NOx | CO | SO2 | PM10 | PM2.5 | CO2 | CH4 | N2O | CO2e4 | HAPs2
Single Unit Short-Haul Truck | 306480 | 0.3842 | 3.2571 | 1.2963 | 0.013674 | 0.21706 | 0.18849 | 1624.18 | 0.10181 | 0.0041394 | 1627.9589 | 0.070461 | 0.1298 | 1.1004 | 0.43793 | 0.0046196 | 0.07333 | 0.06368 | 548.7099 | 0.034396 | 0.0013984 | 549.9866 | 0.023805
Light Commercial Truck | 191040 | 0.078998 | 0.79598 | 1.642 | 0.0061158 | 0.040517 | 0.041121 | 729.512 | 0.041815 | 0.0034016 | 731.571 | 0.020137 | 0.016636 | 0.16762 | 0.34579 | 0.0012879 | 0.0085323 | 0.0086596 | 153.6255 | 0.0088056 | 0.00071633 | 154.0591 | 0.0042407
Intercity Bus | 100800 | 0.59448 | 5.7314 | 1.8417 | 0.019521 | 0.43991 | 0.26924 | 2310.04 | 0.097527 | 0.0033102 | 2313.4646 | 0.076487 | 0.066055 | 0.63684 | 0.20463 | 0.0021691 | 0.04888 | 0.029916 | 256.6768 | 0.010837 | 0.00036781 | 257.0573 | 0.0084987
Passenger Truck | 1384800 | 0.078973 | 0.88712 | 1.4871 | 0.0065899 | 0.040966 | 0.043718 | 786.544 | 0.048027 | 0.0041167 | 788.9714 | 0.021826 | 0.12055 | 1.3542 | 2.27 | 0.010059 | 0.062534 | 0.066736 | 1200.6505 | 0.073312 | 0.0062841 | 1204.356 | 0.033316
[12 empty] | TOTAL PER POLLUTANT (tpy) | 0.33304 | 3.259 | 3.2583 | 0.018136 | 0.19328 | 0.16899 | 2159.6627 | 0.12735 | 0.0087667 | 2165.459 | 0.06986
Note 1: Emissions estimates are based on EPA's MOVES2014 motor vehicle emissions estimation program. Year 2027 is used as the base year for North Slope Borough, based on latest county-specific MOVES2014 input data available from Alaska DEC.
Note 2: HAPs are aggregated for benzene, 1,3-butadiene, formaldehyde, acetaldehyde, acrolein, toluene, and xylene
Note 3: tons/year emissions = (Average distance traveled (mi/year)) * Emission factor (g/mi) / (453.59 g/lb) * (1 / 2000)
Note 4: Greenhouse gasses (GHG) are converted to carbon dioxide equivalents (CO2e) using 100-year Global Warming Potentials values from IPCC's Fourth Assessment Report (AR4) Chapter 2, Table 2.14 of Climate Change 2007: The Physical Science Basis. Contribution of Working Group I to the Fourth Assessment Report of the IPCC
CO2 = 1, CH4 = 25, N2O = 298

## Non-Road Emissions
Non-Road/Portable Diesel Emissions - tpy
[7 empty] | Emission Factors (g/hp-hr) 2 | [8 empty] | Deterioration Factors 2 |  |  |  | Adjusted Emission Factors (g/hp-hr) 2 |  |  |  |  | Emissions (ton/year)
Engine Description | Equipment category based on NONROAD classification | SCC 1 | Fuel Type | Equipment Horsepower | Operating hrs/year | BSFC 2 | NOx | CO | PM | THC | Age Factor 3 | NOx | CO | PM | THC | NOx | CO | PM | THC | NOx | CO | PM5 | THC | Load Factor 2 | NOx | CO | PM | VOC6
[12 empty] | "A" 3 | "A" 3 | "A" 3 | "A" 3
Air Compressor -900CFM (Sullair; caterpillar C-9 ATAAC engine) | Light Commercial Air Compressor | 2270006015 | Diesel | 300 | 2880 | 0.367 | 0.276 | 0.084 | 0.0092 | 0.1314 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.27821 | 0.096684 | 0.013552 | 0.13495 | 0.43 | 0.34655 | 0.12044 | 0.016881 | 0.17701
Motor Grader - Cat 16G (6 tires, 7gph, 6-cylinder engine) | Graders | 2270002048 | Diesel | 250 | 3600 | 0.371 | 0.28 | 0.11 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.12661 | 0.013552 | 0.13351 | 0.59 | 0.402 | 0.18033 | 0.019302 | 0.20024
Backhoe (CAT 966F) | Tractors/Loaders/Backhoes | 2270002066 | Diesel | 220 | 720 | 0.433 | 0.28 | 0.19 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.21869 | 0.013552 | 0.13351 | 0.21 | 0.12591 | 0.097562 | 0.0060457 | 0.062718
Crane (small) - 50/60 ton , Grove, RT700E (Cummins QSB engine) | Crane | 2270002045 | Diesel | 240 | 2880 | 0.367 | 0.28 | 0.07 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.08057 | 0.013552 | 0.13351 | 0.43 | 0.28126 | 0.08029 | 0.013505 | 0.1401
Crane (large) - 200 ton, Manitowoc 888 (Cummins M11 engine) | Crane | 2270002045 | Diesel | 330 | 720 | 0.367 | 0.28 | 0.08 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.09208 | 0.013552 | 0.13351 | 0.43 | 0.38673 | 0.12617 | 0.018569 | 0.19264
Crane (large) - 90 ton, Grove 890E (Cummins QSB engine) | Crane | 2270002045 | Diesel | 275 | 720 | 0.367 | 0.28 | 0.07 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.08057 | 0.013552 | 0.13351 | 0.43 | 0.32228 | 0.091999 | 0.015474 | 0.16053
Dozer - Cat D9, 475 HP | Rubber Tire Dozer | 2270002063 | Diesel | 475 | 1500 | 0.371 | 0.28 | 0.13 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.14963 | 0.013552 | 0.13351 | 0.59 | 0.76379 | 0.40493 | 0.036673 | 0.38045
Boom Truck (National Crane 800D) | Crane | 2270002045 | Diesel | 350 | 720 | 0.367 | 0.28 | 0.08 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.09208 | 0.013552 | 0.13351 | 0.43 | 0.41017 | 0.13382 | 0.019694 | 0.20431
Loader - Cat 988H, 501HP | Rubber Tire Loader | 2270002060 | Diesel | 501 | 7200 | 0.371 | 0.28 | 0.13 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.14963 | 0.013552 | 0.13351 | 0.59 | 0.8056 | 0.42709 | 0.03868 | 0.40128
Light Plants (Genie TML-4000) | Light Commercial Generator Set | 2270006005 | Diesel | 15 | 36000 | 0.408 | 0.28 | 0.22 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.25322 | 0.013552 | 0.13351 | 0.43 | 0.017579 | 0.015771 | 0.00084404 | 0.0087561
Forklift - 15 Ton (Cat P30000) | Forklifts | 2270003020 | Diesel | 148 | 1440 | 0.371 | 0.28 | 0.13 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.14963 | 0.013552 | 0.13351 | 0.59 | 0.23798 | 0.12617 | 0.011427 | 0.11854
Forklift - Cat (2P5000) | Forklifts | 2270003020 | Diesel | 61 | 4320 | 0.412 | 0.28 | 0.36 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.41436 | 0.013552 | 0.13351 | 0.59 | 0.098087 | 0.144 | 0.0047096 | 0.048858
Generator - 100 kW | Light Commercial Generator Set | 2270006005 | Diesel | 135 | 2880 | 0.367 | 0.28 | 0.09 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.10359 | 0.013552 | 0.13351 | 0.43 | 0.15821 | 0.058067 | 0.0075963 | 0.078805
Generator - 50 kW | Light Commercial Generator Set | 2270006005 | Diesel | 67 | 14400 | 0.408 | 0.28 | 0.24 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.27624 | 0.013552 | 0.13351 | 0.43 | 0.078519 | 0.076849 | 0.00377 | 0.039111
Man lifts - 80' Gemie (Z80/60) | Aerial Lift | 2270003010 | Diesel | 78 | 1440 | 0.481 | 0.28 | 0.61 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.70211 | 0.013552 | 0.13351 | 0.21 | 0.044642 | 0.11105 | 0.0021435 | 0.022237
Man lift - 45' Genie (Z45, Perkins 404D-22 4 cylinder engine) | Aerial Lift | 2270003010 | Diesel | 51 | 2880 | 0.481 | 0.28 | 0.61 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.70211 | 0.013552 | 0.13351 | 0.21 | 0.029189 | 0.072611 | 0.0014015 | 0.014539
Zoom Boom - Telehandler (used on warehouse), GTH-1056 | Forklifts | 2270003020 | Diesel | 125 | 7200 | 0.371 | 0.28 | 0.13 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.14963 | 0.013552 | 0.13351 | 0.59 | 0.201 | 0.10656 | 0.0096508 | 0.10012
Bobcat (2500 lb capacity, 75 hp, Kubota S250 ) | Skid Steer Loader | 2270002072 | Diesel | 75 | 8640 | 0.481 | 0.28 | 0.61 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.70211 | 0.013552 | 0.13351 | 0.21 | 0.042925 | 0.10678 | 0.002061 | 0.021381
Welding Machines (in shop) (Lincoln Electric) | Light Commercial Welders | 2270006025 | Diesel | 36 | 8640 | 0.481 | 0.28 | 0.39 | 0.0092 | 0.13 | 1 | 0.008 | 0.151 | 0.473 | 0.027 | 1.008 | 1.151 | 1.473 | 1.027 | 0.28224 | 0.44889 | 0.013552 | 0.13351 | 0.21 | 0.020604 | 0.03277 | 0.00098929 | 0.010263
Heater Description | Fuel Type | Equipment MMBtu/hr | Operating hrs/year | Emission Factors (lb/MMBtu) |  |  |  | Emissions (ton/year)
|  |  |  | NOx | CO | PM | THC | NOx | CO | PM | THC
Ground thaw Heater (E3000) | Diesel | 0.6 | 8640 | 0.14493 | 0.036232 | 0.023913 | 0.0024638 | 0.37565 | 0.093913 | 0.061983 | 0.0063861
Tioga Heaters (600,000 Btu/hr heater) | Diesel | 0.6 | 56160 | 0.14493 | 0.036232 | 0.023913 | 0.0024638 | 2.4417 | 0.61043 | 0.40289 | 0.04151
| Total Non-Road/Portable Emissions | Emissions (ton/year)
|  | NOx | CO | Emission Factors (lb/MMBtu) NOx: PM; Emission Factors (lb/MMBtu) CO: THC
|  | 7.5904 | 3.2176 | Emission Factors (lb/MMBtu) NOx: 0.69429; Emission Factors (lb/MMBtu) CO: 2.4298
NOTES:
Note 1: SCC code based on Appendix A of "Median Life, Annual Activity, and Load Factor Values for Nonroad Engine Emissions Modeling", July 2010, EPA-420-R-10-018.
Note 2: Brake-specific fuel consumption, zero hour steady state emission factor (EFss; g/hp-hr), and load factor are from NMIM/NONROAD08 model factors dated April 5, 2009.
Note 3: Median life is taken from Table 1 of "Median Life, Annual Activity, and Load Factor Values for Nonroad Engine Emissions Modeling", April 2004, EPA-420-P-04-005.
EFss from NMIM/NONROAD08 have transient adjustment factors (TAFs) built in. The EFss are weighted averages based on Tier 4 engines.
Note 3: Age factor and Deterioration factors calculated using Equation 4 from "Exhaust and Crankcase Emission Factors for Nonroad Engine Modeling - Compression-Ignition", July 2010, EPA-420-R-10-018.
Age Factor = LF * cumulative hours / median life {where Age factor is capped at 1. For this calculation, age factor is assumed to be 1 for simplification purposes}.
Deterioration Factor = 1 + ( A * Age Factor^b), where b = 1 for diesel engines and A is taken from Table A6 from above mentioned source
Note 4: Adjusted Emission Factors are calculated using Equation 1 from, "Exhaust and Crankcase Emission Factors for Nonroad Engine Modeling - Compression-Ignition", July 2010, EPA-420-R-10-018.
Adjusted EF = Efss * TAF * DF (as stated in Note 2, EFss have TAFs built in)
Note 5: Adjusted Emission Factors for PM10 are calculated using Equation 2 from, "Exhaust and Crankcase Emission Factors for Nonroad Engine Modeling - Compression-Ignition", July 2010, EPA-420-R-10-018.
The correction factor SPMadj is made to account for fuel sulfur variations; inputs specific to this calculation are noted below
|  |  | 0.02247 | Emission Factors (lb/MMBtu) NOx: soxcnv (fraction of fuel sulfur converted to direct PM) for Base, T0, T1, T2, T3, T3B, T4A, T4B
|  |  | 0.3 | Emission Factors (lb/MMBtu) NOx: soxcnv (fraction of fuel sulfur converted to direct PM) for Base, T4 and T4N
|  |  | 0.03 | Emission Factors (lb/MMBtu) NOx: soxcnv (fraction of fuel sulfur converted to direct PM) for gasoline engines
|  |  | 0.0015 | Emission Factors (lb/MMBtu) NOx: soxdsl (weight percent of sulfur in diesel fuel)
|  |  | 0.0015 | Emission Factors (lb/MMBtu) NOx: soxbas (default certification fuel sulfur weight percent, 0.0015 is default for Tier 4 engines)
Note 6: Adjusted emissions from THC to VOC by 1.053 is the ratio of VOC to THC (for diesel equipment) from "Conversion Factors for Hydrocarbon Components", July 2010, EPA-420-R-10-015.

## Emission Factors
Source Type | Gas-Fired Combustion Turbines |  |  | Gas-Fired Combustion Turbines |  |  | Diesel Combustion Turbines |  |  | Diesel Combustion Turbines |  |  | Gas-Fired Heaters/Boilers |  |  | Diesel-Fired Heaters |  |  |  |  | Gas-Fired ICEs 2-stroke, Lean-Burn |  |  | Gas-Fired ICEs 4-stroke, Rich-Burn |  |  | Diesel-Fired ICEs <600 hp |  |  | Diesel-Fired ICEs >600 hp |  |  | Flares |  |  | Refuse Incinerators (MOD/SA) |  |  | Used Oil (Atomizing) Burner
| Loads >80% (GRI-HAPCalc v.3.01) |  |  | All Loads |  |  | All Loads |  |  | >80% Load Only
HAP | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set | EF | units | Factor Set
1,1,2,2-Tetrachloroethane | [20 empty] | 6.63e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 2.53e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
1,1,2-Trichloroethane | [20 empty] | 5.27e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 1.53e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
1,3-Butadiene | 4.3e-07 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 4.29e-07 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 1.65e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 1.6e-05 | lb/MMBtu | AP-42 Table 3.1-4 (4/00) | [8 empty] | 0.00082 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.000663 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 3.91e-05 | lb/MMBtu | AP-42 Table 3.3-2 (10/96)
1,3-Dichloropropene | [20 empty] | 4.38e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 1.27e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
1,4-Dichlorobenzene | [6 empty] | 2.97e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00)
2,2,4-Trimethylpentane | [20 empty] | 0.000846 | lb/MMBtu | AP-42 Table 3.2-1 (8/00)
Acetaldehyde | 4e-05 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 4.45e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 3.03e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [11 empty] | 0.00776 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.00279 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 0.000767 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 2.52e-05 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 4.2157e-05 | lb/MMBtu | VCAPCD (5/172001)
Acrolein | 6.4e-06 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 8.31e-06 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [14 empty] | 0.00778 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.00263 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 9.25e-05 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 7.88e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 9.8039e-06 | lb/MMBtu | VCAPCD (5/172001)
Antimony | [38 empty] | 0.0045 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
Arsenic | [6 empty] | 1.1e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 1.1e-05 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 4 | lb/TBtu | 4000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98) | [15 empty] | 0.000669 | lb/ton | AP-42 Table 2.1-9 (10/96) | 0.06 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
Benzene | 1.2e-05 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 0.000103 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 5.48e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 5.5e-05 | lb/MMBtu | AP-42 Table 3.1-4 (4/00) | 2.0588e-06 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 0.00194 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.00158 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 0.000933 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 0.000776 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 0.00015588 | lb/MMBtu | VCAPCD (5/172001)
Beryllium | [6 empty] | 3.07e-07 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 3.1e-07 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 3 | lb/TBtu | 3000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98) | [18 empty] | 0.0018 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
Biphenyl | [20 empty] | 3.95e-06 | lb/MMBtu | AP-42 Table 3.2-1 (8/00)
Cadmium | [6 empty] | 3.75e-06 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 4.8e-06 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 3 | lb/TBtu | 3000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98) | [15 empty] | 0.00241 | lb/ton | AP-42 Table 2.1-9 (10/96) | 0.012 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
Carbon Tetrachloride | [6 empty] | 3.06e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [11 empty] | 6.07e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 1.77e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
Chlorobenzene | [6 empty] | 2.49e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [11 empty] | 4.44e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 1.29e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
Chloroform | [6 empty] | 2.55e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [11 empty] | 4.71e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 1.37e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
Chromium | [6 empty] | 8.43e-06 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 1.1e-05 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 3 | lb/TBtu | 3000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98) | [15 empty] | 0.00331 | lb/ton | AP-42 Table 2.1-9 (10/96) | 0.18 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
Cobalt | [38 empty] | 0.0052 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
Dibutylphthalate | [38 empty] | 3.4e-05 | lb/1000 gal. | AP-42 Table 1.11-5 (10/96)
Ethylbenzene | 3.2e-05 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 2.58e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [14 empty] | 0.000108 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 2.48e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | [6 empty] | 0.0014157 | lb/MMBtu | VCAPCD (5/172001)
Ethylene Dibromide | [20 empty] | 7.34e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 2.13e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
Ethylene Dichloride | [6 empty] | 2.02e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00)
Formaldehyde | 0.00071 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 0.00312 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 0.000245 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 0.00028 | lb/MMBtu | AP-42 Table 3.1-4 (4/00) | 7.3529e-05 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | 0.061 | lb/1000 gal. | 453.3631 | lb/MMBtu | AP-42 Table 1.3-8 (9/98) | 0.0552 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.0205 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 0.00118 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 7.89e-05 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 0.0011461 | lb/MMBtu | VCAPCD (5/172001)
HCl | [35 empty] | 2.15 | lb/ton | AP-42 Table 2.1-9 (10/96)
Lead | [6 empty] | 1.34e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 1.4e-05 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) | 4.902e-07 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | 9 | lb/TBtu | 9000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98)
Manganese | [6 empty] | 0.000789 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 0.00079 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 6 | lb/TBtu | 6000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98) | [18 empty] | 0.05 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
Mercury | [6 empty] | 1.2e-06 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 1.2e-06 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 3 | lb/TBtu | 3000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98) | [15 empty] | 0.0056 | lb/ton | AP-42 Table 2.1-9 (10/96)
Methanol | [20 empty] | 0.00248 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.00306 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
Methylene Chloride | [6 empty] | 2.13e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [11 empty] | 0.000147 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 4.12e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
n-Hexane | [12 empty] | 0.0017647 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 0.000445 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | [9 empty] | 2.8431e-05 | lb/MMBtu | VCAPCD (5/172001)
Nickel | [6 empty] | 1.62e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 4.6e-06 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 3 | lb/TBtu | 3000000 | lb/MMBtu | AP-42 Table 1.3-8 (9/98) | [15 empty] | 0.00552 | lb/ton | AP-42 Table 2.1-9 (10/96) | 0.16 | lb/1000 gal. | AP-42 Table 1.11-4 (10/96)
PAHs | 2.2e-06 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 2.25e-06 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 4.03e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 4e-05 | lb/MMBtu | AP-42 Table 3.1-4 (4/00) | [8 empty] | 0.000134 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.000141 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 0.000168 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 0.000212 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 1.3725e-05 | lb/MMBtu | VCAPCD (5/172001)
Phenol | [20 empty] | 4.21e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | [15 empty] | 2.8e-05 | lb/1000 gal. | AP-42 Table 1.11-5 (10/96)
Phosphorus
POM (Total) | 1.3e-06 | g/bhp-hr |  | 1.37e-06 |  |  | 3.52e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 3.5e-05 | lb/MMBtu | AP-42 Table 3.1-4 (4/00) | 6.848e-07 | lb/MMBtu |  | 0.0033 | lb/1000 gal. | 24.5262 | lb/MMBtu | AP-42 Table 1.3-8 (9/98) | 0.00013014 |  |  | 9.71e-05 |  |  | 0.00016826 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 0.00021153 |  |  | 1.0573e-08 | lb/MMBtu | VCAPCD (5/172001) | 0 |  |  | 0.0002003 | lb/1000 gal. | AP-42 (10/96)
POM 2-Methylnaphthalene | [12 empty] | 2.35e-08 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 2.14e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00)
POM 3-Methylcholanthrene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98)
POM 7,12-Dimethylbenz(a)anthracene | [12 empty] | 1.57e-08 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98)
POM Acenaphthene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 1.33e-06 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 1.42e-06 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 4.68e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Acenaphthylene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 3.17e-06 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 5.06e-06 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 9.23e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Anthracene | [12 empty] | 2.4e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 7.18e-07 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 1.87e-06 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 1.23e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Benz(a)anthracene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 3.36e-07 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 1.68e-06 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 6.22e-07 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Benzo(a)pyrene | [12 empty] | 1.2e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 5.68e-09 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 1.88e-07 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 2.57e-07 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Benzo(b)fluoranthene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 8.51e-09 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 9.91e-08 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 1.11e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Benzo(g,h,i)perylene | [12 empty] | 1.2e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 2.48e-08 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 4.89e-07 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 5.56e-07 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Benzo(k)fluoranthene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 4.26e-09 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 1.55e-07 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 2.18e-07 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Chrysene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 6.72e-07 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 3.53e-07 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 1.53e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Dibenz(a,h)anthracene | [12 empty] | 1.2e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [11 empty] | 5.83e-07 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 3.46e-07 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Fluoranthene | [12 empty] | 2.9e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 3.61e-07 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 7.61e-06 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 4.03e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Fluorene | [12 empty] | 2.7e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 1.69e-06 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 2.94e-05 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 1.28e-05 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Indeno(1,2,3-c,d)pyrene | [12 empty] | 1.8e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 9.93e-09 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 3.75e-07 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 4.14e-07 | lb/MMBtu | AP-42 Table 3.4-3 (10/96)
POM Naphthalene | 1.3e-06 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 1.37e-06 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 3.52e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 3.5e-05 | lb/MMBtu | AP-42 Table 3.1-4 (4/00) | 5.98e-07 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 9.63e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 9.71e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 8.48e-05 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 0.00013 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 1.0784e-05 | lb/MMBtu | VCAPCD (5/172001) |  |  |  | 9.2e-05 | lb/1000 gal. | AP-42 Table 1.11-5 (10/96)
POM Phenanthrene | [12 empty] | 1.67e-08 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 3.53e-06 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 2.94e-05 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 4.08e-05 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | [6 empty] | 0.0001 | lb/1000 gal. | AP-42 Table 1.11-5 (10/96)
POM Pyrene | [12 empty] | 4.9e-09 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 5.84e-07 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) |  |  |  | 4.78e-06 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 3.71e-06 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | [6 empty] | 8.3e-06 | lb/1000 gal. | AP-42 Table 1.11-5 (10/96)
Propional[dehyde]
Propylene Oxide | 2.9e-05 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 2.86e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00)
Selenium | [6 empty] | 2.88e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | 2.5e-05 | lb/MMBtu | AP-42 Table 3.1-5 (4/00) |  |  |  | 15 | lb/TBtu | 15000000 | lb/MMBtu | AP-42 Table 1.3-10 (9/98)
Styrene | [20 empty] | 5.48e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 1.19e-05 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
Tetrachloroethylene | [6 empty] | 3.24e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00)
Toluene | 0.00013 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 9.37e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [6 empty] | 3.3333e-06 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98) | [5 empty] | 0.000963 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.000558 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 0.000409 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 0.000281 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 5.6863e-05 | lb/MMBtu | VCAPCD (5/172001)
Trichloroethylene | [6 empty] | 2.75e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00)
Vinyl Chloride | [6 empty] | 5.27e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [11 empty] | 2.47e-05 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 7.18e-06 | lb/MMBtu | AP-42 Table 3.2-3 (8/00)
Vinylidene Chloride | [6 empty] | 2.02e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00)
Xylenes(m,p,o) | 6.4e-05 | lb/MMBtu | EPA AP-42 Table 3.1-3 (4/00) | 5.48e-05 | lb/MMBtu | Background report for AP-42 Section 3.1 (4/00) | [14 empty] | 0.000268 | lb/MMBtu | AP-42 Table 3.2-1 (8/00) | 0.000195 | lb/MMBtu | AP-42 Table 3.2-3 (8/00) | 0.000285 | lb/MMBtu | AP-42 Table 3.3-2 (10/96) | 0.000193 | lb/MMBtu | AP-42 Table 3.4-3 (10/96) | 2.8431e-05 | lb/MMBtu | VCAPCD (5/172001)
CDD/CDF | [35 empty] | 2.94e-06 | lb/ton | AP-42 Table 2.1-9 (10/96)
[17 empty] | Diesel HHV | 134550 | Btu/gal | [13 empty] | Fuel Gas HHV | 1020 | Btu/scf
TOTAL | 0.0010273 |  |  | 0.0034828 |  |  | 0.0015792 |  |  | 0.0012879 |  |  | 0.0018448 | lb/MMBtu | All |  |  | 49000477.8893 |  |  | 0.079535 |  |  | 0.032418 |  |  | 0.0040419 |  |  | 0.0017855 |  |  | 0.0028971 |  |  | 2.1675 |  |  | 0.47376
[13 empty] | 0.0018448 | lb/MMBtu | EPA AP-42 Table 1.4-3 (7/98)
Note on AK1: Aleksa, Deborah: Emission Factors do not line up with using Heat Duty. Need to adjust calculation in HAPs calc sheet if equipment present
Note on Y36: kmalmquist: PAH emission factor in AP-42 Table 3.2-3 (7/00) missing in GRI-HAPCalc. Assume 7,276 Btu/hp-hr.
Note on Q39: kmalmquist: Includes AP-42 EF for total POM plus the FIRE EF for fluoranthene
Note on P62: kmalmquist: Revised 10/21/02 - see letter from Paul Drayton (GRI)

## Emission Factor Look Up (hidden)
Equipment/Fuel | 1,1,2,2-Tetrachloroethane | 1,1,2-Trichloroethane | 1,3-Butadiene | 1,3-Dichloropropene | 1,4-Dichlorobenzene | 2,2,4-Trimethylpentane | Acetaldehyde | Acrolein | Antimony | Arsenic | Benzene | Beryllium | Biphenyl | Cadmium | Carbon Tetrachloride | Chlorobenzene | Chloroform | Chromium | Cobalt | Dibutylphthalate | Ethylbenzene | Ethylene Dibromide | Ethylene Dichloride | Formaldehyde | HCl | Lead | Manganese | Mercury | Methanol | Methylene Chloride | n-Hexane | Nickel | PAHs | Phenol | Phosphorus | POM (Total) | POM 2-Methylnaphthalene | POM 3-Methylcholanthrene | POM 7,12-Dimethylbenz(a)anthracene | POM Acenaphthene | POM Acenaphthylene | POM Anthracene | POM Benz(a)anthracene | POM Benzo(a)pyrene | POM Benzo(b)fluoranthene | POM Benzo(g,h,i)perylene | POM Benzo(k)fluoranthene | POM Chrysene | POM Dibenz(a,h)anthracene | POM Fluoranthene | POM Fluorene | POM Indeno(1,2,3-c,d)pyrene | POM Naphthalene | POM Phenanthrene | POM Pyrene | Propional[dehyde] | Propylene Oxide | Selenium | Styrene | Tetrachloroethylene | Toluene | Trichloroethylene | Vinyl Chloride | Vinylidene Chloride | Xylenes(m,p,o) | CDD/CDF
CT¦>80%¦NG | 0 | 0 | 4.3e-07 | 0 | 0 | 0 | 4e-05 | 6.4e-06 | 0 | 0 | 1.2e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2e-05 | 0 | 0 | 0.00071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2e-06 | 0 | 0 | 1.3e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3e-06 | 0 | 0 | 0 | 2.9e-05 | 0 | 0 | 0 | 0.00013 | 0 | 0 | 0 | 6.4e-05 | 0
CT¦0¦NG | 0 | 0 | 4.29e-07 | 0 | 0 | 0 | 4.45e-05 | 8.31e-06 | 0 | 0 | 0.000103 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.58e-05 | 0 | 0 | 0.00312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.25e-06 | 0 | 0 | 1.37e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.37e-06 | 0 | 0 | 0 | 2.86e-05 | 0 | 0 | 0 | 9.37e-05 | 0 | 0 | 0 | 5.48e-05 | 0
CT¦>80%¦D | 0 | 0 | 1.6e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 1.1e-05 | 5.5e-05 | 3.1e-07 | 0 | 4.8e-06 | 0 | 0 | 0 | 1.1e-05 | 0 | 0 | 0 | 0 | 0 | 0.00028 | 0 | 1.4e-05 | 0.00079 | 1.2e-06 | 0 | 0 | 0 | 4.6e-06 | 4e-05 | 0 | 0 | 3.5e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5e-05 | 0 | 0 | 0 | 0 | 2.5e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CT¦0¦D | 0 | 0 | 1.65e-05 | 0 | 2.97e-05 | 0 | 3.03e-05 | 0 | 0 | 1.1e-05 | 5.48e-05 | 3.07e-07 | 0 | 3.75e-06 | 3.06e-05 | 2.49e-05 | 2.55e-05 | 8.43e-06 | 0 | 0 | 0 | 0 | 2.02e-05 | 0.000245 | 0 | 1.34e-05 | 0.000789 | 1.2e-06 | 0 | 2.13e-05 | 0 | 1.62e-05 | 4.03e-05 | 0 | 0 | 3.52e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.52e-05 | 0 | 0 | 0 | 0 | 2.88e-05 | 0 | 3.24e-05 | 0 | 2.75e-05 | 5.27e-05 | 2.02e-05 | 0 | 0
Heater¦0¦NG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.0588e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3529e-05 | 0 | 4.902e-07 | 0 | 0 | 0 | 0 | 0.0017647 | 0 | 0 | 0 | 0 | 6.848e-07 | 2.35e-08 | 1.8e-09 | 1.57e-08 | 1.8e-09 | 1.8e-09 | 2.4e-09 | 1.8e-09 | 1.2e-09 | 1.8e-09 | 1.2e-09 | 1.8e-09 | 1.8e-09 | 1.2e-09 | 2.9e-09 | 2.7e-09 | 1.8e-09 | 5.98e-07 | 1.67e-08 | 4.9e-09 | 0 | 0 | 0 | 0 | 0 | 3.3333e-06 | 0 | 0 | 0 | 0 | 0
Heater¦0¦D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4000000 | 0 | 3000000 | 0 | 3000000 | 0 | 0 | 0 | 3000000 | 0 | 0 | 0 | 0 | 0 | 453.3631 | 0 | 9000000 | 6000000 | 3000000 | 0 | 0 | 0 | 3000000 | 0 | 0 | 0 | 24.5262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ICE¦2-Stroke¦NG | 6.63e-05 | 5.27e-05 | 0.00082 | 4.38e-05 | 0 | 0.000846 | 0.00776 | 0.00778 | 0 | 0 | 0.00194 | 0 | 3.95e-06 | 0 | 6.07e-05 | 4.44e-05 | 4.71e-05 | 0 | 0 | 0 | 0.000108 | 7.34e-05 | 0 | 0.0552 | 0 | 0 | 0 | 0 | 0.00248 | 0.000147 | 0.000445 | 0 | 0.000134 | 4.21e-05 | 0 | 0.00013014 | 2.14e-05 | 0 | 0 | 1.33e-06 | 3.17e-06 | 7.18e-07 | 3.36e-07 | 5.68e-09 | 8.51e-09 | 2.48e-08 | 4.26e-09 | 6.72e-07 | 0 | 3.61e-07 | 1.69e-06 | 9.93e-09 | 9.63e-05 | 3.53e-06 | 5.84e-07 | 0 | 0 | 0 | 5.48e-05 | 0 | 0.000963 | 0 | 2.47e-05 | 0 | 0.000268 | 0
ICE¦4-Stroke¦NG | 2.53e-05 | 1.53e-05 | 0.000663 | 1.27e-05 | 0 | 0 | 0.00279 | 0.00263 | 0 | 0 | 0.00158 | 0 | 0 | 0 | 1.77e-05 | 1.29e-05 | 1.37e-05 | 0 | 0 | 0 | 2.48e-05 | 2.13e-05 | 0 | 0.0205 | 0 | 0 | 0 | 0 | 0.00306 | 4.12e-05 | 0 | 0 | 0.000141 | 0 | 0 | 9.71e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.71e-05 | 0 | 0 | 0 | 0 | 0 | 1.19e-05 | 0 | 0.000558 | 0 | 7.18e-06 | 0 | 0.000195 | 0
ICE¦<600hp¦D | 0 | 0 | 3.91e-05 | 0 | 0 | 0 | 0.000767 | 9.25e-05 | 0 | 0 | 0.000933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00118 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.000168 | 0 | 0 | 0.00016826 | 0 | 0 | 0 | 1.42e-06 | 5.06e-06 | 1.87e-06 | 1.68e-06 | 1.88e-07 | 9.91e-08 | 4.89e-07 | 1.55e-07 | 3.53e-07 | 5.83e-07 | 7.61e-06 | 2.94e-05 | 3.75e-07 | 8.48e-05 | 2.94e-05 | 4.78e-06 | 0 | 0 | 0 | 0 | 0 | 0.000409 | 0 | 0 | 0 | 0.000285 | 0
ICE¦>600hp¦D | 0 | 0 | 0 | 0 | 0 | 0 | 2.52e-05 | 7.88e-06 | 0 | 0 | 0.000776 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.89e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.000212 | 0 | 0 | 0.00021153 | 0 | 0 | 0 | 4.68e-06 | 9.23e-06 | 1.23e-06 | 6.22e-07 | 2.57e-07 | 1.11e-06 | 5.56e-07 | 2.18e-07 | 1.53e-06 | 3.46e-07 | 4.03e-06 | 1.28e-05 | 4.14e-07 | 0.00013 | 4.08e-05 | 3.71e-06 | 0 | 0 | 0 | 0 | 0 | 0.000281 | 0 | 0 | 0 | 0.000193 | 0
Flare¦0¦NG | 0 | 0 | 0 | 0 | 0 | 0 | 4.2157e-05 | 9.8039e-06 | 0 | 0 | 0.00015588 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0014157 | 0 | 0 | 0.0011461 | 0 | 0 | 0 | 0 | 0 | 0 | 2.8431e-05 | 0 | 1.3725e-05 | 0 | 0 | 1.0573e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0784e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.6863e-05 | 0 | 0 | 0 | 2.8431e-05 | 0
Incinerators¦0¦NG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.000669 | 0 | 0 | 0 | 0.00241 | 0 | 0 | 0 | 0.00331 | 0 | 0 | 0 | 0 | 0 | 0 | 2.15 | 0 | 0 | 0.0056 | 0 | 0 | 0 | 0.00552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.94e-06
Burners¦0¦D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0045 | 0.06 | 0 | 0.0018 | 0 | 0.012 | 0 | 0 | 0 | 0.18 | 0.0052 | 3.4e-05 | 0 | 0 | 0 | 0 | 0 | 0 | 0.05 | 0 | 0 | 0 | 0 | 0.16 | 0 | 2.8e-05 | 0 | 0.0002003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.2e-05 | 0.0001 | 8.3e-06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Tank¦0¦D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Fugitive¦0¦D | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0