## July 2022 ETT
July 2022 ETT List
Note: Column titled "Est. New ETT Score" is the estimated new score based on the violations that have Returned to Compliance (RTCd) during the Quarter. Please note that this score will likely change on the next quarter's list due to further violations being generated. Comments submitted by Drinking Water Program staff on July 29, 2022.
Staff | RMW | Est. New ETT Score | System Information | 10 Point |  |  | 5 Point | [7 empty] | 1 Point | [12 empty] | General Comments | How to Return to Compliance | Known Hardware Problems
|  |  |  | RTCR | SW | Nitrate | RTCR | SW | GWR | Nitrate | Arsenic | DBP | LCR | Rads | RTCR | TCR | SW | GWR | Arsenic | DBP | LCR | IOC | VOC | SOC | Rads | CCR | PN
ZELLMER | DEC | 29 | AKHIOK / AK2250037 (90 / C) | [6 empty] | 3 | [8 empty] | 1 | 6 |  | 1 | 3 |  |  |  |  | Last sampled for Nitrate, DBPs, and VOCs in 2018, Arsenic in 2009, and IOCs in 2010. | Sample for annual Nitrate, Arsenic, DBPs, IOCs, and VOCs. | N/A
VANSANDT | DEC | 70 | AKUTAN / AK2260252 (95 / C) | [6 empty] | 2 | [6 empty] | 48 |  |  | 4 | 2 |  | 2 |  |  |  |  | Last sampled Nitrate and VOCs in 2019, DBP2 in 2018, Lead & Copper in 2014, LT2 in 2017. Fails to collect monthly total coliform sample w/chlorine residual. System reports lack of sufficient funding and staffing. | Monitor for overdue samples in 2022: Nitrate, LT2, monthly RTCR, TTHM & HAA5, VOCs, and lead and copper. Submit adequate monthly operator reports timely. Monitor consistently for distribution chlorine residual at the same time and location as the monthly TC. | N/A
ZELLMER | YKHC | 86 | ALAKANUK WATER SYSTEM / AK2270362 (570 / C) |  |  |  | 1 | [9 empty] | 35 |  |  | 32 | 1 |  | 5 |  |  | 3 |  | Last sampled for VOCs and DBPs in 2015. Incomplete E. coli (LT2) sampling in 2021. 2019 and 2020 CCRs not certified as distributed. Overdue corrective actions from 2021 Level 1 assessment. System fails to comply with monthly operator reports. | Sample for VOCs, DBPs, and E. coli (LT2). Collect monthly TOC and alkalinity samples. Submit CCR certification page for current CCR. Address Level 1 Assessment corrective actions. Submit adequate monthly operator reports timely. | N/A
VANSANDT | No RMW | 21 | ALASKA RAINBOW LODGE / AK2261680 (36 / NC) | [6 empty] | 2 |  |  |  |  | 5 | [12 empty] | Last sample Nitrate in 2018. Last total coliform sampled on 8/27/2019. Seasonal PWS closed in 2020. | Sample for Nitrate and total coliform during 2022 seasonal operation. | N/A
MORRISON | YKHC | 12 | ANVIK WATER SYSTEM / AK2280171 (96 / C) | [14 empty] | 1 |  | 5 |  | 1 | [5 empty] | Last sampled of DBPs and Inorganics in 2010. System did not collect triggered source water sample after total coliform positive sample in 2018. | Sample for DBPs in July and Inorganics ASAP. Collect monthly total coliform sample. | N/A
ELMORE | NSHC | 16 | BERING ST SD - TELLER SC/WASH / AK2340248 (295 / C) | [6 empty] | 1 | [8 empty] | 1 | 3 | 1 | 1 | 4 |  |  |  |  | Last sampled for Nitrate, Arsenic, DBPs, VOCs, and IOCs in 2020. | Sample for annual Nitrate, Arsenic, DBPs, IOCs, and VOCs.
MORRISON | No RMW | 12 | BETHEL LONGHOUSE HOTEL / AK2270401 (90 / NC) | [5 empty] | 1 | 1 | [17 empty] | Last sampled for Nitrate in 2020. Corrective Actions from 2016 sanitary survey have not been addressed. | Sample for annual Nitrate. Address Corrective Actions from 2016 sanitary survey. | N/A
MORRISON | No RMW | 31 | BETHEL-CITY S/D WATER / AK2271999 (1650 / C) | [8 empty] | 6 | [15 empty] | System has exceeded MCL for HAA5 since 3rd quarter 2020. | Sample for DBPs in September 2022. Achieve a quarterly HAA5 LRAA below the MCL. | N/A
SHARP | TCC | 28 | CHALKYITSIK VILLAGE WATER / AK2300183 (76 / C) | [8 empty] | 5 | [8 empty] | 2 | [6 empty] | Last sampled for Lead/Copper in 2020. System currently exceeding DBP LRAA MCL. | Sample for Lead/Copper. Adjust treatment and collect DBP samples until levels return to sub-MCL LRAA levels. | To date, guidelines for adequate change out frequency of GAC media have not been fully documented. Adequate change out frequency will reduce chances of DBP exceedance.
MORRISON | YKHC | 12 | CHEFORNAK WATER SYSTEM / AK2270338 (454 / C) | [6 empty] | 2 | [10 empty] | 1 | [6 empty] | Last sample for Nitrate in 2019. Missed sampling for Lead & Copper in 2021 and is on a 3 year schedule. | Sample for annual Nitrate and Lead & Copper in 2022. | N/A
HARRIS | DEC | 18 | CHENEGA / AK2291952 (50 / C) | [8 empty] | 3 |  |  |  |  | 1 |  |  |  | 1 | [6 empty] | System currently exceeding HAA5 LRAA MCL. Did not collect required number of Lead & Copper samples in 2021. | Achieve an HAA5 LRAA of 0.060 mg/L or below. Collect 5 Pb/Cu samples from approved locations. Collect final LT2 sample within specified timeframe in July 2022 (7/24-7/30). | N/A
VANSANDT | BBAHC | 12 | CHIGNIK LAKE WATER SYSTEM / AK2261096 (200 / C) | [5 empty] | 1 | 1 | [17 empty] | Last sampled for Nitrate in 2020 and TC in 11/2021. Corrective Action for booster station has not been completed (due 5/2020). | Sample for annual Nitrate in 2022. Address the outstanding corrective action. | N/A
ZELLMER | YKHC | 13 | CITY OF HOOPER BAY / AK2270312 (1200 / C) | [5 empty] | 1 | [10 empty] | 1 | [5 empty] | 2 |  | Last sampled for DBPs in 2020. Overdue sanitary survey deficiencies. PWS has not confirmed or certified distribution of 2021 or 2020 CCR to consumers (a copy was received by DEC). | Sample for DBPs per approved sampling plan. Correct all unresolved sanitary survey deficiencies. Distribute current CCR and submit the completed CCR certification form to DEC. | N/A
ZELLMER | BBAHC | 27 | CLARKS POINT WATER SYSTEM / AK2260202 (128 / C) | [6 empty] | 4 | [8 empty] | 1 |  | 1 | 1 | 1 |  |  |  |  | Last sampled for Nitrate in 2017, Arsenic in 2012, IOCs in 2011, VOCs in 2014, and Lead & Copper in 2017. | Sample for annual Nitrate, Arsenic, IOCs, VOCs, and collect a 5 Lead & Copper sample set. | N/A
HARRIS | DEC | 26 | COFFMAN COVE / AK2120436 (199 / C) | [8 empty] | 5 | [15 empty] | System exceeding DBP Precursor (TOC) requirements since 2021. | System needs to achieve an RAA Ratio of 1.0 or above. | N/A
ZELLMER | YKHC | 27 | CROOKED CREEK WATERING POINT / AK2280302 (147 / C) | [5 empty] | 1 | 1 | [9 empty] | 11 | 2 | [6 empty] | System has four overdue sanitary survey deficiencies from 2018 inspection. Last sampled for Nitrate in 2020, DBPs in 2016, and Lead & Copper in 2020. | Correct the sanitary survey deficiencies. Sample for annual Nitrate. Collect routine monthly total coliform samples with dist. chlorine residual level (at same time/place as TC). Collect TTHM/HAA5 samples during 2022. Collect 5 Lead & Copper samples 1st half 2023 per approved plan. | N/A
VANSANDT | No RMW | 11 | D & D RESTAURANT / AK2262660 (25 / NC) | [11 empty] | 9 | [12 empty] | System did not monitor for total coliform in 2022. | Collect a monthly coliform sample, if operational in 2022. | N/A
SHARP | NSHC | 67 | DIOMEDE JOINT UTILITIES / AK2340141 (184 / C) |  |  | 1 |  |  |  |  | 11 | [16 empty] | System currently exceeding RAA MCL for Arsenic and the MCL for Nitrate. System currently in compliance with public notice posting for MCL exceedances. | System needs treatment installed to address historic Nitrate and Arsenic MCLs. | ANTHC is planning to develop and install treatment plant upgrades to meet SWTR (Direct Filtration), Nitrate & Arsenic MCLs (GAC and ion exchange), and corrosion control (calcite contactor). WTP design 95% completion expected mid Aug. Final design for DEC review expected Sept-Oct. 2022.
NAKANISHI | No RMW | 15 | FOREST PARK TC / AK2210794 (175 / C) | [5 empty] | 2 | [18 empty] | System has outstanding Sanitary Survey deficiencies from the 2016 and 2019 sanitary surveys. Last sampled Well 2 for Nitrate in 2020. | Sample Well 2 for Nitrate. Address sanitary survey deficiencies. Communicate with DEC engineers regarding NOV. | Modifications to distribution system are temporary.
SHARP | TCC | 51 | GALENA WTP1 - CITY / AK2360272 (490 / C) | [8 empty] | 9 | [8 empty] | 4 | [6 empty] | Currently exceeding MCL for TTHM and HAA5. System exceeded Copper AL in 2018 and then had a single set of samples that were below the AL in the last half of 2019. Once COVID hit, the system has not been allowed to sample in homes and continues to have issues with the community allowing access for sampling with covid cases persisting. | Optimize or upgrade treatment system to limit DBP formation and increase TOC removal. System needs to submit 2 six month sets of lead/copper samples that are below the AL once community guidelines allow for sampling in homes to occur. | Galena will be replacing their aging WTP with a new conventional package WTP with dissolved air flotation process and GAC to help with DBP precursor reduction. Construction Approval request received in July 2022 and is pending review. Construction may not start until Spring 2023.
LATIMER | No RMW | 14 | GEORGE INLET CANNERY / AK2121501 (129 / NC) |  |  |  | 1 |  |  | 1 |  |  |  |  | 1 | [12 empty] | Awaiting confirmation of operation in 2022. System did not operate in 2020 or 2021 season due to lack of cruise ship customers due to COVID-19 there were no ships in port the past two seasons. | Complete all sampling and reporting and have a sanitary survey conducted during next operational season. | N/A
ZELLMER | YKHC | 122 | GRAYLING WATER SYSTEM / AK2280066 (195 / C) |  | 7 |  |  |  |  | 1 | [6 empty] | 38 |  |  | 3 | 2 |  | 1 |  |  |  |  | Struggles to consistently meet turbidity monitoring requirements. Last sampled for Nitrate in 2020, E. coli (LT2) in 02/2018, DBPs in 2020, and Lead & Copper in 2019. Last distribution Cl residual was reported with 10/2021 TC sample. | Submit a completed MOR that meets SWTR requirements. Sample for E. coli (LT2), DBPs, VOCs and Lead/Copper. Provide a Chlorine residual collected at the same time and place as every total coliform sample. | System on long-term BWN due to inadequate treatment.
VANSANDT | No RMW | 13 | HEART OF THE SHIRE / AK2263061 (79 / NC) | [5 empty] | 1 | 1 |  |  |  |  | 1 | [12 empty] | Seasonal system missed annual nitrate in 2020. System has outstanding sanitary survey deficiency. | Sample for annual Nitrate, correct outstanding sanitary deficiency, and consistently monitor for monthly TC. | N/A
LATIMER | No RMW | 13 | HIGHLAND PRIDE MOBILE TRAILER PARK / AK2240503 (100 / C) | [6 empty] | 1 | [15 empty] | 5 |  | System has not collected annual Nitrate sample since 2020 and has not completed annual CCR since 2019. | Sample for annual Nitrate and submit 2021 CCR (due in 2022) and CCR certification page. | N/A
BJORKMAN | No RMW | 17 | HOLLIS SCHOOL / AK2120541 (42 / NTNC) | [13 empty] | 12 |  |  | 4 | [7 empty] | Last sampled DBPs June 2022, however the TTHM sample could not be analyzed and needed to be resampled. Result for TTHM resample has not been received to date. Monthly operator reporting is not submitted on time and is incomplete. | Submit a completed MOR on time. Collect a set of DBPs that can be analyzed. | N/A
BJORKMAN | DEC | 59 | HYDABURG / AK2120224 (415 / C) | [6 empty] | 1 |  | 10 | [8 empty] | 1 | [6 empty] | System is overdue for annual Nitrate and Lead & Copper samples. System currently exceeding MCL for HAA5 LRAA. | Collect a set of DBP samples that allows the LRAA to be below the MCL for HAA%, collect an annual Nitrate sample and set of Lead and Copper samples asap. | N/A
BJORKMAN | DEC | 79 | KAKE MUNICIPAL WATER / AK2130083 (415 / C) | [8 empty] | 15 | [15 empty] | Currently exceeding the LRAA for HAA5. | Collect a set of DBPS that allows the LRAAs to be calculated below the MCL. | N/A
BJORKMAN | No RMW | 13 | KB SUB. WATER SERVICE ASSOC. / AK2243658 (170 / C) | [7 empty] | 11 | [7 empty] | 1 | [8 empty] | System is exceeding Arsenic RAA and is working with the State to pursue WINN grant funding to install a treatment system. | Install treatment or find another long term solution to lower arsenic levels. | N/A
BJORKMAN | DEC | 78 | KLAWOCK / AK2120169 (904 / C) | [8 empty] | 15 | [15 empty] | Currently exceeding LRAA for HAA5. | Collect a set of DBP samples that allow for the LRAA for HAA5 to be calculated below the MCL. | N/A
ELMORE | No RMW | 99 | KOTZEBUE MUN. WATER SYSTEM / AK2340060 (3234 / C) | [8 empty] | 19 | [15 empty] | System is exceeding the MCL for TTHM and HAA5; they have exceeded the HAA5 MCL since 2015 and the TTHM MCL since 2019. | System must upgrade their current treatment, which is expected to be completed by end of summer 2022. | Plans for a new micro-Nano membrane filtration system were approved for construction in 2020. The new WTP will help reduce DBPs. Construction began summer 2021, and completion date is expected for fall 2022.
ZELLMER | No RMW | 20 | KSD ANIAK SECONDARY SCHOOL / AK2271732 (80 / NTNC) | [5 empty] | 1 | 1 |  |  | 1 | [7 empty] | 1 | [5 empty] | 2 | PWS has unresolved sanitary survey deficiencies from their last survey. Last nitrate sample was 9/17/2020. PWS has not taken all required corrosion control steps and has not verified performance of required public notification for lead & copper exceedances. | Correct sanitary survey deficiencies. Collect an annual nitrate sample. Perform required corrosion control steps. Verify public notification requirements have been satisfied. | N/A
ZELLMER | YKHC | 24 | KWETHLUK NEW PIPED WATER SYSTEM / AK2272017 (760 / C) | [8 empty] | 3 | [8 empty] | 1 |  |  | 4 |  |  |  | Last sampled for annual Lead & Copper in 2020. PWS not meeting DBP TOC % removal requirements. No current SOC waiver on file and no SOC samples collected in the absence of an SOC waiver. | Collect an annual Lead & Copper sample set in 2022. Improve DBP Precursor sample management and consistently meet DBP TOC removal requirements. Submit an SOC waiver and collect quarterly SOC samples until a waiver is submitted and approved. | N/A
MORRISON | YKHC | 45 | KWIGILLINGOK WASHETERIA / AK2271700 (400 / C) | [13 empty] | 36 |  |  | 4 | 1 | [6 empty] | System has not completed LT2 sampling (last sampled in 07/2017). Has not monitored for TTHM since 2014 and is required to monitor annually. Did not monitor for lead and copper in 2020 and is on 3 year schedule. | Take LT2 samples biweekly when making water. Sample for lead and copper in 2022 and DBPs in February 2023. | System is on long term BWN, experiences difficulty meeting community demand.
MORRISON | No RMW | 18 | LKSD MEKORYUK NUNIVAARMIUT SC / AK2270972 (67 / NTNC) | [5 empty] | 1 |  |  | 2 | [7 empty] | 1 | [7 empty] | Overdue corrective actions from previous sanitary survey. Currently exceeding the MCL for TTHM. | Complete corrective actions to resolve survey deficiencies. Sample of DBPs that allow the LRAA for TTHM to be calculated below the MCL. | N/A
MORRISON | No RMW | 12 | LKSD NAPASKIAK Z J WILLIAMS SC / AK2270980 (148 / NTNC) | [5 empty] | 2 | [18 empty] | System has unresolved deficiencies from 2019 sanitary survey. | Complete correction actions to resolve 2019 sanitary survey deficiencies. | N/A
MORRISON | No RMW | 25 | LKSD NEWTOK AYAPRUN SCHOOL / AK2272007 (175 / NTNC) | [8 empty] | 4 | [15 empty] | System has exceeded MCL for TTHM since 1st quarter 2021. | Collect sample of DBPs that allow the LRAA for TTHM to be calculated below the MCL. | N/A
MORRISON | No RMW | 26 | LKSD NIGHTMUTE HS & ELEM / AK2271261 (259 / NTNC) |  | 1 |  |  |  |  | 1 | [6 empty] | 10 | [10 empty] | Last sample for Nitrate in 2020. Entry point chlorine levels on MOR do not meet requirements. | Sample for annual Nitrate. Work on WTP operations to meet treatment requirements. | This GU system is on a BWN since December 2021 due to inadequate chlorine treatment and no turbidity monitoring.
MORRISON | YKHC | 13 | LOWER KALSKAG WATER SYSTEM / AK2270697 (302 / C) | [16 empty] | 1 |  |  |  |  | 5 | 2 |  | System did not sample for DBPs in 2021. Has not sampled for quarterly RADs since 10/21. Did not submit CCR Certification in 2020 or 2021. | Sample for DBPs in August 2022. Sample quarterly for RADs for four consecutive quarters. Submit CCR Certification in 2022. | N/A
VANSANDT | BBAHC | 13 | MANOKOTAK HEIGHTS W/S / AK2262246 (215 / C) | [15 empty] | 1 |  | 1 | 1 | 1 | 4 |  |  |  | Last sampled for Arsenic in 2014, Lead/Copper in 2013, IOCs in 2008, and VOCs in 2014. | Sample for Arsenic, Lead/Copper, IOCs, and VOCs. Submit an Initial SOC Monitoring Waiver and/or collect quarterly SOC samples. | N/A
VANSANDT | BBAHC | 11 | MANOKOTAK WATER SYSTEM / AK2260090 (293 / C) | [5 empty] | 1 | [9 empty] | 1 |  | 1 | 1 | 1 |  |  |  |  | System last sampled Arsenic in 2013, IOCs in 2009, and VOCs in 2013. System has outstanding deficiencies from 2017 sanitary survey. | Sample for Arsenic, IOCs, and VOCs. Address outstanding sanitary survey deficiencies. | N/A
GILLESPIE | No RMW | 47 | MEADOW BROOK SUBDIVISION / AK2220037 (465 / C) | [7 empty] | 9 | [16 empty] | Exceeding MCL for Arsenic. System working with DEC engineers to add additional pumps to Well 5 (no Arsenic detected) in order to meet capacity. Intend to disconnect from Wells that exceeds the Arsenic MCL. | System will RTC once the Arsenic RAA is below the MCL. System needs to properly disconnect wells 1, 2, & 3 (scheduled for the summer of 2022). Systems engineer also needs to submit approval to operate to the Department. | N/A
MORRISON | No RMW | 23 | MERTARVIK WATER SYSTEM / AK2272756 (170 / C) | [6 empty] | 1 | [10 empty] | 4 |  | 4 |  | 8 |  |  | Last sampled for Nitrate and VOCs in 2020, and TC in 07/20. System has no record of Lead/Copper or Rads sampling history. | Sample for annual Nitrate, quarterly VOCs, quarterly Rads, monthly TC, and Lead/Copper in first and second half of 2022. | N/A
LATIMER | No RMW | 11 | MOOSE RIVER RV PARK / AK2249009 (100 / NC) | [6 empty] | 2 | [17 empty] | Last sample for Nitrate in 2019. | Collect annual nitrate samples for each active well. | N/A
BJORKMAN | DEC | 17 | NANWALEK / AK2240464 (281 / C) | [6 empty] | 1 |  |  |  |  | 3 |  | 3 |  |  | 2 |  |  | 1 |  |  | 2 |  | Last sampled Nitrate, VOCs, and DBPs in 2020. Last sample for total coliform and distribution chlorine residual was collected October 2021. | Sample for annual Nitrate, annual VOC, and DBPs quarterly (Feb, May, Aug, Nov). Sample monthly for total coliform and measure & record chlorine residual at the same time and place. | N/A
MORRISON | YKHC | 22 | NATIVE VILLAGE OF SLEETMUTE / AK2271874 (82 / C) |  | 1 |  |  |  |  | 1 | [9 empty] | 4 | [7 empty] | System violated SWTR in March 2022. Has not sampled for Nitrate since 2020. Has not sampled for DBPs since 2017 and is on annual schedule. | Submit monthly operator report meeting all requirements. Sample for annual Nitrate ASAP. Sample for DBPs in August 2022. | N/A
VANSANDT | DEC | 12 | NELSON LAGOON WATER SYSTEM / AK2260804 (60 / C) | [6 empty] | 1 | [9 empty] | 1 | 1 |  | 1 |  |  |  |  | Last sampled for Nitrate, HAA5, and VOCs in 2020. Only collected 1 of the 5 required Lead/Copper samples in May 2019. | In 2022, monitor for annual Nitrate, HAA5, VOCS and every-3-year Lead and Copper 5-sample set. | N/A
MORRISON | YKHC | 20 | NEWTOK WATER SYSTEM / AK2271431 (435 / C) | [8 empty] | 3 | [7 empty] | 1 | 1 |  |  |  |  | 2 |  | Exceeded DBP MCL (TTHM & HAA5) since 3rd quarter 2021. Last sampled for DBPs during 3rd quarter 2021. Did not sample for Lead & Copper in 2021. Did not submit CCR Certification for 2019 or 2020 CCRs. | Reduce DBP (TTHM & HAA5) LRAA. Sample for DBPs (TTHM & HAA5) in September 2022. Sample for Lead & Copper in 2022. Submit CCR Certification for 2021 CCR by 10/01/2022. | N/A
MORRISON | YKHC | 19 | NIGHTMUTE NEW WATERING POINT / AK2271721 (243 / C) | [14 empty] | 1 |  |  | 13 | [6 empty] | No triggered source sample was collected following a TC positive in 2019. No Lead & Copper samples collected since 2007 (annual schedule). | Sample for Lead & Copper in 2022. Sample the source for total coliform. | N/A
VANSANDT | No RMW | 19 | NINA NICHOLSON SUBDIVISION / AK2263010 (31 / C) | [6 empty] | 1 | [8 empty] | 1 |  | 1 |  | 1 |  |  | 7 |  | Last sample Nitrate in 2020, Arsenic in 2009, VOCs in 2015, and Lead & Copper in 2016. No CCR or certification submitted since 2019. | Sample for annual Nitrate, Arsenic, VOCs, and Lead/Copper. Complete & distribute 2021 and submit certification to DEC. | N/A
VANSANDT | DEC | 25 | NONDALTON / AK2260260 (205 / C) | [6 empty] | 1 | [6 empty] | 14 |  | 1 | 1 | 2 |  | 1 |  |  | 1 |  | PWS does not have current water operator dedicated to PWS operations since 2021. Struggles to meet M&R requirements. Last adequate MOR submitted in May 2021. Last Nitrate in TTHM & HAA5, Arsenic, and VOCs in 2020, and last CCR report submitted in 2020. | In 2022, monitor for overdue nitrate, TTHM & HAA5, Arsenic, VOCs and submit CCR. | N/A
ZELLMER | YKHC | 38 | NUNAM IQUA WATER SYSTEM / AK2270207 (213 / C) | [6 empty] | 3 |  | 2 |  |  |  |  | 3 |  |  | 3 | 1 |  | 2 |  |  |  |  | Last sampled for Nitrate in 2018, VOCs in 2019, Lead/Copper in 2017. Quarterly DBP TT violations being accrued due to not collecting all required monthly TOC/Alkalinity samples. E.coli (LT2) sampling is incomplete. | Sample for annual Nitrate, VOCs, and Lead/Copper. Collect all monthly TOC/Alkalinity samples. Complete E.coli (LT2) raw water monitoring per approved sampling plan. | PWS's Inline turbidimeter is not functioning. Attempts to bring the turbidimeter online with RMW assistance have been unsuccessful. System must collect grab samples and is unable to comply with continuous monitoring requirements.
MORRISON | YKHC | 11 | NUNAPITCHUK WATER SYSTEM / AK2260820 (496 / C) | [6 empty] | 1 | [9 empty] | 1 | [7 empty] | Last sampled for Nitrate in 2020 and DBPs in 2017. | Sample for Nitrate in 2022. Sample TTHM in 3rd quarter 2022. | N/A
VANSANDT | DEC | 16 | OLD HARBOR / AK2250061 (216 / C) | [6 empty] | 1 | [9 empty] | 2 | 5 |  | 1 |  |  |  |  | Last sampled for Nitrate, VOCs, and DBPs in 2020, and Lead/Copper in 2021. | Sample for annual Nitrate, DBPs, and VOCs. Collect Lead & Copper sample sets every six-months | N/A
MORRISON | YKHC | 14 | OLD KASIGLUK - AKIUK / AK2272752 (240 / C) | [5 empty] | 1 | [5 empty] | 5 |  |  | 1 |  | 1 | [7 empty] | System missed deadline to consult with the State, and has open corrective actions from a sanitary survey. Has not sampled for total coliform or distribution system chlorine residual since September 2021. | Sample for total coliform and distribution system chlorine residual. Consult with the State regarding deficiencies, develop corrective action plan. | N/A
MORRISON | YKHC | 57 | OSCARVILLE WATERING POINT / AK2270061 (75 / C) |  |  |  |  | 1 |  | 3 |  |  |  |  | 1 |  | 2 |  | 3 | 2 | 7 | 1 | 3 |  | 8 | 5 |  | Overdue for Nitrate, Arsenic, VOCs, IOCs, Rads, Lead/Copper. Has no history of DBP sampling and TC overdue as well. System does not submit the required MORs. No record of CCR completion for several years. | Sample for annual Nitrate, Arsenic VOCs, IOCs, Rads, Lead/Copper, DBPs, and monthly TC. Submit timely monthly operator reports. Complete and distribute 2021 CCR and submit certification to DEC. | System is on a long term BWN due to inadequate treatment.
MORRISON | YKHC | 15 | PILOT STATION WATER SYSTEM / AK2260163 (580 / C) | [5 empty] | 1 | 1 | [9 empty] | 1 | 2 | [6 empty] | Last sampled Nitrate in 2020, DBPs in 2020, and Lead/Copper in 2016. System has overdue Corrective Actions from sanitary survey. | Sample for annual Nitrate, DBPs in 3rd quarter, and Lead & Copper. Address outstanding sanitary survey deficiencies. | System is on a BWN since February 2021 due to inability to maintain adequate distribution system pressure.
BJORKMAN | No RMW | 24 | PIT BAR AND LIQUOR STORE / AK2240781 (250 / NC) | [6 empty] | 1 |  |  |  |  | 10 |  | 5 | [10 empty] | Last sample Nitrate in 2020 and total coliform (with same time/place chlorine residual) in April 2021. MORs are not being submitted as required. | Sample annual Nitrate and monthly total coliform (with same time and place chlorine residual). Submit MOR every month by the 10th of the following month. | N/A
MORRISON | YKHC | 51 | PLATINUM CITY WATER SYSTEM / AK2271059 (51 / C) |  |  |  |  | 1 | [6 empty] | 1 | [5 empty] | 20 | 1 | 5 | 4 |  | 10 |  | Classified as GU but does not filter or treat. Did not monitor for IOCs during 2011-2019 cycle, annual VOCs since 2012, did not apply for SOC monitoring waiver, missed RAD sampling between 2008-2016, overdue for CCRs and Certifications. Still needs to submit RTCR Sample Siting Plan. Has not sampled for lead/copper since 2005 and is on a 6 month schedule. | Install filtration/treatment. Monitor for IOC, VOC, Rads, Lead and Copper in 2022. Apply for 2020-2022 SOC Initial Waiver. Submit overdue CCRs and CCR Certification forms. Submit RTCR sample siting plan and monitor for total coliform monthly according to plan. | No WTP to meet GU/SWTR requirements, not filter or treat, and has been on BWN since 2014.
LITTLE | No RMW | 43 | QUIET CIRCLE APARTMENTS / AK2224476 (90 / C) | [7 empty] | 8 | [16 empty] | The system has been near or at the Arsenic MCL for years and placed on quarterly Arsenic monitoring in 2016. System only using well #2. Arsenic sample from well #2, collected May 2022 exceeded the MCL. | Install treatment to address the Arsenic MCL exceedance. | Construction contract to install POU treatment in place, POU components have been ordered. Construction is expected to be complete by August 12, 2022.
VANSANDT | No RMW | 11 | RED DOG INN / AK2260749 (145 / NC) | [6 empty] | 2 | [17 empty] | Last sample Nitrate in 2019. New owner in 2021. | Sample for annual Nitrate. | N/A
VANSANDT | DEC | 29 | SAINT GEORGE WATER SYSTEM / AK2260074 (65 / C) | [6 empty] | 4 | [10 empty] | 3 |  | 1 |  |  |  |  | Last sampled for Nitrate in 2017, LCR in 2006, VOCs in 2012, and total coliform in May 2022. | Sample for annual Nitrate, VOCs, Lead & Copper, and monthly total coliform. | N/A
VANSANDT | DEC | 11 | SAINT PAUL WATER SYSTEM / AK2260286 (380 / C) | [6 empty] | 1 |  |  |  |  | 1 |  |  |  |  | 2 | 1 | [6 empty] | Last sampled for annual Nitrate in 2020, DBPs in 2016, and Lead & Copper in 2016. Note that the LCR samples collected in March 2021 were not analyzed for compliance by the lab since PWS did not follow sampling protocols for first-draw samples. | Sample for annual Nitrate, DBPs (TTHM & HAA5), and Lead & Copper. | N/A
MORRISON | YKHC | 41 | SCAMMON BAY WATER SYSTEM / AK2270184 (637 / C) | [13 empty] | 36 |  |  |  | 2 | [6 empty] | Last sampled for Lead/Copper in 2015. Fails to comply with entry point chlorine reporting on MOR since September 2018. | Sample for Lead & Copper. Record entry point chlorine readings each day per month on MOR. | System is prone to freezing and experiences high water demand during the winter.
ELMORE | NSHC | 31 | SHISHMAREF WATER SYSTEM / AK2340484 (572 / C) | [8 empty] | 6 | [15 empty] | System has been exceeding the MCL for TTHM since 4th quarter 2020. | Collect set of DBPs that allow the LRAA for TTHM to be calculated below the MCL. | GAC filter media was not changed at the recommended frequency in 2021, which resulted in high TTHM levels. The GAC has since been changed and is on a regular schedule, so TTHM levels have started to come back down.
VANSANDT | No RMW | 13 | SOUTHEAST ALASKA LOGGING / AK2250427 (45 / NTNC) | [6 empty] | 1 | [6 empty] | 1 |  |  | 3 | 1 |  | 1 |  |  |  |  | Last sampled for Nitrate in 2020, VOCs in 2016, DBPs in 2008, and Lead & Copper in 2016. | Sample for annual Nitrate, VOCs, DBPs, and Lead & Copper. Submit MOR with adequate chlorine and turbidity data. | N/A
LATIMER | No RMW | 23 | STERLING HARBOR MENNONITE CHURCH / AK2249223 (100 / NC) | [6 empty] | 1 |  |  |  |  | 13 | [12 empty] | Last sampled for Nitrate in 2020 and total coliform December 2020. | Sample for annual Nitrate and monthly total coliform. | N/A
HARRIS | DEC | 84 | TATITLEK WATER SYSTEM / AK2291130 (95 / C) | [8 empty] | 16 | [15 empty] | System exceeding HAA5 LRAA MCL since 2015. | Collect set of DBPs that allow the LRAA for HAA5 to be calculated below the MCL. | DEC RMW & ANTHC were scheduled to complete a site visit to clean the raw water and treatment storage tanks. No indication this has occurred yet.
MORRISON | YKHC | 14 | TULUKSAK WATER SYSTEM / AK2270223 (373 / C) | [16 empty] | 6 | 1 |  |  |  |  | 2 | 1 | Last sampled for DBPs in 2016 and Lead & Copper in 2016. Did not submit CCR Certification form for 2019 or 2020 CCRs. Did not issue public notice for boil water notice in January 2021. | Sample DBPs in July 2022. Sample lead and copper between July and end of December 2022. Submit 2021 CCR Certification form.
ZELLMER | YKHC | 24 | TUNTUTULIAK WASHETERIA AND WATERING PT / AK2271211 (350 / C) | [5 empty] | 1 | 1 |  |  | 1 | [5 empty] | 1 |  | 3 |  | 1 |  |  |  |  | Last sampled Nitrate sample in 2020, VOCs in 2016, and Arsenic in 2020. Follow-up Lead & Copper corrosion control monitoring/steps have not been completed. System has three unresolved sanitary survey deficiencies. | Sample for annual Nitrate, Arsenic, and VOCs. Complete required Lead & Copper corrosion control monitoring/steps and/or collect satisfactory 1st half 2023 Lead & Copper samples. Address outstanding sanitary survey deficiencies. Collect an annual nitrate sample. | N/A
ZELLMER | BBAHC | 12 | TWIN HILLS WATER SYSTEM / AK2260032 (87 / C) | [6 empty] | 2 | [10 empty] | 1 | [6 empty] | Last sampled for Nitrate in 2019 and Lead/Copper in 2017. | Sample for annual Nitrate and Lead/Copper. | N/A
ELMORE | NSHC | 110 | UNALAKLEET CITY WATER SUPPLY / AK2340387 (757 / C) |  | 11 | [22 empty] | System has been out of compliance with turbidity TT since July 2021 and is on a BWN. | Submit monthly operator report showing turbidity, entry point chlorine residual, and distribution chlorine residual requirements are being met. | DEC granted construction approval, for WTP improvements to help with turbidity spikes during off-hours. Construction has been delayed due to COVID 19. Additionally, a project to develop a groundwater source was granted construction approval 12/2021. Construction expected to start Summer 2022 and end in 2023.
ELMORE | TCC | 34 | VENETIE WATER SYSTEM / AK2300248 (181 / C) | [6 empty] | 1 | [6 empty] | 19 |  |  | 7 | 1 |  | 1 |  |  |  |  | Last sampled for Nitrate, DBPs, and VOCs in 2020, and Lead & Copper in 2017. Last submitted complete MOR in November 2021 for SW entry point chlorine residual and turbidity monitoring, and hasn't done distribution system chlorine residual monitoring since October 2020. On a BWN and operated without an operator for several months. | Sample for annual Nitrate, DBPs, VOCs, Lead & Copper. Submit a complete MOR, including turbidity and entry point chlorine residual data. | Project approved June 2020 to construct a new WTP/washeteria building and move the existing water treatment system to the new building. SS deficiencies are scheduled to be addressed by the project. Construction was postponed due to pandemic. Constructing has restarted and new WTP completion is scheduled for fall 2022.
VANSANDT | No RMW | 11 | VFW KODIAK POST #7056 / AK2250493 (46 / NC) | [5 empty] | 1 | [7 empty] | 2 | [10 empty] | System did not complete or notify DEC of corrective actions for the 2017 survey deficiencies. PWS does not consistently submit monthly operator reports (MORs) with adequate turbidity and chlorine data. | Address outstanding sanitary survey deficiencies: provide corrective action plan with timelines and notify DEC of any corrective actions completed. Submit MORs consistently with adequate monitoring data. | N/A
SHARP | NSHC | 36 | WALES WATER SYSTEM / AK2340191 (173 / C) | [10 empty] | 6 | [10 empty] | 3 | 2 |  | Currently exceeding RAA MCL for Uranium following the 2nd quarter 2020 results. Exceeded the RAA MCL intermittently since 2011. System failed to submit 2020 CCR and certification form. | Sample Uranium quarterly and address the Uranium RAA MCL. Complete and distribute 2021 CCR and submit certification to DEC. | Construction approval for new surface water source (infiltration gallery) and a cartridge filtration WTP. Construction was delayed due to COVID but is currently underway with expected completion in 2023.

## Definitions
DW Program Staff Contact Information
Mat-Su = Office located in Wasilla, AK. Covers the Mat-Su area. Staff: Amy Hill (Program Coordinator) 376-1861, Tee Little (EPS) 376‐1860, Darryl Gillespie (EPS) 376-1824, Charity Bare (Engineering Supervisor) 262-3400
Northern = Office located in Fairbanks, AK. Covers the Northern Alaska PWSs. Staff: Marci Irwin (Program Coordinator) 451-2168, Feyne Elmore (EPS) 451‐2169, Michael Sharp (EPS) 451-2178, Miki Smelter (EPS) 451-2231, Johnny Mendez (Engineering Supervisor) 451-5193
Southcentral / ANC= Office located in Anchorage, AK. Covers Anchorage bowl, Bethel/YK Delta, Dillingham area, Aleutian Chain, Pribilof and Kodiak Island area PWSs. Staff: Heather Murray (Program Coordinator) 269-7619, Elizabeth Nakanishi (EPS) 269‐7517, Kristine Crippen (EPS) 269‐7521, Doug Zellmer (EPS) 269-3068, Leslie Morrison (EPS) 269-7518, Leah Van Sandt (EPS) 269-7653, Roy Robertson (Engineering Supervisor) 269‐7631.
Kenai / Southeast = Office located in Soldotna, AK. Covers the Kenai Peninsula and Southeast area. Staff: Amy Hill (Program Coordinator) 376-1861, Jamie Bjorkman (EPS) 262‐3423, James Latimer (EPS) 262-3410, Christina Harris (EPS) 262-3420, Charity Bare (Engineering Supervisor) 262-3400
GENERAL ETT QUESTIONS: Jeanine Vance (EPM) 269-2007, Karen Garland (EPS) 451-2137, Eric Burg (EPS) 262-3401
Link to DW Program Directory (contact information) | http://dec.alaska.gov/eh/dw/contact/
Resource Links
Best Practices (BP) Score
The Best Practices (BP) Score is criteria for assessing operations and maintenance capacity of rural water and wastewater utilities. Used for determining eligibility and prioritization for community sanitation projects. STATEMENT FROM BP SCORE WEBSITE: The most effective way to increase a community's chance of receiving project funding is by improving their Best Practice score.
Link to BP Webpage | https://dec.alaska.gov/water/technical-assistance-and-financing/best-practices/
Alaska Community Database Online
The Community Database Online is a portal for information resources about Alaskan Communities and Places of Interest in an interactive format.
Link to Database Online Webpage | https://dcra-cdo-dcced.opendata.arcgis.com/
Alaska Community Photo Library
The Community Photo Library offers a glimpse into Alaska's communities and lifestyle by providing images of places, people, cultural events, public facilities, landscapes, and other dimensions of community life.
Link to Photo Library Webpage | https://www.commerce.alaska.gov/dcra/dcrarepoext/Pages/PhotoLibrary.aspx
Remote Maintenance Worker (RMW) Service Area Abbreviations
BBAHC= Bristol Bay area Health Corporation | Maniilaq= Maniilaq Health Corporation | TCC= Tanana Chiefs Conference
DEC= AK Department of Environmental Conservation | NSHC= Norton Sound Health Corporation | YKHC= Yukon Kuskokwim Health Corporation
No‐RMW= Not served by an RMW Program
Link to RMW Directory | https://dec.alaska.gov/media/23045/rmw-directory.pdf
Definitions
AL= Action Level | HAA5= Haloacetic Acids (Stage 1 Rule) | Rads= Radionuclides Rule
ANTHC= Alaska Native Tribal Health Consortium | IFE= Individual Filter Effluent | RMW= Remote Maintenance Worker
BACTI or t‐Coli = Total Coliform Sample | IOC= Inorganic Chemicals | RTC= Return to compliance (fall off ETT list)
BWN= Boil Water Notice | LCR= Lead/Copper Rule | RTCR= Revised Total Coliform Rule
CCR= Consumer Confidence Report | LRAA= Locational Running Annual Average (Stage 2) | SOC= Synthetic Organic Chemicals
CFE= Combined Filter Effluent | LT1= Long Term 1 Enhanced Surface Water Treatment Rule | Surface Water (SW)= Surface Water violations Surface Water Treatment Rules (SWTR, LT1, and LT2)
DPB= Disinfection by Products | LT2= Long Term 2 Enhanced Surface Water Treatment Rule
DSRD= Distribution Chlorine Residual | M/R= Monitoring and Reporting (type of violation) | TC= Total Coliform
EHO= Environmental Health Officer | MCL= Maximum Contaminant Level (type of violation) | TOC= Total Organic Carbon
EP= Entry Point | MOR= Monthly operator report | TCR= Total Coliform Rule (Also called Bacti)
EPA= Environmental Protection Agency | NOV= Notice of Violation | TT= Treatment Technique (violation)
EPRD= Entry Point Residual Distribution | OCC= Optimal corrosion control (Pb/Cu Rule) | TTHM= Total Trihalomethanes (Stage 1 Rule)
ETT= Enforcement Targeting Tool | PER= Preliminary Engineering Report | VOC= Volatile Organic Chemicals
FANLs= Facility Analyte Level (refers to SW/Stage 1 monitoring requirements) | PN= Public Notice | VSW= Village Safe Water
GAC= Granular Activated Carbon | PWS= Public Water System | WTP= Water Treatment Plant
GWUDI= Groundwater under the direct influence of surface water | RAA= Running Annual Average