## July 2025 ETT List
July 2025 ETT List
Note: Column titled "Est. New ETT Score" is the estimated new score based on the violations that have Returned to Compliance (RTCd) during the Quarter. Please note that this score will likely change on the next quarter's list due to further violations being generated. Comments submitted by Drinking Water Program staff on August 11, 2025.
Staff | RMW | Est. New ETT Score | System Information | 10 Point |  |  | 5 Point | [7 empty] | 1 Point | [11 empty] | General Comments | How to Return to Compliance | Known Hardware Problems
|  |  |  | SW | GWR | Nitrate | RTCR | SW | GWR | Nitrate | Arsenic | DBP | LCR | Rads | RTCR | SW | GWR | Arsenic | DBP | LCR | IOC | VOC | SOC | Rads | CCR | PN
NAKANISHI | YKHC | 105 | ALAKANUK WATER SYSTEM / AK2270362 (570 / C) | [8 empty] | 1 | 1 |  |  | 61 |  |  | 25 | 3 |  |  | 1 |  |  |  | LSLI not completed in 2024. Last complete Monthly Operating report was April 2024. Last LT2 samples collected in 2021. Lead/Copper sampling overdue since 2015 (partial set of Lead/copper samples completed in 2025), TOC raw not sampled since 2021. Alkalinity/TOC treated not sampled since 2016. | DEC is completing the LSLI. Submit their SOC waiver application, complete the Lead/Copper sample set, collect LT2, DBP's TOC treated and TOC/ALK Raw samples. | None known
SHARP | TCC | 17 | ALLAKAKET PUBLIC WATER SYSTEM / AK2300816 (135 / C) | [5 empty] | 1 | [10 empty] | 3 |  |  | 5 |  | 1 |  | Did not submit 2023 CCR certification or lead consumer notice cert. (2022 & 2023). PWS did not collect enough Lead/Copper samples during their July-Dec. 2024 sample set nor have they completed the 2023-2025 SOC waiver. Also needs to address sanitary survey deficiencies from 2023 survey. | Complete 2024 CCR certification process, lead consumer notice certification, correct outstanding survey deficiencies, complete 2023-2025 SOC waiver application, and collect a complete set of lead/copper samples during next sampling event. | No known hardware issues related to violations.
HOYT | No RMW | 11 | ALPINE INN / AK2244808 (30 / NC) |  |  |  | 1 | [7 empty] | 1 | [11 empty] | System has not completed seasonal start-up procedures or certification for 2024 and 2025 season. | Submit SSUP and certification for 2025 season. | None known
LATIMER | DEC | 38 | ANGOON PUBLIC WATER / AK2130017 (450 / C) | [9 empty] | 1 |  | 5 | 8 |  |  | 15 | 2 | [5 empty] | 1 | On BWN since April 2022. Not meeting sampling & reporting requirements. Operator is working on certification & system recently started training a 2nd operator. Admin continues to express interest in regaining compliance. | Operator needs to pass the planned August op-cert exam, need to collect monthly coliform & other routine samples & submit daily EP residuals along with turbidity on time. | Disinfectant and turbidity monitoring and dosing equipment needs repair or replacement, plus spare parts/units.
SHARP | TCC | 12 | ARCTIC VILLAGE WATER SYSTEM / AK2300222 (175 / C) | [12 empty] | 11 | [6 empty] | 1 |  |  |  | System has not submitted a complete monthly operator report with adequate entry point chlorine and turbidity readings since September 2024. PWS did not complete 2023-2025 SOC waiver and has not collected a SOC sample during 2025. | Submit complete monthly operator reports on time and either complete the SOC waiver or begin sampling quarterly for SOC. | No known hardware issues related to violations.
LATIMER | No RMW | 11 | BAY VIEW TRAILER COURT / AK2241101 (51 / C) | [6 empty] | 1 |  |  | 1 | [6 empty] | 1 | [6 empty] | Owner indicated nitrate sample to be collected week of Aug 11, 2025. Reminded owner of LSLI requirements, and they indicated planning to complete the LSLI soon. | Complete LSLI | None known
SHARP | TCC | 30 | CHALKYITSIK VILLAGE WATER / AK2300183 (76 / C) | [8 empty] | 3 |  |  |  | 8 |  |  | 1 | 2 | [6 empty] | System accrued monthly operator report violations due to operator turnover in 2024 and 2025; last completed report received was August 2024. Currently exceeding HAA5 MCL. System did not sample for lead/copper in 2024. System did not complete OEL for 3rd quarter 2024. | System must begin to submit complete monthly operator reports on time, collect overdue Lead/Copper samples, continue collecting quarterly DBPs samples, and optimize treatment to reduce DBP levels. | Adequate change out frequency would reduce chances of DBP exceedance. DEC approved plans for a water treatment plant project intended to reduce DBPs. The new WST is in operation, GAC upgrades are not yet constructed. Scope of project has been reduced due to funding but the CT contactor tanks and new GAC media are still planned.
POEPPEL | YKHC | 13 | CITY OF HOOPER BAY / AK2270312 (1200 / C) | [5 empty] | 1 | [9 empty] | 2 | 1 | [6 empty] | Overdue for DBPs and Lead/Copper. EPS will continue to reach out to the system about their overdue corrective actions. | Sample for DBPs between October and December 2025. Address the outstanding corrective actions from the 2023 sanitary survey. Sample for Lead/Copper. | None known
DAVIS | BBAHC | 16 | CLARKS POINT WATER SYSTEM / AK2260202 (128 / C) | [9 empty] | 1 |  |  |  | 1 |  |  | 7 | [6 empty] | PWS has not completed LSLI. Overdue for a triggered source sample after recent TC positive. Submitted Lead/Copper samples 2/12/25; however, 2 out of 10 samples were invalid, and make-up samples were collected late. Since collected past the January - June monitoring period, they will go towards the 10-sample set schedule for July-December. The OP plans to collect the remaining 8 by September 1, 2025. | Complete LSLI. Collect a TG TC sample. Collect 8 Lead/Copper samples for monitoring period July to December 2025. | None known
SHARP | NSHC | 106 | DIOMEDE JOINT UTILITIES / AK2340141 (184 / C) |  |  | 2 |  |  |  |  | 10 |  |  |  |  | 32 | [10 empty] | Diomede continues to exceed the RAA MCL for Arsenic and Nitrate due to poor source quality. System has continued to accrue monthly operator report violations since August 2023 for failure to submit complete operator reports. | Needs to install and optimize treatment to address Nitrate, Arsenic, and SWTR. Submit complete monthly operator reports and continue to send chemical samples in whenever flights are available or during site visits from regional partners. | A new WTP is currently under construction to meet SWTR, Nitrate and arsenic MCLs, and corrosion control. A temporary WTP was placed into operation 2024 but did not receive approval because it had not met conditions of operation. Permanent WTP is expected to begin operation summer 2025. Water in storage tank that was treated with temp plant is planned to be recirculated through new WTP to treat for microbials, arsenic and nitrate before winter.
DAVIS | No RMW | 11 | EKUK FISHERIES / AK2261208 (150 / NC) | [5 empty] | 1 | 1 | [16 empty] | Significant Deficiency corrections from 2021 are overdue. No annual Nitrate samples since 2023. | Correct significant deficiencies: fix the gap between sanitary seal and well casing, and well casing vent. Collect annual Nitrate during the current operating season. | None known
AGUE | YKHC | 29 | EMMONAK WATER SYSTEM / AK2270299 (820 / C) |  |  |  | 1 | [5 empty] | 1 | [5 empty] | 12 | 2 |  | 1 | 1 |  |  |  | Operational Evaluation Level Reports and Level 1 Assessment from 2023 are overdue. Last collected TOC/Alkalinity samples (due monthly) in June 2024. System did not complete LSLI or submit SOC monitoring waiver renewal for 2023-2025 period. Lead/Copper and VOC samples overdue. | Collect TOC/alkalinity, Lead/Copper, and VOC samples. Complete overdue reports and LSLI, and submit SOC monitoring waiver. | None known
MORRISON | No RMW | 29 | FOREST PARK TC / AK2210794 (175 / C) | [5 empty] | 2 | 1 |  |  | 1 | [6 empty] | 2 |  | 2 |  |  |  |  | PWS has violations for not correcting significant deficiencies from past surveys; reportedly does not have the financial capacity to address the deficiencies. Last sampled for nitrate in 2023. Did not submit LSLI. Did not sample for Lead/Copper in 2024. Has not sampled for VOC since 2Q 2024 and is on quarterly sampling schedule. | System must submit engineering plans to correct deficiencies. Sample for nitrate, Lead/Copper and VOC ASAP. Submit LSLI. | None known
POEPPEL | YKHC | 47 | GRAYLING WATER SYSTEM / AK2280066 (195 / C) | 1 |  |  | 1 | [5 empty] | 1 |  |  | 25 |  |  |  | 1 | [6 empty] | System is only collecting one LT2 sample per month. ANTHC obtained PER funding to determine the best alternative for repair/replacement of the storage tank. | Address the remaining sanitary defects. Submit monthly operator reports that meet operating requirements. Collect LT2 samples according to LT2 sample plan. | System on long-term BWN until the PWS submits monthly operator reports and consistently samples. Storage tank is aged and too small to meet community needs.
NAKANISHI | YKHC | 11 | HOLY CROSS WATER SYSTEM / AK2280074 (182 / C) | [9 empty] | 1 | [6 empty] | 1 | [6 empty] | LSLI not completed in 2024. | DEC is completing the LSLI. | None known
SHARP | TCC | 19 | HUGHES PUBLIC WATER SUPPLY / AK2300272 (107 / C) | [12 empty] | 10 |  |  | 4 | 3 | [6 empty] | PWS overdue for lead consumer notice certification since 2022. Overdue on DBP sampling. PWS is submitting incomplete monthly operator reports (MORs), has not submitted completed MOR since October 2024. Hasn't reported distribution chlorine residual since December 2024. | Submit complete monthly operator report, complete outstanding lead consumer notice process, report a detectable chlorine residual with next TCR sample, and collect DBP sample during December 2025. | No known hardware issues related to violations.
HOYT | DEC | 21 | KAKE MUNICIPAL WATER / AK2130083 (415 / C) | [8 empty] | 4 | [14 empty] | System is trying to perform operational changes to lower values. Operator is working with RMW to find a solution for exceedances. Treatment plant upgrades may be needed. | Collect set of DBP samples that allows the LRAA to be calculated below the MCL. | None known
CAHILL | No RMW | 22 | KING FOR A DAY / AK2299036 (53 / NC) |  |  |  | 2 |  |  | 1 |  |  |  |  | 5 | [11 empty] | PWS did not complete seasonal startup procedures for 2023 - 2025. Last TC and Nitrate sample results from 2023. Certified letter sent when PWS moved to monthly TC due to # of violations, letter not picked up. | Submit Nitrate sample and monthly Total Coliform samples. Complete and submit 2026 season SSUP. Sanitary Survey due in 2026. | None known
HOYT | DEC | 99 | KLAWOCK / AK2120169 (904 / C) | [8 empty] | 19 | [14 empty] | System made repairs to their WST and installed a pax mixer in hopes to decrease their DBP levels. System is looking for funding to replace anthracite in all four filters at the WTP. | Collect set of DBP samples that allows for the LRAA to fall below the MCL for HAA5. | None known
SHARP | No RMW | 99 | KOTZEBUE MUN. WATER SYSTEM / AK2340060 (3234 / C) | [8 empty] | 19 | [14 empty] | System has exceeded the TTHM MCL since 2019 and the HAA5 LRAA since 3rd quarter 2023. | System needs to optimize their treatment system to increase DBP precursor removal and reduce DBP levels. | Monitoring of new WTP will continue throughout the interim operation period (extended to January 2026). DBP precursor removal data is to be analyzed by the design engineering firm to improve DBP results. Long term fixes are being designed for implementation this spring and include possibly installing greensand filtration pre-treatment; this may also have an effect on DBP precursor removal.
AGUE | YKHC | 29 | KWETHLUK NEW PIPED WATER SYSTEM / AK2272017 (760 / C) | [8 empty] | 5 | [14 empty] | TOC removal ratio for this conventional filtration system has been below 1.00 since February 2024. Samples collected in 2025 for both TOC removal met requirements, but the LRAA is still out of compliance. | Continue collecting monthly TOC and quarterly DBP samples. | None known
NAKANISHI | No RMW | 12 | LKSD NIGHTMUTE HS & ELEM / AK2271261 (259 / NTNC) | [12 empty] | 10 | [10 empty] | No LT2 samples collected since 2/14/2024 | Sample for LT2 | None known
BARNES | BBAHC | 11 | MANOKOTAK WATER SYSTEM / AK2260090 (293 / C) | [16 empty] | 1 |  | 1 | 5 |  |  |  | Last Lead/Copper sample 2024, last VOC since 2013. System has not submitted SOC waiver or sampled quarterly for SOC. | Collect VOC and SOC samples and collect a Lead/Copper sample set. | None known
KEIM | TCC | 12 | MINTO COMMUNITY WATER SYSTEM / AK2300159 (205 / C) | [5 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [6 empty] | PWS hasn't completed corrective actions from 2023 sanitary survey; bolt holes in the Pumphouse well sanitary seal must be sealed. PWS hasn't completed and submitted initial LSLI, due 10/16/2024. | PWS must seal the Pumphouse well and provide documentation, and submit initial LSLI. | No known hardware issues related to violations.
AGUE | YKHC | 12 | MOUNTAIN VILLAGE WATER SYSTEM / AK2270150 (850 / C) | [5 empty] | 1 | [8 empty] | 1 | 2 | 1 | 1 | [5 empty] | System has not collected a fourth quarterly arsenic sample following an exceedance in 2024. Overdue for Inorganics sampling at one of its treatment plants (TP004) since 2012, DBPs since 2022, and Lead/Copper since 2021. There are open significant deficiencies identified in the 2022 sanitary survey. | Collect arsenic, IOC, DBP, and Lead/Copper samples. Address significant deficiencies. | Lower loop of distribution system does not maintain pressure above 20 PSI and is on long-term BWN. Open significant deficiencies from 2022 survey include: improperly abandoned well within 200' of an active well, issues with the caps or seals on 2 active wells, no backflow prevention on the water haul point, and a hose that is not NSF-certified at the water haul point.
HOYT | DEC | 33 | NANWALEK / AK2240464 (281 / C) | [11 empty] | 10 | 11 |  |  | 8 | [6 empty] | 1 | On BWN since February 2025. Operator has not completed operator certification. Routine sampling is not being completed. ARWA visiting system mid-August to work with operator. | Complete all routine sampling and submit completed monthly operator reports on time. Meet operator certification requirements. | None known
NAKANISHI | YKHC | 17 | NAPASKIAK WEST WATER SYSTEM / AK2260139 (200 / C) | [5 empty] | 2 | [9 empty] | 1 | 1 | [6 empty] | DBP's and LCR overdue since 2023, GWR TT violations overdue since 4/2024 | Work with DEC to resolve deficiencies, sample for DBP's and Lead/Copper. | None known
AGUE | YKHC | 12 | NIGHTMUTE NEW WATERING POINT / AK2271721 (243 / C) |  |  |  | 1 |  | 1 | [17 empty] | PWS has open significant deficiencies and sanitary defects from a sanitary survey and Level 1 Assessment. A single check valve was installed on the watering point in May 2025, but it was determined that this is not adequate backflow prevention and must be replaced. | Correct sanitary defects and significant deficiencies. | The watering point hose is not NSF-certified, is long enough that it is a high-touch point, and does not have adequate backflow protection.
DAVIS | DEC | 26 | NONDALTON / AK2260260 (205 / C) | 2 | [14 empty] | 3 | [7 empty] | TT violations for not meeting EP chlorine. No annual DBP sample collected since 2020. | Collect annual DBP in August and submit MOR that meets all requirements. | None known
CAHILL | No RMW | 13 | PALMER LIFEWAYS DAYCARE / AK2226055 (56 / NTNC) | [7 empty] | 2 | [6 empty] | 1 | [8 empty] | PWS continues to have high Arsenic, Conditional Approval to Construct granted 02/18/25 for installation of POU treatment. | Submit Arsenic sample below the MCL after receiving approval to operate Arsenic treatment system. | PWS plans to install POU treatment. Engineering construction approval has been granted.
NAKANISHI | No RMW | 12 | PETERS CREEK TERRACE / AK2211473 (70 / C) | [9 empty] | 1 | [6 empty] | 3 | [6 empty] | LSLI not completed in 2024, Lead/Copper samples last collected in 2017 . | Complete LSLI, sample for Lead/Copper. | None known
BARNES | YKHC | 15 | PLATINUM CITY WATER SYSTEM / AK2271059 (51 / C) |  |  |  |  | 1 | [6 empty] | 1 | [6 empty] | 4 |  |  |  |  | System does not meet applicable water treatment and filtration requirements. PWS does not have RTCR sample siting plan on file. System has not collected valid VOC sample since 2012. | System needs to collect VOC sample in 2025 and submit a RTCR sample siting plan. | System does not filter.
KEIM | TCC | 13 | RUBY WATER SYSTEM / AK2360866 (215 / C) | [15 empty] | 11 | 2 1 | [6 empty] | PWS hasn't submitted a distribution chlorine sample since December 2023. PWS didn't follow proper sampling protocol for 2024 lead/copper samples so could not be used for compliance. | Submit distribution chlorine sample at the same time and place as monthly TCR sample. Collect lead/copper samples in 2025. | No known hardware issues related to violations.
LATIMER | No RMW | 14 | S & S CENTER / AK2244719 (54 / NTNC) | [9 empty] | 1 | [6 empty] | 3 |  | 1 |  |  |  |  | Per call with owner/operator, overdue sampling (Pb/CU & VOC) will be completed by August 15, and resent LSLI info, which we discussed & he plans to complete asap. | Needs to collect lead/copper and VOC samples, and to complete LSLI. | None known
POEPPEL | DEC | 14 | SAINT GEORGE WATER SYSTEM / AK2260074 (65 / C) | [5 empty] | 1 | [10 empty] | 4 | [6 empty] | Overdue for Lead/Copper samples, last sampled in 2013. System has open significant deficiencies from 2021. | Sample for Lead/Copper. Address the outstanding corrective actions from the 2021 sanitary survey. | Water storage tank is unstable/failing.
GILLESPIE | No RMW | 36 | SET FREE ALASKA SNODGRASS / AK2220483 (47 / NTNC) | [7 empty] | 7 | [15 empty] | Currently exceeding Arsenic MCL. | PWS can return to compliance by testing below the Arsenic MCL. | System needs to install an Arsenic Treatment system in order to be able to return to compliance. Request for Construction Approval has been submitted by design engineer for installation of Point of Use devices and is going through the engineering review process.
CAHILL | No RMW | 14 | SHEENA MAY ESTATES / AK2224337 (74 / C) | [7 empty] | 2 | [6 empty] | 1 |  |  | 1 | [5 empty] | PWS blends two sources to help mitigate high Arsenic. Arsenic sample collected in 1st quarter 2024 collected from incorrect sample point. RAA for 2024 = .011 Mg/L | PWS can return to compliance by testing below the Arsenic MCL - blending could need adjustment. | None known
NAKANISHI | No RMW | 12 | SNOWCREST VIEW SOUTH / AK2210891 (25 / C) | [9 empty] | 1 | [6 empty] | 3 |  |  | 1 |  | 2 |  | CCR overdue from 2024, SOC waiver needed for 2023-2025. LSLI not completed in 2024. Lead consumer notification overdue from 2023 and 2024. | Complete CCR, SOC waiver application, two 2 Lead Consumer Notifications, and LSLI. | None known
NAKANISHI | YKHC | 16 | ST. MARYS WATER SYSTEM / AK2270176 (548 / C) | [12 empty] | 12 |  |  |  | 3 | [6 empty] | Insufficient turbidity readings reported since March 2024. Last Lead/Copper samples collected in 12/2023. | Collect 20 Lead/Copper samples every six months. Collect Turbidity readings every 4 hours while making water. | SCADA equipment non functional. WTP upgrade project and examining replacing SCADA equipment and is in PER stage.
LATIMER | No RMW | 11 | STERLING HARBOR MENNONITE CHURCH / AK2249223 (100 / NC) | [5 empty] | 1 | [7 empty] | 1 | [9 empty] | PWS needs to correct deficiencies or provide plan of action. Includes compromised electrical connection at wellhead & unapproved modification with added non-NSF softener. | Correct two sanitary survey deficiencies, or submit approved corrective action plan. | None known
HARRIS | No RMW | 12 | STERLING MOOSE RIVER MANOR / AK2249099 (33 / C) | [5 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [6 empty] | Overdue for LSLI and has unresolved significant deficiency. | Complete and submit the LSLI to DEC for approval. Address open CASS schedule items identified in the 2023 sanitary survey. | None known
KEIM | DEC | 17 | TAKOTNA WATER SYSTEM / AK2280163 (70 / C) | [12 empty] | 11 |  |  | 1 | 3 | [6 empty] | Has not submitted a complete monthly operator report since September 2024. PWS didn't submit annual DBP samples in August 2024 and has not collected annual lead/copper samples since 2021. | Submit complete monthly operator reports on time each month. PWS must sample for Lead/Copper in 2025 and DBPs in August 2025. | No known hardware issues related to violations.
HARRIS | DEC | 54 | TATITLEK WATER SYSTEM / AK2291130 (95 / C) | [8 empty] | 10 | [14 empty] | PWS has ongoing DBP exceedances and exceeding Lead at one location. System will continue to research water storage tank mixer and will continue to work with NUS/ANTHC/RMW on updating chlorine injection equipment. System to perform faucet replacement along with other renovations at Lead AL site by 9/1/2025 before school session begins. | Install treatment to reduce DBP's. Replace faucets where Lead is exceeding. | High Lead levels in distribution system. Chlorine injection equipment likely not operating smoothly. Water storage tank may be cold stratifying water into unmixed layers of highly concentrated CL2/DBP's.
NAKANISHI | YKHC | 16 | TULUKSAK WATER SYSTEM / AK2270223 (373 / C) | [5 empty] | 1 | 1 | [7 empty] | 1 |  | 3 |  | 1 |  |  |  |  | Significant deficiencies overdue since January 2025. Nitrate, VOCs and Arsenic samples collected on 8/7/2025, waiting for sample results to be submitted to DEC. | New WTP is in construction and should resolve all significant deficiencies. Additional Lead/Copper samples should be collected before 12/31/2025 to complete the sample set. | New WTP under construction and estimated to be completed by end of 2025.
AGUE | YKHC | 25 | TUNTUTULIAK WASHETERIA AND WATERING PT / AK2271211 (350 / C) | [5 empty] | 2 |  |  |  | 1 |  |  |  |  | 4 |  | 1 | [6 empty] | System last sampled for arsenic in 2020, has open violations for not conducting a desktop study or collecting water quality samples following a lead exceedance in 2016, and has open significant deficiencies from sanitary survey. | Collect arsenic and water quality parameter samples, and address significant deficiencies. | There is an inadequate air gap at the settling tank overflow drain, sources of contamination within minimum separation distance of the well, and improper drainage around the well.
DAVIS | BBAHC | 12 | TWIN HILLS WATER SYSTEM / AK2260032 (87 / C) | [6 empty] | 2 | [12 empty] | 1 |  |  |  | No annual Nitrate collected since 2022. SOC waiver application for the 2023-2025 monitoring period has not been submitted. | Collect annual Nitrate ASAP. Submit SOC waiver application or collect quarterly SOCs. | None known
LATIMER | DEC | 11 | TYONEK WATER SYSTEM / AK2240472 (206 / C) | [16 empty] | 6 | [6 empty] | PWS is overdue for Lead/Copper sampling, with last samples collected in 2018. | Collect set of 5 lead/copper samples during Aug/Sept, the warmest water months. | None known
SHARP | No RMW | 16 | VALLEY WATER COMPANY / AK2310926 (1575 / C) | [9 empty] | 2 | [6 empty] | 1 | [6 empty] | Violation for lack of corrosion control was issued in 2006 and PWS still does not have corrosion control. PWS hasn't completed and submitted initial LSLI, due 10/16/2024. | System must install corrosion control to address high copper levels and submit LSLI. | Valley Water does not have corrosion control treatment. PWS working to secure funding to implement some of the corrective actions in the Master Plan, including ones related to copper exceedance.
SHARP | NSHC | 52 | WALES WATER SYSTEM / AK2340191 (173 / C) | [6 empty] | 1 |  |  |  | 7 |  |  |  |  | 1 | 1 |  | 1 |  | 5 |  |  | System exceeds the RAA MCL for Uranium. System changed to a SW source in fall 2024, but had to resort to old GW source after new source was not producing enough water. Did not collect required nitrate, lead/copper, VOC, DBPs, or Rad samples in 2024 . | Collect all overdue samples New SW source and WTP should reduce Uranium levels once fully brought online. | New source and WTP to address Uranium MCL has been completed, but due to low production from the source, system has been operating with groundwater source during summer 2025 and not treating through new WTP. Still waiting for new source to be redeveloped before new WTP will be used again.
WHITEAKER | No RMW | 13 | WHITE BIRCH APARTMENTS / AK2313233 (72 / C) | [9 empty] | 1 |  |  |  | 1 |  |  | 3 | [6 empty] | System only collected 4 of 5 lead/copper samples in 2024 and has not since collected a complete set. System has not completed their initial LSLI. | System must submit a complete set of Lead/Copper samples and complete their LSLI. | No known hardware issues related to violations.
KEIM | No RMW | 12 | WILDWOOD HOMES LLC / AK2310853 (114 / C) | [5 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [6 empty] | PWS hasn't completed corrective actions from 2023 sanitary survey: modifications were made to the water system without prior approval from DEC and there is a separation distance issue between the well and wastewater lines. PWS didn't submit initial LSLI in 2024. | PWS must continue to work with DW engineering to complete sanitary survey corrective actions by submitting a complete waiver and other necessary information related to the modifications. PWS must complete and submit initial LSLI. | A separation distance waiver was submitted and reviewed as part of the project (sanitary survey deficiency), but the project has been incomplete since June 2023. They will also need approval from the Wastewater Program for the project; no wastewater approval request has been received.

## Definitions+Contact List
DW Program Staff Contact Information
Mat-Su = Office located in Wasilla, AK. Covers the Mat-Su area. Staff: Jamie Bjorkman (Program Coordinator) 262‐3423, Darryl Gillespie (EPS) 376-1849, Jessica Cahill (EPS) 376-1824, Charity Bare (Engineering Supervisor) 262-3400
Northern = Office located in Fairbanks, AK. Covers the Northern Alaska PWSs. Staff: Teslyn Hakala (Program Coordinator) 451-3038, Michael Sharp (EPS) 451-2178, Jenny Roberts (EPS) 451‐2137, Gretchen Keim (EPS) 451-2231, Johnny Mendez (Engineering Supervisor) 451-5193.
Southcentral / ANC= Office located in Anchorage, AK. Covers Anchorage bowl, Prudhoe Bay, Bethel/YK Delta, Dillingham area, Aleutian Chain, Pribilof and Kodiak Island area PWSs. Staff: Leslie Morrison (Program Coordinator) 269-7619, Elizabeth Nakanishi (EPS) 269‐7517, Kristine Poeppel (EPS) 269‐7521, Monica Ague (EPS) 269-7653, John Davis (EPS) 262-8201, Karis Barnes (EPS) 262-8204, Chris Pletnikoff (Engineering Supervisor) 269‐6064.
Kenai / Southeast = Office located in Soldotna, AK. Covers the Kenai Peninsula and Southeast area. Staff: Jamie Bjorkman (Program Coordinator) 262‐3423, James Latimer (EPS) 262-3410, Christina Harris (EPS) 262-3420, Emily Hoyt (EPS) 465-5108, Charity Bare (Engineering Supervisor) 262-3400
GENERAL ETT QUESTIONS: Jeanine Vance (EPM) 269-2007, Karen Garland (EPS) 269-7576, Eric Burg (EPS) 262-3401
Link to DW Program Directory (contact information) | http://dec.alaska.gov/eh/dw/contact/
Resource Links
Alaska Community Database Online
The Community Database Online is a portal for information resources about Alaskan Communities and Places of Interest in an interactive format.
Link to Database Online Webpage | https://dcra-cdo-dcced.opendata.arcgis.com/
Alaska Community Photo Library
The Community Photo Library offers a glimpse into Alaska's communities and lifestyle by providing images of places, people, cultural events, public facilities, landscapes, and other dimensions of community life.
Link to Photo Library Webpage | https://www.commerce.alaska.gov/dcra/admin/Photo
Remote Maintenance Worker (RMW) Service Area Abbreviations
BBAHC= Bristol Bay area Health Corporation | Maniilaq= Maniilaq Health Corporation | TCC= Tanana Chiefs Conference
DEC= AK Department of Environmental Conservation | NSHC= Norton Sound Health Corporation | YKHC= Yukon Kuskokwim Health Corporation
No‐RMW= Not served by an RMW Program
Link to RMW Directory | https://dec.alaska.gov/media/p4dntxhf/rmw-directory.pdf
Definitions
AL= Action Level | IFE= Individual Filter Effluent | RMW= Remote Maintenance Worker
ANTHC= Alaska Native Tribal Health Consortium | IOC= Inorganic Chemicals | RTC= Return to compliance (fall off ETT list)
BACTI or t‐Coli = Total Coliform Sample | LCR= Lead/Copper Rule | RTCR= Revised Total Coliform Rule
BWN= Boil Water Notice | LRAA= Locational Running Annual Average (Stage 2) | SOC= Synthetic Organic Chemicals
CCR= Consumer Confidence Report | LT1= Long Term 1 Enhanced Surface Water Treatment Rule | Surface Water (SW)= Surface Water violations Surface Water Treatment Rules (SWTR, LT1, and LT2)
CFE= Combined Filter Effluent | LT2= Long Term 2 Enhanced Surface Water Treatment Rule
DPB= Disinfection by Products | M/R= Monitoring and Reporting (type of violation) | SSUP = Seasonal Startup Procedures
DSRD= Distribution Chlorine Residual | MCL= Maximum Contaminant Level (type of violation) | TC= Total Coliform (also called Bacti)
EHO= Environmental Health Officer | MOR= Monthly operator report | TOC= Total Organic Carbon
EP= Entry Point | NOV= Notice of Violation | TCR= Total Coliform Rule
EPA= Environmental Protection Agency | OCC= Optimal corrosion control (Lead/Copper Rule) | TT= Treatment Technique (violation)
EPRD= Entry Point Residual Distribution | PE= Public Education (requirement under Lead/Copper Rule) | TTHM= Total Trihalomethanes (Stage 1 Rule)
ETT= Enforcement Targeting Tool | PER= Preliminary Engineering Report | VOC= Volatile Organic Chemicals
FANLs= Facility Analyte Level (refers to SW/DBP monitoring requirements) | PN= Public Notice | VSW= Village Safe Water
GAC= Granular Activated Carbon | PWS= Public Water System | WTP= Water Treatment Plant
GWUDI= Groundwater under the direct influence of surface water | RAA= Running Annual Average
HAA5= Haloacetic Acids (Stage 1 Rule) | Rads= Radionuclides Rule