## EU113_PTE
Table A-1. Potential to Emit Calculations - SO2 Emissions
EU ID | Description | Make/Model | SO2 Emission Factor |  | Maximum Rating |  | Allowable Annual Operation |  | Potential SO2 Emissions
113 | Circulating Bed Boiler1 | Babcock and Wilcox | 0.2 | lb/MMBtu2 | 295.6 | MMBtu/hr | 8760 | hr/yr | 258.9456 | tpy
Notes:
1 EU 113 is permitted to combust coal and up to 20 percent woody biomass (see Item 15 of Section 2.2 in Technical Analysis Report to Permit AQ0316MSS06 Revision 2). EU 113 is currently configured for coal firing only, and combusts subbituminous coal from Usibelli Coal Mine in Healy, AK.
2 SO2 emission factor per 40 CFR 60.42b(k)(1) and Conditions 36.1 and 61.2 of Permit AQ0316TVP03.
THIS TABLE APPEARS IN APPENDIX A OF REPORT, NOT MAIN BODY OF REPORT

## EU113_Actuals
Table A-2. Actual SO2 Emissions
EU ID | Description | Make/Model | CY2020 |  | CY2021 |  | Average Annual SO2 Emissions
113 | Circulating Bed Boiler | Babcock and Wilcox | 12.3 | tpy1 | 8.5 | tpy2 | 10.4 | tpy3
Notes:
1 CY 2020 SO2 emissions per totalized CEMS data for CY 2020 in Table 1 of University of Alaska Fairbanks Assessable Emissions Estimate for FY 2022, submitted to ADEC March 12, 2021.
2 CY 2021 SO2 emissions per totalized CEMS data for CY 2021 provided by University of Alaska Fairbanks.
3 SO2 emissions from 2022 are not included. EU 113 operated minimally between January and June 2022 as a result of an unplanned outage.
THIS TABLE APPEARS IN APPENDIX A OF REPORT, NOT MAIN BODY OF REPORT

## 2-Available
TABLE 2
Available SO2 Emission Control Technologies
Available SO2 Emission Control Technologies
WFGD
SDA
CDS
DSI
FBLI - Base Case

## 3 - Vendor Summary
TABLE 3
Summary of Vendor Responses
SO2 Control Technology
Vendor | WFGD | SDA | CDS | DSI
B&W | Declined to quote without funded study. | Declined to quote without funded study. | Declined to quote without funded study. | Declined to quote without funded study.
Andritz | Declined to quote - Andritz deemed this technology to be not economical. | Declined to quote - Andritz stated cost would be similar to CDS with lower SO2 removal rate. | Provided quote. | Declined to quote.
BPE | Declined to quote without funded study, uncertain of feasibility. | Quote not requested. | Provided quote. | Quote not requested.
Tri-Mer | Provided quote for a caustic soda wet scrubber. SCI determined this technology was not technically feasible. | Quote not requested. | Provided quotes for two types of CDS. | Provided quote.
GE | Unable to quote within timeframe for this report. | Quote not requested. | Quote not requested. | Quote not requested.
Wood Group | Declined to quote. | Declined to quote. | Quote not requested. | Quote not requested.
BACT Inc | Quote not requested. | Quote not requested. | Quote not requested. | Provided quote.
GEA | Declined to quote. | Declined to quote. | Quote not requested. | Quote not requested.

## 4-Technically_Feasible
TABLE 4
Technically Feasible SO2 Emission Control Technologies
Technically Feasible SO2 Emission Control Technologies
WFGD
CDS
DSI
FBLI - Base Case

## 5-Ranking
TABLE 5
Ranking of Technically Feasible SO2 Emission Control Technologies
Control Technology | Control Efficiency (pct.) | Emission Rate (lb/MMBtu) | SO2 Emissions (tpy) | Emissions Reduction (tpy)
WFGD | 95 | 0.01 | 12.945 | 245.955
CDS | 90 | 0.02 | 25.89 | 233.01
DSI - Tri-Mer system | 90 | 0.02 | 25.89 | 233.01
DSI - BACT, Inc system | 85 | 0.03 | 38.835 | 220.065
FBLI - Base Case | 0 | 0.2 | 258.9 | 0

## 6-CostEffective_Summary
TABLE 6
SO2 Cost-Effectiveness Summary
Control Technology | Total Capital Investment ($) | Total Annual Cost ($/year) | Emissions Reduction (tpy)1 | Cost-Effectiveness ($/ton SO2 avoided) | Incremental Cost-Effectiveness ($/ton SO2 avoided)2,3
WFGD | 52968345 | 7589888 | 245.955 | 30858.8482 | 141556.6628
CDS | 32505815 | 5757437 | 233.01 | 24708.9696 | 203589.8803
DSI - Tri-Mer system | 5794396 | 5193086 | 233.01 | 22286.9662 | 159993.82
DSI - BACT, Inc system | 11565826 | 3121966 | 220.065 | 14186.5631 | ~
FBLI - Base Case | ~ | ~ | 0 | ~ | ~
Notes:
1Emissions reductions are calculated in Table 5.
2Calculation of incremental cost-effectiveness: [TAC of technology - TAC of next lowest removal technology]
[Emission reduction of technology - emission reduction of next lowest removal technology]
3 The incremental cost-effectiveness values for CDS and the Tri-Mer DSI system are each calculated in comparison to the DSI system proposed by BACT.

## 7-Costs_ActualBasis
TABLE 7
Cost-Effectiveness Analysis Based on Actual Emissions
Control Technology | Control Efficiency (pct.) | SO2 Emissions (tpy)1 | Emissions Reduction (tpy) | Total Annual Cost ($/year) | Cost-Effectiveness ($/ton SO2 avoided)
WFGD | 95 | 0.52 | 9.88 | 7589888 | 768207.2874
CDS | 90 | 1.04 | 9.36 | 5757437 | 615110.7906
DSI - Tri-Mer system | 90 | 1.04 | 9.36 | 5193086 | 554816.8803
DSI - BACT, Inc system | 85 | 1.56 | 8.84 | 3121966 | 353163.5747
FBLI - Base Case | 0 | 10.4 | 0 | ~ | ~
Notes:
1The FBLI base case actual emission rate is the 12-month average of CY2020 and CY2021 SO2 emissions as calculated from the totalized CEMS data.