## 5-1 Available-SO2
Table 5-1. Summary of Available SO2 Emission Control Technology
Emission Unit |  | Available Emission Control Technology
1, 2 | Simple Cycle Gas Turbine | ULSD
Low Sulfur Fuel
Good Combustion Practices
5, 6 | Combined Cycle Gas Turbine | ULSD
LSR
Limited Operation
Good Combustion Practices
7 | Emergency Generator Engine | ULSD
Low Sulfur Fuel
Limited Operation
Good Combustion Practices
11, 12 | Propane-Fired Boiler | Low Sulfur Fuel
Good Combustion Practices

## 5-2 Feasible-SO2
Table 5-2. Summary of Technically Feasible SO2 Emission Control Technology
Emission Unit |  | Technically Feasible Control Technology
1, 2 | Simple Cycle Gas Turbine | ULSD
Low Sulfur Fuel
Good Combustion Practices
5, 6 | Combined Cycle Gas Turbine | ULSD
Good Combustion Practices and LSR
7 | Emergency Generator Engine | ULSD
Low Sulfur Fuel
Limited Operation
Good Combustion Practices
11, 12 | Propane-Fired Boiler | Low Sulfur Fuel
Good Combustion Practices

## 5-3 Ranking-SO2
Table 5-3. Ranking of Technically Feasible SO2 Emission Control Technology
Emission Unit |  | Emission Control Technology | Control Efficiency (pct.) | SO2 Emissions (tpy) | SO2 Emissions Reduction (tpy)
1 | Simple Cycle Turbine | ULSD (0.0015 wt. pct. S) | 99.7 | 4.4592 | 1481.9408
|  | Low Sulfur Fuel (0.05 wt. pct. S) | 90 | 148.64 | 1337.76
|  | Good Combustion Practices (0.50 wt. pct. S) (existing) | 0 | 1486.4 | 0
2 | Simple Cycle Turbine | Limited Operation + ULSD (0.0015 wt. pct. S) | 99.7 | 4.0683 | 1352.0317 | 0.3 | wt % S (existing for EUs 5 & 6)
|  | Limited Operation + Low Sulfur Fuel (0.05 wt. pct. S) | 90 | 135.61 | 1220.49 | 0.005 | wt % S (existing for Naphtha)
|  | Good Combustion Practices (0.50 wt. pct. S) (existing) | 0 | 1356.1 | 0 | 0.0015 | wt % S ULSD
5, 6 | Combined Cycle Gas Turbines (per turbine) | ULSD (0.0015 wt. pct. S) | 70% | 2.8614 | 6.6766 | 455 | MMBtu/hr EUs 5 and 6 heat rate
|  | ULSD (0.0015 wt. pct. S) compared to JetA/No. 1 | 0 | 36 | 0
|  | LSR (0.0050 wt. pct. S) + JetA/No. 1 Diesel (0.3 wt. pct. S, 1.5x10^6 gal/yr) Good Combustion Practices (existing) | 0 | 9.538 | 0 | 1500000 | gal/yr limit for startup on EUs 5 and 6
7 | Emergency Generator Engine | ULSD (0.0015 wt. pct. S) + Limited Operation | 98.5% | 0.00017722 | 0.011637 | 6.8 | lb/gal Density for Jet A/No. 1 Diesel
|  | Low Sulfur Fuel (0.05 wt. pct. S) + Limited Operation | 50 | 0.0059072 | 0.0059072 | 1.01 | AP-42 Table 3.1-2a E.F. for Sulfur X wt% S
|  | Limited Operation (0.1 wt. pct. S) (existing) | 0 | 0.011814 | 0 | 8302 | hr/yr each, based on the use of 1.5 million gallons allowed during startup equating to 458 hours per year
11, 12 | Propane-Fired Boiler | Low Sulfur Fuel (existing) | 0 | 0.0002 | 0

## 5-4 EU ID 1 ULSD CE -
Table 5-4. Annualized Costs for ULSD on
the Diesel-fired Simple Cycle Gas Turbine (EU ID 1)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU ID 1 - GE Frame 7 CT) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities
| (a) | ULSD Costs: | 45282461.54 | GAL | 0.185 | 8377255.3849 |  |  | 8377255.3849
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 8377255.3849
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.093051
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) (refer to Table 5-10) | [7 empty] | TIAC = | 1446967.4695
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 9824222.8544
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 1481.9408
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 6629.2951
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON ACTUAL HISTORIC RUN TIMES, AVOIDING 142.3 TONS PER YEAR)1 | [7 empty] | (TAC)/(TPY) = | 9653.329
COST EFFECTIVENESS ($ PER TON PM AVOIDED BASED ON 6 TONS SO2 AVOIDED = 1 TON PM AVOIDED)2 | [7 empty] | (TAC)/(TPY) = | 57919.9739
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 8.5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 30 | years
1 | Annual average run hours for EU 1 from 2009-2016 is 833 hours, and the peak in the last four years has been 587 hours. 833 hours equates to 4,305,969 gallons of fuel, a TDAC of $1,148,832, and a TAC of $3,068,356. The capital cost of bulk fuel storage would be less and the TIAC for actuals is shown in Table 5-10.
2 | Alaska Department of Environmental Conservation, Amendments to State Air Quality Control Plan Vol. III: Appendix III.D.5.7, page 52. In reference to fuel oil emissions, "Ambient sampling and modeling in FNSB indicates that reduction of six tons of SOX emissions result in the same reduction in ambient PM2.5 concentration as the reduction of one ton of directly emitted PM2.5".
Note on E13: Author: Based on unlimited operation. 672 MMBtu/hr @ 8760 hrs/yr and HHV of 0.13 MMBtu/gallon.
Note on G13: Author: Difference in cost for delivery of ULSD compared to #2 fuel oil from September 2019 - October 2020 based on data provided by GVEA .

## 5-4 EU ID 1 ULSD CE +
Table 5-4. Annualized Costs for ULSD on
the Diesel-fired Simple Cycle Gas Turbine (EU ID 1)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU ID 1 - GE Frame 7 CT) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities
| (a) | ULSD Costs: | 45282461.54 | GAL | 0.424 | 19199763.693 |  |  | 19199763.693
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 19199763.693
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.093051
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) (refer to Table 5-10) | [7 empty] | TIAC = | 1446967.4695
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 20646731.1624
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 1481.9408
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 13932.224
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON ACTUAL HISTORIC RUN TIMES, AVOIDING 142.3 TONS PER YEAR)1 | [7 empty] | (TAC)/(TPY) = | 16885.4207
COST EFFECTIVENESS ($ PER TON PM AVOIDED BASED ON 6 TONS SO2 AVOIDED = 1 TON PM AVOIDED)2 | [7 empty] | (TAC)/(TPY) = | 101312.524
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 8.5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 30 | years
1 | Annual average run hours for EU 1 from 2009-2016 is 833 hours, and the peak in the last four years has been 587 hours. 833 hours equates to 4,305,969 gallons of fuel, a TDAC of $1,148,832, and a TAC of $3,068,356. The capital cost of bulk fuel storage would be less and the TIAC for actuals is shown in Table 5-10.
2 | Alaska Department of Environmental Conservation, Amendments to State Air Quality Control Plan Vol. III: Appendix III.D.5.7, page 52. In reference to fuel oil emissions, "Ambient sampling and modeling in FNSB indicates that reduction of six tons of SOX emissions result in the same reduction in ambient PM2.5 concentration as the reduction of one ton of directly emitted PM2.5".
Note on E13: Author: Based on unlimited operation. 672 MMBtu/hr @ 8760 hrs/yr and HHV of 0.13 MMBtu/gallon.
Note on G13: Author: Difference in cost for delivery of ULSD compared to #2 fuel oil from January 2017 - October 2018 based on data provided by GVEA .

## 5-5 EU ID 2 ULSD CE -
Table 5-5. Annualized Costs for ULSD on
the Diesel-fired Simple Cycle Gas Turbine (EU ID 2)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU ID 2 - GE Frame 7 CT) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities
| (a) | ULSD Costs: | 41312492.31 | GAL | 0.185 | 7642811.0773 |  |  | 7642811.0773
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 7642811.0773
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.093051
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) (refer to Table 5-10) | [7 empty] | TIAC = | 1446967.4695
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 9089778.5468
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 1352.0317
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 6723.0514
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON ACTUALS, AVOIDING 422.3 TONS PER YEAR)1 | [7 empty] | (TAC)/(TPY) = | 6964.3785
COST EFFECTIVENESS ($ PER TON PM AVOIDED BASED ON 6 TONS SO2 AVOIDED = EQUIVALENT TO 1 TON PM AVOIDED)2 | [7 empty] | (TAC)/(TPY) = | 41786.2707
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 8.5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 30 | years
1 | Annual average run hours for EU 2 from 2009-2016 is 2472 hours, and the peak in the last four years has been 2873 hours. 2472 hours equates to 12,778,338 gallons of fuel, a TDAC of $3,409,261, and a TAC of $5,328,784. The capital cost of bulk fuel storage would be less and the TIAC for actuals is shown in Table 5-10.
2 | Alaska Department of Environmental Conservation, Amendments to State Air Quality Control Plan Vol. III: Appendix III.D.5.7, page 52. In reference to fuel oil emissions, "Ambient sampling and modeling in FNSB indicates that reduction of six tons of SOX emissions result in the same reduction in ambient PM2.5 concentration as the reduction of one ton of directly emitted PM2.5".
Note on E13: Author: Based on limited operations. 672 MMBtu/hr @ 7992 hrs/yr and HHV of 0.13 MMBtu/gal
Note on G13: Author: Difference in cost for delivery of ULSD compared to #2 fuel oil from September 2019 - October 2020 based on data provided by GVEA .

## 5-5 EU ID 2 ULSD +
Table 5-5. Annualized Costs for ULSD on
the Diesel-fired Simple Cycle Gas Turbine (EU ID 2)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU ID 2 - GE Frame 7 CT) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities
| (a) | ULSD Costs: | 41312492.31 | GAL | 0.424 | 17516496.7394 |  |  | 17516496.7394
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 17516496.7394
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.093051
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) (refer to Table 5-10) | [7 empty] | TIAC = | 1446967.4695
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 18963464.2089
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 1352.0317
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON PTE) | [7 empty] | (TAC)/(TPY) = | 14025.9021
COST EFFECTIVENESS ($ PER TON AVOIDED BASED ON ACTUALS, AVOIDING 422.3 TONS PER YEAR)1 | [7 empty] | (TAC)/(TPY) = | 14196.2584
COST EFFECTIVENESS ($ PER TON PM AVOIDED BASED ON 6 TONS SO2 AVOIDED = EQUIVALENT TO 1 TON PM AVOIDED)2 | [7 empty] | (TAC)/(TPY) = | 85177.5503
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 8.5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 30 | years
1 | Annual average run hours for EU 2 from 2009-2016 is 2472 hours, and the peak in the last four years has been 2873 hours. 2472 hours equates to 12,778,338 gallons of fuel, a TDAC of $3,409,261, and a TAC of $5,328,784. The capital cost of bulk fuel storage would be less and the TIAC for actuals is shown in Table 5-10.
2 | Alaska Department of Environmental Conservation, Amendments to State Air Quality Control Plan Vol. III: Appendix III.D.5.7, page 52. In reference to fuel oil emissions, "Ambient sampling and modeling in FNSB indicates that reduction of six tons of SOX emissions result in the same reduction in ambient PM2.5 concentration as the reduction of one ton of directly emitted PM2.5".
Note on E13: Author: Based on limited operations. 672 MMBtu/hr @ 7992 hrs/yr and HHV of 0.13 MMBtu/gal
Note on G13: Author: Difference in cost for delivery of ULSD compared to #2 fuel oil from January 2017 - October 2018 based on data provided by GVEA.

## 5-6 EU ID 5&6 ULSD CE Norm -
Table 5-6. Annualized Costs for ULSD on
the Diesel-fired Combined Cycle Gas Turbines (EU IDs 5 and 6)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU IDs 5 and 6 - GE LM6000PC CT) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities
| (a) | ULSD Costs: | 29057000 | GAL | 0.588 | 17085516 |  |  | 17085516
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 17085516
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.093051
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 0
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 17085516
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 6.6766
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 2559025.1333
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 8.5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 30 | years
Note on E14: Author: Based on HHV of 0.13 MMBtu/gal and maximum allowed operations of 455 MMBtu/hr for 8,302 hr/yr (8,760 - 458 hours per year for startup which equates to 1.5 million gallon limit).
Note on G14: Author: Difference in cost for delivery of ULSD compared to LSR fuel from September 2019 - October 2020 based on data provided by GVEA .

## 5-6 EU ID 5&6 ULSD CE Norm +
Table 5-6. Annualized Costs for ULSD on
the Diesel-fired Combined Cycle Gas Turbines (EU IDs 5 and 6)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU IDs 5 and 6 - GE LM6000PC CT) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities
| (a) | ULSD Costs: | 29057000 | GAL | 1.117 | 32456669 |  |  | 32456669
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 32456669
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.093051
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 0
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 32456669
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 6.6766
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 4861277.3365
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 8.5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 30 | years
Note on E14: Author: Based on HHV of 0.13 MMBtu/gal and maximum allowed operations of 455 MMBtu/hr for 8,302 hr/yr (8,760 - 458 hours per year for startup which equates to 1.5 million gallon limit).
Note on G14: Author: Difference in cost for delivery of ULSD compared to LSR fuel from January 2017 - October 2018 based on data provided by GVEA.

## 5-7 EU ID 7 ULSD CE -
Table 5-7. Annualized Costs for ULSD on
the Diesel-fired Emergency Generator Engine (EU ID 7)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU ID 7 - Generac Gen Set Engine) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities
| (a) | ULSD Costs: | 1664 | GAL | 0.2668 | 443.9552 |  |  | 443.9552
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 443.9552
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.093051
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 0
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 443.9552
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 0.011637
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 38149.7104
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 8.5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 30 | years
Note on E13: Author: Based on engine fuel consumption rate of 32 gals/hr and limited operations of 52 hours/yr.
Note on G13: Author: Difference in cost for delivery of ULSD compared to No. 1 fuel oil from September 2019 - October 2020 based on data provided by GVEA .

## 5-7 EU ID 7 ULSD +
Table 5-7. Annualized Costs for ULSD on
the Diesel-fired Emergency Generator Engine (EU ID 7)
Shaded cells indicate user inputs
Project: |  | GVEA North Pole - PM2.5 BACT Analysis (EU ID 7 - Generac Gen Set Engine) | [5 empty] | Prepared By:
Checked By:
Rev:
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT |  | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating & Maintenance Costs |  |  | % |  |  | 0 |  | 0
(2) | Repair & Replacement Costs |  |  | % |  |  | 0 |  | 0
(3) | Maintenance Materials |  |  | LOT |  | excluded in this estimate
(4) | Utilities
| (a) | ULSD Costs: | 1664 | GAL | 0.651 | 1083.264 |  |  | 1083.264
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 1083.264
INDIRECT ANNUAL COSTS
(5) | Overhead |  |  | % |  | excluded in this estimate | 0 |  | 0
(6) | Administrative Charges, Property Taxes, Insurance |  |  | % of capital |  |  | 0 |  | 0
| Capital Recovery Factor [see inputs below] |  | 0.093051
(7) | Capital Recovery | [6 empty] | CRF * TCI = | 0
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 0
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 1083.264
Cost Effectiveness Summary
TOTAL TONS SO2 AVOIDED PER YEAR | [7 empty] | = | 0.011637
COST EFFECTIVENESS ($ PER TON AVOIDED) | [7 empty] | (TAC)/(TPY) = | 93086.4374
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 8.5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 30 | years
Note on E13: Author: Based on engine fuel consumption rate of 32 gals/hr and limited operations of 52 hours/yr.
Note on G13: Author: Difference in cost for delivery of ULSD compared to No. 1 fuel oil from October 2021 - April 2023 based on data provided by GVEA .

## Table 5-8
Table 5-8. GVEA North Pole Facility - SO2 BACT Cost Effectiveness
Summary1 for Each Emission Unit Based on PTE
Simple Cycle Gas Turbine (EU ID 1)
ULSD (0.0015 wt. pct. S) | 4.4592 | 10875319.1489 | 20646731.1624 | 19199763.693 | 13932.224
Good Combustion Practices (0.50 wt. pct. S) (existing) | 1486.4 | ~ | ~ | ~ | ~
Simple Cycle Gas Turbine (EU ID 2)
Limited Operation + ULSD (0.0015 wt. pct. S) | 4.0683 | 10875319.1489 | 18963464.2089 | 17516496.7394 | 14025.9021
Good Combustion Practices (0.50 wt. pct. S) (existing) | 1356.1 | ~ | ~ | ~ | ~
Combined Cycle Gas Turbines (EU IDs 5 and 6)
ULSD (0.0015 wt. pct. S) | 2.8614 | ~ | 32456669 | ~ | 4861277.3365
LSR (0.0050 wt. pct. S) + JetA/No. 1 Diesel (0.3 wt. pct. S, 1.5x10^6 gal/yr) Good Combustion Practices (existing) | 9.538 | ~ | ~ | ~ | ~
Emergency Generator Engine (EU ID 7)
ULSD (0.0015 wt. pct. S) + Limited Operation | 0.00017722 | ~ | 1083.264 | ~ | 93086.4374
Limited Operation (0.1 wt. pct. S) (existing) | 0.011814 | ~ | ~ | ~ | ~
Propane Fired Boilers (EU IDs 11 and 12)
Low Sulfur Fuel (propane) (existing) | 0 | ~ | ~ | ~ | ~
Summary1 for Each Emission Unit Based on Actuals
Control Technology Option | SO2 Emissions (tpy) | Total Installed Capital ($) | Total Annualized Cost ($/year) | Annual O&M Cost ($/year) | Cost Effectiveness ($/ton SO2 removed)
Simple Cycle Gas Turbine (EU ID 1)
ULSD (0.0015 wt. pct. S) | 4.4592 | 10875319.1489 | 3068356 | 1148832 | 21562.5861
Good Combustion Practices (0.50 wt. pct. S) (existing) | 1486.4 | ~ | ~ | ~ | ~
Simple Cycle Gas Turbine (EU ID 2)
Limited Operation + ULSD (0.0015 wt. pct. S) | 4.0683 | 10875319.1489 | 5328784 | 3409261 | 12618.4798
Good Combustion Practices (0.50 wt. pct. S) (existing) | 1356.1 | ~ | ~ | ~ | ~
Combined Cycle Gas Turbines (EU IDs 5 and 6)
ULSD (0.0015 wt. pct. S) | 2.8614 | ~ | 32456669 | ~ | 4861277.3365
LSR (0.0050 wt. pct. S) + JetA/No. 1 Diesel (0.3 wt. pct. S, 1.5x10^6 gal/yr) Good Combustion Practices (existing) | 9.538 | ~ | ~ | ~ | ~
Emergency Generator Engine (EU ID 7)
ULSD (0.0015 wt. pct. S) + Limited Operation | 0.00017722 | ~ | 1083.264 | ~ | 93086.4374
Limited Operation (0.1 wt. pct. S) (existing) | 0.011814 | ~ | ~ | ~ | ~
Propane Fired Boilers (EU IDs 11 and 12)
Low Sulfur Fuel (propane) (existing) | 0 | ~ | ~ | ~ | ~
1 All emission costs are on a per emission unit basis.

## Table - 5-9
Table 5-9. GVEA North Pole Facility - Proposed SO2 BACT and Associated
Emission Rate for Each Emission Unit
ID | Description |  | Description | Emission Rate1
1, 2 | Simple Cycle Gas Turbine | Fuel Oil | Good Combustion Practices (existing) | 500 ppm S in fuel
5, 6 | Combined Cycle Gas Turbine | LSR | LSR (existing) | 30 ppm S in fuel
7 | Emergency Generator Engine | Fuel Oil | Good Combustion Practices (existing) | 500 ppm S in fuel
11, 12 | Boiler | Propane | Low Sulfur Fuel - Propane (existing) | 0.0012 lb/kgal
1 Emissions are on a per emission unit basis.

## 5-10 TCI ULSD EU1-2
Table 5-10. Capital Cost for New ULSD Storage Based on
Maximum Fuel Use and Actual Fuel Use
| North Pole EUs 1 and 2 Maximum Fuel Use | Zehnder EUs 1 and 2 Maximum Fuel Use | North Pole EUs 1 and 2 Actual Fuel Use | Zehnder EUs 1 and 2 Actual Fuel Use
Capital Cost Estimate | 30425000 |  | 21050000
Heat Input, MMBtu/day (combined for each set of combustion turbines) | 32256 | 12864 | 32256 | 12864
Percentage of Heat Input | 71.49% | 28.51% | 71.49% | 28.51%
Capital Cost (apportioned based on heat input ratio) | 21750638.2979 | 8674361.7021 | 15048510.6383 | 6001489.3617
Capital Cost (apportioned per combustion turbine) | 10875319.1489 | 4337180.8511 | 7524255.3191 | 3000744.6809
Capital Recovery (per combustion turbine) | 1011954.7035 | 403577.1734 | 700136.2862 | 279221.0189
Administrative Charges, Property Taxes, Insurance (per combustion turbine) | 435012.766 | 173487.234 | 300970.2128 | 120029.7872
Total Annual Indirect Cost (per combustion turbine) | 1446967.4695 | 577064.4075 | 1001106.499 | 399250.8061
Capital recovery factor | 0.093051
Data Inputs for Capital Recovery Factor:
Annual Interest Rate (EPA OAQPS Control |  | 8.5 | pct.
Cost Manual)
Project Life (EPA OAQPS Control Cost |  | 30 | years
Manual)
Administrative Charges, Property Taxes |  | 4%
Insurance (percentage of total capital
cost)
Capital cost estimate for 1.27 million gallons of storage capacity.

## ESRI_MAPINFO_SHEET (hidden)
DO NOT EDIT
For Esri use only