## April 2025 ETT List
April 2025 ETT List
Note: Column titled "Est. New ETT Score" is the estimated new score based on the violations that have Returned to Compliance (RTCd) during the Quarter. Please note that this score will likely change on the next quarter's list due to further violations being generated. Comments submitted by Drinking Water Program staff on May 27, 2025.
Staff | RMW | Est. New ETT Score | System Information | RTCR | SW | Nitrate | RTCR | SW | GWR | Nitrate | Arsenic | DBP | LCR | Rads | RTCR | SW | GWR | Arsenic | DBP | LCR | IOC | VOC | SOC | Rads | CCR | PN | General Comments | How to Return to Compliance | Known Hardware Problems
NAKANISHI | YKHC | 90 | ALAKANUK WATER SYSTEM / AK2270362 (570 / C) | [8 empty] | 1 | 1 |  |  | 52 |  |  | 21 | 2 | [6 empty] | DBP LRAA MCL exceeded since 12/2024, no MOR meeting requirements submitted since May 2024. LT2 and DBP rule violations (E. coli, TOC and Alkalinity) overdue since April 2021. Overdue for Lead Service Line Inventory. | System should sample quarterly for DBP's, submit monthly operating reports, and sample for TOC, Alkalinity, and E. coli. Lead and copper samples taken 4/2025 are currently being evaluated. Complete & submit Lead Service Line Inventory . | None known
SHARP | TCC | 15 | ALLAKAKET PUBLIC WATER SYSTEM / AK2300816 (135 / C) | [5 empty] | 1 | [10 empty] | 2 |  |  | 4 |  | 1 |  | System did not complete 2023 CCR certification or 2024 lead consumer notice certification. System has outstanding sanitary survey deficiencies from their 2023 survey to address. Has not completed 2023-2025 SOC waiver, nor sampled for SOC. | System must complete 2024 CCR certification process, lead consumer notice certification, correct outstanding survey deficiencies, and complete 2023-2025 SOC waiver application or collect SOC samples. | No known hardware issues related to violations.
HOYT | No RMW | 18 | ALPINE INN / AK2244808 (30 / NC) |  |  |  | 1 | [7 empty] | 8 | [11 empty] | No response from system via email and phone to confirm when system will be opening for 2025 season. | PWS can return to compliance by taking monthly TC samples and submit SSUP for 2025 season.
LATIMER | DEC | 29 | ANGOON PUBLIC WATER / AK2130017 (450 / C) | [9 empty] | 1 |  | 2 | 8 |  |  | 11 | 1 | [5 empty] | 1 | On BWN since April 2022. Treatment reports are mostly complete and most indicate adequate filtration and disinfection, though chlorine residual page was not reported for recent months. Overdue for Lead Service Line Inventory . Additionally, operator needs to complete certification testing. | Submit completed turbidity/residual reports on time, and complete routine sampling. Complete & submit Lead Service Line Inventory . | One storage tank remains out of service which contributes to lower pressure in part of the distribution system. Replacement of mains to start in 2025, and the inactive storage tank is expected to be back in service early summer.
POEPPEL | YKHC | 15 | ANVIK WATER SYSTEM / AK2280171 (96 / C) | [5 empty] | 1 | [17 empty] | System has open significant deficiencies from 2023. | Address the outstanding corrective actions from the 2023 sanitary survey. | N/A
LATIMER | No RMW | 11 | BAY VIEW TRAILER COURT / AK2241101 (51 / C) | [6 empty] | 1 |  |  | 1 | [6 empty] | 1 | [6 empty] | Owner plans to collect Nitrate sample before end of May and to follow up on Lead Service Line Inventory requirements next week. Owner/operator continues to express trouble understanding requirements, yet appears to want to meet requirements and expresses increase understanding compared to past two years. | Collect 2025 Nitrate sample asap, and complete Lead Service Line Inventory . | None
ROBERTS | No RMW | 11 | BIRCHVIEW RENTAL PROPERTIES, LLC / AK2310837 (31 / C) | [9 empty] | 1 | [6 empty] | 1 | [6 empty] | PWS hasn't completed and submitted initial Lead Service Line Inventory , due 10/16/2024. | PWS must complete and submit initial Lead Service Line Inventory . | No known hardware issues related to violations.
SHARP | TCC | 21 | CHALKYITSIK VILLAGE WATER / AK2300183 (76 / C) | [8 empty] | 2 |  |  |  | 5 |  |  | 1 | 1 | [6 empty] | System accrued monthly operator report violations due to operator turnover; last completed report received was August 2024. PWS exceeds both TTHM and HAA5 LRAA. System did not sample for lead/copper in 2024. | New operator needs to learn how to complete and submit monthly operator reports. System also needs to optimize treatment to reduce DBP levels and submit lead/copper samples. | Adequate change out frequency would reduce chances of DBP exceedance. DEC approved plans for a water treatment plant project intended to reduce DBPs. The new WST is in operation, GAC upgrades are not yet constructed. Scope of project has been reduced due to funding but the CT contactor tanks and new GAC media are still planned.
POEPPEL | YKHC | 13 | CITY OF HOOPER BAY / AK2270312 (1200 / C) | [5 empty] | 1 | [7 empty] | 1 |  | 2 | [7 empty] | Overdue for DBPs. Statewide EPS will continue to reach out to the system about their overdue corrective actions. | Sample for DBPs between October and December 2025. Address the outstanding corrective actions from the 2023 sanitary survey. | N/A
DAVIS | BBAHC | 14 | CLARKS POINT WATER SYSTEM / AK2260202 (128 / C) | [9 empty] | 1 | [6 empty] | 6 | [6 empty] | System submitted L&C samples 2/13/2025, however 2 out of 10 were invalid or rejected. Lead Service Line Inventory currently overdue. | Collect two more L&C samples for monitoring period January-June 2025, and complete Lead Service Line Inventory . | N/A
HOYT | No RMW | 20 | CLOVER PASS RESORT / AK2120020 (133 / NC) |  | 2 | [21 empty] | System currently operating for 2025 season. | Receive operator report with turbidity levels within compliance range.
DAVIS | No RMW | 16 | DILLINGHAM WATER SYSTEM / AK2260197 (2419 / C) | [5 empty] | 2 | [9 empty] | 1 | [7 empty] | Corrective Actions Sanitary Survey (CASS) from 2022 unresolved. No annual DBP collected since 2023. | For CASS replace conduit housing and install backflow preventer in the waterline going to the harbor. Collect annual DBP in June 2025. | N/A
SHARP | NSHC | 107 | DIOMEDE JOINT UTILITIES / AK2340141 (184 / C) |  |  | 2 |  |  |  |  | 11 |  |  |  |  | 28 | [10 empty] | Diomede continues to exceed the RAA MCL for Arsenic and Nitrate due to poor source quality. System has continued to accrue monthly operator report violations since August 2023 for failure to submit complete operator reports. | System needs to install and optimize treatment to address Nitrate, Arsenic, and SWTR. System needs to begin sending in complete monthly operator reports and continue to send chemical samples in whenever flights are available or during site visits from regional partners. | A new WTP is currently under construction to meet SWTR, Nitrate and arsenic MCLs, and corrosion control. A temporary WTP was placed into operation 2024 but did not receive approval because it had not met conditions of operation. Permanent WTP is expected to begin operation summer 2025. The WST was cleaned in August 2024 to improve water quality issues.
DAVIS | No RMW | 12 | EKUK FISHERIES / AK2261208 (150 / NC) | [5 empty] | 1 | 1 | [16 empty] | Corrective Actions Sanitary Survey (CASS) from 2021 unresolved. No annual Nitrate collected in 2024. | For CASS repair gap in well casing/sanitary seal and re-install screen for vent correctly. Collect annual Nitrate. | N/A
AGUE | YKHC | 25 | EMMONAK WATER SYSTEM / AK2270299 (820 / C) |  |  |  | 1 | [5 empty] | 1 | [5 empty] | 9 | 1 |  | 1 |  |  |  |  | System last collected monthly Total Organic Carbon and Alkalinity samples in June 2024. Annual VOC sample not collected in 2024. Three OEL reports triggered by TTHM exceedances are overdue, and the Level 1 Assessment triggered in 2023 was partly completed. Lead Service Line Inventory not completed. | Collect TOC/Alkalinity and VOC samples. Complete OEL Report, Level 1 Assessment, and Lead Service Line Inventory . | N/A
MORRISON | No RMW | 29 | FOREST PARK TC / AK2210794 (175 / C) | [5 empty] | 2 | 1 |  |  | 1 | [6 empty] | 2 |  | 2 |  |  |  |  | System has open violations for not correcting significant deficiencies from the 2016 and 2019 sanitary surveys; the system reportedly does not have the financial capacity to address the deficiencies. Last sampled for Nitrate in 2023. Did not submit Lead Service Line Inventory . Did not sample for lead and copper in 2023. Has not sampled for VOC since 2Q 2024 and is on quarterly sampling schedule. | System must submit engineering plans to correct deficiencies. Sample for Nitrate, lead and copper and VOC ASAP. Submit Lead Service Line Inventory . | System has ongoing issues with maintaining adequate distribution system pressure.
POEPPEL | YKHC | 41 | GRAYLING WATER SYSTEM / AK2280066 (195 / C) |  | 1 |  | 1 | [5 empty] | 1 |  |  | 19 |  |  |  | 1 | [6 empty] | Overdue for LT2, last sampled July 2024. ANTHC obtained PER funding to determine the best alternative for repair/replacement of the storage tank. An ANTHC project to connect 10 homes to service has started. Overdue for Lead Service Line Inventory . | Address the remaining sanitary defects. Submit monthly operator reports that meet operating requirements. Take LT2 samples according to LT2 sample plan. Complete & submit Lead Service Line Inventory . | System on long-term BWN until the PWS submits monthly operator reports and consistently samples. Storage tank is aged and too small to meet community needs.
NAKANISHI | YKHC | 11 | HOLY CROSS WATER SYSTEM / AK2280074 (182 / C) | [9 empty] | 1 | [6 empty] | 1 | [6 empty] | Lead Service Line Inventory overdue since 2024. | System should contact DEC regarding Lead Service Line Inventory . | None known
HOYT | DEC | 15 | KAKE MUNICIPAL WATER / AK2130083 (415 / C) | [8 empty] | 3 | [14 empty] | System is trying to preform operational changes to lower values. Operator has contacted RMW for further assistance. Treatment plant upgrades may be needed. | Collect set of samples that allows the LRAA to be calculated below the MCL.
CAHILL | No RMW | 21 | KING FOR A DAY / AK2299036 (53 / NC) |  |  |  | 2 |  |  | 1 |  |  |  |  | 5 | [11 empty] | PWS did not complete SSUP in 2023 or 2024 seasons. Last TC and Nitrate sample results from 10/01/2023. Certified letter sent when PWS moved to monthly TC due to # of violations, letter not picked up. | PWS can return to compliance by taking annual Nitrate and monthly Total Coliform. Needs to complete and return 2025 season SSUP. | None
HOYT | DEC | 99 | KLAWOCK / AK2120169 (904 / C) | [8 empty] | 19 | [14 empty] | System made repairs to their WST and installed a pax mixer in hopes to decrease the DBP levels. The samples collected in 4Q2024 and 1Q2025 reflect levels are decreasing. | Continue to collect DBP samples that allow for the LRAA to fall below the MCL for HAA5.
AGUE | DEC | 19 | KOKHANOK WATER & WW SYSTEM / AK2263006 (160 / C) |  | 1 | [10 empty] | 9 | [10 empty] | Monthly operator reports have not had a sufficient number of readings since March 2024, and often contain chlorine residuals below 0.2 mg/L. | Submit a complete monthly operator report showing all operating parameters were met for the month. | System on a Boil Water Notice (BWN) due to inadequate treatment. New treatment plant is up and running. BWN will be closed when a monthly operator report shows the new plant meets all treatment requirements.
SHARP | No RMW | 99 | KOTZEBUE MUN. WATER SYSTEM / AK2340060 (3234 / C) | [8 empty] | 19 | [14 empty] | TTHM & HAA5 LRAA MCL violations are valid. They have exceeded the TTHM MCL since 2019 and the HAA5 LRAA since 3rd quarter 2023. | System needs to optimize their treatment system to increase DBP precursor removal and reduce DBP levels. | Monitoring of new WTP will continue throughout the interim operation period (extended to June 2025). DBP precursor removal data is to be analyzed by the design engineering firm to improve DBP results. Long term fixes are being designed for implementation this spring and include possibly installing greensand filtration pre-treatment; this may also have an effect on DBP precursor removal. A NF membrane pilot test was to be implemented this winter to determine if existing membranes are damaged or if the natural organic constituents in the water are not properly removed by this type of membrane and require additional treatment steps.
ROBERTS | NSHC | 11 | KOYUK PUBLIC WATER SYSTEM / AK2340167 (277 / C) | [9 empty] | 1 | [6 empty] | 1 | [6 empty] | PWS hasn't completed and submitted initial Lead Service Line Inventory , due 10/16/2024. | PWS must complete and submit initial Lead Service Line Inventory . | System began operating new bag and cartridge WTP and WST in summer 2025. Updated 5/15/2025.
AGUE | YKHC | 38 | KWETHLUK NEW PIPED WATER SYSTEM / AK2272017 (760 / C) | [8 empty] | 5 | [6 empty] | 1 | [7 empty] | System exceeded the HAA5 MCL in July 2024 and has had open TT violations for Total Organic Carbon removal since 1st quarter 2024. A complete set of DBP samples was collected in February, but only the TTHM sample could be analyzed. March sample met TOC removal ratio, but first quarter did not. | Collect HAA5 samples below the MCL, and maintain quarterly RAA for TOC removal above 1.0. | N/A
NAKANISHI | No RMW | 13 | LKSD NIGHTMUTE HS & ELEM / AK2271261 (259 / NTNC) | [12 empty] | 7 |  |  |  | 1 |  | 3 |  |  |  |  | Surface Water LT2 violations valid since February 2024. Last lead and copper sample was due in 2022. VOC's not taken since 2018. | System should sample for Lead and copper, VOC's and take LT2 samples. | None known
BARNES | BBAHC | 13 | MANOKOTAK HEIGHTS W/S / AK2262246 (215 / C) | [9 empty] | 1 | [6 empty] | 1 |  |  | 4 |  |  |  | System has not submitted a Lead Service Line Inventory which was due in 2024. System does not have a valid SOC waiver. | System needs to submit an SOC waiver. System must submit a Lead Service Line Inventory and make it publicly available. | N/A
KEIM | TCC | 13 | MINTO COMMUNITY WATER SYSTEM / AK2300159 (205 / C) | [5 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [5 empty] | 1 | PWS hasn't completed corrective actions from 2023 sanitary survey; bolt holes in the Pumphouse well sanitary seal must be sealed. PWS hasn't completed and submitted initial Lead Service Line Inventory , due 10/16/2024. | PWS must seal the Pumphouse well and provide documentation to the DWP, and submit initial Lead Service Line Inventory . | No known hardware issues related to violations.
HOYT | DEC | 28 | NANWALEK / AK2240464 (281 / C) | [11 empty] | 7 | 7 |  |  | 9 | [5 empty] | 2 |  | On BWN since February 2025. Operator has not completed operator cert. Routine sampling is not being completed. ARWA reached out to EPS May 2025 for insight on how to get system back to compliance. | Complete all routine sampling and submit completed monthly operator reports on time. Meet operator certification requirements. Submit 2024 CCR and Cert page on time.
NAKANISHI | YKHC | 19 | NAPASKIAK WEST WATER SYSTEM / AK2260139 (200 / C) | [5 empty] | 2 | [7 empty] | 1 |  | 1 | 1 | [6 empty] | DBP's overdue since 2023. Lead and Copper samples overdue since 1/1/2024. Overdue sanitary survey deficiencies since 2022. | Sample for PbCu in 2025 and DBP's in 4th quarter of 2025. DEC is working to come up with a suitable corrective action plan for the deficiencies. | None known
AGUE | YKHC | 13 | NIGHTMUTE NEW WATERING POINT / AK2271721 (243 / C) |  |  |  | 1 |  | 1 | [5 empty] | 1 | [11 empty] | System has open significant deficiencies and sanitary defects from 2022 sanitary survey and level 1 assessment. Last collected a TC sample in December 2024. System has new operator who is just beginning training, and two of the previously identified defects/deficiencies will be re-classified as findings. A new sanitary survey was conducted in May. | Collect a TC sample and address significant deficiencies. | The watering point lacks appropriate backflow prevention, and its self-service hose is not NSF-certified.
DAVIS | DEC | 26 | NONDALTON / AK2260260 (205 / C) |  | 2 | [13 empty] | 3 | [7 empty] | No annual DBP2 sampled since 2020. | Collect DBP. | N/A
NAKANISHI | YKHC | 40 | NUNAM IQUA WATER SYSTEM / AK2270207 (213 / C) | [11 empty] | 3 | 3 |  |  | 12 | [7 empty] | Last Total Coliform on record was taken 9/24/2024. TOC/Alkalinity from Intake, TOC from treatment plant, and last set of DBP's taken 3/27/2024. | System should sample for DBP's, TC, TOC/ALK (intake) and TOC (treatment plant) as soon as possible. | None known
CAHILL | No RMW | 14 | PALMER LIFEWAYS DAYCARE / AK2226055 (56 / NTNC) | [7 empty] | 2 | [6 empty] | 1 |  |  | 1 | [5 empty] | PWS continues to have high Arsenic, Conditional Approval to Construct granted 02/18/2025 for installation of POU treatment. | PWS can return to compliance by testing below the Arsenic MCL after receiving approval to operate Arsenic treatment system. | PWS plans to install POU treatment. Engineering construction approval has been granted.
AGUE | No RMW | 11 | PETER PAN SEAFOODS PORT MOLLER / AK2261216 (140 / NC) |  |  |  |  | 1 | [6 empty] | 1 | [11 empty] | System does not meet surface water treatment requirements with current configuration.
NAKANISHI | No RMW | 12 | PETERS CREEK TERRACE / AK2211473 (70 / C) | [9 empty] | 1 | [6 empty] | 3 | [6 empty] | Lead and copper samples overdue since 2020. Lead Service Line Inventory overdue since 2024. | System should sample for Lead and Copper and submit Lead Service Line Inventory . | None known
BARNES, KARIS | YKHC | 15 | PLATINUM CITY WATER SYSTEM / AK2271059 (51 / C) |  |  |  |  | 1 | [6 empty] | 1 | [6 empty] | 4 |  |  |  |  | System does not meet applicable water treatment and filtration requirements. PWS does not have RTCR plan on file. System has not taken valid VOC sample since 2012. | System needs to take VOC sample in 2025. System needs to submit RTCR plan. | System does not filter.
HARRIS | DEC | 13 | PORT PROTECTION / AK2121123 (60 / C) |  |  |  | 1 | 1 | [18 empty] | PWS classified as a GWUDISW & has not installed filtration/disinfection. PWS on a long-term BWN due to lack of treatment & repeated TC+/EC+ results. ARWA completed Level 2 Assessment/Sanitary Survey combo on 1/7/2025. | Install filtration & disinfection treatment system. | Remote system with no electrical grid or financial means to install treatment system. Source water infiltration gallery currently intaking raw water & substrate deposits from creek.
SHARP | TCC | 11 | RAMPART WASHETERIA / AK2360816 (88 / C) | [5 empty] | 1 | [9 empty] | 2 | 1 |  | 1 |  |  |  |  | System did not collect 2024 VOC sample and did not collect 3rd or 4th quarter 2024 DBP samples in correct month. System did not complete 2024 lead consumer notice certification. System has outstanding survey deficiencies from 2022 sanitary survey to address. | System must collect June 2025 DBP sample, complete lead consumer notice process, collect annual VOC samples, and correct outstanding survey deficiencies. | No known hardware issues related to violations.
HOYT | No RMW | 12 | RAZDOLNA ELEMENTARY SCHOOL / AK2244222 (50 / NTNC) | [6 empty] | 1 |  |  |  |  | 5 | [6 empty] | 1 |  |  |  |  | System has not met 2024 annual compliance requirements and has not collected TC samples since 5/1/2024. | PWS can return to compliance by taking TC, VOC, Nitrate, and 4 lead and copper samples.
LATIMER | No RMW | 14 | S & S CENTER / AK2244719 (54 / NTNC) | [9 empty] | 1 | [6 empty] | 3 |  | 1 |  |  |  |  | Informed owner/operator of VOC & lead/copper sampling violations and of Lead Service Line Inventory deadlines overdue. | Collect overdue VOC and lead/copper samples during 2025/asap. Complete Lead Service Line Inventory requirements. | None
POEPPEL | DEC | 13 | SAINT GEORGE WATER SYSTEM / AK2260074 (65 / C) | [5 empty] | 1 | [10 empty] | 3 | [6 empty] | Overdue for Lead/Copper samples last sampled in 2013. System has open significant deficiencies from 2021. | Sample for lead and copper. Address the outstanding corrective actions from the 2021 sanitary survey. | Water storage tank is unstable/failing.
LATIMER | No RMW | 11 | SALMON CREEK TRAILER COURT / AK2241062 (125 / C) | [6 empty] | 1 |  |  | 1 | [6 empty] | 1 | [6 empty] | Owner plans to collect Nitrate sample before end of May, & to follow up on Lead Service Line Inventory requirements next week. | Collect 2025 Nitrate sample asap, and complete Lead Service Line Inventory . | None
LATIMER | No RMW | 12 | SALTRY / AK2243161 (75 / NC) | [6 empty] | 1 |  |  |  |  | 4 | 1 | [10 empty] | Was informed that SSUPs were completed and form sent to Soldotna, and that they plan to collect Nitrate & total coliform samples by end of May. | Submit completed turbidity/residual reports on time, and complete routine sampling. | None
DAVIS | YKHC | 16 | SCAMMON BAY WATER SYSTEM / AK2270184 (637 / C) | [12 empty] | 7 |  |  | 2 | 2 | [6 empty] | No quarterly DBP collected since 05/13/2024. No 3-yr L&C collected since 2015. SW-System not reporting turbidity due to turbidity meter malfunction. | Collect quarterly DBP and 3-year L&C ASAP. Meet daily turbidity requirements. | Turbidity Meter
GILLESPIE | No RMW | 26 | SET FREE ALASKA SNODGRASS / AK2220483 (47 / NTNC) | [7 empty] | 5
SHARP | NSHC | 15 | SHAKTOOLIK WATER SYSTEM / AK2340442 (270 / C) | [12 empty] | 6 | [10 empty] | System stopped collecting and reporting an adequate number of entry point chlorine readings in March 2024. | System must begin submitting monthly operator reports with an adequate number of entry point chlorine readings. | No known hardware issues related to violations.
CAHILL | No RMW | 13 | SHEENA MAY ESTATES / AK2224337 (74 / C) | [7 empty] | 2 | [9 empty] | 1 | [5 empty] | PWS blends two sources to help mitigate high Arsenic. Arsenic sample collected in 1st quarter 2024 taken from incorrect sample point. RAA for 2024 = .011 Mg/L | PWS can return to compliance by testing below the Arsenic MCL - blending could need adjustment. | None
NAKANISHI | No RMW | 11 | SNOWCREST VIEW SOUTH / AK2210891 (25 / C) | [9 empty] | 1 | [6 empty] | 3 |  |  |  |  | 2 |  | System overdue for CCR/CCR Certification due in 2024. System overdue for Lead Consumer Notifications due in 2024. | CCR and Lead Consumer Notifications should be provided to consumers. System should contact DEC regarding Lead Service Line Inventory . | None known
NAKANISHI | YKHC | 12 | ST. MARYS WATER SYSTEM / AK2270176 (548 / C) | [12 empty] | 9 |  |  |  | 2 | [6 empty] | Last PbCu sample results were taken in 2023. | Sample for PbCu every 6 months in 2025. | SCADA is outdated and needs replacement/repairs. Waiting for details on possible project in summer of 2025 that might include these needed repairs.
ROBERTS | NSHC | 11 | ST. MICHAEL WATER SYSTEM / AK2340337 (495 / C) | [9 empty] | 1 | [6 empty] | 1 | [6 empty] | PWS hasn't completed and submitted initial Lead Service Line Inventory , due 10/16/2024. | PWS must complete and submit initial Lead Service Line Inventory . | No known hardware issues related to violations.
LATIMER | No RMW | 11 | STERLING HARBOR MENNONITE CHURCH / AK2249223 (100 / NC) | [5 empty] | 1 | [7 empty] | 1 | [9 empty] | Talked with new contact who plans to get back into compliance, and requested copies of documents and reminders of what needs to be completed, which was provided May 2025. | Provide verification of well cap electrical connection correction. | None
HARRIS | No RMW | 12 | STERLING MOOSE RIVER MANOR / AK2249099 (33 / C) | [5 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [6 empty] | System has a history of not responding to DEC inquiries. However, system has a new Director who may be more responsive. | Complete and submit the Lead Service Line Inventory to DEC for approval. Address open CASS schedule items identified in the 2023 sanitary survey. | N/A
KEIM | DEC | 11 | TAKOTNA WATER SYSTEM / AK2280163 (70 / C) | [12 empty] | 6 |  |  | 1 | 2 | [6 empty] | PWS didn't submit a monthly operator report for October, November, or December 2024. PWS didn't submit 2024 DBP samples in August 2024. PWS didn't submit lead and copper samples in 2023 or 2024. | Takotna must begin submitting complete monthly operator reports on time each month. PWS must sample for lead and copper in 2025 and DBPs in August 2025. | Systems generator was failing fall 2023 which resulted in frequent loss of power/pressure issues. During this time the system was not completing monthly operator reports or sampling and the system was operating under a Boil Water Notice due to frequent pressure losses.
HARRIS | DEC | 54 | TATITLEK WATER SYSTEM / AK2291130 (95 / C) | [8 empty] | 10 | [14 empty] | System has ongoing DBP exceedances since 2015. System still exceeding Lead at one location. DW Program staff met with PWS to discuss actions for DBP MCL & Lead AL resolutions. System will continue to research water storage tank mixer and will continue to work with NUS/ANTHC/RMW on updating chlorine injection equipment. System to perform faucet replacement along with other renovations at Lead AL site by 9/1/2025 before school session begins. | Install treatment to reduce DBP's. Replace faucets where Lead is exceeding. | High Lead levels in distribution system. Chlorine injection equipment likely not operating smoothly. Water storage tank may be cold stratifying water into unmixed layers of highly concentrated CL2/DBP's.
NAKANISHI | YKHC | 11 | TULUKSAK WATER SYSTEM / AK2270223 (373 / C) | [6 empty] | 1 | [7 empty] | 1 |  | 2 |  | 1 |  |  | 1 |  | System last sampled for Nitrate, VOC's and arsenic in 2023. | System should sample for Nitrate, VOC's, Arsenic, and Lead and Copper. | None known
DAVIS | No RMW | 11 | TUNDRA CENTER WATER SYSTEM / AK2271473 (80 / NC) | [6 empty] | 2 | [16 empty] | No annual Nitrate collected since 2022. | Collect annual Nitrate ASAP. | N/A
AGUE | YKHC | 25 | TUNTUTULIAK WASHETERIA AND WATERING PT / AK2271211 (350 / C) | [5 empty] | 2 |  |  |  | 1 |  |  |  |  | 4 |  | 1 | [6 empty] | System had a lead action level exceedance in 2016 and last collected an arsenic sample in 2020 following an MCL exceedance in 2017. Open significant deficiencies were re-identified in 2024 sanitary survey. Lead and copper samples collected in April 2025 were below the action level. | Collect second 6-month lead and copper sample set between July-December of this year. Collect arsenic sample ASAP and address significant deficiencies. | System has the following open deficiencies: insufficient distance between the well head and possible sources of contamination, insufficient drainage around the well head, two potential cross connections, a missing flow switch on the potassium permanganate feed, and an inoperable distribution pump.
DAVIS | BBAHC | 11 | TWIN HILLS WATER SYSTEM / AK2260032 (87 / C) | [6 empty] | 2 | [16 empty] | No annual Nitrate collected since 2022. | Collect annual Nitrate ASAP. | N/A
SHARP | No RMW | 16 | VALLEY WATER COMPANY / AK2310926 (1575 / C) | [9 empty] | 2 | [6 empty] | 1 | [6 empty] | Violation for lack of corrosion control was issued in 2006 and PWS still does not have corrosion control. PWS hasn't completed and submitted initial Lead Service Line Inventory , due 10/16/2024. | System must install corrosion control to address high copper levels and submit initial Lead Service Line Inventory . | Valley Water does not have corrosion control treatment. Currently PWS is applying for funding to implement some of the corrective actions in the Master Plan, including ones related to copper exceedance.
SHARP | NSHC | 51 | WALES WATER SYSTEM / AK2340191 (173 / C) | [6 empty] | 1 |  |  |  | 7 |  |  |  |  | 1 | 1 |  | 1 |  | 4 |  |  | System exceeds the RAA MCL for Uranium. System changed sources to a SW source in fall 2024, but had to resort to old source after new source quantity issues. Did not collect required Nitrate lead/copper, VOC, DBPs, or Rad samples. | Must collect overdue samples once new source is online this summer. New SW source and WTP should reduce Uranium levels. | New source and WTP to address Uranium MCL has been completed, but due to low production from the source, the system had to revert back to using GW well to fill the remainder of the WST for the winter. System ran out of water in Spring 2025 and switched to traditional sources until transmission line to wells is thawed or surface water source is rehabilitated in summer 2025.
WHITEAKER | No RMW | 12 | WHITE BIRCH APARTMENTS / AK2313233 (72 / C) | [9 empty] | 1 | [6 empty] | 2 | [6 empty] | System only collected 4 of 5 lead/copper samples in 2024 and has not completed their initial Lead Service Line Inventory . | System must submit a complete set of lead and copper samples and complete their Lead Service Line Inventory . | No known hardware issues related to violations.
KEIM | No RMW | 12 | WILDWOOD HOMES LLC / AK2310853 (114 / C) | [5 empty] | 1 |  |  |  | 1 | [6 empty] | 1 | [6 empty] | PWS hasn't completed corrective actions from 2023 sanitary survey. Modifications were made to the water system without prior approval from DEC and there is a separation distance issue between the well and wastewater lines; a waiver request was submitted but was incomplete. PWS hasn't completed and submitted initial Lead Service Line Inventory , due 10/16/2024. | PWS must continue to work with DWP engineering to complete sanitary survey corrective actions by submitting a complete waiver and other necessary information related to the modifications. PWS must complete and submit initial Lead Service Line Inventory . | A separation distance waiver was submitted and reviewed as part of the project (sanitary survey deficiency), but the project has been incomplete since June 2023. They will also need approval from the Wastewater Program for the project; no wastewater approval request has been received.

## Definitions+Contact List
DW Program Staff Contact Information
Mat-Su = Office located in Wasilla, AK. Covers the Mat-Su area. Staff: Jamie Bjorkman (Program Coordinator) 262‐3423, Darryl Gillespie (EPS) 376-1849, Jessica Cahill (EPS) 376-1824, Charity Bare (Engineering Supervisor) 262-3400
Northern = Office located in Fairbanks, AK. Covers the Northern Alaska PWSs. Staff: Teslyn Hakala (Program Coordinator) 451-3038, Michael Sharp (EPS) 451-2178, Jenny Roberts (EPS) 451‐2137, Gretchen Keim (EPS) 451-2231, Johnny Mendez (Engineering Supervisor) 451-5193.
Southcentral / ANC= Office located in Anchorage, AK. Covers Anchorage bowl, Prudhoe Bay, Bethel/YK Delta, Dillingham area, Aleutian Chain, Pribilof and Kodiak Island area PWSs. Staff: Leslie Morrison (Program Coordinator) 269-7619, Elizabeth Nakanishi (EPS) 269‐7517, Kristine Poeppel (EPS) 269‐7521, Monica Ague (EPS) 269-7653, John Davis (EPS) 262-8201, Karis Barnes (EPS) 262-8204, Chris Pletnikoff (Engineering Supervisor) 269‐6064.
Kenai / Southeast = Office located in Soldotna, AK. Covers the Kenai Peninsula and Southeast area. Staff: Jamie Bjorkman (Program Coordinator) 262‐3423, James Latimer (EPS) 262-3410, Christina Harris (EPS) 262-3420, Emily Hoyt (EPS) 465-5108, Charity Bare (Engineering Supervisor) 262-3400
GENERAL ETT QUESTIONS: Jeanine Vance (EPM) 269-2007, Karen Garland (EPS) 269-7576, Eric Burg (EPS) 262-3401
Link to DW Program Directory (contact information) | http://dec.alaska.gov/eh/dw/contact/
Resource Links
Alaska Community Database Online
The Community Database Online is a portal for information resources about Alaskan Communities and Places of Interest in an interactive format.
Link to Database Online Webpage | https://dcra-cdo-dcced.opendata.arcgis.com/
Alaska Community Photo Library
The Community Photo Library offers a glimpse into Alaska's communities and lifestyle by providing images of places, people, cultural events, public facilities, landscapes, and other dimensions of community life.
Link to Photo Library Webpage | https://www.commerce.alaska.gov/dcra/admin/Photo
Remote Maintenance Worker (RMW) Service Area Abbreviations
BBAHC= Bristol Bay area Health Corporation | Maniilaq= Maniilaq Health Corporation | TCC= Tanana Chiefs Conference
DEC= AK Department of Environmental Conservation | NSHC= Norton Sound Health Corporation | YKHC= Yukon Kuskokwim Health Corporation
No‐RMW= Not served by an RMW Program
Link to RMW Directory | https://dec.alaska.gov/media/p4dntxhf/rmw-directory.pdf
Definitions
AL= Action Level | IFE= Individual Filter Effluent | RMW= Remote Maintenance Worker
ANTHC= Alaska Native Tribal Health Consortium | IOC= Inorganic Chemicals | RTC= Return to compliance (fall off ETT list)
BACTI or t‐Coli = Total Coliform Sample | LCR= Lead/Copper Rule | RTCR= Revised Total Coliform Rule
BWN= Boil Water Notice | LRAA= Locational Running Annual Average (Stage 2) | SOC= Synthetic Organic Chemicals
CCR= Consumer Confidence Report | LT1= Long Term 1 Enhanced Surface Water Treatment Rule | Surface Water (SW)= Surface Water violations Surface Water Treatment Rules (SWTR, LT1, and LT2)
CFE= Combined Filter Effluent | LT2= Long Term 2 Enhanced Surface Water Treatment Rule
DPB= Disinfection by Products | M/R= Monitoring and Reporting (type of violation) | SSUP = Seasonal Startup Procedures
DSRD= Distribution Chlorine Residual | MCL= Maximum Contaminant Level (type of violation) | TC= Total Coliform (also called Bacti)
EHO= Environmental Health Officer | MOR= Monthly operator report | TOC= Total Organic Carbon
EP= Entry Point | NOV= Notice of Violation | TCR= Total Coliform Rule
EPA= Environmental Protection Agency | OCC= Optimal corrosion control (Lead/Copper Rule) | TT= Treatment Technique (violation)
EPRD= Entry Point Residual Distribution | PE= Public Education (requirement under Lead/Copper Rule) | TTHM= Total Trihalomethanes (Stage 1 Rule)
ETT= Enforcement Targeting Tool | PER= Preliminary Engineering Report | VOC= Volatile Organic Chemicals
FANLs= Facility Analyte Level (refers to SW/DBP monitoring requirements) | PN= Public Notice | VSW= Village Safe Water
GAC= Granular Activated Carbon | PWS= Public Water System | WTP= Water Treatment Plant
GWUDI= Groundwater under the direct influence of surface water | RAA= Running Annual Average
HAA5= Haloacetic Acids (Stage 1 Rule) | Rads= Radionuclides Rule