## Total Capital Investment
Shaded cells indicate user inputs.
Total Capital Investment - DSI (Dry Sorbent Injection) | [7 empty] | Date: | 2022-12-28
Project: |  | UAF - BACT Analysis | [5 empty] | Prepared By: | M. Jahn
Vendor: |  | Tri-Mer | [5 empty] | Updated By: | C. Kimball
[8 empty] | Rev: | B
Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs
| (a) | Basic equipment
|  | DSI System | 1 | EA | 978475
|  | ID Fan | 1 | EA | 431588.04
|  | Total DSI System | [5 empty] | TOTAL = | 1410063.04
| (b) | Instrumentation
|  | Total Instrumentation | 1 | EA | 142000
[8 empty] | TOTAL = | 142000
| (c) | Freight
|  | ID Fan Freight | 1 | EA | 85120
[8 empty] | TOTAL = | 85120
| (d) | Extended Outage Costs
|  | Additional days beyond a typical 3 week outage | 35 | MH | 48028
[8 empty] | TOTAL = | 1680980
| (e) | Vendor representatives fees
|  | Onsite Vendor Representatives fees (enter no. of days and daily rate) | 5 | Days | 2000 |  | 10000
[8 empty] | TOTAL = | 10000
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope. |  |  |  |  | PEMC = | 3328163.04
(2) | Direct Installation Costs
| (a) | Concrete | 1 | LOT | 196000 | 196000 |  |  | 196000
| (b) | Site Vibro Compaction (DSI Unloading Building/Storage Silo) | 1 | LOT | 62000 | 62000 |  |  | 62000
| (c) | Structural steel | 1 | LOT | 42000 | 42000 |  |  | 42000
| (d) | Electrical | 1 | LOT | 771000 | 771000 |  |  | 771000
| (e) | Abovegrade piping | 1 | LOT | 367000 | 367000 |  |  | 367000
Direct Installation Costs (DIC) - Guess at new building, foundation, piping, electrical, etc. | [7 empty] | DIC = | 1438000
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 4766163.04
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 10% | % TDC |  |  | 476616.304
(4) | Performance tests |  | 1 | EA | 75000 |  | 75000
Total Indirect Costs (TIC) | [7 empty] | TIC = | 551616.304
MANAGEMENT AND CONTINGENCY COSTS
(5) | Contingency |  | 10% | % TDC |  |  | 476616.304
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 476616.304
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 5794395.648
|  | Line Number/Description | Title |  | Comment
|  | Line Number 1a | Total DSI System |  | DSI price provided by OEM Vendor. Cost includes equipment supply and installation costs. Installation costs of vendor supplied equipment was assumed to be 25% of equipment cost.
|  | Line Number 1a | ID Fan |  | Pricing provided by Clarage for new ID Fan for CDS system. Fan pricing was scaled from 1250 HP to 950 HP. Fan shipping is provided in line number 1c.
|  | Line Number 1b | Total Instrumentation |  | Total costs for new communication links and I/O integration into existing DCS room.
|  | Line Number 1c | ID Fan Shipping Costs |  | Costs to ship ID fan to site. CDS pricing was used and scaled from 1250 HP to 950 HP.
|  | Line Number 1d | Extended Outage Costs |  | UAF typically schedules for a 3 week outage on Boiler #5. A DSI outage will take 8 weeks and the University will incur 5 additional weeks of outage costs that inlcude purchasing electric power and running additional boilers for steam generation. Costs per day were provided by UAF personnel. The daily outage cost calculations are presented in the last section of Appendix H beginning on page H-74.
|  | Line Number 1e | Vendor Representative Costs |  | Costs incurred for OEM to send a Field Technician to the field to confirm installation and provide technical guidance if needed. Cost per day includes hourly burdened rate for employee daily allowances and travel expenses.
|  | Line Number 2a thru 2e | Direct Install Costs |  | Costs broken down into individual disciplines for balance of plant equipment, materials and labor for the DSI System. Cost estimate basis for each discipline are provided as attachments.
|  | Line Number 3 | Engineering Services |  | Costs for Preliminary Engineering costs to assist the University in soliciting bidders with specifications, preliminary drawings and procurement support for the AQCS system. Additional services include home office support for shop drawing review and occasional site support during construction for potential issues. Engineering is a percentage of the Total Direct Costs of the Project.
|  | Line Number 4 | Performance Test |  | Costs for a 3rd party performance testing company to validate emissions and performance guarantees by DSI vendor during operation
|  | Line Number 5 | Construction Contingency |  | Construction Contingency is an allottment for additonal or unexpected costs during the project. RS Means defines contingency allowances and ranges between 3-20% depending on what design stage the project is in. A 10% contingency is a project that is in Design Development, wheras a Conceptual Design phase allows for a 20% contingency. A 10% contingency for this cost estimate is considered low as the project is still in a Development phase.

## Cost Effectiveness
Shaded cells indicate user inputs
Total Annualized Costs - DSI (Dry Sorbent Injection) | [7 empty] | Date: | 2022-12-28
Project: |  | UAF - BACT Analysis | [5 empty] | Prepared By: | M. Jahn
Vendor: |  | Tri-Mer | [5 empty] | Checked By: | C. Kimball
[8 empty] | Rev: | B
Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 8864 | MH | 49.09 | Excluded | 435133.76 |  | 435133.76
(2) | Supervisory Labor |  |  | MH |  | Excluded | Excluded |  | Excluded
(3) | Maintenance Labor |  | 520 | MH | 49.09 | Excluded | 25526.8 |  | 25526.8
(4) | Maintenance Materials |  | 1 | LOT | 25526.8 | 25526.8 | Excluded |  | 25526.8
(5) | Utilities
| (a) | Hydrated Lime: | 2465.94 | TON | 1377 | 3395599.38 | Excluded |  | 3395599.38
| (b) | Electricity: | 2380179.6 | kWh | 0.205 | 487936.818 | Excluded |  | 487936.818
| (c) | Water: | 8935.2 | (k)Gallons | 11.3 | 100967.76 | Excluded |  | 100967.76
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 4470691.318
INDIRECT ANNUAL COSTS
(6) | Overhead |  | 1% | % |  |  | 57943.9565 |  | 57943.9565
(7a) | Administrative Charges, Insurance |  | 3% | % total capital |  |  | 173831.8694 |  | 173831.8694
(7b) | Capital Recovery Factor [see inputs below] |  | 0.084671
(8) | Capital Recovery | [6 empty] | CRF * TCI = | 490618.64
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 722394.466
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 5193085.784
Data Inputs for Capital Recovery Factor:
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7.5 | %
|  | Project Life (EPA OAQPS Control Cost Manual) | 30 | years
Line Number/Description |  |  | Title |  | Comment
Line Number 1 and 3 |  |  | Operating/Maintenance Labor |  | Provided by UAF. Rate is burdoned rate for level of personnel operating and performing maintenance on this type of equipment. Additional FT operations person is assumed per shift. Four total shifts per week. Quarter FT maintenance persons is assumed for the new DSI system.
Line Number 4 |  |  | Maintenance Material |  | Allotment for maintenance materials. Item is equal to the maintenance labor allotment in line 3.
Line Number 5a |  |  | Hydrated Lime |  | Hydrated Lime consumption rates provided by DSI vendor. Hydrated Lime costs provided by L'hoist.
Line Number 5b |  |  | Electricity |  | Pricing provided by UAF for published utility rates on campus. Electical consumption rate provided by DSI vendor. Additional consumption by larger ID Fan was also included.
Line Number 5c |  |  | Water |  | Pricing provided by UAF for published utility rates on campus. Water consumption rate provided by DSI vendor.
Line Number 6 |  |  | Overhead |  | Calculated as percent of Total Capital Investment
Line Number 7a |  |  | Admin Charges, etc |  | Calculated as percent of Total Capital Investment
Line Number 7b |  |  | Capital Recovery Factor |  | EPA calculated factor using Interest Rate and Project Life Span
Line Number 8 |  |  | Capital Recovery |  | Capital Recovery Factor times Total Capital Investment.
Annual Interest Rate (EPA OAQPS Control Cost Manual) |  |  | Annual Interest Rate |  | Latest federal prime rate. https://www.federalreserve.gov/releases/h15/
Project Life (EPA OAQPS Control Cost Manual) |  |  | Project Life |  | Project Life expectancy in years.